## Summary
[16 empty] | Correction Net Output | [7 empty] | Correction Heat Input
Run | Start | End | Gross Output (MW) | Net Output (MW) | Diesel Flow (L/h) | Density (kg/m3) | High Heating Value (kCal/kg) | Heat Input (kCal) | Specific Heat Consumption (kCal/kWh) | CTIM (°F) | GT Air Intake DP (inH2O) | Power Factor | Reference GT Exhaust DP (inH2O) | GT Exhaust DP (inH2O) | Delta Exhaust GT DP (inH2O) | CF Power Factor | CF Inlet Temperature | CF Relative Humidity | CF DP @ Air Intake | CF DP @ GT Exhaust | Corrected Gross Power (MW) | Corrected Net Power (MW) | Corrected Net Power (kW) | CF Power Factor | CF Inlet Temperature | CF Relative Humidity | CF DP @ Air Intake | CF DP @ GT Exhaust | Corrected Heat Input (kCal) | Corrected Specific Heat Consumption (kCal/kWh) | Corrected Specific Heat Consumption (kJ/kWh)
136MW (peak firing) | 9/04/2025 5:30PM | 9/04/2025 6:00PM | 136.1374 | 134.9278 | 42240 | 837.5 | 10925 | 386482800 | 2864.3683 | 70.3344 | 3.4122 | 0.9993 | 3.25 | 1.05 | -2.2 | 0.99931 | 0.96 | 1.0002 | 0.9935 | 1.003 | 142.3833 | 141.1182 | 141118.1515 | 1.0007 | 0.97 | 0.99973 | 0.99525 | 1.0012 | 399669895.3151 | 2832.165 | 11849.7785
126MW (base) | 9/04/2025 6:45PM | 9/04/2025 7:15PM | 127.4838 | 126.3448 | 39390 | 837.5 | 10927 | 360472168.875 | 2853.0835 | 65.4389 | 3.4168 | 0.9988 | 3.32 | 0.332 | -2.988 | 0.99936 | 0.98 | 1 | 0.9935 | 1.005 | 130.366 | 129.2012 | 129201.216 | 1.0006 | 0.985 | 1 | 0.99525 | 1.0015 | 366922640.0531 | 2839.9318 | 11882.2746
107MW | 9/04/2025 8:00PM | 9/04/2025 8:30PM | 106.587 | 105.6128 | 34050 | 838 | 10925 | 311732857.5 | 2951.6572 | 61.0898 | 3.4485 | 0.9986 | 3.4 | 0.6275 | -2.7725 | 0.98683 | 0.99 | 0.99978 | 0.9935 | 1.0045 | 109.3464 | 108.347 | 108346.9945 | 1.0133 | 0.9925 | 1.0003 | 0.99525 | 1.0015 | 310882497.438 | 2869.3228 | 12005.2464
88MW | 9/04/2025 9:15PM | 9/04/2025 9:45PM | 87.5829 | 86.7193 | 28900 | 837.5 | 10927 | 264474376.25 | 3049.7739 | 61.438 | 3.4885 | 0.9995 | 3.4 | 0.1575 | -3.2425 | 0.99952 | 0.99 | 0.99967 | 0.9935 | 1.0055 | 88.6311 | 87.7572 | 87757.1827 | 1.0005 | 0.9925 | 1.0005 | 0.99525 | 1.002 | 266948616.2574 | 3041.9005 | 12727.3116
68MW | 9/04/2025 10:30PM | 9/04/2025 11:00PM | 67.7328 | 66.9527 | 23265 | 838 | 10925 | 212994564.75 | 3181.2671 | 58.5809 | 3.3887 | 0.99699 | 3.42 | 0.33 | -3.09 | 0.9996 | 1 | 0.99973 | 0.9935 | 1.005 | 67.8822 | 67.1005 | 67100.4568 | 1.0004 | 1 | 1.0003 | 0.99525 | 1.002 | 213436653.6094 | 3180.8525 | 13308.6867
49MW | 9/04/2025 11:45PM | 10/04/2025 00:15AM | 48.8001 | 48.0947 | 18825 | 837.5 | 10927 | 172274399.0625 | 3581.9822 | 58.9297 | 2.5761 | 0.9931 | 3.42 | 0.4125 | -3.0075 | 0.99967 | 0.995 | 0.9998 | 0.9975 | 1.005 | 48.9496 | 48.242 | 48242.0203 | 1.0003 | 0.995 | 1.0003 | 0.99825 | 1.002 | 172995348.9447 | 3585.9889 | 15003.7775
30MW | 10/04/2025 01:00AM | 10/04/2025 01:30AM | 29.8675 | 29.3367 | 14760 | 838 | 10925 | 135130014 | 4606.17 | 58.7345 | 2.2346 | 0.993 | 3.42 | 0.6425 | -2.7775 | 0.99957 | 1 | 0.9997 | 0.9975 | 1.0045 | 29.83 | 29.2999 | 29299.898 | 1.0004 | 0.995 | 1.0003 | 0.99825 | 1.0015 | 135744265.9044 | 4632.9262 | 19384.1633

## MkVI
|  | 0.00069444 |  | G1\CSGV | E1\G1\AUTO_FB | G1\AFPAP | G1\AFQ | G1\BB_MAX | G1\CMHUM | G1\CPD | G1\CPD1A | G1\CPD1B | G1\CPD1C | G1\CPR | G1\CPRLIM | G1\CTD | G1\CTDA1 | G1\CTDA2 | G1\CTIFR | G1\CTIM | G1\DF | G1\DVX | G1\DWATT | G1\EX2K_TRM_V | G1\FQLM1 | G1\FSR | G1\L60GVMAX | G1\SFL1 | G1\STATUS_FLD | G1\TFT_P | G1\TFT_PCNT | G1\TFT_PTIM | G1\TMVAR_CNT | G1\TMW_CNT | G1\TNH | G1\TNHA | G1\TNHA_RPM | G1\TOTLIQ | G1\TOTLIQ1 | G1\TTK_C | G1\TTRXB | G1\TTRXGV | G1\TTRXGVB | G1\TTRXP | G1\TTRXS | G1\TTWS2FO1 | G1\TTWS2FO2 | G1\TTXD1_22 | G1\TTXM | G1\TTXSP1 | G1\TTXSPL | G1\WQ | G1\WQK_M | G1\WQR2 | G1\aap | G1\aap4a | G1\aap4b | G1\aat1 | G1\afpcs | G1\afpcs3 | G1\ca43psel | G1\csrgv | G1\ctif1a | G1\ctif2a | G1\dv | G1\dvar | G1\dwatt1 | G1\fal | G1\fql1 | G1\ftd | G1\itdp | G1\l77fl | G1\tmgv | G1\ttws1ao1 | G1\ttws1ao2 | G1\ttws1fi1 | G1\ttws1fi2 | G1\ttws2ao1 | G1\ttws2ao2 | G1\ttws3ao1 | G1\ttws3ao2 | G1\ttws3fo1 | G1\ttws3fo2 | G1\ttxd_1 | G1\ttxd_10 | G1\ttxd_11 | G1\ttxd_12 | G1\ttxd_13 | G1\ttxd_14 | G1\ttxd_15 | G1\ttxd_16 | G1\ttxd_17 | G1\ttxd_18 | G1\ttxd_19 | G1\ttxd_2 | G1\ttxd_20 | G1\ttxd_21 | G1\ttxd_23 | G1\ttxd_24 | G1\ttxd_3 | G1\ttxd_4 | G1\ttxd_5 | G1\ttxd_6 | G1\ttxd_7 | G1\ttxd_8 | G1\ttxd_9
DATA | DIA | HORA | MINUTO | IGV angle in deg | Exciter is in Auto Regulator | Flow Inlet Barometric Pressure Transducer 96AP | Compressor Inlet Air Mass Flow | Maximum vibration | Specific Humidity | Compressor Discharge Press Max Select |  |  |  | COMPRESSOR PRESSURE RATIO | COMPRESSOR PRESSURE RATIO OPERATING LIMIT | Compressor Discharge Temperature |  |  |  | Compressor Inlet Temperature | Generator Frequency | Generator Volts - VTUR | Generator Watts Max Selected | EX2K Generator Terminal Volts | Liquid Fuel Mass Flow | Fuel Stroke Reference | IGV at Maximum Position | Bus PT Frequency | Status Field | Peak fired time | Peak fired time - Current Count | Peak fired time - Current Time | Total Per Unit MVAR | Total Per Unit Mwatt | Turbine HP shaft speed in % | Turbine High Pressure Acceleration | Turbine accelleration, RPM/sec |  |  | Exhaust Temp Control Curve CPR Ref Corner Array | Speed Biased Temperature Control Reference | IGV Temp Control Reference | Comp Op Lim Prot Biased IGV Exhaust Temp Command | Temp Control Primary Temp Reference | Temp Control Backup Temp Reference |  |  |  | Exhaust Temp Median Corrected By Average |  |  | Water Injection Flow from Feedback | Steam Injection Curve Max Flow Limit Array | Steam Injection Wet Low NOx Injection Reference | Atomizing Air Compressor Diff Pressure Sensor | ATOMIZING AIR MANIFOLD PRESSURE TRANSMITTER#A | ATOMIZING AIR MANIFOLD PRESSURE TRANSMITTER#B | Atomizing Air Temperature Sensor#1 | Compressor Inlet Pressure Transducers 96CS | Flow Inlet Duct Press Diff Transm 96CS-3 | Cable Remote Peak Control Select | IGV REFERENCE | Compressor Inlet Thermocouple 1A | Compressor Inlet Thermocouple 2A | Generator Volts - VTUR | Generator VARS | Generator Watts 96GG-1 Transducer | Liquid Fuel Bypass Valve Servo Current | Flow Divider Mag Pickup - Speed | Distillate Fuel Temperature | Flow Inlet Dewpoint Sensor Xmitter | Distillate Fuel Purge Flow Count | Starting Means Torque Conv Guide Vane Position | Turbine Temperature Wheelspace 1ST Stg Aft Outer | Turbine Temperature Wheelspace 1ST Stg Aft Outer | Turbine Temperature Wheelspace 1ST Stg Fwd Inner | Turbine Temperature Wheelspace 1ST Stg Fwd inner | Turbine Temperature Wheelspace 2nd Stg Aft Outer | Turbine Temperature Wheelspace 2nd Stg Aft Outer | Turbine Temperature Wheelspace 2nd Stg Fwd Outer | Turbine Temperature Wheelspace 3rd Stg Aft Outer | Turbine Temperature Wheelspace 3rd Stg Fwd Outer | Turbine Temperature Wheelspace 3rd Stg Fwd Outer | Exhaust Thermocouple 1 | Exhaust Thermocouple 10 | Exhaust Thermocouple 11 | Exhaust Thermocouple 12 | Exhaust Thermocouple 13 | Exhaust Thermocouple 14 | Exhaust Thermocouple 15 | Exhaust Thermocouple 16 | Exhaust Thermocouple 17 | Exhaust Thermocouple 18 | Exhaust Thermocouple 19 | Exhaust Thermocouple 2 | Exhaust Thermocouple 20 | Exhaust Thermocouple 21 | Exhaust Thermocouple 23 | Exhaust Thermocouple 24 | Exhaust Thermocouple 3 | Exhaust Thermocouple 4 | Exhaust Thermocouple 5 | Exhaust Thermocouple 6 | Exhaust Thermocouple 7 | Exhaust Thermocouple 8 | Exhaust Thermocouple 9
2025-04-09 18:28 | 9 | 18 | 28 | 6.2817e-272 | 1 | 29.3968 | 634.8494 | 0.24427 | 0.0074818 | 163.6781 | 163.6707 | 163.6707 | 163.6707 | 12.6191 | 13.6119 | 673.6568 | 673.648 | 673.648 | 673.648 | 67.1455 | 50.1267 | 15.7381 | 127.2056 | 15.6 | 21.4753 | 76.9446 | 1 | 50.1273 | 15 | 22.1 | 221 | 154840 | 237463.9189 | 3542856.4324 | 100.2533 | -0.0087511 | -0.26253 | -0.2205 | -0.2205 | 7.9917 | 1016.5895 | 1014.0692 | 1014.0649 | 1016.5895 | 1040.0911 | 1040.1144 | 1040.1144 | 1040.1144 | 1016.5989 | 1016.6006 | 1016.6006 | 16.624 | 0 | 16.6163 | 83.7294 | 240.2162 | 240.3755 | 233.7599 | 2.0803 | 3.4027 | 0 | 86 | 67.0305 | 67.1057 | 104.9206 | 8.2116 | 127.2056 | -1.2508 | 77.1567 | 62.5922 | 48.8802 | 0 | 66.8609 | 823.5971 | 819.7446 | 743.5318 | 743.8241 | 738.1685 | 737.4213 | 568.8639 | 560.6317 | 774.2828 | 797.8929 | 1016.0578 | 1025.2738 | 1037.2916 | 1051.6643 | 1042.5346 | 1018.1695 | 1041.62 | 1016.2314 | 1047.1378 | 1016.0535 | 1025.6397 | 1032.3692 | 1004.1347 | 1025.3403 | 1029.6024 | 1031.9641 | 1030.9854 | 1032.8932 | 1029.8181 | 999.7709 | 1059.8603 | 1011.3143 | 1026.8905
2025-04-09 18:29 | 9 | 18 | 29 | 6.2817e-272 | 1 | 29.4 | 634.0837 | 0.24604 | 0.0074879 | 163.6706 | 163.6706 | 163.6706 | 163.6706 | 12.6173 | 13.6061 | 673.0422 | 673.0422 | 673.0422 | 673.0422 | 67.2552 | 50.118 | 15.7394 | 127.1311 | 15.5998 | 21.4885 | 76.9807 | 1 | 50.1182 | 15 | 22.1 | 221 | 154840 | 237465.2979 | 3542875.3191 | 100.2361 | 0.0015941 | 0.047823 | 0.047823 | 0.047823 | 7.9917 | 1016.6234 | 1014.1032 | 1014.1038 | 1016.6234 | 1040.1872 | 1040.1872 | 1040.1872 | 1040.1872 | 1016.5677 | 1016.5677 | 1016.5677 | 16.6219 | 0 | 16.6249 | 83.6756 | 240.1667 | 240.3251 | 233.6939 | 2.1075 | 3.4049 | 0 | 86 | 66.3638 | 67.2552 | 104.9292 | 8.3315 | 127.1311 | -1.2912 | 77.2042 | 62.5895 | 48.9087 | 0 | 66.8609 | 823.4068 | 819.6495 | 743.3148 | 743.4626 | 737.9394 | 737.1164 | 568.3839 | 560.5106 | 774.0937 | 798.9731 | 1015.9802 | 1025.2381 | 1037.757 | 1052.7226 | 1042.7004 | 1018.7396 | 1040.8168 | 1015.4523 | 1045.6117 | 1015.7474 | 1026.3636 | 1032.8004 | 1005.0825 | 1025.8126 | 1029.3536 | 1031.7587 | 1031.4087 | 1033.2181 | 1029.253 | 999.9179 | 1059.9334 | 1010.693 | 1026.3251
2025-04-09 18:30 | 9 | 18 | 30 | 6.2817e-272 | 1 | 29.3947 | 634.1588 | 0.24375 | 0.0074752 | 163.7629 | 163.7629 | 163.7629 | 163.7629 | 12.626 | 13.5991 | 671.7488 | 671.7488 | 671.7488 | 671.7488 | 66.9133 | 50.0861 | 15.7383 | 127.3896 | 15.6006 | 21.4996 | 77.1267 | 1 | 50.0865 | 15 | 22.1 | 221 | 154840 | 237466.5745 | 3542896.4894 | 100.172 | -0.00067358 | -0.020207 | -0.020207 | -0.020207 | 7.9917 | 1016.4653 | 1013.9417 | 1013.9404 | 1016.4653 | 1039.8509 | 1039.8509 | 1039.8509 | 1039.8509 | 1016.4428 | 1016.4428 | 1016.4428 | 16.6421 | 0 | 16.6408 | 83.6398 | 240.2671 | 240.4246 | 233.6318 | 2.0581 | 3.4057 | 0 | 86 | 65.4235 | 66.9133 | 104.9217 | 8.5598 | 127.3896 | -1.3327 | 77.244 | 62.5944 | 48.8507 | 0 | 66.861 | 823.0673 | 819.3309 | 743.0106 | 743.0346 | 737.6348 | 736.7099 | 567.8823 | 560.2658 | 773.8067 | 799.6873 | 1015.7819 | 1025.2151 | 1038.4266 | 1053.8617 | 1042.6143 | 1019.6555 | 1040.2189 | 1014.497 | 1044.134 | 1014.9981 | 1026.0223 | 1032.9413 | 1005.963 | 1026.5291 | 1030.0996 | 1030.936 | 1030.8947 | 1032.6438 | 1028.7009 | 999.7681 | 1060.0545 | 1010.6785 | 1025.8321
2025-04-09 18:31 | 9 | 18 | 31 | 6.2817e-272 | 1 | 29.3933 | 636.6045 | 0.24389 | 0.007455 | 164.0046 | 164.0046 | 164.0046 | 164.0046 | 12.6437 | 13.6082 | 670.5877 | 670.5877 | 670.5877 | 670.5877 | 66.4041 | 50.0827 | 15.7397 | 127.7307 | 15.6007 | 21.5434 | 77.3079 | 1 | 50.0827 | 15 | 22.1 | 221 | 154840 | 237468.0213 | 3542917.6809 | 100.1654 | 0.0015658 | 0.046973 | 0.046973 | 0.046973 | 7.9917 | 1016.1438 | 1013.6102 | 1013.6106 | 1016.1438 | 1039.4055 | 1039.4055 | 1039.4055 | 1039.4055 | 1016.1143 | 1016.1143 | 1016.1143 | 16.6835 | 0 | 16.68 | 83.7713 | 240.5941 | 240.7687 | 233.6781 | 2.0129 | 3.3963 | 0 | 86 | 64.7614 | 66.4041 | 104.9313 | 8.2267 | 127.7307 | -1.3434 | 77.4014 | 62.5928 | 48.7694 | 0 | 66.8609 | 822.6424 | 818.857 | 742.7025 | 742.563 | 737.3062 | 736.2973 | 567.2699 | 559.7383 | 773.4799 | 799.1818 | 1013.9957 | 1023.5234 | 1039.2883 | 1054.2347 | 1041.3821 | 1019.2004 | 1039.14 | 1013.5926 | 1039.3249 | 1014.774 | 1024.7889 | 1033.7704 | 1009.9414 | 1028.1272 | 1031.2638 | 1029.8109 | 1031.6928 | 1033.1626 | 1028.0034 | 999.938 | 1060.346 | 1009.0896 | 1025.4149
2025-04-09 18:32 | 9 | 18 | 32 | 6.2817e-272 | 1 | 29.3942 | 638.7803 | 0.24083 | 0.0074357 | 163.7622 | 163.7622 | 163.7622 | 163.7622 | 12.6261 | 13.5898 | 669.3339 | 669.3339 | 669.3339 | 669.3339 | 66.2441 | 50.0325 | 15.7406 | 127.5932 | 15.5976 | 21.5473 | 77.2791 | 1 | 50.0337 | 15 | 22.1 | 221 | 154840 | 237469.413 | 3542938.6304 | 100.0649 | -0.024624 | -0.73872 | -0.73872 | -0.73872 | 7.9917 | 1016.46 | 1013.9348 | 1013.938 | 1016.46 | 1039.5852 | 1039.5852 | 1039.5852 | 1039.5852 | 1016.515 | 1016.515 | 1016.515 | 16.6481 | 0 | 16.6518 | 83.5584 | 240.132 | 240.3226 | 233.6167 | 2.0191 | 3.4019 | 0 | 86 | 64.3449 | 66.2441 | 104.9371 | 8.2871 | 127.5932 | -1.306 | 77.4152 | 62.5769 | 48.6928 | 0 | 66.8606 | 822.2408 | 818.3335 | 742.292 | 741.9986 | 736.8624 | 735.7961 | 566.7274 | 559.5733 | 773.1776 | 798.2022 | 1014.7722 | 1024.5515 | 1039.9059 | 1054.8567 | 1042.2796 | 1020.4354 | 1040.0515 | 1014.6461 | 1039.7157 | 1013.615 | 1025.4976 | 1034.0859 | 1008.5241 | 1028.1074 | 1031.7043 | 1030.1528 | 1031.9004 | 1033.1072 | 1029.0974 | 1000.2995 | 1061.6357 | 1009.5524 | 1025.77
2025-04-09 18:33 | 9 | 18 | 33 | 6.2817e-272 | 1 | 29.3961 | 641.1125 | 0.24133 | 0.007414 | 163.7858 | 163.7858 | 163.7858 | 163.7858 | 12.6271 | 13.5932 | 669.1527 | 669.1527 | 669.1527 | 669.1527 | 65.9833 | 50.0283 | 15.7421 | 127.6128 | 15.5973 | 21.5395 | 77.3326 | 1 | 50.0275 | 15 | 22.1 | 221 | 154840 | 237470.6809 | 3542959.5957 | 100.0565 | 0.018274 | 0.54822 | 0.54822 | 0.54822 | 7.9917 | 1016.4466 | 1013.9206 | 1013.9191 | 1016.4466 | 1039.5598 | 1039.5598 | 1039.5598 | 1039.5598 | 1016.394 | 1016.394 | 1016.394 | 16.6432 | 0 | 16.6494 | 83.4505 | 240.0922 | 240.2969 | 233.451 | 2.0569 | 3.4126 | 0 | 86 | 64.1471 | 65.9833 | 104.9476 | 8.56 | 127.6128 | -1.2642 | 77.3873 | 62.5887 | 48.6062 | 0 | 66.8608 | 821.8933 | 817.9548 | 741.9449 | 741.4959 | 736.4882 | 735.2906 | 566.2577 | 559.4761 | 772.8875 | 797.9456 | 1015.1166 | 1024.6511 | 1038.8423 | 1054.1819 | 1042.4172 | 1019.6015 | 1039.8898 | 1014.3791 | 1039.5853 | 1014.563 | 1025.3694 | 1033.414 | 1007.9267 | 1028.4213 | 1030.4349 | 1030.0219 | 1032.1049 | 1033.3489 | 1028.4132 | 1000.9395 | 1060.676 | 1009.6734 | 1026.7572
2025-04-09 18:34 | 9 | 18 | 34 | 6.2817e-272 | 1 | 29.3967 | 642.7821 | 0.2454 | 0.0074193 | 164.0356 | 164.0356 | 164.0356 | 164.0356 | 12.6445 | 13.6128 | 668.8618 | 668.8618 | 668.8618 | 668.8618 | 65.5596 | 50.0524 | 15.7383 | 127.8807 | 15.601 | 21.5732 | 77.3953 | 1 | 50.0534 | 15 | 22.1 | 221 | 154840 | 237472.2766 | 3542980.766 | 100.1047 | -0.00092284 | -0.027685 | -0.027685 | -0.027685 | 7.9917 | 1016.1291 | 1013.5947 | 1013.5972 | 1016.1291 | 1039.2115 | 1039.2115 | 1039.2115 | 1039.2115 | 1016.1204 | 1016.1204 | 1016.1204 | 16.6695 | 0 | 16.6628 | 83.732 | 240.5682 | 240.7605 | 233.3424 | 2.0849 | 3.4164 | 0 | 86 | 63.8774 | 65.5596 | 104.9222 | 8.6107 | 127.8807 | -1.2642 | 77.5084 | 62.5681 | 48.6284 | 0 | 66.8605 | 821.5386 | 817.5654 | 741.6184 | 741.1277 | 736.0929 | 734.8869 | 565.7916 | 559.2492 | 772.6277 | 797.8841 | 1014.9849 | 1024.8423 | 1037.8785 | 1052.7636 | 1041.0494 | 1019.4498 | 1040.1723 | 1014.6996 | 1044.8798 | 1014.3432 | 1025.9191 | 1032.5989 | 1004.766 | 1026.3457 | 1029.3313 | 1030.8023 | 1031.7315 | 1033.6606 | 1027.5217 | 1000.626 | 1060.2 | 1010.3711 | 1026.2609
2025-04-09 18:35 | 9 | 18 | 35 | 6.2817e-272 | 1 | 29.3953 | 644.0147 | 0.24355 | 0.0074634 | 164.2453 | 164.2453 | 164.2453 | 164.2453 | 12.6599 | 13.6254 | 668.4254 | 668.4254 | 668.4254 | 668.4254 | 65.0319 | 50.0563 | 15.7381 | 128.1447 | 15.6018 | 21.5925 | 77.5071 | 1 | 50.0565 | 15 | 22.1 | 221 | 154840 | 237473.5957 | 3543001.9574 | 100.1124 | 0.0021136 | 0.063408 | 0.063408 | 0.063408 | 7.9917 | 1015.8513 | 1013.3089 | 1013.3083 | 1015.8513 | 1038.8674 | 1038.8674 | 1038.8674 | 1038.8674 | 1015.8706 | 1015.8706 | 1015.8706 | 16.6592 | 0 | 16.6584 | 83.8429 | 240.9332 | 241.1208 | 233.3342 | 2.0676 | 3.4247 | 0 | 86 | 63.2176 | 65.0319 | 104.9204 | 8.5639 | 128.1447 | -1.2483 | 77.5778 | 62.5878 | 48.806 | 0 | 66.8608 | 821.1636 | 817.2424 | 741.2041 | 740.8136 | 735.6123 | 734.4776 | 565.3053 | 558.8394 | 772.3265 | 796.1052 | 1014.2279 | 1024.3762 | 1039.0617 | 1053.416 | 1040.6883 | 1019.7957 | 1040.3162 | 1014.7115 | 1042.0785 | 1012.716 | 1025.0138 | 1033.1483 | 1005.6747 | 1027.0266 | 1029.8304 | 1029.8319 | 1031.7704 | 1033.5096 | 1026.9009 | 999.6693 | 1060.2753 | 1009.514 | 1025.0889
2025-04-09 18:36 | 9 | 18 | 36 | 6.2817e-272 | 1 | 29.3954 | 644.7505 | 0.24215 | 0.0074945 | 164.2954 | 164.2954 | 164.2954 | 164.2954 | 12.6634 | 13.6306 | 668.3363 | 668.3363 | 668.3363 | 668.3363 | 64.6767 | 50.0521 | 15.7393 | 128.2384 | 15.6 | 21.5927 | 77.5101 | 1 | 50.0532 | 15 | 22.1 | 221 | 154840 | 237475.1064 | 3543023.1489 | 100.1041 | -0.017261 | -0.51784 | -0.51784 | -0.51784 | 7.9917 | 1015.7889 | 1013.2443 | 1013.2436 | 1015.7889 | 1038.7453 | 1038.7453 | 1038.7453 | 1038.7453 | 1015.7523 | 1015.7523 | 1015.7523 | 16.6098 | 0 | 16.6155 | 83.8587 | 240.9797 | 241.1697 | 233.273 | 2.0542 | 3.4191 | 0 | 86 | 62.9256 | 64.6767 | 104.9288 | 8.6742 | 128.2384 | -1.3012 | 77.5784 | 62.579 | 48.9311 | 0 | 66.8609 | 820.7728 | 816.9508 | 740.7793 | 740.402 | 735.169 | 734.1021 | 564.8129 | 558.6279 | 772.0661 | 797.0269 | 1014.4638 | 1025.3881 | 1037.1574 | 1052.054 | 1040.1579 | 1019.4551 | 1039.9477 | 1015.0345 | 1045.5598 | 1014.4719 | 1026.0115 | 1031.623 | 1003.6729 | 1026.1738 | 1028.4589 | 1029.676 | 1031.0364 | 1032.6323 | 1026.5417 | 999.8174 | 1058.7268 | 1010.184 | 1026.2313
2025-04-09 18:37 | 9 | 18 | 37 | 6.2817e-272 | 1 | 29.3981 | 644.0061 | 0.23298 | 0.0075032 | 163.4492 | 163.4492 | 163.4492 | 163.4492 | 12.6024 | 13.5651 | 666.3148 | 666.3148 | 666.3148 | 666.3148 | 64.4228 | 49.8896 | 15.7411 | 127.6416 | 15.5999 | 21.5123 | 77.4613 | 1 | 49.8898 | 15 | 22.1 | 221 | 154840 | 237476.5532 | 3543044.3404 | 99.7792 | 0.00097298 | 0.02919 | 0.02919 | 0.02919 | 7.9917 | 1016.8885 | 1014.3774 | 1014.3755 | 1016.8885 | 1039.5228 | 1039.5228 | 1039.5228 | 1039.5228 | 1016.9191 | 1016.9191 | 1016.9191 | 16.5016 | 0 | 16.491 | 82.9908 | 239.3397 | 239.558 | 232.9436 | 2.0536 | 3.3922 | 0 | 86 | 62.8171 | 64.4228 | 104.9407 | 9.4254 | 127.6416 | -1.3788 | 77.2895 | 62.5771 | 48.9675 | 0 | 66.862 | 820.1071 | 816.3492 | 739.9196 | 739.591 | 734.4744 | 733.5163 | 564.2529 | 558.2983 | 771.6708 | 795.2806 | 1015.8555 | 1026.7596 | 1037.937 | 1052.7164 | 1041.8228 | 1021.1887 | 1042.0255 | 1017.4653 | 1046.66 | 1014.4262 | 1027.3098 | 1032.1723 | 1003.4622 | 1027.1049 | 1029.3381 | 1031.1532 | 1032.4198 | 1034.2828 | 1027.5806 | 1002.1111 | 1059.8026 | 1010.5457 | 1027.1521
2025-04-09 18:38 | 9 | 18 | 38 | 6.2817e-272 | 1 | 29.4014 | 644.4151 | 0.23677 | 0.0074906 | 163.6207 | 163.6207 | 163.6207 | 163.6207 | 12.6132 | 13.5843 | 666.9538 | 666.9538 | 666.9538 | 666.9538 | 64.4642 | 49.9365 | 15.7413 | 127.6823 | 15.5997 | 21.4772 | 77.4797 | 1 | 49.9368 | 15 | 22.1 | 221 | 154840 | 237478.1915 | 3543065.5319 | 99.8731 | 0.001824 | 0.05472 | 0.05472 | 0.05472 | 7.9917 | 1016.6949 | 1014.1774 | 1014.1766 | 1016.6949 | 1039.4691 | 1039.4691 | 1039.4691 | 1039.4691 | 1016.6536 | 1016.6536 | 1016.6536 | 16.535 | 0 | 16.5116 | 83.2532 | 239.7343 | 239.9344 | 232.5814 | 2.0812 | 3.4084 | 0 | 86 | 62.8582 | 64.4642 | 104.9418 | 9.3816 | 127.6823 | -1.3093 | 77.1635 | 62.5748 | 48.9192 | 0 | 66.8605 | 819.6647 | 815.9051 | 739.3369 | 739.0815 | 733.927 | 733.0806 | 563.96 | 558.1206 | 771.3518 | 794.8724 | 1014.8998 | 1025.776 | 1039.0683 | 1053.5249 | 1040.7923 | 1020.4374 | 1040.7045 | 1015.9349 | 1045.6177 | 1014.316 | 1027.2366 | 1032.2281 | 1005.3729 | 1026.9651 | 1029.5662 | 1031.0696 | 1032.6221 | 1034.5045 | 1027.8491 | 1001.3358 | 1059.9153 | 1010.1385 | 1026.8983
2025-04-09 18:39 | 9 | 18 | 39 | 6.2817e-272 | 1 | 29.402 | 644.8549 | 0.24549 | 0.0074824 | 163.8747 | 163.8747 | 163.8747 | 163.8747 | 12.631 | 13.6098 | 668.4976 | 668.4976 | 668.4976 | 668.4976 | 64.593 | 50.0017 | 15.7411 | 127.9066 | 15.5978 | 21.5849 | 77.4378 | 1 | 49.9997 | 15 | 22.1 | 221 | 154840 | 237479.6383 | 3543086.7234 | 100.0033 | 0.043846 | 1.3154 | 1.3154 | 1.3154 | 7.9917 | 1016.3738 | 1013.8453 | 1013.8451 | 1016.3738 | 1039.1768 | 1039.1768 | 1039.1768 | 1039.1768 | 1016.4349 | 1016.4349 | 1016.4349 | 16.5731 | 0 | 16.5746 | 83.5468 | 240.2449 | 240.449 | 232.4083 | 2.1038 | 3.3946 | 0 | 86 | 63.0371 | 64.593 | 104.9406 | 9.2321 | 127.9066 | -1.2934 | 77.5504 | 62.5939 | 48.8885 | 0 | 66.8603 | 819.5913 | 815.7851 | 739.05 | 739.0512 | 733.6148 | 732.9436 | 563.6634 | 557.9609 | 771.1134 | 794.7261 | 1015.4738 | 1025.6721 | 1036.9423 | 1051.9483 | 1040.7238 | 1020.0421 | 1041.9206 | 1016.5564 | 1050.5123 | 1014.4779 | 1026.997 | 1032.0643 | 1001.049 | 1024.8217 | 1028.3394 | 1031.5247 | 1032.1123 | 1033.8762 | 1027.3043 | 999.951 | 1059.1715 | 1010.8204 | 1027.0543
2025-04-09 18:40 | 9 | 18 | 40 | 6.2817e-272 | 1 | 29.4039 | 643.0127 | 0.23839 | 0.0074852 | 163.3513 | 163.3513 | 163.3513 | 163.3513 | 12.5931 | 13.582 | 668.8603 | 668.8603 | 668.8603 | 668.8603 | 64.7655 | 49.9441 | 15.7405 | 127.3283 | 15.6026 | 21.5148 | 77.2968 | 1 | 49.9455 | 15 | 22.1 | 221 | 154840 | 237481.3261 | 3543107.6739 | 99.8882 | -0.0088518 | -0.26555 | -0.26555 | -0.26555 | 7.9917 | 1017.0567 | 1014.5504 | 1014.5498 | 1017.0567 | 1039.9304 | 1039.9304 | 1039.9304 | 1039.9304 | 1017.0489 | 1017.0489 | 1017.0489 | 16.4808 | 0 | 16.4817 | 83.1824 | 239.3747 | 239.5728 | 232.2756 | 2.1251 | 3.3805 | 0 | 86 | 63.5215 | 64.7655 | 104.9365 | 9.4957 | 127.3283 | -1.29 | 77.2987 | 62.5685 | 48.9034 | 0 | 66.8613 | 819.5346 | 815.7127 | 738.7619 | 738.8993 | 733.3607 | 732.8627 | 563.3471 | 557.6449 | 770.9724 | 793.9819 | 1015.5026 | 1026.0883 | 1038.3711 | 1053.4452 | 1042.3687 | 1019.8746 | 1042.6263 | 1017.2404 | 1045.1154 | 1015.382 | 1027.2676 | 1031.9354 | 1005.1285 | 1027.4498 | 1030.1622 | 1031.5491 | 1032.7209 | 1034.1343 | 1028.2039 | 1002.0004 | 1059.8911 | 1009.9009 | 1027.8907
2025-04-09 18:41 | 9 | 18 | 41 | 6.2817e-272 | 1 | 29.4046 | 642.3769 | 0.24427 | 0.007496 | 163.5256 | 163.5256 | 163.5256 | 163.5256 | 12.6052 | 13.5881 | 669.4127 | 669.4127 | 669.4127 | 669.4127 | 64.8195 | 49.9614 | 15.7387 | 127.6455 | 15.6008 | 21.4727 | 77.3401 | 1 | 49.9619 | 15 | 22.1 | 221 | 154840 | 237482.766 | 3543128.6383 | 99.9228 | 0.0023662 | 0.070986 | 0.070986 | 0.070986 | 7.9917 | 1016.8398 | 1014.3257 | 1014.3253 | 1016.8398 | 1039.517 | 1039.517 | 1039.517 | 1039.517 | 1016.8638 | 1016.8638 | 1016.8638 | 16.5315 | 0 | 16.5374 | 83.3164 | 239.6753 | 239.9029 | 232.2811 | 2.1457 | 3.3856 | 0 | 86 | 63.9182 | 64.8195 | 104.9245 | 9.4792 | 127.6455 | -1.0029 | 77.1472 | 62.5715 | 48.9449 | 0 | 66.8608 | 819.5274 | 815.7102 | 738.8102 | 738.9096 | 733.3333 | 732.8891 | 563.11 | 557.4203 | 770.839 | 793.1074 | 1014.9932 | 1024.9749 | 1039.3091 | 1054.7351 | 1041.5598 | 1020.9743 | 1042.3645 | 1015.4632 | 1043.8774 | 1014.4426 | 1026.0343 | 1032.794 | 1007.1859 | 1029.5189 | 1030.3581 | 1030.5296 | 1032.3687 | 1033.2738 | 1028.3547 | 1000.7565 | 1060.2723 | 1009.5864 | 1026.4783
2025-04-09 18:42 | 9 | 18 | 42 | 6.2817e-272 | 1 | 29.4028 | 642.6214 | 0.24825 | 0.0075233 | 163.5739 | 163.5739 | 163.5739 | 163.5739 | 12.6094 | 13.5919 | 669.4498 | 669.4498 | 669.4498 | 669.4498 | 65.0326 | 49.9802 | 15.7375 | 127.5065 | 15.5993 | 21.5444 | 77.3392 | 1 | 49.9802 | 15 | 22.1 | 221 | 154840 | 237484.4255 | 3543149.8085 | 99.9604 | 0.0097855 | 0.29356 | 0.29356 | 0.29356 | 7.9917 | 1016.7647 | 1014.2491 | 1014.2489 | 1016.7647 | 1039.6987 | 1039.6987 | 1039.6987 | 1039.6987 | 1016.7457 | 1016.7457 | 1016.7457 | 16.5191 | 0 | 16.5173 | 83.3431 | 239.7929 | 240.0024 | 232.4573 | 2.1261 | 3.3807 | 0 | 86 | 64.2411 | 65.0326 | 104.9164 | 9.3238 | 127.5065 | -1.4269 | 77.4049 | 62.5676 | 49.0539 | 0 | 66.8598 | 819.6296 | 815.7027 | 738.789 | 738.8783 | 733.3597 | 732.9092 | 562.8648 | 557.0607 | 770.6671 | 793.0397 | 1015.2585 | 1024.6485 | 1038.4115 | 1053.2526 | 1041.234 | 1019.873 | 1041.2464 | 1015.9666 | 1044.7179 | 1015.6564 | 1026.4577 | 1032.5926 | 1007.1282 | 1028.4528 | 1030.0945 | 1030.7651 | 1032.7738 | 1033.5323 | 1028.187 | 1000.3145 | 1059.8411 | 1009.4294 | 1027.3502
2025-04-09 18:43 | 9 | 18 | 43 | 6.2817e-272 | 1 | 29.4019 | 642.9516 | 0.24609 | 0.0075484 | 163.7006 | 163.7006 | 163.7006 | 163.7006 | 12.6187 | 13.5841 | 668.4267 | 668.4267 | 668.4267 | 668.4267 | 65.167 | 49.9699 | 15.7368 | 127.7492 | 15.6008 | 21.5312 | 77.4252 | 1 | 49.9702 | 15 | 22.1 | 221 | 154840 | 237485.9574 | 3543171 | 99.9397 | -0.002566 | -0.076981 | -0.076981 | -0.076981 | 7.9917 | 1016.597 | 1014.0762 | 1014.0745 | 1016.597 | 1039.3828 | 1039.3828 | 1039.3828 | 1039.3828 | 1016.5526 | 1016.5526 | 1016.5526 | 16.5418 | 0 | 16.5484 | 83.367 | 239.9625 | 240.1664 | 232.4981 | 2.0916 | 3.4046 | 0 | 86 | 63.9002 | 65.167 | 104.912 | 9.4434 | 127.7492 | -1.4931 | 77.3574 | 62.5714 | 49.1542 | 0 | 66.8602 | 819.4711 | 815.5511 | 738.7285 | 738.7717 | 733.312 | 732.8694 | 562.6233 | 556.8908 | 770.4773 | 794.6818 | 1015.2774 | 1025.0391 | 1038.3957 | 1053.2991 | 1040.8804 | 1020.6915 | 1040.5794 | 1014.9962 | 1046.1768 | 1014.6219 | 1027.4274 | 1032.7009 | 1005.5634 | 1027.6932 | 1029.5691 | 1030.8509 | 1031.9581 | 1033.1591 | 1027.786 | 999.7046 | 1060.0285 | 1009.9628 | 1026.6691
2025-04-09 18:44 | 9 | 18 | 44 | 6.2817e-272 | 1 | 29.4031 | 643.9604 | 0.2451 | 0.0075743 | 163.8884 | 163.8884 | 163.8884 | 163.8884 | 12.6315 | 13.5991 | 668.8509 | 668.8509 | 668.8509 | 668.8509 | 65.0168 | 49.9954 | 15.7412 | 127.9355 | 15.5982 | 21.5723 | 77.4685 | 1 | 49.9952 | 15 | 22.1 | 221 | 154840 | 237487.5319 | 3543192.1915 | 99.9908 | -0.0038824 | -0.11647 | -0.11647 | -0.11647 | 7.9917 | 1016.3655 | 1013.8383 | 1013.8394 | 1016.3655 | 1039.1396 | 1039.1396 | 1039.1396 | 1039.1396 | 1016.3823 | 1016.3823 | 1016.3823 | 16.5761 | 0 | 16.57 | 83.6406 | 240.3492 | 240.5507 | 232.468 | 2.0858 | 3.3947 | 0 | 86 | 63.5511 | 65.0168 | 104.9415 | 9.4614 | 127.9355 | -1.2496 | 77.505 | 62.5864 | 49.2599 | 0 | 66.8596 | 819.1206 | 815.3716 | 738.666 | 738.7275 | 733.2517 | 732.8601 | 562.3804 | 556.6186 | 770.1353 | 794.541 | 1015.0421 | 1024.4004 | 1039.7698 | 1053.8983 | 1041.1432 | 1021.0466 | 1040.6187 | 1014.9806 | 1043.6647 | 1013.7655 | 1025.5734 | 1032.723 | 1006.3987 | 1027.3179 | 1030.6783 | 1030.7557 | 1031.65 | 1033.2198 | 1027.8517 | 999.5801 | 1059.9494 | 1009.3506 | 1025.6219
2025-04-09 18:45 | 9 | 18 | 45 | 6.2817e-272 | 1 | 29.4042 | 644.5952 | 0.24532 | 0.0075972 | 163.8547 | 163.8547 | 163.8547 | 163.8547 | 12.6287 | 13.6031 | 669.2304 | 669.2304 | 669.2304 | 669.2304 | 64.8338 | 49.9974 | 15.7376 | 127.8078 | 15.602 | 21.5518 | 77.4353 | 1 | 49.9965 | 15 | 22.1 | 221 | 154840 | 237489.1489 | 3543213.3617 | 99.9947 | 0.026713 | 0.80139 | 0.80139 | 0.80139 | 7.9917 | 1016.4168 | 1013.8904 | 1013.8891 | 1016.4168 | 1039.3057 | 1039.3057 | 1039.3057 | 1039.3057 | 1016.4081 | 1016.4081 | 1016.4081 | 16.5323 | 0 | 16.5312 | 83.5746 | 240.2883 | 240.4749 | 232.5276 | 2.0886 | 3.4076 | 0 | 86 | 64.0834 | 64.8338 | 104.9174 | 9.331 | 127.8078 | -1.323 | 77.4313 | 62.5631 | 49.3523 | 0 | 66.8594 | 818.9069 | 815.2054 | 738.5604 | 738.7535 | 733.1737 | 732.8414 | 562.1904 | 556.452 | 769.7816 | 794.1662 | 1015.3468 | 1024.0087 | 1038.6813 | 1053.58 | 1040.9021 | 1020.3874 | 1040.2264 | 1014.647 | 1045.2683 | 1014.6638 | 1026.8404 | 1032.8147 | 1006.2957 | 1027.8715 | 1029.6649 | 1030.7389 | 1031.4428 | 1033.0881 | 1027.826 | 1000.0851 | 1060.1104 | 1010.3687 | 1025.6998
2025-04-09 18:46 | 9 | 18 | 46 | 6.2817e-272 | 1 | 29.4041 | 644.6798 | 0.24432 | 0.0075955 | 163.6208 | 163.6208 | 163.6208 | 163.6208 | 12.6122 | 13.601 | 670.087 | 670.087 | 670.087 | 670.087 | 65.1765 | 50.0086 | 15.7403 | 127.5911 | 15.6001 | 21.5368 | 77.303 | 1 | 50.0088 | 15 | 22.1 | 221 | 154840 | 237490.617 | 3543234.5532 | 100.0172 | -0.0060235 | -0.1807 | -0.1807 | -0.1807 | 7.9917 | 1016.7138 | 1014.1966 | 1014.196 | 1016.7138 | 1039.5877 | 1039.5877 | 1039.5877 | 1039.5877 | 1016.7315 | 1016.7315 | 1016.7315 | 16.5088 | 0 | 16.5083 | 83.4603 | 239.9291 | 240.1241 | 232.4736 | 2.1048 | 3.3958 | 0 | 86 | 64.3243 | 65.1765 | 104.9353 | 9.3735 | 127.5911 | -1.3337 | 77.3777 | 62.5788 | 49.3455 | 0 | 66.8592 | 818.8247 | 815.2769 | 738.5659 | 738.7821 | 733.1334 | 732.8755 | 561.9723 | 556.1594 | 769.445 | 793.3829 | 1015.3111 | 1024.2264 | 1037.8119 | 1053.3413 | 1041.9017 | 1018.8723 | 1039.9257 | 1015.2181 | 1043.476 | 1016.0683 | 1027.2272 | 1033.6079 | 1008.625 | 1028.3049 | 1031.1877 | 1031.1613 | 1031.7943 | 1033.3189 | 1028.3934 | 999.4271 | 1060.2204 | 1010.3664 | 1026.9417
2025-04-09 18:47 | 9 | 18 | 47 | 6.2817e-272 | 1 | 29.405 | 644.3472 | 0.24779 | 0.0075795 | 163.2704 | 163.2704 | 163.2704 | 163.2704 | 12.5869 | 13.5852 | 670.8912 | 670.8912 | 670.8912 | 670.8912 | 65.6741 | 49.9947 | 15.7377 | 127.219 | 15.6004 | 21.4627 | 77.105 | 1 | 49.9952 | 15 | 22.1 | 221 | 154840 | 237492.2979 | 3543255.7234 | 99.9895 | 0.004749 | 0.14247 | 0.14247 | 0.14247 | 7.9917 | 1017.1657 | 1014.6626 | 1014.663 | 1017.1657 | 1040.0726 | 1040.0726 | 1040.0726 | 1040.0726 | 1017.266 | 1017.266 | 1017.266 | 16.4753 | 0 | 16.4748 | 83.2748 | 239.444 | 239.6292 | 232.3837 | 2.1329 | 3.3925 | 0 | 86 | 64.9438 | 65.6741 | 104.9178 | 9.3063 | 127.219 | -1.209 | 77.1112 | 62.5895 | 49.2822 | 0 | 66.8615 | 818.9639 | 815.4692 | 738.5894 | 738.8928 | 733.1486 | 732.9668 | 561.7419 | 555.9958 | 769.2453 | 794.6323 | 1016.2345 | 1025.4153 | 1039.9072 | 1055.2864 | 1043.6753 | 1020.1549 | 1041.1632 | 1015.4485 | 1043.3364 | 1015.7817 | 1025.8296 | 1034.124 | 1008.2909 | 1028.607 | 1031.3062 | 1031.3247 | 1031.8402 | 1033.1619 | 1030.2172 | 1000.169 | 1061.2966 | 1010.6468 | 1026.0804
2025-04-09 18:48 | 9 | 18 | 48 | 6.2817e-272 | 1 | 29.4128 | 642.3301 | 0.25059 | 0.0075812 | 163.0749 | 163.0749 | 163.0749 | 163.0749 | 12.57 | 13.5742 | 672.254 | 672.254 | 672.254 | 672.254 | 66.8799 | 50.0284 | 15.7406 | 126.7894 | 15.603 | 21.4354 | 76.9354 | 1 | 50.0278 | 15 | 22.1 | 221 | 154840 | 237493.6739 | 3543276.587 | 100.0568 | 0.024067 | 0.722 | 0.722 | 0.722 | 7.9917 | 1017.4741 | 1014.9793 | 1014.9811 | 1017.4741 | 1040.6315 | 1040.6315 | 1040.6315 | 1040.6315 | 1017.5037 | 1017.5037 | 1017.5037 | 16.4944 | 0 | 16.5025 | 83.2902 | 239.1805 | 239.3809 | 232.2524 | 2.2149 | 3.3832 | 0 | 86 | 66.0159 | 66.8799 | 104.9371 | 9.1722 | 126.7894 | -1.2157 | 77.0131 | 62.5929 | 49.2968 | 0 | 66.8634 | 819.4814 | 815.9137 | 738.7028 | 739.1143 | 733.263 | 733.2566 | 561.5451 | 555.7929 | 769.3352 | 793.417 | 1016.5196 | 1026.0039 | 1038.3409 | 1053.7307 | 1043.9724 | 1019.6796 | 1041.953 | 1016.1463 | 1048.0404 | 1017.035 | 1025.8346 | 1033.7578 | 1006.3949 | 1026.6715 | 1029.3937 | 1033.4574 | 1032.922 | 1034.4254 | 1030.7991 | 1001.0988 | 1061.0243 | 1011.0572 | 1027.3787
2025-04-09 18:49 | 9 | 18 | 49 | 6.2817e-272 | 1 | 29.414 | 639.967 | 0.2486 | 0.0075965 | 162.988 | 162.988 | 162.988 | 162.988 | 12.5634 | 13.5472 | 672.3796 | 672.3796 | 672.3796 | 672.3796 | 68.0852 | 50.0226 | 15.7418 | 126.7593 | 15.5996 | 21.4121 | 76.9272 | 1 | 50.0232 | 15 | 22.1 | 221 | 154840 | 237495.3404 | 3543297.4255 | 100.0453 | 0.0071192 | 0.21358 | 0.21358 | 0.21358 | 7.9917 | 1017.5947 | 1015.1049 | 1015.1038 | 1017.5947 | 1040.6717 | 1040.6717 | 1040.6717 | 1040.6717 | 1017.5645 | 1017.5645 | 1017.5645 | 16.5484 | 0 | 16.5594 | 83.2283 | 239.066 | 239.2507 | 232.2223 | 2.2347 | 3.3915 | 0 | 86 | 66.7103 | 68.0852 | 104.9452 | 9.2003 | 126.7593 | -1.2103 | 76.9294 | 62.585 | 49.36 | 0 | 66.8636 | 820.2474 | 816.3348 | 739.0237 | 739.4982 | 733.4877 | 733.5769 | 561.3119 | 555.668 | 769.583 | 794.5501 | 1016.3145 | 1025.9094 | 1039.4721 | 1055.2234 | 1044.5715 | 1020.53 | 1041.8911 | 1015.5172 | 1044.6213 | 1015.9774 | 1024.9172 | 1034.1106 | 1007.8606 | 1027.5211 | 1031.1787 | 1032.4794 | 1032.6462 | 1033.5879 | 1032.213 | 1001.2002 | 1061.9534 | 1011.4438 | 1026.4047
2025-04-09 18:50 | 9 | 18 | 50 | 6.2817e-272 | 1 | 29.4128 | 637.9924 | 0.24808 | 0.0075686 | 162.9969 | 162.9969 | 162.9969 | 162.9969 | 12.5645 | 13.5395 | 671.573 | 671.573 | 671.573 | 671.573 | 68.2931 | 50.0151 | 15.7409 | 126.8134 | 15.6056 | 21.4342 | 76.9328 | 1 | 50.0144 | 15 | 22.1 | 221 | 154840 | 237496.7447 | 3543318.5319 | 100.0302 | 0.022898 | 0.68695 | 0.68695 | 0.68695 | 7.9917 | 1017.5723 | 1015.0823 | 1015.08 | 1017.5723 | 1040.6011 | 1040.6011 | 1040.6011 | 1040.6011 | 1017.56 | 1017.56 | 1017.56 | 16.5799 | 0 | 16.579 | 83.1997 | 239.064 | 239.2282 | 232.2912 | 2.2306 | 3.403 | 0 | 86 | 66.6286 | 68.2931 | 104.9395 | 9.1528 | 126.8134 | -1.3554 | 77.0088 | 62.5987 | 49.2459 | 0 | 66.8634 | 820.6972 | 816.5 | 739.0868 | 739.5753 | 733.6233 | 733.6881 | 561.036 | 555.5847 | 769.7818 | 794.8997 | 1017.3926 | 1025.9966 | 1037.9868 | 1053.3517 | 1043.9117 | 1019.05 | 1041.9445 | 1015.9574 | 1044.6757 | 1016.8106 | 1025.5077 | 1034.0219 | 1006.4394 | 1026.7583 | 1030.1277 | 1033.4511 | 1033.3174 | 1034.6551 | 1031.5785 | 1002.0188 | 1061.2955 | 1011.7409 | 1028.5074
2025-04-09 18:51 | 9 | 18 | 51 | 6.2817e-272 | 1 | 29.4108 | 635.8154 | 0.24799 | 0.0075626 | 162.7005 | 162.7005 | 162.7005 | 162.7005 | 12.5443 | 13.5102 | 671.4852 | 671.4852 | 671.4852 | 671.4852 | 69.1156 | 49.9914 | 15.7372 | 126.5335 | 15.6027 | 21.3526 | 76.8254 | 1 | 49.9927 | 15 | 22.1 | 221 | 154840 | 237498.4043 | 3543339.5532 | 99.9827 | -0.0052278 | -0.15684 | -0.15684 | -0.15684 | 7.9917 | 1017.936 | 1015.4562 | 1015.4562 | 1017.936 | 1040.966 | 1040.966 | 1040.966 | 1040.966 | 1018.004 | 1018.004 | 1018.004 | 16.585 | 0 | 16.5898 | 83.0275 | 238.6166 | 238.7845 | 232.2201 | 2.1828 | 3.3915 | 0 | 86 | 66.6714 | 69.1156 | 104.9148 | 9.2618 | 126.5335 | -1.1847 | 76.7157 | 62.6106 | 49.2191 | 0 | 66.8634 | 821.2322 | 816.8313 | 739.2951 | 739.6484 | 733.8863 | 733.7814 | 560.7189 | 555.3364 | 770.0034 | 795.32 | 1017.1691 | 1026.3011 | 1038.8462 | 1055.3811 | 1045.3951 | 1020.0883 | 1041.66 | 1015.4862 | 1044.1053 | 1016.6464 | 1025.4551 | 1035.3506 | 1008.2338 | 1027.607 | 1030.5838 | 1033.5268 | 1034.2768 | 1035.0398 | 1032.8055 | 1002.4255 | 1062.7328 | 1011.7011 | 1028.1617
2025-04-09 18:52 | 9 | 18 | 52 | 6.2817e-272 | 1 | 29.4077 | 635.8497 | 0.25165 | 0.0075649 | 162.8111 | 162.8111 | 162.8111 | 162.8111 | 12.5534 | 13.5221 | 671.5952 | 671.5952 | 671.5952 | 671.5952 | 69.1663 | 50.0192 | 15.7405 | 126.5349 | 15.5992 | 21.405 | 76.8082 | 1 | 50.0177 | 15 | 22.1 | 221 | 154840 | 237499.8298 | 3543360.5106 | 100.0384 | 0.029864 | 0.89592 | 0.89592 | 0.89592 | 7.9917 | 1017.7728 | 1015.2883 | 1015.2902 | 1017.7728 | 1040.9638 | 1040.9638 | 1040.9638 | 1040.9638 | 1017.7617 | 1017.7617 | 1017.7617 | 16.5948 | 0 | 16.594 | 83.1543 | 238.8046 | 238.9531 | 232.2704 | 2.1571 | 3.4009 | 0 | 86 | 66.6386 | 69.1663 | 104.9369 | 9.0432 | 126.5349 | -1.2522 | 76.9039 | 62.5917 | 49.2269 | 0 | 66.8637 | 821.6019 | 817.1632 | 739.5074 | 739.7562 | 734.1631 | 733.92 | 560.4273 | 555.5433 | 770.3101 | 795.3196 | 1017.5404 | 1027.474 | 1036.9153 | 1052.3072 | 1044.6472 | 1018.5915 | 1042.727 | 1017.1085 | 1049.3021 | 1017.6209 | 1026.7138 | 1033.4345 | 1002.6956 | 1024.2921 | 1028.2432 | 1034.0589 | 1034.2549 | 1035.3806 | 1032.3266 | 1003.3462 | 1061.9021 | 1012.8234 | 1029.0721
2025-04-09 18:53 | 9 | 18 | 53 | 6.2817e-272 | 1 | 29.4095 | 635.3616 | 0.25167 | 0.0075606 | 162.9413 | 162.9413 | 162.9413 | 162.9413 | 12.5619 | 13.5327 | 671.8901 | 671.8901 | 671.8901 | 671.8901 | 68.6912 | 50.0187 | 15.7409 | 126.7099 | 15.6015 | 21.4028 | 76.8979 | 1 | 50.0179 | 15 | 22.1 | 221 | 154840 | 237501.4043 | 3543381.4468 | 100.0373 | 0.024544 | 0.73632 | 0.73632 | 0.73632 | 7.9917 | 1017.6196 | 1015.1311 | 1015.1309 | 1017.6196 | 1040.7362 | 1040.7362 | 1040.7362 | 1040.7362 | 1017.5713 | 1017.5713 | 1017.5713 | 16.5892 | 0 | 16.5888 | 83.165 | 238.9869 | 239.1577 | 232.4304 | 2.199 | 3.382 | 0 | 86 | 66.9587 | 68.6912 | 104.9392 | 8.511 | 126.7099 | -1.3382 | 76.8962 | 62.5899 | 49.2103 | 0 | 66.863 | 821.7131 | 817.3688 | 739.6311 | 739.9102 | 734.3345 | 734.0763 | 560.2285 | 555.3218 | 770.5416 | 794.832 | 1016.1804 | 1026.3764 | 1037.8557 | 1054.0898 | 1044.2702 | 1019.8626 | 1041.6283 | 1015.6455 | 1046.8604 | 1017.2555 | 1026.0406 | 1034.054 | 1007.1453 | 1026.6106 | 1028.9947 | 1032.8291 | 1033.4798 | 1034.1821 | 1031.5143 | 1001.6913 | 1061.9817 | 1012.0751 | 1028.2926
2025-04-09 18:54 | 9 | 18 | 54 | 6.2817e-272 | 1 | 29.4056 | 635.9628 | 0.24997 | 0.0075787 | 163.1234 | 163.1234 | 163.1234 | 163.1234 | 12.5763 | 13.5482 | 671.6535 | 671.6535 | 671.6535 | 671.6535 | 67.7257 | 50.0088 | 15.74 | 126.966 | 15.5995 | 21.4346 | 77.0022 | 1 | 50.0071 | 15 | 22.1 | 221 | 154840 | 237502.6596 | 3543402.5106 | 100.0176 | 0.025027 | 0.7508 | 0.7508 | 0.7508 | 7.9917 | 1017.3606 | 1014.8626 | 1014.8636 | 1017.3606 | 1040.4023 | 1040.4023 | 1040.4023 | 1040.4023 | 1017.3721 | 1017.3721 | 1017.3721 | 16.5626 | 0 | 16.5733 | 83.2726 | 239.2537 | 239.4285 | 232.5465 | 2.1329 | 3.3828 | 0 | 86 | 66.3853 | 67.7257 | 104.9333 | 8.0408 | 126.966 | -1.2058 | 77.0102 | 62.5854 | 49.2802 | 0 | 66.8623 | 821.6009 | 817.3181 | 739.5721 | 739.9398 | 734.3223 | 734.1307 | 560.0132 | 555.1186 | 770.6466 | 795.5291 | 1016.7204 | 1025.1734 | 1037.7238 | 1053.3828 | 1043.4311 | 1019.0079 | 1042.207 | 1016.393 | 1045.764 | 1016.6809 | 1025.9013 | 1033.3617 | 1006.3263 | 1026.3391 | 1029.7472 | 1033.1066 | 1033.124 | 1034.3981 | 1030.8832 | 1002.177 | 1061.3766 | 1011.716 | 1028.1081
2025-04-09 18:55 | 9 | 18 | 55 | 6.2817e-272 | 1 | 29.4021 | 637.088 | 0.2532 | 0.0075995 | 163.2859 | 163.2859 | 163.2859 | 163.2859 | 12.5892 | 13.5618 | 671.662 | 671.662 | 671.662 | 671.662 | 67.4707 | 50.0277 | 15.7422 | 126.9921 | 15.6026 | 21.4503 | 76.9992 | 1 | 50.0272 | 15 | 22.1 | 221 | 154840 | 237504.0213 | 3543423.617 | 100.0554 | 0.015883 | 0.4765 | 0.4765 | 0.4765 | 7.9917 | 1017.1272 | 1014.6226 | 1014.6226 | 1017.1272 | 1040.3691 | 1040.3691 | 1040.3691 | 1040.3691 | 1017.0915 | 1017.0915 | 1017.0915 | 16.5575 | 0 | 16.5496 | 83.3928 | 239.4963 | 239.6673 | 232.6138 | 2.0938 | 3.3967 | 0 | 86 | 65.8448 | 67.4707 | 104.9482 | 7.4297 | 126.9921 | -1.2496 | 77.0668 | 62.5932 | 49.3593 | 0 | 66.8623 | 821.5069 | 817.326 | 739.5184 | 739.9431 | 734.2912 | 734.1781 | 559.8001 | 555.1468 | 770.6737 | 795.6879 | 1015.9417 | 1025.9691 | 1037.3613 | 1053.2509 | 1043.1432 | 1019.1704 | 1041.5894 | 1015.6687 | 1047.4347 | 1016.6481 | 1025.9849 | 1032.8147 | 1005.7013 | 1026.8191 | 1028.5981 | 1032.3868 | 1032.5757 | 1033.7632 | 1030.0209 | 1001.3538 | 1060.7528 | 1011.5813 | 1027.8094
2025-04-09 18:56 | 9 | 18 | 56 | 6.2817e-272 | 1 | 29.4013 | 639.3447 | 0.25128 | 0.0076123 | 163.4951 | 163.4951 | 163.4951 | 163.4951 | 12.6044 | 13.5789 | 671.2636 | 671.2636 | 671.2636 | 671.2636 | 66.7555 | 50.0321 | 15.7433 | 127.2529 | 15.5999 | 21.4826 | 77.139 | 1 | 50.0314 | 15 | 22.1 | 221 | 154840 | 237505.3404 | 3543444.766 | 100.0642 | 0.022186 | 0.66557 | 0.66557 | 0.66557 | 7.9917 | 1016.8519 | 1014.3396 | 1014.34 | 1016.8519 | 1040.0279 | 1040.0279 | 1040.0279 | 1040.0279 | 1016.8191 | 1016.8191 | 1016.8191 | 16.5441 | 0 | 16.5521 | 83.5185 | 239.8581 | 240.0352 | 232.7154 | 2.045 | 3.3995 | 0 | 86 | 65.5945 | 66.7555 | 104.9551 | 7.7544 | 127.2529 | -1.3321 | 77.183 | 62.6134 | 49.4099 | 0 | 66.8608 | 821.1915 | 817.2197 | 739.4084 | 739.8761 | 734.1992 | 734.105 | 559.5617 | 554.8001 | 770.5903 | 795.4307 | 1015.5545 | 1025.7064 | 1037.5547 | 1053.104 | 1042.2589 | 1019.1579 | 1040.9223 | 1014.9211 | 1045.7704 | 1016.5402 | 1026.3464 | 1033.0204 | 1006.6953 | 1027.2274 | 1028.787 | 1031.6113 | 1032.3257 | 1033.6215 | 1028.9713 | 1000.2525 | 1059.8313 | 1010.9549 | 1027.7245
2025-04-09 18:57 | 9 | 18 | 57 | 6.2817e-272 | 1 | 29.4027 | 640.7022 | 0.25204 | 0.0075996 | 163.6521 | 163.6521 | 163.6521 | 163.6521 | 12.6149 | 13.5907 | 670.8319 | 670.8319 | 670.8319 | 670.8319 | 66.199 | 50.0342 | 15.7428 | 127.5071 | 15.6013 | 21.5082 | 77.2199 | 1 | 50.0335 | 15 | 22.1 | 221 | 154840 | 237506.5217 | 3543465.7174 | 100.0684 | 0.022997 | 0.68991 | 0.68991 | 0.68991 | 7.9917 | 1016.6624 | 1014.1448 | 1014.1443 | 1016.6624 | 1039.6978 | 1039.6978 | 1039.6978 | 1039.6978 | 1016.6685 | 1016.6685 | 1016.6685 | 16.5525 | 0 | 16.5591 | 83.536 | 240.0615 | 240.2369 | 232.7145 | 2.0865 | 3.399 | 0 | 86 | 65.1687 | 66.199 | 104.952 | 7.5695 | 127.5071 | -1.3252 | 77.275 | 62.5966 | 49.3608 | 0 | 66.8578 | 820.9684 | 817.0506 | 739.3076 | 739.6766 | 734.0276 | 733.855 | 559.1601 | 554.6288 | 770.5395 | 795.5619 | 1015.5763 | 1025.3622 | 1037.2113 | 1052.8959 | 1041.5641 | 1018.8448 | 1041.2943 | 1015.2993 | 1047.7065 | 1015.7961 | 1026.4817 | 1033.0274 | 1004.7378 | 1026.0939 | 1029.0493 | 1031.4857 | 1032.1274 | 1033.3785 | 1028.9459 | 999.6602 | 1060.3215 | 1011.2324 | 1027.235
2025-04-09 18:58 | 9 | 18 | 58 | 6.2817e-272 | 1 | 29.4018 | 642.3552 | 0.25068 | 0.0075978 | 163.6581 | 163.6581 | 163.6581 | 163.6581 | 12.6157 | 13.5933 | 670.6219 | 670.6219 | 670.6219 | 670.6219 | 65.8113 | 50.0212 | 15.7418 | 127.5667 | 15.6026 | 21.5209 | 77.2744 | 1 | 50.0203 | 15 | 22.1 | 221 | 154840 | 237507.7447 | 3543486.6809 | 100.0424 | 0.025276 | 0.75829 | 0.75829 | 0.75829 | 7.9917 | 1016.6494 | 1014.1304 | 1014.13 | 1016.6494 | 1039.62 | 1039.62 | 1039.62 | 1039.62 | 1016.5611 | 1016.5611 | 1016.5611 | 16.5444 | 0 | 16.542 | 83.5502 | 240.056 | 240.2206 | 232.6774 | 2.0533 | 3.3934 | 0 | 86 | 65.118 | 65.8113 | 104.9457 | 7.7657 | 127.5667 | -1.295 | 77.3205 | 62.5953 | 49.3529 | 0 | 66.8579 | 820.7419 | 816.8408 | 739.0983 | 739.3771 | 733.7427 | 733.5321 | 558.783 | 554.3923 | 770.5063 | 795.9063 | 1015.0094 | 1025.234 | 1037.8864 | 1053.4702 | 1041.8545 | 1020.0717 | 1041.3198 | 1015.2921 | 1044.2264 | 1015.1849 | 1026.3826 | 1032.5491 | 1006.3262 | 1027.2581 | 1029.5566 | 1031.4172 | 1031.8028 | 1032.9528 | 1028.5785 | 999.725 | 1059.8723 | 1010.3168 | 1026.554
2025-04-09 18:59 | 9 | 18 | 59 | 6.2817e-272 | 1 | 29.3993 | 644.4449 | 0.25324 | 0.0075971 | 163.943 | 163.943 | 163.943 | 163.943 | 12.6369 | 13.6127 | 670.3394 | 670.3394 | 670.3394 | 670.3394 | 65.3455 | 50.041 | 15.7438 | 127.8567 | 15.5982 | 21.553 | 77.3494 | 1 | 50.0418 | 15 | 22.1 | 221 | 154840 | 237509.1915 | 3543507.8511 | 100.082 | -0.015361 | -0.46084 | -0.46084 | -0.46084 | 7.9917 | 1016.267 | 1013.7374 | 1013.7364 | 1016.267 | 1039.2426 | 1039.2426 | 1039.2426 | 1039.2426 | 1016.2704 | 1016.2704 | 1016.2704 | 16.5631 | 0 | 16.5585 | 83.7395 | 240.5026 | 240.6741 | 232.5951 | 2.0449 | 3.405 | 0 | 86 | 64.8732 | 65.3427 | 104.9589 | 7.9092 | 127.8567 | -1.3064 | 77.4359 | 62.6066 | 49.3466 | 0 | 66.8579 | 820.5069 | 816.5722 | 738.8333 | 739.0893 | 733.463 | 733.2023 | 558.3498 | 554.1333 | 770.3845 | 795.3733 | 1014.3732 | 1024.5696 | 1039.4996 | 1054.8687 | 1041.0519 | 1020.4862 | 1040.7811 | 1014.0836 | 1043.3087 | 1014.516 | 1024.934 | 1032.6483 | 1007.1463 | 1028.1572 | 1029.8389 | 1030.6534 | 1031.2381 | 1032.0191 | 1028.0464 | 998.3867 | 1059.6787 | 1009.597 | 1025.5572
2025-04-09 19:00 | 9 | 19 | 0 | 6.2817e-272 | 1 | 29.4026 | 645.1711 | 0.25517 | 0.0076 | 163.9817 | 163.9817 | 163.9817 | 163.9817 | 12.6383 | 13.6202 | 670.2316 | 670.2316 | 670.2316 | 670.2316 | 64.9915 | 50.0425 | 15.7398 | 127.7644 | 15.599 | 21.5398 | 77.3633 | 1 | 50.0441 | 15 | 22.1 | 221 | 154840 | 237510.4681 | 3543529.0426 | 100.0849 | -0.0035429 | -0.10629 | -0.10629 | -0.10629 | 7.9917 | 1016.2417 | 1013.7109 | 1013.71 | 1016.2417 | 1039.3621 | 1039.3621 | 1039.3621 | 1039.3621 | 1016.2328 | 1016.2328 | 1016.2328 | 16.5362 | 0 | 16.5385 | 83.7298 | 240.5547 | 240.7295 | 232.5786 | 2.0935 | 3.4035 | 0 | 86 | 64.9573 | 64.8363 | 104.932 | 8.7633 | 127.7644 | -1.2762 | 77.3884 | 62.5819 | 49.3629 | 0 | 66.8578 | 820.2429 | 816.3069 | 738.5992 | 738.8056 | 733.1596 | 732.8628 | 557.8792 | 553.9538 | 770.2801 | 795.411 | 1015.317 | 1024.9411 | 1037.8717 | 1053.1602 | 1040.8285 | 1019.1353 | 1041.2672 | 1015.1423 | 1045.2309 | 1014.6106 | 1025.9666 | 1032.136 | 1004.8908 | 1027.2898 | 1028.9719 | 1031.247 | 1031.7449 | 1032.7687 | 1026.6781 | 998.7953 | 1058.6743 | 1009.473 | 1026.9726
2025-04-09 19:01 | 9 | 19 | 1 | 6.2817e-272 | 1 | 29.4039 | 646.1823 | 0.25818 | 0.0076104 | 164.2985 | 164.2985 | 164.2985 | 164.2985 | 12.6602 | 13.6462 | 670.0889 | 670.0889 | 670.0889 | 670.0889 | 64.4362 | 50.0751 | 15.7425 | 128.1638 | 15.602 | 21.6066 | 77.4747 | 1 | 50.0759 | 15 | 22.1 | 221 | 154840 | 237512.0213 | 3543550.234 | 100.1501 | 0.0013322 | 0.039967 | 0.039967 | 0.039967 | 7.9917 | 1015.8487 | 1013.3055 | 1013.3043 | 1015.8487 | 1038.8428 | 1038.8428 | 1038.8428 | 1038.8428 | 1015.8351 | 1015.8351 | 1015.8351 | 16.543 | 0 | 16.5578 | 84.0545 | 241.1412 | 241.3294 | 232.5689 | 2.0981 | 3.4031 | 0 | 86 | 64.3523 | 64.3932 | 104.9498 | 9.3889 | 128.1638 | -1.284 | 77.6284 | 62.603 | 49.4056 | 0 | 66.858 | 820.0872 | 816.086 | 738.4511 | 738.5737 | 732.9304 | 732.6097 | 557.4753 | 553.7348 | 770.1836 | 795.3348 | 1013.7304 | 1023.1804 | 1038.4794 | 1054.1332 | 1039.8943 | 1018.8364 | 1040.4913 | 1014.0021 | 1040.3528 | 1014.3223 | 1024.337 | 1032.2549 | 1008.2446 | 1028.7472 | 1030.4579 | 1029.973 | 1031.4677 | 1032.2736 | 1026.8957 | 998.4112 | 1059.143 | 1008.946 | 1026.2381
2025-04-09 19:02 | 9 | 19 | 2 | 6.2817e-272 | 1 | 29.4047 | 646.6008 | 0.26145 | 0.0076055 | 164.5791 | 164.5791 | 164.5791 | 164.5791 | 12.6798 | 13.6776 | 671.1801 | 671.1801 | 671.1801 | 671.1801 | 64.5106 | 50.1497 | 15.7428 | 128.1679 | 15.6025 | 21.6047 | 77.4113 | 1 | 50.1498 | 15 | 22.1 | 221 | 154840 | 237513.5532 | 3543571.4255 | 100.2995 | 0.0072716 | 0.21815 | 0.21815 | 0.21815 | 7.9917 | 1015.494 | 1012.9387 | 1012.9383 | 1015.494 | 1038.8374 | 1038.8374 | 1038.8374 | 1038.8374 | 1015.523 | 1015.523 | 1015.523 | 16.5921 | 0 | 16.5894 | 84.3968 | 241.7139 | 241.87 | 232.5383 | 2.1453 | 3.4113 | 0 | 86 | 64.5087 | 64.1768 | 104.9522 | 9.1815 | 128.1679 | -1.2954 | 77.6217 | 62.5979 | 49.3853 | 0 | 66.8582 | 820.0626 | 816.0746 | 738.5436 | 738.6246 | 732.8375 | 732.43 | 557.1091 | 553.6834 | 770.0527 | 794.7917 | 1014.9887 | 1023.7249 | 1037.1506 | 1052.4151 | 1039.4919 | 1017.9496 | 1041.6013 | 1014.5768 | 1044.5528 | 1014.4677 | 1023.9447 | 1031.1628 | 1003.4174 | 1026.5466 | 1028.4579 | 1030.8819 | 1031.1911 | 1032.5883 | 1026.7379 | 998.1058 | 1058.4189 | 1008.6704 | 1025.5385
2025-04-09 19:03 | 9 | 19 | 3 | 6.2817e-272 | 1 | 29.4046 | 647.0404 | 0.26446 | 0.0075861 | 164.6846 | 164.6846 | 164.6846 | 164.6846 | 12.6873 | 13.6871 | 671.3269 | 671.3269 | 671.3269 | 671.3269 | 64.4135 | 50.1665 | 15.7427 | 128.2402 | 15.5974 | 21.6245 | 77.4188 | 1 | 50.1668 | 15 | 22.1 | 221 | 154840 | 237515.0851 | 3543592.6383 | 100.3331 | -0.00011756 | -0.0035265 | -0.0035265 | -0.0035265 | 7.9917 | 1015.3598 | 1012.8021 | 1012.8004 | 1015.3598 | 1038.7423 | 1038.7423 | 1038.7423 | 1038.7423 | 1015.3143 | 1015.3143 | 1015.3143 | 16.5936 | 0 | 16.5985 | 84.4854 | 241.9032 | 242.079 | 232.5614 | 2.1173 | 3.4197 | 0 | 86 | 64.4135 | 64.0205 | 104.951 | 8.4375 | 128.2402 | -1.2889 | 77.6928 | 62.6048 | 49.3078 | 0 | 66.8576 | 820.0347 | 816.194 | 738.6424 | 738.7351 | 732.8701 | 732.4798 | 556.8434 | 553.5123 | 770.0086 | 794.5434 | 1014.5789 | 1024.5347 | 1036.2349 | 1051.3287 | 1039.6762 | 1017.6523 | 1041.5036 | 1014.9834 | 1045.9834 | 1014.5032 | 1024.7919 | 1030.6291 | 1001.1576 | 1025.1764 | 1027.5883 | 1030.4194 | 1031.2534 | 1032.8357 | 1026.2072 | 997.5361 | 1057.1243 | 1008.4221 | 1025.8743
2025-04-09 19:04 | 9 | 19 | 4 | 6.2817e-272 | 1 | 29.4053 | 647.5125 | 0.26256 | 0.0075859 | 164.8336 | 164.8336 | 164.8336 | 164.8336 | 12.6976 | 13.6986 | 671.4739 | 671.4739 | 671.4739 | 671.4739 | 64.2235 | 50.187 | 15.7419 | 128.4734 | 15.6006 | 21.6503 | 77.4622 | 1 | 50.1873 | 15 | 22.1 | 221 | 154840 | 237516.4681 | 3543613.8936 | 100.3741 | 0.0028965 | 0.086895 | 0.086895 | 0.086895 | 7.9917 | 1015.174 | 1012.61 | 1012.6104 | 1015.174 | 1038.4391 | 1038.4391 | 1038.4391 | 1038.4391 | 1015.2481 | 1015.2481 | 1015.2481 | 16.6246 | 0 | 16.6207 | 84.5602 | 242.1368 | 242.3314 | 232.6643 | 2.1553 | 3.4434 | 0 | 86 | 64.2165 | 63.9845 | 104.9456 | 8.2291 | 128.4734 | -1.3009 | 77.7855 | 62.619 | 49.3092 | 0 | 66.8576 | 819.9514 | 816.2234 | 738.708 | 738.8426 | 732.9066 | 732.5628 | 556.7629 | 553.4789 | 769.9477 | 795.0281 | 1013.8621 | 1023.7609 | 1037.1466 | 1052.2413 | 1039.363 | 1018.574 | 1040.9802 | 1014.4315 | 1044.8013 | 1014.2462 | 1022.9904 | 1031.1174 | 1003.3123 | 1026.6555 | 1028.6002 | 1030.1713 | 1031.0883 | 1032.4987 | 1025.9079 | 998.0233 | 1057.7738 | 1007.6402 | 1024.7609
2025-04-09 19:05 | 9 | 19 | 5 | 6.2817e-272 | 1 | 29.4063 | 648.5726 | 0.26409 | 0.0076105 | 164.9097 | 164.9097 | 164.9097 | 164.9097 | 12.7026 | 13.6998 | 671.9521 | 671.9521 | 671.9521 | 671.9521 | 64.6214 | 50.206 | 15.7392 | 128.6364 | 15.5989 | 21.6645 | 77.5121 | 1 | 50.2065 | 15 | 22.1 | 221 | 154840 | 237517.7174 | 3543634.9783 | 100.4121 | -0.0017888 | -0.053663 | -0.053663 | -0.053663 | 7.9917 | 1015.0841 | 1012.5178 | 1012.517 | 1015.0841 | 1038.227 | 1038.227 | 1038.227 | 1038.227 | 1015.0109 | 1015.0109 | 1015.0109 | 16.6542 | 0 | 16.6514 | 84.7453 | 242.3804 | 242.5723 | 232.6577 | 2.1214 | 3.4377 | 0 | 86 | 64.6214 | 64.1816 | 104.928 | 8.0764 | 128.6364 | -1.3418 | 77.8365 | 62.6098 | 49.4086 | 0 | 66.8574 | 820.0722 | 816.2842 | 738.8553 | 739.032 | 733.0046 | 732.6539 | 556.6427 | 553.3158 | 769.9047 | 795.2575 | 1013.1002 | 1022.4183 | 1038.2196 | 1053.805 | 1038.8039 | 1018.4509 | 1039.6513 | 1012.6261 | 1040.3863 | 1013.9765 | 1021.9137 | 1031.6941 | 1006.1393 | 1027.4007 | 1029.7937 | 1029.5709 | 1030.39 | 1031.5691 | 1026.4513 | 997.0707 | 1058.4548 | 1008.2178 | 1024.5354
2025-04-09 19:06 | 9 | 19 | 6 | 6.2817e-272 | 1 | 29.4046 | 648.3084 | 0.26213 | 0.0076151 | 164.9384 | 164.9384 | 164.9384 | 164.9384 | 12.7053 | 13.7 | 670.7721 | 670.7721 | 670.7721 | 670.7721 | 64.04 | 50.1788 | 15.7417 | 128.6366 | 15.5995 | 21.6689 | 77.575 | 1 | 50.1792 | 15 | 22.1 | 221 | 154840 | 237519.1915 | 3543656.1915 | 100.3574 | 0.0026542 | 0.079627 | 0.079627 | 0.079627 | 7.9917 | 1015.0326 | 1012.4645 | 1012.467 | 1015.0326 | 1038.2266 | 1038.2266 | 1038.2266 | 1038.2266 | 1015.0185 | 1015.0185 | 1015.0185 | 16.6337 | 0 | 16.6289 | 84.6554 | 242.3456 | 242.5346 | 232.7481 | 2.1359 | 3.4377 | 0 | 86 | 63.9102 | 63.9398 | 104.9444 | 8.1972 | 128.6366 | -1.3149 | 77.852 | 62.5941 | 49.4232 | 0 | 66.857 | 819.9058 | 816.251 | 738.9222 | 739.0454 | 733.0536 | 732.6409 | 556.6025 | 553.0174 | 769.7213 | 795.2017 | 1012.453 | 1022.333 | 1038.9626 | 1053.8045 | 1038.8553 | 1018.8262 | 1039.66 | 1012.9802 | 1039.24 | 1014.2762 | 1021.4313 | 1031.8445 | 1006.8031 | 1028.2964 | 1029.8913 | 1028.9687 | 1030.2081 | 1031.5377 | 1026.5491 | 997.1351 | 1058.9566 | 1008.426 | 1024.4643
2025-04-09 19:07 | 9 | 19 | 7 | 6.2817e-272 | 1 | 29.403 | 649.4767 | 0.26428 | 0.0076127 | 164.9968 | 164.9968 | 164.9968 | 164.9968 | 12.71 | 13.6945 | 669.4873 | 669.4873 | 669.4873 | 669.4873 | 63.8056 | 50.1538 | 15.7406 | 128.9205 | 15.5997 | 21.6893 | 77.6751 | 1 | 50.1539 | 15 | 22.1 | 221 | 154840 | 237520.5106 | 3543677.617 | 100.3076 | -0.00019506 | -0.0058522 | -0.0058522 | -0.0058522 | 7.9917 | 1014.9502 | 1012.3789 | 1012.3802 | 1014.9502 | 1037.8557 | 1037.8557 | 1037.8557 | 1037.8557 | 1014.8994 | 1014.8994 | 1014.8994 | 16.6307 | 0 | 16.6379 | 84.6142 | 242.3762 | 242.5797 | 232.7599 | 2.1143 | 3.4555 | 0 | 86 | 62.9569 | 63.8056 | 104.9374 | 8.4886 | 128.9205 | -1.2999 | 77.9256 | 62.6143 | 49.4139 | 0 | 66.8574 | 819.5694 | 816.0625 | 738.9372 | 738.9182 | 733.0255 | 732.4954 | 556.4896 | 552.9494 | 769.5436 | 794.3293 | 1012.9185 | 1022.7283 | 1038.1145 | 1053.0587 | 1038.2334 | 1018.3319 | 1039.4253 | 1012.9615 | 1041.3845 | 1013.934 | 1023.5462 | 1031.1904 | 1005.0513 | 1026.464 | 1029.2021 | 1029.3379 | 1029.9123 | 1031.4843 | 1026.4383 | 998.2051 | 1059.3298 | 1009.6794 | 1024.7187
2025-04-09 19:08 | 9 | 19 | 8 | 6.2817e-272 | 1 | 29.4015 | 652.2125 | 0.2663 | 0.0076156 | 165.3827 | 165.3827 | 165.3827 | 165.3827 | 12.738 | 13.7195 | 669.8159 | 669.8159 | 669.8159 | 669.8159 | 63.6636 | 50.2054 | 15.7411 | 129.187 | 15.5995 | 21.7425 | 77.7769 | 1 | 50.206 | 15 | 22.1 | 221 | 154840 | 237521.9149 | 3543699.1277 | 100.4109 | -0.0040474 | -0.12142 | -0.12142 | -0.12142 | 7.9917 | 1014.4428 | 1011.8572 | 1011.8587 | 1014.4428 | 1037.5096 | 1037.5096 | 1037.5096 | 1037.5096 | 1014.4426 | 1014.4426 | 1014.4426 | 16.6963 | 0 | 16.692 | 84.9718 | 243.0322 | 243.2531 | 232.7403 | 2.1081 | 3.4522 | 0 | 86 | 62.624 | 63.6636 | 104.9407 | 8.4187 | 129.187 | -1.3038 | 78.1165 | 62.6004 | 49.422 | 0 | 66.8573 | 819.3552 | 815.7966 | 738.9882 | 738.8405 | 733.0537 | 732.4363 | 556.2295 | 552.6883 | 769.4577 | 794.3877 | 1012.2238 | 1021.7526 | 1038.89 | 1053.3198 | 1038.0353 | 1018.0709 | 1038.7979 | 1012.2009 | 1039.1755 | 1013.0255 | 1021.8998 | 1031.9379 | 1005.4727 | 1026.8417 | 1029.9619 | 1028.3153 | 1030.1151 | 1031.2383 | 1025.3157 | 997.3143 | 1058.5294 | 1007.6121 | 1023.7117
2025-04-09 19:09 | 9 | 19 | 9 | 6.2817e-272 | 1 | 29.3999 | 653.7668 | 0.26463 | 0.0076092 | 165.4051 | 165.4051 | 165.4051 | 165.4051 | 12.7403 | 13.7223 | 669.7634 | 669.7634 | 669.7634 | 669.7634 | 63.4674 | 50.2014 | 15.7406 | 129.1304 | 15.5993 | 21.7239 | 77.7559 | 1 | 50.2017 | 15 | 22.1 | 221 | 154840 | 237523.383 | 3543720.5957 | 100.4027 | 0.0042574 | 0.12772 | 0.12772 | 0.12772 | 7.9917 | 1014.4038 | 1011.8172 | 1011.8189 | 1014.4038 | 1037.5823 | 1037.5823 | 1037.5823 | 1037.5823 | 1014.397 | 1014.397 | 1014.397 | 16.6625 | 0 | 16.6751 | 85.0096 | 243.0654 | 243.2729 | 232.8047 | 2.1008 | 3.4625 | 0 | 86 | 62.6317 | 63.4674 | 104.9374 | 8.4499 | 129.1304 | -1.2775 | 78.0497 | 62.5939 | 49.3978 | 0 | 66.8571 | 819.3578 | 815.6509 | 739.1228 | 738.8992 | 733.1459 | 732.3416 | 555.9765 | 552.7088 | 769.6236 | 793.0833 | 1012.5194 | 1022.5634 | 1036.3364 | 1051.2706 | 1037.9396 | 1017.7955 | 1039.5549 | 1012.7474 | 1043.9562 | 1013.9423 | 1023.5683 | 1030.9251 | 1002.8748 | 1026.0011 | 1028.0702 | 1028.6381 | 1029.8583 | 1030.9868 | 1024.6611 | 997.0738 | 1057.413 | 1008.546 | 1024.9232
2025-04-09 19:10 | 9 | 19 | 10 | 6.2817e-272 | 1 | 29.401 | 654.6 | 0.26715 | 0.0076345 | 165.4979 | 165.4979 | 165.4979 | 165.4979 | 12.7464 | 13.7183 | 669.1424 | 669.1424 | 669.1424 | 669.1424 | 63.4821 | 50.193 | 15.741 | 129.334 | 15.5997 | 21.7447 | 77.8468 | 1 | 50.1933 | 15 | 22.1 | 221 | 154840 | 237524.6809 | 3543742.0851 | 100.3858 | 0.00027528 | 0.0082581 | 0.0082581 | 0.0082581 | 7.9917 | 1014.2977 | 1011.7068 | 1011.7072 | 1014.2977 | 1037.3179 | 1037.3179 | 1037.3179 | 1037.3179 | 1014.2768 | 1014.2768 | 1014.2768 | 16.7 | 0 | 16.6911 | 84.9458 | 243.1433 | 243.3545 | 232.8203 | 2.1214 | 3.4621 | 0 | 86 | 62.1029 | 63.4821 | 104.9399 | 8.546 | 129.334 | -1.2554 | 78.1246 | 62.6103 | 49.4995 | 0 | 66.857 | 819.3078 | 815.4734 | 739.2098 | 738.8677 | 733.1745 | 732.2852 | 555.7054 | 552.5449 | 769.7492 | 790.5727 | 1012.7815 | 1021.6564 | 1038.2089 | 1052.666 | 1037.6977 | 1018.7355 | 1039.6113 | 1012.3538 | 1042.7951 | 1012.2238 | 1022.0302 | 1031.6128 | 1002.8309 | 1025.6317 | 1028.946 | 1028.3557 | 1029.8217 | 1030.8291 | 1024.9043 | 996.1883 | 1058.1138 | 1008.1347 | 1023.5085
2025-04-09 19:11 | 9 | 19 | 11 | 6.2817e-272 | 1 | 29.401 | 655.5211 | 0.26671 | 0.007668 | 165.3597 | 165.3597 | 165.3597 | 165.3597 | 12.7366 | 13.7077 | 668.434 | 668.434 | 668.434 | 668.434 | 63.3576 | 50.1628 | 15.7405 | 129.2036 | 15.5992 | 21.7335 | 77.8238 | 1 | 50.1633 | 15 | 22.1 | 221 | 154840 | 237526.2766 | 3543763.5745 | 100.3256 | 0.0031502 | 0.094507 | 0.094507 | 0.094507 | 7.9917 | 1014.4723 | 1011.8862 | 1011.8891 | 1014.4723 | 1037.4877 | 1037.4877 | 1037.4877 | 1037.4877 | 1014.5028 | 1014.5028 | 1014.5028 | 16.6429 | 0 | 16.6508 | 84.7945 | 242.8738 | 243.0732 | 232.8606 | 2.1119 | 3.4457 | 0 | 86 | 61.7896 | 63.3576 | 104.9365 | 8.7593 | 129.2036 | -1.2795 | 78.0844 | 62.6066 | 49.6337 | 0 | 66.8571 | 819.2261 | 815.1953 | 739.1481 | 738.7155 | 733.1311 | 732.1453 | 555.5001 | 552.5021 | 769.8607 | 793.9424 | 1012.9494 | 1022.4864 | 1037.8528 | 1052.2126 | 1037.9832 | 1018.5228 | 1039.7977 | 1012.5883 | 1042.0294 | 1013.0317 | 1023.0587 | 1031.6315 | 1003.8463 | 1026.3306 | 1028.4717 | 1028.5877 | 1030.4351 | 1031.0517 | 1024.5689 | 997.1314 | 1057.88 | 1008.1183 | 1024.527
2025-04-09 19:12 | 9 | 19 | 12 | 6.2817e-272 | 1 | 29.4026 | 656.7074 | 0.26525 | 0.007686 | 165.3686 | 165.3686 | 165.3686 | 165.3686 | 12.7365 | 13.7077 | 668.1742 | 668.1742 | 668.1742 | 668.1742 | 63.1547 | 50.1531 | 15.7401 | 129.2826 | 15.5983 | 21.7337 | 77.8624 | 1 | 50.1538 | 15 | 22.1 | 221 | 154840 | 237527.617 | 3543785.0638 | 100.3062 | -0.0056356 | -0.16907 | -0.16907 | -0.16907 | 7.9917 | 1014.4709 | 1011.8864 | 1011.8868 | 1014.4709 | 1037.3849 | 1037.3849 | 1037.3849 | 1037.3849 | 1014.4381 | 1014.4381 | 1014.4381 | 16.6463 | 0 | 16.6337 | 84.8177 | 242.8961 | 243.1029 | 232.7952 | 2.1096 | 3.4434 | 0 | 86 | 61.7719 | 63.1547 | 104.9337 | 8.8314 | 129.2826 | -1.2168 | 78.085 | 62.5926 | 49.7078 | 0 | 66.8571 | 819.1367 | 814.8713 | 739.0144 | 738.5223 | 733.0232 | 731.9664 | 555.3441 | 552.5821 | 769.9016 | 794.875 | 1012.8634 | 1022.0402 | 1037.7117 | 1052.1009 | 1037.9355 | 1019.1634 | 1040.12 | 1012.4211 | 1041.4417 | 1012.7434 | 1024.2587 | 1031.4974 | 1003.2065 | 1026.3183 | 1028.2623 | 1028.6809 | 1030.604 | 1031.1709 | 1024.6317 | 997.5731 | 1058.7434 | 1007.9866 | 1024.0928
2025-04-09 19:13 | 9 | 19 | 13 | 6.2817e-272 | 1 | 29.4033 | 657.6508 | 0.2635 | 0.0077038 | 165.1483 | 165.1483 | 165.1483 | 165.1483 | 12.7207 | 13.6818 | 666.9142 | 666.9142 | 666.9142 | 666.9142 | 62.944 | 50.0849 | 15.7405 | 129.1417 | 15.5998 | 21.7153 | 77.8777 | 1 | 50.0851 | 15 | 22.1 | 221 | 154840 | 237529.2174 | 3543806.3043 | 100.1697 | 0.0015914 | 0.047742 | 0.047742 | 0.047742 | 7.9917 | 1014.758 | 1012.1822 | 1012.1804 | 1014.758 | 1037.5683 | 1037.5683 | 1037.5683 | 1037.5683 | 1014.7404 | 1014.7404 | 1014.7404 | 16.5708 | 0 | 16.5841 | 84.4841 | 242.3741 | 242.575 | 232.6208 | 2.1202 | 3.4493 | 0 | 86 | 61.7025 | 62.944 | 104.9364 | 9.188 | 129.1417 | -1.2983 | 78.0188 | 62.5939 | 49.7809 | 0 | 66.8567 | 818.8544 | 814.458 | 738.6315 | 738.1677 | 732.7055 | 731.7179 | 555.112 | 552.4725 | 769.8391 | 794.3291 | 1013.9222 | 1023.533 | 1037.3211 | 1051.8165 | 1038.3604 | 1019.9217 | 1041.0509 | 1012.5287 | 1046.1487 | 1012.8196 | 1024.9248 | 1030.9367 | 1000.9433 | 1026.1813 | 1027.0513 | 1028.7502 | 1030.4259 | 1030.9257 | 1024.5865 | 998.1407 | 1058.368 | 1008.8133 | 1024.8567
2025-04-09 19:14 | 9 | 19 | 14 | 6.2817e-272 | 1 | 29.4037 | 657.0693 | 0.25961 | 0.0076997 | 164.9447 | 164.9447 | 164.9447 | 164.9447 | 12.7061 | 13.664 | 666.507 | 666.507 | 666.507 | 666.507 | 62.8315 | 50.0394 | 15.7418 | 129.1169 | 15.5986 | 21.7222 | 77.9484 | 1 | 50.0393 | 15 | 22.1 | 221 | 154840 | 237530.6596 | 3543827.5745 | 100.0787 | 0.0068177 | 0.20453 | 0.20453 | 0.20453 | 7.9917 | 1015.0219 | 1012.4545 | 1012.4528 | 1015.0219 | 1037.6002 | 1037.6002 | 1037.6002 | 1037.6002 | 1015.0221 | 1015.0221 | 1015.0221 | 16.5827 | 0 | 16.5814 | 84.2982 | 242.0258 | 242.2182 | 232.342 | 2.1569 | 3.4515 | 0 | 86 | 61.7926 | 62.8315 | 104.9453 | 9.5932 | 129.1169 | -1.2717 | 78.0438 | 62.6089 | 49.7643 | 0 | 66.8563 | 818.5181 | 813.8666 | 738.1018 | 737.7742 | 732.2461 | 731.4627 | 554.9209 | 552.0861 | 769.6796 | 794.5361 | 1013.1915 | 1022.0226 | 1039.6411 | 1053.3772 | 1038.0564 | 1020.4172 | 1040.1089 | 1012.7734 | 1040.0638 | 1012.2811 | 1025.5277 | 1031.9068 | 1005.6306 | 1027.9557 | 1029.6734 | 1028.8274 | 1031.3021 | 1031.5572 | 1025.0094 | 998.8924 | 1059.1936 | 1008.1947 | 1023.9455
2025-04-09 19:15 | 9 | 19 | 15 | 6.2817e-272 | 1 | 29.402 | 658.9463 | 0.25972 | 0.0077134 | 165.1536 | 165.1536 | 165.1536 | 165.1536 | 12.7216 | 13.6863 | 666.7161 | 666.7161 | 666.7161 | 666.7161 | 62.5948 | 50.0801 | 15.7396 | 129.1911 | 15.5993 | 21.7161 | 77.9387 | 1 | 50.0803 | 15 | 22.1 | 221 | 154840 | 237532.383 | 3543849.0638 | 100.16 | -0.0011102 | -0.033308 | -0.033308 | -0.033308 | 7.9917 | 1014.7417 | 1012.1653 | 1012.1664 | 1014.7417 | 1037.5032 | 1037.5032 | 1037.5032 | 1037.5032 | 1014.7615 | 1014.7615 | 1014.7615 | 16.5813 | 0 | 16.5744 | 84.5137 | 242.4336 | 242.628 | 232.1182 | 2.1229 | 3.4517 | 0 | 86 | 61.6388 | 62.5948 | 104.9309 | 9.61 | 129.1911 | -1.2808 | 78.0218 | 62.5808 | 49.8186 | 0 | 66.8562 | 818.1213 | 813.451 | 737.7261 | 737.5586 | 731.8751 | 731.2196 | 554.7553 | 552.0708 | 769.378 | 793.9092 | 1013.4383 | 1022.2757 | 1038.1587 | 1052.2281 | 1037.9972 | 1020.333 | 1041.033 | 1013.2857 | 1043.6555 | 1012.4357 | 1025.0374 | 1031.807 | 1002.6834 | 1025.9043 | 1028.3974 | 1028.9085 | 1031.3104 | 1031.4289 | 1024.1366 | 997.8044 | 1058.1717 | 1007.5672 | 1023.867
2025-04-09 19:16 | 9 | 19 | 16 | 6.2817e-272 | 1 | 29.4041 | 658.3434 | 0.25992 | 0.0077311 | 164.861 | 164.861 | 164.861 | 164.861 | 12.7 | 13.6616 | 666.1914 | 666.1914 | 666.1914 | 666.1914 | 62.7718 | 50.0311 | 15.7412 | 129.0659 | 15.598 | 21.7098 | 77.9363 | 1 | 50.0305 | 15 | 22.1 | 221 | 154840 | 237533.9362 | 3543870.5319 | 100.0621 | 0.016456 | 0.49367 | 0.49367 | 0.49367 | 7.9917 | 1015.1321 | 1012.567 | 1012.5655 | 1015.1321 | 1037.667 | 1037.667 | 1037.667 | 1037.667 | 1015.0845 | 1015.0845 | 1015.0845 | 16.5529 | 0 | 16.5505 | 84.2193 | 241.8959 | 242.0856 | 231.8766 | 2.1502 | 3.4275 | 0 | 86 | 61.6947 | 62.7718 | 104.9411 | 9.9625 | 129.0659 | -1.3028 | 77.9993 | 62.5942 | 49.8908 | 0 | 66.8563 | 817.7812 | 813.2727 | 737.4242 | 737.3633 | 731.5294 | 731.0478 | 554.5818 | 551.6959 | 769.098 | 793.3607 | 1013.1781 | 1022.1923 | 1039.1781 | 1053.1966 | 1038.1747 | 1020.4087 | 1040.3334 | 1012.5753 | 1041.5632 | 1012.3566 | 1025.9274 | 1032.184 | 1005.2047 | 1027.0055 | 1029.59 | 1029.2668 | 1031.1345 | 1031.6321 | 1025.0138 | 998.3063 | 1059.2645 | 1008.2943 | 1024.7417
2025-04-09 19:17 | 9 | 19 | 17 | 6.2817e-272 | 1 | 29.4042 | 658.1981 | 0.25769 | 0.0077465 | 164.7407 | 164.7407 | 164.7407 | 164.7407 | 12.6914 | 13.6511 | 665.6474 | 665.6474 | 665.6474 | 665.6474 | 62.7435 | 50.0055 | 15.7432 | 128.9369 | 15.6038 | 21.7106 | 77.9203 | 1 | 50.0036 | 15 | 22.1 | 221 | 154840 | 237535.5957 | 3543892.0426 | 100.011 | 0.037908 | 1.1372 | 1.1372 | 1.1372 | 7.9917 | 1015.2855 | 1012.724 | 1012.7234 | 1015.2855 | 1037.8349 | 1037.8349 | 1037.8349 | 1037.8349 | 1015.3064 | 1015.3064 | 1015.3064 | 16.5198 | 0 | 16.5293 | 84.0706 | 241.6448 | 241.82 | 231.6698 | 2.1654 | 3.4455 | 0 | 86 | 61.5746 | 62.7435 | 104.9543 | 10.3657 | 128.9369 | -1.296 | 78.002 | 62.6037 | 49.9526 | 0 | 66.856 | 817.4691 | 813.0879 | 736.979 | 737.079 | 731.1819 | 730.8003 | 554.4354 | 551.4419 | 768.6855 | 792.7588 | 1012.6479 | 1022.9023 | 1039.9119 | 1054.4074 | 1038.5511 | 1021.4481 | 1040.1174 | 1013.0881 | 1040.7249 | 1012.1189 | 1024.8166 | 1032.4826 | 1007.0317 | 1028.103 | 1030.5649 | 1028.303 | 1030.8104 | 1030.82 | 1025.6936 | 998.6596 | 1059.774 | 1008.9913 | 1024.1415
2025-04-09 19:18 | 9 | 19 | 18 | 6.2817e-272 | 1 | 29.4051 | 658.4292 | 0.25708 | 0.0077588 | 164.8231 | 164.8231 | 164.8231 | 164.8231 | 12.6969 | 13.6519 | 665.4907 | 665.4907 | 665.4907 | 665.4907 | 62.8238 | 50.0109 | 15.7387 | 128.9934 | 15.5958 | 21.6933 | 77.9683 | 1 | 50.0107 | 15 | 22.1 | 221 | 154840 | 237537.4468 | 3543913.4894 | 100.0219 | 0.00019105 | 0.0057312 | 0.0057312 | 0.0057312 | 7.9917 | 1015.1877 | 1012.624 | 1012.6236 | 1015.1877 | 1037.7621 | 1037.7621 | 1037.7621 | 1037.7621 | 1015.1617 | 1015.1617 | 1015.1617 | 16.5423 | 0 | 16.5369 | 84.2224 | 241.8253 | 242.0171 | 231.4265 | 2.1621 | 3.4269 | 0 | 86 | 61.5739 | 62.8238 | 104.9249 | 10.5489 | 128.9934 | -1.3817 | 77.9399 | 62.5889 | 49.9994 | 0 | 66.8556 | 817.0264 | 812.9015 | 736.6138 | 736.851 | 730.8298 | 730.6054 | 554.2594 | 551.3737 | 768.3019 | 793.0635 | 1012.5487 | 1022.7419 | 1039.8917 | 1053.6268 | 1037.9291 | 1021.2011 | 1039.7734 | 1013.3602 | 1042.2683 | 1011.9083 | 1025.6817 | 1032.446 | 1005.4789 | 1027.2434 | 1029.9117 | 1028.7423 | 1030.7409 | 1031.263 | 1025.3764 | 998.81 | 1059.4104 | 1008.8857 | 1023.6847
2025-04-09 19:19 | 9 | 19 | 19 | 6.2817e-272 | 1 | 29.4023 | 659.2996 | 0.25771 | 0.007767 | 164.937 | 164.937 | 164.937 | 164.937 | 12.7061 | 13.6587 | 665.3751 | 665.3751 | 665.3751 | 665.3751 | 62.8094 | 50.0248 | 15.7391 | 129.1112 | 15.6009 | 21.7126 | 77.9518 | 1 | 50.0245 | 15 | 22.1 | 221 | 154840 | 237539.1915 | 3543934.9574 | 100.0497 | 0.017281 | 0.51843 | 0.51843 | 0.51843 | 7.9917 | 1015.0191 | 1012.4513 | 1012.4498 | 1015.0191 | 1037.6083 | 1037.6083 | 1037.6083 | 1037.6083 | 1015.0557 | 1015.0557 | 1015.0557 | 16.5513 | 0 | 16.551 | 84.2908 | 242.0441 | 242.2233 | 231.3176 | 2.0888 | 3.4121 | 0 | 86 | 61.2571 | 62.8094 | 104.9273 | 10.6019 | 129.1112 | -1.2739 | 78.0092 | 62.5947 | 50.0239 | 0 | 66.8551 | 816.7713 | 812.7673 | 736.3206 | 736.7617 | 730.5453 | 730.4575 | 554.1094 | 551.2373 | 768.0304 | 791.4746 | 1012.6221 | 1022.3864 | 1040.5098 | 1053.2594 | 1037.8136 | 1021.0845 | 1040.3023 | 1013.6743 | 1040.1845 | 1011.4753 | 1024.0972 | 1032.8447 | 1005.4728 | 1027.4323 | 1029.7732 | 1028.0923 | 1031.1915 | 1031.9898 | 1025.6153 | 998.6691 | 1059.066 | 1008.1987 | 1023.677
2025-04-09 19:20 | 9 | 19 | 20 | 6.2817e-272 | 1 | 29.4035 | 659.376 | 0.26095 | 0.007758 | 165.0106 | 165.0106 | 165.0106 | 165.0106 | 12.7108 | 13.6631 | 665.2498 | 665.2498 | 665.2498 | 665.2498 | 62.6577 | 50.0282 | 15.7394 | 129.108 | 15.5979 | 21.7227 | 77.9995 | 1 | 50.0288 | 15 | 22.1 | 221 | 154840 | 237540.9149 | 3543956.4681 | 100.0564 | 0.0028656 | 0.085969 | 0.085969 | 0.085969 | 7.9917 | 1014.9343 | 1012.3638 | 1012.364 | 1014.9343 | 1037.6123 | 1037.6123 | 1037.6123 | 1037.6123 | 1014.9128 | 1014.9128 | 1014.9128 | 16.5469 | 0 | 16.5535 | 84.3608 | 242.1681 | 242.3447 | 231.2837 | 2.1483 | 3.4334 | 0 | 86 | 61.0584 | 62.6577 | 104.9296 | 10.4945 | 129.108 | -1.2778 | 78.0455 | 62.6052 | 49.9973 | 0 | 66.8549 | 816.5104 | 812.5986 | 736.047 | 736.5993 | 730.2802 | 730.3018 | 553.9477 | 550.997 | 767.7248 | 791.5729 | 1012.7113 | 1022.6928 | 1039.0736 | 1052.3132 | 1037.0768 | 1020.3364 | 1039.2066 | 1013.2219 | 1040.7038 | 1012.4404 | 1024.7513 | 1032.8474 | 1005.0599 | 1026.1434 | 1029.473 | 1028.5609 | 1031.5209 | 1032.3491 | 1024.6783 | 998.497 | 1058.0523 | 1008.4706 | 1025.0513
2025-04-09 19:21 | 9 | 19 | 21 | 6.2817e-272 | 1 | 29.4009 | 661.013 | 0.26094 | 0.0077507 | 164.9783 | 164.9783 | 164.9783 | 164.9783 | 12.7096 | 13.6655 | 665.1847 | 665.1847 | 665.1847 | 665.1847 | 62.3596 | 50.0206 | 15.7386 | 129.2051 | 15.6041 | 21.7096 | 77.9796 | 1 | 50.0204 | 15 | 22.1 | 221 | 154840 | 237542.6087 | 3543977.7174 | 100.0412 | 0.005955 | 0.17865 | 0.17865 | 0.17865 | 7.9917 | 1014.9546 | 1012.3837 | 1012.385 | 1014.9546 | 1037.4861 | 1037.4861 | 1037.4861 | 1037.4861 | 1015.0087 | 1015.0087 | 1015.0087 | 16.5339 | 0 | 16.5383 | 84.3457 | 242.1169 | 242.2687 | 231.2745 | 2.0975 | 3.4343 | 0 | 86 | 60.8164 | 62.3596 | 104.9241 | 10.6401 | 129.2051 | -1.1968 | 77.9984 | 62.5952 | 49.9648 | 0 | 66.855 | 816.225 | 812.4895 | 735.816 | 736.403 | 730.0502 | 730.1473 | 553.7838 | 550.7662 | 767.4578 | 792.7063 | 1012.8596 | 1022.8141 | 1038.4446 | 1051.9257 | 1037.083 | 1020.4426 | 1039.8904 | 1014.0687 | 1043.9248 | 1012.0526 | 1025.2211 | 1031.9357 | 1003.5697 | 1025.9657 | 1028.7804 | 1028.5252 | 1030.7893 | 1032.2989 | 1025.5593 | 999.0501 | 1058.6437 | 1009.6804 | 1024.5704
2025-04-09 19:22 | 9 | 19 | 22 | 6.2817e-272 | 1 | 29.4019 | 661.6928 | 0.25048 | 0.007742 | 162.6043 | 162.6043 | 162.6043 | 162.6043 | 12.541 | 13.6739 | 661.5605 | 661.5605 | 661.5605 | 661.5605 | 62.459 | 50.0432 | 15.7462 | 122.4021 | 15.6048 | 20.633 | 74.0121 | 1 | 50.0438 | 17.9362 | 22.1 | 221 | 154840 | 237544.4255 | 3543998.5106 | 100.0863 | -0.010061 | -0.30184 | -0.30184 | -0.30184 | 7.9917 | 1017.9932 | 1015.5151 | 1015.5123 | 1017.9932 | 1046.3472 | 1046.3472 | 1046.3472 | 1046.3472 | 985.1669 | 985.1669 | 985.1669 | 15.2414 | 0 | 15.1768 | 83.0913 | 238.556 | 238.7073 | 230.951 | 2.1357 | 3.441 | 0 | 86 | 60.6355 | 62.459 | 104.9745 | 9.7431 | 122.4021 | -1.2243 | 74.1305 | 62.5988 | 49.9342 | 0 | 66.8555 | 815.1525 | 811.5321 | 735.1814 | 735.7809 | 729.6999 | 730.2073 | 553.8128 | 550.4929 | 766.9528 | 791.8725 | 984.5844 | 994.7305 | 1004.6896 | 1022.5324 | 1015.2806 | 986.2009 | 1007.523 | 985.267 | 1011.2096 | 989.2103 | 983.9118 | 1000.5339 | 977.78 | 987.6655 | 991.384 | 1002.0304 | 1004.4468 | 1000.9689 | 1004.6319 | 968.4007 | 1020.3891 | 979.1583 | 993.6141
2025-04-09 19:23 | 9 | 19 | 23 | 6.2817e-272 | 1 | 29.4023 | 661.1942 | 0.21946 | 0.0077334 | 159.2975 | 159.2975 | 159.2975 | 159.2975 | 12.3067 | 13.6657 | 656.0273 | 656.0273 | 656.0273 | 656.0273 | 62.5264 | 50.0286 | 15.7484 | 113.6541 | 15.6031 | 19.2782 | 69.2146 | 1 | 50.029 | 18 | 22.1 | 221 | 154840 | 237545.8723 | 3544018.1277 | 100.0572 | -0.024486 | -0.73459 | -0.73459 | -0.73459 | 7.9917 | 1022.2168 | 1019.8677 | 1019.8634 | 1022.2168 | 1057.743 | 1057.743 | 1057.743 | 1057.743 | 943.5636 | 943.5636 | 943.5636 | 13.5153 | 0 | 13.4714 | 81.1235 | 233.2914 | 233.4821 | 230.184 | 2.1814 | 3.4328 | 0 | 86 | 60.8842 | 62.5264 | 104.9894 | 8.7138 | 113.6541 | -1.1837 | 69.2629 | 62.6226 | 49.8984 | 0 | 66.8568 | 811.2546 | 807.5393 | 733.7388 | 734.4023 | 728.9779 | 730.1568 | 553.8188 | 548.5455 | 765.1803 | 790.2081 | 944.492 | 958.6245 | 960.7789 | 976.373 | 979.0628 | 951.1628 | 958.8023 | 947.3552 | 963.5573 | 954.9392 | 938.0274 | 952.2687 | 945.7323 | 938.3049 | 939.3663 | 961.3501 | 964.8726 | 955.9226 | 961.2844 | 941.9322 | 956.0921 | 945.8573 | 954.5953
2025-04-09 19:24 | 9 | 19 | 24 | 6.2817e-272 | 1 | 29.4029 | 661.1152 | 0.20589 | 0.0077157 | 157.0948 | 157.0948 | 157.0948 | 157.0948 | 12.1504 | 13.6531 | 651.8108 | 651.8108 | 651.8108 | 651.8108 | 62.7985 | 50.0126 | 15.7425 | 107.9421 | 15.5977 | 18.4229 | 66.2764 | 1 | 50.0141 | 15.7447 | 22.1 | 221 | 154840 | 237547.3404 | 3544036.383 | 100.0251 | -0.030994 | -0.92982 | -0.92982 | -0.92982 | 7.9917 | 1025.036 | 1022.7732 | 1022.7728 | 1025.036 | 1065.1836 | 1065.1836 | 1065.1836 | 1065.1836 | 914.0477 | 914.0477 | 914.0477 | 12.4192 | 0 | 12.4019 | 79.8042 | 229.7111 | 229.9112 | 229.1469 | 2.1415 | 3.4395 | 0 | 86 | 60.9792 | 62.7985 | 104.9499 | 7.9245 | 107.9421 | -1.2733 | 66.1897 | 62.6727 | 49.8268 | 0 | 66.8538 | 805.7757 | 801.8364 | 731.9804 | 732.6991 | 727.7661 | 729.0685 | 553.3504 | 545.1607 | 762.0354 | 786.5745 | 917.8958 | 930.8247 | 931.3393 | 942.5828 | 947.7645 | 927.8997 | 925.7228 | 922.0459 | 924.2867 | 925.4822 | 910.1468 | 917.8759 | 923.3347 | 908.4899 | 908.3952 | 928.9512 | 933.4691 | 921.2329 | 925.9804 | 918.2896 | 921.0234 | 921.9477 | 925.2446
2025-04-09 19:25 | 9 | 19 | 25 | 6.2817e-272 | 1 | 29.4032 | 660.8394 | 0.20223 | 0.0077092 | 156.5593 | 156.5593 | 156.5593 | 156.5593 | 12.1124 | 13.6581 | 650.9824 | 650.9824 | 650.9824 | 650.9824 | 62.7748 | 50.0226 | 15.7407 | 106.3303 | 15.5981 | 18.2184 | 65.4539 | 1 | 50.0251 | 13.4894 | 22.1 | 221 | 154840 | 237548.5957 | 3544054.1915 | 100.0453 | -0.021936 | -0.65808 | -0.65808 | -0.65808 | 7.9917 | 1025.723 | 1023.4798 | 1023.4821 | 1025.723 | 1067.2819 | 1067.2819 | 1067.2819 | 1067.2819 | 904.1385 | 904.1385 | 904.1385 | 12.1108 | 0 | 12.1116 | 79.4963 | 228.819 | 229.0046 | 228.3228 | 2.1558 | 3.4334 | 0 | 86 | 60.9012 | 62.7748 | 104.9378 | 7.9585 | 106.3303 | -1.2048 | 65.4551 | 62.711 | 49.8014 | 0 | 66.8534 | 801.081 | 796.8971 | 730.5996 | 731.2689 | 726.2971 | 726.8548 | 552.6148 | 542.6921 | 758.9055 | 782.6747 | 907.749 | 921.0945 | 921.0937 | 930.5791 | 935.6007 | 919.1223 | 914.9266 | 912.3243 | 912.5543 | 915.7204 | 899.8305 | 907.1336 | 915.485 | 898.5736 | 899.3423 | 920.0164 | 921.9212 | 910.4045 | 915.2069 | 909.4122 | 910.9712 | 913.5571 | 914.8283
2025-04-09 19:26 | 9 | 19 | 26 | 6.2817e-272 | 1 | 29.4045 | 660.6862 | 0.21191 | 0.0076971 | 156.9065 | 156.9065 | 156.9065 | 156.9065 | 12.1364 | 13.6652 | 651.6702 | 651.6702 | 651.6702 | 651.6702 | 62.6939 | 50.035 | 15.7414 | 107.1597 | 15.5997 | 18.4002 | 65.9864 | 1 | 50.0347 | 14.7234 | 22.1 | 221 | 154840 | 237549.8936 | 3544071.8511 | 100.0699 | 0.014032 | 0.42096 | 0.42096 | 0.42096 | 7.9917 | 1025.2889 | 1023.0326 | 1023.0357 | 1025.2889 | 1066.2017 | 1066.2017 | 1066.2017 | 1066.2017 | 905.2894 | 905.2894 | 905.2894 | 12.2949 | 0 | 12.3004 | 79.7727 | 229.4961 | 229.6701 | 227.7437 | 2.1715 | 3.4425 | 0 | 86 | 60.7789 | 62.6939 | 104.9429 | 7.7422 | 107.1597 | -1.2451 | 66.1084 | 62.75 | 49.7553 | 0 | 66.8533 | 797.4621 | 793.1609 | 729.676 | 730.2697 | 724.9389 | 724.52 | 551.8712 | 541.1054 | 756.2804 | 779.1243 | 908.6934 | 922.5958 | 921.6456 | 929.7762 | 934.231 | 919.2386 | 915.7238 | 912.7793 | 915.0546 | 918.1837 | 901.396 | 908.4619 | 917.3907 | 899.5935 | 900.2691 | 922.4092 | 920.6077 | 910.8557 | 916.9877 | 910.9348 | 912.484 | 914.5936 | 917.0721
2025-04-09 19:27 | 9 | 19 | 27 | 6.2817e-272 | 1 | 29.4025 | 660.8464 | 0.20971 | 0.0076853 | 156.7065 | 156.7065 | 156.7065 | 156.7065 | 12.123 | 13.6654 | 651.6841 | 651.6841 | 651.6841 | 651.6841 | 62.7399 | 50.0384 | 15.7426 | 106.6276 | 15.6003 | 18.2854 | 65.686 | 1 | 50.0378 | 13.7447 | 22.1 | 221 | 154840 | 237551.2979 | 3544089.6809 | 100.0768 | 0.014315 | 0.42946 | 0.42946 | 0.42946 | 7.9917 | 1025.5304 | 1023.2813 | 1023.2813 | 1025.5304 | 1066.8951 | 1066.8951 | 1066.8951 | 1066.8951 | 902.93 | 902.93 | 902.93 | 12.1977 | 0 | 12.2034 | 79.7054 | 229.1907 | 229.3602 | 227.3489 | 2.1571 | 3.437 | 0 | 86 | 60.7428 | 62.7399 | 104.9504 | 7.8206 | 106.6276 | -1.1548 | 65.6959 | 62.7623 | 49.706 | 0 | 66.8526 | 794.9496 | 790.5756 | 728.8429 | 729.3503 | 723.5307 | 722.3681 | 551.0963 | 540.071 | 754.0771 | 775.9646 | 906.6669 | 919.9798 | 918.6576 | 927.13 | 931.4994 | 917.0088 | 912.666 | 910.8216 | 912.074 | 915.7257 | 899.3209 | 905.6561 | 915.4166 | 896.794 | 897.3817 | 921.1535 | 917.6273 | 908.2918 | 914.3902 | 909.0801 | 910.4173 | 912.7661 | 914.4325
2025-04-09 19:28 | 9 | 19 | 28 | 6.2817e-272 | 1 | 29.4011 | 661.8524 | 0.21693 | 0.0076742 | 156.8335 | 156.8335 | 156.8335 | 156.8335 | 12.1326 | 13.6646 | 651.8067 | 651.8067 | 651.8067 | 651.8067 | 62.6142 | 50.0294 | 15.7409 | 106.801 | 15.6024 | 18.3453 | 65.8045 | 1 | 50.0293 | 14.383 | 22.1 | 221 | 154840 | 237552.5319 | 3544107.4255 | 100.0587 | 0.0071397 | 0.21419 | 0.21419 | 0.21419 | 7.9917 | 1025.3574 | 1023.1032 | 1023.1034 | 1025.3574 | 1066.67 | 1066.67 | 1066.67 | 1066.67 | 903.6972 | 903.6972 | 903.6972 | 12.2679 | 0 | 12.2545 | 79.8035 | 229.3784 | 229.5467 | 226.974 | 2.1118 | 3.4291 | 0 | 86 | 61.0209 | 62.6142 | 104.9395 | 7.9241 | 106.801 | -1.1973 | 65.9109 | 62.7582 | 49.6587 | 0 | 66.8522 | 792.9963 | 788.5681 | 728.1194 | 728.4715 | 722.2624 | 720.6394 | 550.4292 | 539.1041 | 752.0712 | 773.0438 | 907.3854 | 921.3071 | 919.4787 | 927.8696 | 932.0258 | 917.5068 | 913.2158 | 911.1623 | 912.9405 | 916.9143 | 900.7033 | 906.5918 | 917.4314 | 897.6814 | 898.5186 | 920.9159 | 917.594 | 908.4772 | 915.1288 | 909.8282 | 911.4665 | 912.3916 | 915.6766
2025-04-09 19:29 | 9 | 19 | 29 | 6.2817e-272 | 1 | 29.3992 | 662.4006 | 0.21549 | 0.0076637 | 156.7034 | 156.7034 | 156.7034 | 156.7034 | 12.1241 | 13.6569 | 651.9039 | 651.9039 | 651.9039 | 651.9039 | 62.5333 | 50.008 | 15.7414 | 106.9666 | 15.6023 | 18.3715 | 65.9234 | 1 | 50.008 | 14.8696 | 22.1 | 221 | 154840 | 237553.8043 | 3544125.0435 | 100.0159 | -6.8173e-05 | -0.0020451 | -0.0020451 | -0.0020451 | 7.9917 | 1025.5102 | 1023.2607 | 1023.2593 | 1025.5102 | 1066.4535 | 1066.4535 | 1066.4535 | 1066.4535 | 905.1795 | 905.1795 | 905.1795 | 12.282 | 0 | 12.2823 | 79.686 | 229.1809 | 229.377 | 226.8539 | 2.101 | 3.4171 | 0 | 86 | 61.2372 | 62.5333 | 104.9427 | 8.1227 | 106.9666 | -1.229 | 66.0051 | 62.7737 | 49.6148 | 0 | 66.8525 | 791.6432 | 787.16 | 727.4976 | 727.6275 | 721.1236 | 719.097 | 549.7232 | 538.169 | 750.3209 | 770.3213 | 909.1499 | 922.9183 | 920.2347 | 929.5697 | 933.6759 | 919.0157 | 914.9685 | 912.499 | 913.8897 | 917.8685 | 901.8735 | 908.1097 | 918.6296 | 899.4826 | 900.2522 | 923.6088 | 918.9194 | 910.8143 | 917.1807 | 911.3515 | 912.8552 | 913.0052 | 916.6631
2025-04-09 19:30 | 9 | 19 | 30 | 6.2817e-272 | 1 | 29.401 | 662.6196 | 0.22126 | 0.0076545 | 157.1685 | 157.1685 | 157.1685 | 157.1685 | 12.1564 | 13.6553 | 652.2538 | 652.2538 | 652.2538 | 652.2538 | 62.6176 | 50.0081 | 15.7382 | 108.1489 | 15.5973 | 18.5347 | 66.5976 | 1 | 50.0086 | 15.7872 | 22.1 | 221 | 154840 | 237555.2766 | 3544142.5957 | 100.0161 | -0.0015041 | -0.045125 | -0.045125 | -0.045125 | 7.9917 | 1024.9291 | 1022.6621 | 1022.663 | 1024.9291 | 1064.9136 | 1064.9136 | 1064.9136 | 1064.9136 | 908.5192 | 908.5192 | 908.5192 | 12.509 | 0 | 12.5166 | 80.056 | 229.9651 | 230.1564 | 226.906 | 2.1323 | 3.4307 | 0 | 86 | 60.9951 | 62.6176 | 104.921 | 8.25 | 108.1489 | -1.2093 | 66.5917 | 62.7784 | 49.5789 | 0 | 66.8523 | 790.5516 | 786.0235 | 726.9716 | 726.9035 | 720.1365 | 717.6606 | 549.1063 | 537.3608 | 748.8015 | 768.1266 | 912.8091 | 926.7091 | 923.5283 | 932.3745 | 936.1004 | 921.3277 | 918.4813 | 915.4509 | 918.8453 | 921.6445 | 905.4983 | 911.246 | 922.4462 | 902.3972 | 903.192 | 926.5099 | 921.0218 | 913.415 | 920.339 | 914.8081 | 916.7017 | 915.9966 | 921.5045
2025-04-09 19:31 | 9 | 19 | 31 | 6.2817e-272 | 1 | 29.4046 | 662.8257 | 0.22153 | 0.0076465 | 156.5881 | 156.5881 | 156.5881 | 156.5881 | 12.1139 | 13.6642 | 651.4634 | 651.4634 | 651.4634 | 651.4634 | 62.5279 | 50.0238 | 15.7415 | 106.4235 | 15.6018 | 18.2839 | 65.6313 | 1 | 50.0234 | 13.2766 | 22.1 | 221 | 154840 | 237556.5745 | 3544160.4468 | 100.0476 | 0.016434 | 0.49301 | 0.49301 | 0.49301 | 7.9917 | 1025.6974 | 1023.4534 | 1023.453 | 1025.6974 | 1067.1615 | 1067.1615 | 1067.1615 | 1067.1615 | 901.9527 | 901.9527 | 901.9527 | 12.1932 | 0 | 12.1845 | 79.6773 | 229.0501 | 229.234 | 226.8728 | 2.1641 | 3.4135 | 0 | 86 | 60.9709 | 62.5279 | 104.9431 | 8.1365 | 106.4235 | -1.248 | 65.6907 | 62.7914 | 49.5509 | 0 | 66.852 | 789.6867 | 785.3173 | 726.4662 | 726.1451 | 719.2514 | 716.4458 | 548.3899 | 536.74 | 747.4965 | 765.8164 | 905.6477 | 919.253 | 915.7401 | 925.2434 | 929.4461 | 914.8693 | 911.309 | 910.3621 | 910.557 | 915.8185 | 899.4711 | 904.2438 | 914.9688 | 895.9426 | 895.7665 | 921.0982 | 915.9565 | 907.8985 | 913.0369 | 908.6316 | 910.3016 | 910.1923 | 913.7153
2025-04-09 19:32 | 9 | 19 | 32 | 6.2817e-272 | 1 | 29.4024 | 662.4227 | 0.22336 | 0.0076464 | 157.0335 | 157.0335 | 157.0335 | 157.0335 | 12.1462 | 13.6576 | 651.6977 | 651.6977 | 651.6977 | 651.6977 | 62.5108 | 50.0084 | 15.7393 | 107.6784 | 15.6013 | 18.4493 | 66.3352 | 1 | 50.008 | 15.3617 | 22.1 | 221 | 154840 | 237557.9362 | 3544178.234 | 100.0168 | 0.009395 | 0.28185 | 0.28185 | 0.28185 | 7.9917 | 1025.1145 | 1022.8523 | 1022.8515 | 1025.1145 | 1065.5268 | 1065.5268 | 1065.5268 | 1065.5268 | 906.3058 | 906.3058 | 906.3058 | 12.4162 | 0 | 12.4179 | 79.9826 | 229.8303 | 230.0076 | 226.8895 | 2.1607 | 3.4341 | 0 | 86 | 60.7196 | 62.5108 | 104.9288 | 8.3426 | 107.6784 | -1.2438 | 66.2847 | 62.7868 | 49.5496 | 0 | 66.8515 | 788.9205 | 784.5601 | 726.1141 | 725.5224 | 718.4497 | 715.3559 | 547.6615 | 535.8794 | 746.2098 | 764.3466 | 910.1955 | 923.9511 | 919.6165 | 929.7896 | 933.705 | 918.9795 | 916.2101 | 913.9013 | 916.0385 | 920.1074 | 903.2003 | 908.9301 | 919.3951 | 899.9876 | 900.1201 | 925.3226 | 919.8545 | 912.5221 | 918.6861 | 912.7906 | 914.9224 | 913.4518 | 918.3611
2025-04-09 19:33 | 9 | 19 | 33 | 6.2817e-272 | 1 | 29.3993 | 664.9044 | 0.24798 | 0.0076389 | 156.8287 | 156.8287 | 156.8287 | 156.8287 | 12.1329 | 13.6682 | 650.7123 | 650.7123 | 650.7123 | 650.7123 | 62.2429 | 50.0197 | 15.7404 | 106.8852 | 15.6004 | 18.3394 | 65.8489 | 1 | 50.019 | 13.5319 | 22.1 | 221 | 154840 | 237559.383 | 3544196 | 100.0393 | 0.019234 | 0.57703 | 0.57703 | 0.57703 | 7.9917 | 1025.353 | 1023.0979 | 1023.1 | 1025.353 | 1066.5602 | 1066.5602 | 1066.5602 | 1066.5602 | 901.7702 | 901.7702 | 901.7702 | 12.2332 | 0 | 12.2398 | 79.8516 | 229.4479 | 229.6176 | 226.9086 | 2.0917 | 3.4417 | 0 | 86 | 60.399 | 62.2429 | 104.9363 | 8.3606 | 106.8852 | -1.2321 | 65.89 | 62.7896 | 49.5157 | 0 | 66.8514 | 788.1425 | 783.833 | 725.5999 | 724.7756 | 717.7376 | 714.4497 | 547.0107 | 535.2748 | 745.1789 | 763.1261 | 905.2319 | 919.2018 | 915.261 | 925.2379 | 929.5892 | 914.614 | 911.4448 | 910.0455 | 910.2881 | 915.4458 | 899.1703 | 903.912 | 914.9896 | 895.7337 | 895.9383 | 921.4447 | 915.599 | 907.931 | 913.5121 | 907.9797 | 910.1647 | 909.2517 | 913.6774
2025-04-09 19:34 | 9 | 19 | 34 | 6.2817e-272 | 1 | 29.4008 | 666.2142 | 0.3198 | 0.0076234 | 156.9171 | 156.9171 | 156.9171 | 156.9171 | 12.1386 | 13.6705 | 650.7878 | 650.7878 | 650.7878 | 650.7878 | 62.2005 | 50.0228 | 15.742 | 106.7801 | 15.6019 | 18.3134 | 65.8081 | 1 | 50.0235 | 14.0426 | 22.1 | 221 | 154840 | 237560.6809 | 3544213.7872 | 100.0456 | -0.010897 | -0.32691 | -0.32691 | -0.32691 | 7.9917 | 1025.2485 | 1022.9904 | 1022.9879 | 1025.2485 | 1066.6968 | 1066.6968 | 1066.6968 | 1066.6968 | 901.6554 | 901.6554 | 901.6554 | 12.2529 | 0 | 12.2417 | 79.8686 | 229.5454 | 229.7407 | 226.9597 | 2.1077 | 3.4349 | 0 | 86 | 60.2829 | 62.2005 | 104.9467 | 8.4445 | 106.7801 | -1.211 | 65.7965 | 62.786 | 49.4543 | 0 | 66.8515 | 787.5486 | 783.2399 | 725.1066 | 724.3097 | 717.0411 | 713.6627 | 546.5519 | 534.6414 | 744.2586 | 761.8654 | 905.4217 | 919.2179 | 915.1688 | 924.7571 | 929.2838 | 914.1041 | 911.0688 | 910.0081 | 909.8626 | 915.2369 | 898.8897 | 904.2281 | 914.5457 | 895.6989 | 895.3225 | 921.4448 | 915.7614 | 908.473 | 913.2943 | 907.7931 | 910.1806 | 909.2711 | 913.1595
2025-04-09 19:35 | 9 | 19 | 35 | 6.2817e-272 | 1 | 29.4012 | 666.5469 | 0.32308 | 0.0076137 | 157.0585 | 157.0585 | 157.0585 | 157.0585 | 12.1485 | 13.6617 | 651.0344 | 651.0344 | 651.0344 | 651.0344 | 62.3975 | 50.0122 | 15.7401 | 107.4217 | 15.603 | 18.4357 | 66.228 | 1 | 50.0128 | 15.1489 | 22.1 | 221 | 154840 | 237562.234 | 3544231.5745 | 100.0243 | -0.028549 | -0.85648 | -0.85648 | -0.85648 | 7.9917 | 1025.0698 | 1022.8077 | 1022.8081 | 1025.0698 | 1065.8606 | 1065.8606 | 1065.8606 | 1065.8606 | 904.386 | 904.386 | 904.386 | 12.3925 | 0 | 12.3879 | 79.9513 | 229.7963 | 229.9735 | 226.8267 | 2.1354 | 3.4338 | 0 | 86 | 60.3903 | 62.3975 | 104.9342 | 8.3931 | 107.4217 | -1.2662 | 66.236 | 62.7928 | 49.4162 | 0 | 66.851 | 787.1017 | 782.4922 | 724.6096 | 723.8935 | 716.3808 | 713.0547 | 546.0751 | 533.8896 | 743.5156 | 760.7867 | 908.758 | 922.6979 | 918.6324 | 928.004 | 932.1428 | 917.2693 | 914.2216 | 911.9671 | 912.9156 | 917.3051 | 900.9333 | 907.0183 | 918.4361 | 898.0857 | 899.0269 | 922.4725 | 917.762 | 910.2001 | 916.3151 | 910.952 | 913.0134 | 911.0559 | 916.5683
2025-04-09 19:36 | 9 | 19 | 36 | 6.2817e-272 | 1 | 29.4019 | 666.8216 | 0.32328 | 0.0076062 | 156.8573 | 156.8573 | 156.8573 | 156.8573 | 12.1339 | 13.6569 | 650.7569 | 650.7569 | 650.7569 | 650.7569 | 62.4142 | 50.0012 | 15.7392 | 106.8712 | 15.6039 | 18.3285 | 65.8651 | 1 | 50.0023 | 14.2128 | 22.1 | 221 | 154840 | 237563.5532 | 3544249.3617 | 100.0024 | -0.02804 | -0.8412 | -0.8412 | -0.8412 | 7.9917 | 1025.3334 | 1023.0779 | 1023.0745 | 1025.3334 | 1066.5781 | 1066.5781 | 1066.5781 | 1066.5781 | 902.4469 | 902.4469 | 902.4469 | 12.2881 | 0 | 12.2714 | 79.8355 | 229.4504 | 229.6379 | 226.689 | 2.144 | 3.4569 | 0 | 86 | 60.3815 | 62.4142 | 104.9279 | 8.5413 | 106.8712 | -1.1947 | 65.8508 | 62.7838 | 49.3865 | 0 | 66.8509 | 786.7125 | 781.9434 | 724.1332 | 723.4076 | 715.7934 | 712.4118 | 545.4415 | 533.3022 | 742.858 | 759.6219 | 906.5152 | 920.3641 | 916.5717 | 926.0142 | 930.1362 | 915.335 | 912.1051 | 910.1732 | 910.5904 | 915.3942 | 899.4496 | 905.3667 | 916.636 | 896.2214 | 896.8824 | 920.5266 | 916.2049 | 908.0831 | 914.3653 | 908.8724 | 911.0625 | 909.291 | 914.7857
2025-04-09 19:37 | 9 | 19 | 37 | 6.2817e-272 | 1 | 29.4026 | 666.4259 | 0.31819 | 0.0076135 | 156.9719 | 156.9719 | 156.9719 | 156.9719 | 12.1418 | 13.6488 | 650.9008 | 650.9008 | 650.9008 | 650.9008 | 61.9646 | 49.9615 | 15.7411 | 107.5153 | 15.5975 | 18.4749 | 66.2822 | 1 | 49.9617 | 15.5217 | 22.1 | 221 | 154840 | 237564.9783 | 3544266.9565 | 99.9229 | -0.013894 | -0.41682 | -0.41682 | -0.41682 | 7.9917 | 1025.1939 | 1022.9348 | 1022.9328 | 1025.1939 | 1065.7387 | 1065.7387 | 1065.7387 | 1065.7387 | 904.9128 | 904.9128 | 904.9128 | 12.3652 | 0 | 12.3771 | 79.7712 | 229.5334 | 229.6927 | 226.6051 | 2.1361 | 3.4377 | 0 | 86 | 60.2745 | 61.9646 | 104.9409 | 8.5745 | 107.5153 | -1.2244 | 66.3768 | 62.7827 | 49.4172 | 0 | 66.8508 | 786.1923 | 781.2453 | 723.5369 | 722.94 | 715.213 | 711.779 | 544.7897 | 532.5878 | 742.2436 | 758.6807 | 908.5435 | 922.2767 | 918.4046 | 927.9732 | 931.9515 | 917.2572 | 914.6053 | 912.7427 | 914.3293 | 918.3928 | 902.5917 | 907.6677 | 919.4424 | 898.7196 | 899.6786 | 923.7193 | 918.0667 | 910.7203 | 916.9453 | 911.1628 | 913.3075 | 911.3818 | 917.6979
2025-04-09 19:38 | 9 | 19 | 38 | 6.2817e-272 | 1 | 29.4002 | 667.6293 | 0.25275 | 0.0076197 | 156.7192 | 156.7192 | 156.7192 | 156.7192 | 12.1248 | 13.6437 | 650.056 | 650.056 | 650.056 | 650.056 | 61.7528 | 49.9409 | 15.7399 | 107.0417 | 15.5997 | 18.315 | 66.0219 | 1 | 49.9408 | 14.2553 | 22.1 | 221 | 154840 | 237566.4255 | 3544284.617 | 99.8819 | 0.010617 | 0.31851 | 0.31851 | 0.31851 | 7.9917 | 1025.4955 | 1023.2462 | 1023.2462 | 1025.4955 | 1066.3564 | 1066.3564 | 1066.3564 | 1066.3564 | 902.7568 | 902.7568 | 902.7568 | 12.2473 | 0 | 12.2414 | 79.5825 | 229.0919 | 229.2626 | 226.3039 | 2.0785 | 3.4322 | 0 | 86 | 60.1509 | 61.7528 | 104.9325 | 8.4809 | 107.0417 | -1.3015 | 65.8023 | 62.7767 | 49.4388 | 0 | 66.8499 | 785.6522 | 780.5564 | 722.8167 | 722.3806 | 714.4405 | 711.2109 | 544.1489 | 531.7771 | 741.6462 | 757.575 | 906.3179 | 919.7641 | 916.3745 | 926.2292 | 930.1465 | 915.1524 | 912.2324 | 910.4072 | 911.7651 | 916.1365 | 900.1763 | 905.4083 | 917.1695 | 896.7303 | 897.3097 | 921.4926 | 916.5087 | 908.5459 | 914.7803 | 909.1683 | 911.2309 | 909.8811 | 915.2444
2025-04-09 19:39 | 9 | 19 | 39 | 6.2817e-272 | 1 | 29.3995 | 669.3266 | 0.27866 | 0.0076217 | 156.7717 | 156.7717 | 156.7717 | 156.7717 | 12.1289 | 13.6501 | 650.0265 | 650.0265 | 650.0265 | 650.0265 | 61.6305 | 49.9484 | 15.7398 | 107.0518 | 15.5996 | 18.37 | 66.0199 | 1 | 49.9483 | 14.7234 | 22.1 | 221 | 154840 | 237567.7447 | 3544302.3617 | 99.8968 | 0.0034052 | 0.10215 | 0.10215 | 0.10215 | 7.9917 | 1025.424 | 1023.1717 | 1023.1723 | 1025.424 | 1066.3423 | 1066.3423 | 1066.3423 | 1066.3423 | 902.1308 | 902.1308 | 902.1308 | 12.2525 | 0 | 12.2636 | 79.7253 | 229.2891 | 229.4744 | 226.0311 | 2.0903 | 3.4187 | 0 | 86 | 60.0058 | 61.6305 | 104.9319 | 8.506 | 107.0518 | -1.0318 | 65.9998 | 62.7859 | 49.4468 | 0 | 66.8498 | 785.0245 | 779.7715 | 722.1418 | 721.9209 | 713.7551 | 710.7858 | 543.5365 | 531.1955 | 741.0103 | 756.603 | 905.5809 | 919.0857 | 915.8747 | 925.0923 | 928.8444 | 914.6631 | 911.9288 | 909.4186 | 911.2353 | 915.8386 | 899.5939 | 904.8526 | 916.2233 | 896.1899 | 896.3082 | 921.5077 | 915.9876 | 908.1387 | 914.691 | 908.3559 | 910.5927 | 909.032 | 914.2677
2025-04-09 19:40 | 9 | 19 | 40 | 6.2817e-272 | 1 | 29.3996 | 670.6439 | 0.30834 | 0.0076131 | 156.8114 | 156.8114 | 156.8114 | 156.8114 | 12.1316 | 13.6563 | 649.7074 | 649.7074 | 649.7074 | 649.7074 | 61.5535 | 49.9586 | 15.74 | 107.0279 | 15.5999 | 18.3894 | 65.9575 | 1 | 49.9585 | 14.1702 | 22.1 | 221 | 154840 | 237569.2979 | 3544320.1064 | 99.9173 | 0.0034186 | 0.10256 | 0.10256 | 0.10256 | 7.9917 | 1025.3726 | 1023.1191 | 1023.12 | 1025.3726 | 1066.373 | 1066.373 | 1066.373 | 1066.373 | 901.136 | 901.136 | 901.136 | 12.2179 | 0 | 12.231 | 79.7133 | 229.3093 | 229.4993 | 225.8741 | 2.1076 | 3.4217 | 0 | 86 | 59.8591 | 61.5535 | 104.9333 | 8.4468 | 107.0279 | -1.3262 | 66.0695 | 62.774 | 49.4107 | 0 | 66.8496 | 784.4817 | 779.1239 | 721.6089 | 721.4372 | 713.1641 | 710.263 | 542.9158 | 530.4345 | 740.402 | 755.7404 | 904.2016 | 917.9684 | 915.0023 | 924.3327 | 927.8731 | 913.392 | 910.8476 | 908.6437 | 910.3159 | 915.1427 | 898.4516 | 903.872 | 915.7908 | 895.3639 | 895.3515 | 920.0121 | 914.7481 | 906.3175 | 913.0889 | 907.9036 | 909.4853 | 908.5119 | 913.906
2025-04-09 19:41 | 9 | 19 | 41 | 6.2817e-272 | 1 | 29.402 | 671.5723 | 0.32101 | 0.0076036 | 156.6835 | 156.6835 | 156.6835 | 156.6835 | 12.1216 | 13.654 | 649.2486 | 649.2486 | 649.2486 | 649.2486 | 61.6562 | 49.9589 | 15.7384 | 106.6511 | 15.5973 | 18.3132 | 65.7923 | 1 | 49.9596 | 14.0851 | 22.1 | 221 | 154840 | 237570.5957 | 3544337.8511 | 99.9179 | 0.0011875 | 0.035624 | 0.035624 | 0.035624 | 7.9917 | 1025.554 | 1023.306 | 1023.3053 | 1025.554 | 1066.8655 | 1066.8655 | 1066.8655 | 1066.8655 | 899.6036 | 899.6036 | 899.6036 | 12.1724 | 0 | 12.1765 | 79.6026 | 229.0765 | 229.2651 | 225.8084 | 2.1266 | 3.4281 | 0 | 86 | 59.7977 | 61.6562 | 104.9228 | 8.4113 | 106.6511 | -1.2337 | 65.7959 | 62.804 | 49.377 | 0 | 66.8495 | 784.068 | 778.596 | 721.1177 | 721.0205 | 712.6754 | 709.8113 | 542.0921 | 529.832 | 739.8661 | 755.1077 | 902.4758 | 916.2566 | 913.2698 | 922.5709 | 926.2621 | 912.5351 | 909.3407 | 906.6692 | 908.2019 | 913.5905 | 896.029 | 902.3697 | 914.1568 | 893.6799 | 893.5635 | 918.6079 | 913.6483 | 905.0182 | 911.1271 | 906.9158 | 908.3565 | 907.983 | 912.0987
2025-04-09 19:42 | 9 | 19 | 42 | 6.2817e-272 | 1 | 29.4033 | 672.3356 | 0.31186 | 0.0076031 | 156.6546 | 156.6546 | 156.6546 | 156.6546 | 12.1191 | 13.6426 | 649.0145 | 649.0145 | 649.0145 | 649.0145 | 61.9317 | 49.9456 | 15.7425 | 106.7479 | 15.5998 | 18.3555 | 65.8806 | 1 | 49.9459 | 14.1702 | 22.1 | 221 | 154840 | 237572.0851 | 3544355.6596 | 99.8913 | -0.00037564 | -0.011269 | -0.011269 | -0.011269 | 7.9917 | 1025.6015 | 1023.3549 | 1023.3562 | 1025.6015 | 1066.7383 | 1066.7383 | 1066.7383 | 1066.7383 | 900.9439 | 900.9439 | 900.9439 | 12.2226 | 0 | 12.2272 | 79.5756 | 229.0214 | 229.2091 | 225.6795 | 2.106 | 3.4287 | 0 | 86 | 59.9023 | 61.9317 | 104.9502 | 8.4264 | 106.7479 | -1.2321 | 65.9479 | 62.784 | 49.3765 | 0 | 66.849 | 783.7409 | 778.2274 | 720.6656 | 720.6348 | 712.2488 | 709.384 | 541.2868 | 529.2063 | 739.3599 | 754.4997 | 903.7846 | 917.6224 | 914.2616 | 923.8867 | 927.4657 | 913.4471 | 910.4258 | 907.9031 | 909.9459 | 914.9204 | 897.5818 | 903.9119 | 915.4623 | 894.5171 | 895.2253 | 921.0222 | 914.8117 | 906.8242 | 912.8482 | 908.0513 | 909.411 | 908.7732 | 913.4478
2025-04-09 19:43 | 9 | 19 | 43 | 6.2817e-272 | 1 | 29.4048 | 671.4937 | 0.31551 | 0.00759 | 156.6619 | 156.6619 | 156.6619 | 156.6619 | 12.119 | 13.637 | 649.1433 | 649.1433 | 649.1433 | 649.1433 | 62.4465 | 49.9583 | 15.7414 | 106.8121 | 15.6004 | 18.3479 | 65.8906 | 1 | 49.9581 | 14.383 | 22.1 | 221 | 154840 | 237573.4681 | 3544373.4043 | 99.9166 | 0.0066208 | 0.19862 | 0.19862 | 0.19862 | 7.9917 | 1025.6019 | 1023.356 | 1023.3553 | 1025.6019 | 1066.6551 | 1066.6551 | 1066.6551 | 1066.6551 | 901.5296 | 901.5296 | 901.5296 | 12.2784 | 0 | 12.272 | 79.7425 | 229.1643 | 229.3559 | 225.6147 | 2.1628 | 3.4382 | 0 | 86 | 59.9145 | 62.4465 | 104.9426 | 8.2142 | 106.8121 | -1.2496 | 65.9205 | 62.7786 | 49.3229 | 0 | 66.8495 | 783.5103 | 777.885 | 720.3304 | 720.2995 | 711.9154 | 709.069 | 540.5834 | 528.3752 | 738.8661 | 753.8468 | 904.1469 | 917.892 | 914.7127 | 924.3558 | 927.7552 | 914.0519 | 910.6701 | 908.5446 | 910.2473 | 915.3671 | 898.2724 | 904.7951 | 915.903 | 894.9815 | 895.1978 | 921.4301 | 915.5822 | 907.2702 | 913.7174 | 908.9837 | 910.5148 | 909.9055 | 914.4274
2025-04-09 19:44 | 9 | 19 | 44 | 6.2817e-272 | 1 | 29.4048 | 671.0091 | 0.3198 | 0.0075827 | 156.4635 | 156.4635 | 156.4635 | 156.4635 | 12.105 | 13.6136 | 650.0866 | 650.0866 | 650.0866 | 650.0866 | 63.3732 | 49.9468 | 15.7396 | 106.8354 | 15.6009 | 18.3388 | 65.9788 | 1 | 49.9472 | 14.1702 | 22.1 | 221 | 154840 | 237574.7234 | 3544391.1489 | 99.8936 | 0.0022058 | 0.066174 | 0.066174 | 0.066174 | 7.9917 | 1025.8534 | 1023.6147 | 1023.6145 | 1025.8534 | 1066.6243 | 1066.6243 | 1066.6243 | 1066.6243 | 903.9786 | 903.9786 | 903.9786 | 12.3506 | 0 | 12.3291 | 79.5618 | 228.8336 | 229.0351 | 225.6039 | 2.1744 | 3.4429 | 0 | 86 | 60.2948 | 63.3732 | 104.9304 | 8.2687 | 106.8354 | -1.4678 | 65.8879 | 62.78 | 49.2959 | 0 | 66.8489 | 783.6311 | 777.902 | 720.0924 | 720.1012 | 711.6338 | 708.8228 | 539.8049 | 527.8099 | 738.5365 | 753.1411 | 907.2828 | 920.268 | 916.5219 | 926.7271 | 930.1485 | 916.3739 | 912.9293 | 910.9507 | 912.312 | 918.0011 | 900.7907 | 907.7238 | 918.104 | 897.1901 | 897.0467 | 924.3948 | 918.0512 | 910.2395 | 916.4341 | 911.5101 | 913.0769 | 911.9806 | 916.6905
2025-04-09 19:45 | 9 | 19 | 45 | 6.2817e-272 | 1 | 29.4038 | 672.0287 | 0.31332 | 0.007578 | 156.4516 | 156.4516 | 156.4516 | 156.4516 | 12.1045 | 13.6055 | 650.862 | 650.862 | 650.862 | 650.862 | 64.0522 | 49.9618 | 15.7403 | 106.8349 | 15.5981 | 18.3334 | 65.9745 | 1 | 49.9623 | 14.383 | 22.1 | 221 | 154840 | 237576.2766 | 3544408.8936 | 99.9236 | -0.0031554 | -0.094663 | -0.094663 | -0.094663 | 7.9917 | 1025.8645 | 1023.6268 | 1023.6272 | 1025.8645 | 1066.6257 | 1066.6257 | 1066.6257 | 1066.6257 | 903.9781 | 903.9781 | 903.9781 | 12.3706 | 0 | 12.3663 | 79.5744 | 228.8165 | 229.0039 | 225.5052 | 2.1628 | 3.4429 | 0 | 86 | 60.5369 | 64.0522 | 104.9354 | 8.2808 | 106.8349 | -1.284 | 65.8683 | 62.7788 | 49.2745 | 0 | 66.8485 | 783.8141 | 778.0103 | 720.0081 | 719.9824 | 711.4722 | 708.7089 | 539.1028 | 527.1083 | 738.2909 | 752.6567 | 907.2448 | 920.7783 | 917.0643 | 926.8306 | 930.1568 | 916.6277 | 913.1393 | 910.5117 | 912.1886 | 917.8263 | 900.0154 | 907.7841 | 918.4882 | 897.0473 | 897.5126 | 923.9523 | 918.1296 | 910.0299 | 915.7384 | 911.7834 | 913.0126 | 912.2954 | 916.4114
2025-04-09 19:46 | 9 | 19 | 46 | 6.2817e-272 | 1 | 29.4083 | 671.517 | 0.31747 | 0.0075705 | 156.3761 | 156.3761 | 156.3761 | 156.3761 | 12.0974 | 13.5964 | 651.8013 | 651.8013 | 651.8013 | 651.8013 | 65.0812 | 49.9906 | 15.743 | 106.9669 | 15.601 | 18.4048 | 66.0697 | 1 | 49.9921 | 14.1304 | 22.1 | 221 | 154840 | 237577.5435 | 3544426.3913 | 99.9812 | -0.038029 | -1.1409 | -1.1409 | -1.1409 | 7.9917 | 1025.9959 | 1023.762 | 1023.7615 | 1025.9959 | 1066.4528 | 1066.4528 | 1066.4528 | 1066.4528 | 905.0848 | 905.0848 | 905.0848 | 12.4339 | 0 | 12.4564 | 79.7349 | 228.8718 | 229.0536 | 225.4721 | 2.2561 | 3.46 | 0 | 86 | 60.6491 | 65.0812 | 104.9532 | 8.1294 | 106.9669 | -1.3272 | 66.125 | 62.7965 | 49.2488 | 0 | 66.8479 | 784.1123 | 778.2267 | 719.9721 | 719.9609 | 711.4594 | 708.6783 | 538.3016 | 526.7023 | 738.1001 | 752.4318 | 908.0526 | 921.8326 | 917.5586 | 927.595 | 930.8165 | 917.833 | 914.1552 | 911.9515 | 913.1726 | 919.0914 | 901.0243 | 908.6526 | 919.507 | 897.922 | 898.1992 | 925.4939 | 919.2927 | 911.0447 | 917.2921 | 913.3242 | 914.6084 | 913.2649 | 917.9831
2025-04-09 19:47 | 9 | 19 | 47 | 6.2817e-272 | 1 | 29.4114 | 668.3157 | 0.3213 | 0.0075718 | 156.3091 | 156.3091 | 156.3091 | 156.3091 | 12.0914 | 13.5823 | 653.1308 | 653.1308 | 653.1308 | 653.1308 | 65.9197 | 49.9987 | 15.7442 | 106.8695 | 15.6036 | 18.3934 | 66.0402 | 1 | 49.997 | 13.8298 | 22.1 | 221 | 154840 | 237578.8511 | 3544443.9574 | 99.9973 | 0.042935 | 1.2881 | 1.2881 | 1.2881 | 7.9917 | 1026.1011 | 1023.8711 | 1023.8679 | 1026.1011 | 1066.5804 | 1066.5804 | 1066.5804 | 1066.5804 | 907.5673 | 907.5673 | 907.5673 | 12.5372 | 0 | 12.526 | 79.6764 | 228.8036 | 228.9673 | 225.5313 | 2.3218 | 3.4678 | 0 | 86 | 61.4057 | 65.9197 | 104.9611 | 8.1896 | 106.8695 | -1.2233 | 66.0838 | 62.7784 | 49.2577 | 0 | 66.8475 | 784.8094 | 778.9253 | 720.1467 | 720.1513 | 711.5985 | 708.8125 | 537.6327 | 526.0539 | 738.1564 | 752.2684 | 910.5825 | 925.422 | 921.1637 | 931.6648 | 934.6733 | 920.7108 | 916.6579 | 913.8972 | 915.114 | 921.3035 | 903.336 | 911.5227 | 923.2553 | 900.9162 | 901.0533 | 926.2011 | 921.1827 | 912.8329 | 919.9042 | 915.1264 | 916.1781 | 915.3684 | 920.7404
2025-04-09 19:48 | 9 | 19 | 48 | 6.2817e-272 | 1 | 29.4076 | 667.2437 | 0.33026 | 0.0075527 | 156.1515 | 156.1515 | 156.1515 | 156.1515 | 12.0818 | 13.5824 | 653.5662 | 653.5662 | 653.5662 | 653.5662 | 66.204 | 50.0105 | 15.7387 | 106.3721 | 15.5998 | 18.2825 | 65.6866 | 1 | 50.0114 | 13.9149 | 22.1 | 221 | 154840 | 237580.3404 | 3544461.7447 | 100.021 | -0.007809 | -0.23427 | -0.23427 | -0.23427 | 7.9917 | 1026.2743 | 1024.0485 | 1024.0496 | 1026.2743 | 1067.2279 | 1067.2279 | 1067.2279 | 1067.2279 | 905.8286 | 905.8286 | 905.8286 | 12.4278 | 0 | 12.4267 | 79.6284 | 228.5421 | 228.6819 | 225.6725 | 2.2706 | 3.4538 | 0 | 86 | 61.8257 | 66.204 | 104.9249 | 8.2435 | 106.3721 | -1.2113 | 65.6854 | 62.7792 | 49.1782 | 0 | 66.8477 | 785.3765 | 779.5974 | 720.3006 | 720.3272 | 711.7666 | 708.9793 | 536.9987 | 525.5073 | 738.2672 | 751.3646 | 908.975 | 922.8451 | 918.5673 | 929.3878 | 932.7078 | 918.9961 | 914.4737 | 913.1255 | 913.5439 | 920.2062 | 901.8171 | 909.6941 | 920.6511 | 898.6509 | 898.4484 | 925.2961 | 920.1299 | 911.5726 | 917.6875 | 913.8577 | 914.9098 | 914.1263 | 918.2327
2025-04-09 19:49 | 9 | 19 | 49 | 6.2817e-272 | 1 | 29.4058 | 667.6731 | 0.33444 | 0.0075396 | 156.2792 | 156.2792 | 156.2792 | 156.2792 | 12.0915 | 13.5981 | 654.0462 | 654.0462 | 654.0462 | 654.0462 | 66.4503 | 50.0617 | 15.7396 | 106.3059 | 15.602 | 18.284 | 65.631 | 1 | 50.0621 | 13.4468 | 22.1 | 221 | 154840 | 237581.5957 | 3544479.4043 | 100.1232 | 0.00093852 | 0.028156 | 0.028156 | 0.028156 | 7.9917 | 1026.0985 | 1023.8664 | 1023.8689 | 1026.0985 | 1067.3147 | 1067.3147 | 1067.3147 | 1067.3147 | 904.0123 | 904.0123 | 904.0123 | 12.4356 | 0 | 12.4345 | 79.8461 | 228.8668 | 229.0103 | 225.7721 | 2.2201 | 3.4525 | 0 | 86 | 62.2101 | 66.4503 | 104.9305 | 7.8738 | 106.3059 | -1.2246 | 65.6909 | 62.7741 | 49.1229 | 0 | 66.8471 | 785.4314 | 779.8627 | 720.4551 | 720.5447 | 711.976 | 709.3959 | 536.4979 | 524.863 | 738.2284 | 750.8746 | 907.2611 | 920.6979 | 916.8396 | 926.835 | 930.1097 | 917.074 | 912.2879 | 911.4593 | 910.871 | 918.1408 | 900.8823 | 908.0038 | 919.0391 | 896.8239 | 896.8422 | 923.5838 | 918.3851 | 909.7611 | 916.0926 | 911.8774 | 913.3143 | 912.7214 | 915.9436
2025-04-09 19:50 | 9 | 19 | 50 | 6.2817e-272 | 1 | 29.4044 | 667.7899 | 0.34276 | 0.0075295 | 156.6202 | 156.6202 | 156.6202 | 156.6202 | 12.1162 | 13.6034 | 654.5742 | 654.5742 | 654.5742 | 654.5742 | 66.7999 | 50.0874 | 15.7395 | 106.9618 | 15.5987 | 18.3857 | 65.9817 | 1 | 50.0878 | 14.2979 | 22.1 | 221 | 154840 | 237582.8723 | 3544497.0638 | 100.1746 | -0.0024649 | -0.073947 | -0.073947 | -0.073947 | 7.9917 | 1025.6517 | 1023.4079 | 1023.4083 | 1025.6517 | 1066.4587 | 1066.4587 | 1066.4587 | 1066.4587 | 906.1887 | 906.1887 | 906.1887 | 12.5772 | 0 | 12.5879 | 80.1375 | 229.4701 | 229.6203 | 225.8719 | 2.2 | 3.4731 | 0 | 86 | 62.1324 | 66.7999 | 104.9302 | 7.6481 | 106.9618 | -1.272 | 66.0563 | 62.7698 | 49.0798 | 0 | 66.8477 | 785.797 | 780.3263 | 720.7303 | 720.907 | 712.1434 | 709.6254 | 535.9717 | 524.2701 | 738.2853 | 752.7762 | 908.6547 | 923.6357 | 919.1515 | 928.7864 | 932.0687 | 919.0746 | 914.8896 | 913.3714 | 914.0101 | 920.1656 | 902.107 | 909.9976 | 921.074 | 898.9917 | 899.3581 | 926.5302 | 919.9518 | 912.0429 | 919.1197 | 913.9216 | 915.1634 | 914.6748 | 918.4986
2025-04-09 19:51 | 9 | 19 | 51 | 6.2817e-272 | 1 | 29.4059 | 667.7159 | 0.32138 | 0.0075168 | 156.5245 | 156.5245 | 156.5245 | 156.5245 | 12.1088 | 13.6062 | 654.24 | 654.24 | 654.24 | 654.24 | 66.7449 | 50.0922 | 15.7429 | 106.3902 | 15.6024 | 18.2974 | 65.6074 | 1 | 50.0928 | 13.7021 | 22.1 | 221 | 154840 | 237584.2979 | 3544514.8936 | 100.1843 | 0.0040307 | 0.12092 | 0.12092 | 0.12092 | 7.9917 | 1025.7874 | 1023.5462 | 1023.5451 | 1025.7874 | 1067.2045 | 1067.2045 | 1067.2045 | 1067.2045 | 904.2538 | 904.2538 | 904.2538 | 12.4917 | 0 | 12.4822 | 79.9904 | 229.2761 | 229.4107 | 225.9644 | 2.2166 | 3.4666 | 0 | 86 | 62.0766 | 66.7449 | 104.9524 | 7.8135 | 106.3902 | -1.1886 | 65.7389 | 62.7847 | 49.0311 | 0 | 66.8462 | 785.9936 | 780.7328 | 720.9359 | 721.1187 | 712.377 | 709.8151 | 535.5594 | 523.955 | 738.3606 | 752.8472 | 907.0254 | 921.6112 | 917.7684 | 927.75 | 931.1817 | 917.5519 | 912.5122 | 911.7639 | 912.0201 | 917.9492 | 900.6517 | 908.1575 | 918.7035 | 896.5157 | 897.1709 | 923.5588 | 918.3997 | 910.1803 | 916.9372 | 911.641 | 913.5026 | 912.4252 | 915.8356
2025-04-09 19:52 | 9 | 19 | 52 | 6.2817e-272 | 1 | 29.4039 | 668.5811 | 0.35376 | 0.0075118 | 156.7771 | 156.7771 | 156.7771 | 156.7771 | 12.1275 | 13.6158 | 654.7863 | 654.7863 | 654.7863 | 654.7863 | 66.8534 | 50.118 | 15.7389 | 107.1647 | 15.6001 | 18.4096 | 66.0303 | 1 | 50.1184 | 14.766 | 22.1 | 221 | 154840 | 237585.4894 | 3544532.5957 | 100.2359 | -0.0018844 | -0.056531 | -0.056531 | -0.056531 | 7.9917 | 1025.4502 | 1023.1985 | 1023.2009 | 1025.4502 | 1066.1953 | 1066.1953 | 1066.1953 | 1066.1953 | 906.1368 | 906.1368 | 906.1368 | 12.6159 | 0 | 12.6263 | 80.233 | 229.8077 | 229.9521 | 226.091 | 2.1961 | 3.4753 | 0 | 86 | 61.8587 | 66.8534 | 104.926 | 7.6811 | 107.1647 | -1.2509 | 66.1422 | 62.7907 | 49.009 | 0 | 66.8466 | 786.0637 | 780.915 | 721.2442 | 721.2795 | 712.6373 | 710.0829 | 535.0357 | 523.1799 | 738.4325 | 753.186 | 908.9265 | 923.2528 | 918.851 | 928.4787 | 932.3123 | 918.936 | 914.284 | 913.4865 | 914.8816 | 920.5308 | 902.4164 | 909.978 | 920.0014 | 898.3515 | 898.4094 | 926.6723 | 920.0628 | 912.3536 | 919.4204 | 913.6542 | 916.1932 | 914.1605 | 918.1011
2025-04-09 19:53 | 9 | 19 | 53 | 6.2817e-272 | 1 | 29.4028 | 668.3612 | 0.35402 | 0.007504 | 156.904 | 156.904 | 156.904 | 156.904 | 12.1369 | 13.6111 | 654.8179 | 654.8179 | 654.8179 | 654.8179 | 67.3362 | 50.1299 | 15.739 | 107.1851 | 15.5988 | 18.4226 | 66.0462 | 1 | 50.1302 | 14.4255 | 22.1 | 221 | 154840 | 237586.7234 | 3544550.3404 | 100.2599 | 0.0020602 | 0.061806 | 0.061806 | 0.061806 | 7.9917 | 1025.2796 | 1023.0226 | 1023.0232 | 1025.2796 | 1066.1696 | 1066.1696 | 1066.1696 | 1066.1696 | 906.6112 | 906.6112 | 906.6112 | 12.6812 | 0 | 12.6756 | 80.3213 | 229.983 | 230.1156 | 226.1869 | 2.1866 | 3.4653 | 0 | 86 | 61.485 | 67.3362 | 104.9269 | 7.6306 | 107.1851 | -1.2106 | 66.189 | 62.7826 | 48.9762 | 0 | 66.8458 | 786.3971 | 781.3062 | 721.5898 | 721.5151 | 713.003 | 710.2618 | 534.537 | 522.9092 | 738.6148 | 752.5293 | 909.1173 | 924.0936 | 919.8635 | 929.2965 | 933.1189 | 919.5046 | 915.0481 | 913.6232 | 915.221 | 920.7098 | 902.3324 | 910.6691 | 921.1569 | 898.3307 | 898.9101 | 926.4331 | 920.2231 | 912.7999 | 920.2894 | 914.2904 | 916.4938 | 914.7677 | 918.4336
2025-04-09 19:54 | 9 | 19 | 54 | 6.2817e-272 | 1 | 29.396 | 671.3191 | 0.35914 | 0.0074997 | 156.8091 | 156.8091 | 156.8091 | 156.8091 | 12.1328 | 13.6194 | 653.5258 | 653.5258 | 653.5258 | 653.5258 | 67.1675 | 50.1422 | 15.7403 | 106.529 | 15.5979 | 18.3159 | 65.6079 | 1 | 50.143 | 13.6087 | 22.1 | 221 | 154840 | 237588.0652 | 3544567.8913 | 100.2846 | -0.001016 | -0.030481 | -0.030481 | -0.030481 | 7.9917 | 1025.3522 | 1023.0985 | 1023.0993 | 1025.3522 | 1067.023 | 1067.023 | 1067.023 | 1067.023 | 901.8422 | 901.8422 | 901.8422 | 12.4917 | 0 | 12.5074 | 80.2864 | 229.8012 | 229.932 | 226.2318 | 2.0815 | 3.4484 | 0 | 86 | 60.663 | 67.1675 | 104.9354 | 7.644 | 106.529 | -1.2602 | 65.8053 | 62.7901 | 48.9515 | 0 | 66.8456 | 786.3615 | 781.3173 | 721.7856 | 721.5505 | 713.2221 | 710.3074 | 534.0293 | 522.5391 | 738.7446 | 753.3762 | 904.561 | 918.7607 | 914.8231 | 924.1546 | 928.2996 | 914.7902 | 910.072 | 909.8363 | 909.2297 | 915.4138 | 898.5225 | 905.8648 | 915.6141 | 893.4602 | 894.1477 | 921.4744 | 916.5154 | 908.082 | 915.2563 | 909.7527 | 912.1687 | 910.3246 | 913.2837
2025-04-09 19:55 | 9 | 19 | 55 | 6.2817e-272 | 1 | 29.3986 | 672.9973 | 0.35593 | 0.0074958 | 157.0612 | 157.0612 | 157.0612 | 157.0612 | 12.1496 | 13.6288 | 652.9192 | 652.9192 | 652.9192 | 652.9192 | 66.4473 | 50.1287 | 15.7393 | 106.9025 | 15.6016 | 18.3589 | 65.7857 | 1 | 50.1292 | 14.6383 | 22.1 | 221 | 154840 | 237589.3617 | 3544585.5319 | 100.2576 | -0.00079524 | -0.023858 | -0.023858 | -0.023858 | 7.9917 | 1025.0513 | 1022.7881 | 1022.7862 | 1025.0513 | 1066.5377 | 1066.5377 | 1066.5377 | 1066.5377 | 902.7029 | 902.7029 | 902.7029 | 12.5594 | 0 | 12.5504 | 80.425 | 230.2114 | 230.3391 | 226.2132 | 2.1203 | 3.4434 | 0 | 86 | 60.1143 | 66.4473 | 104.9289 | 7.775 | 106.9025 | -1.223 | 65.9599 | 62.7966 | 48.9404 | 0 | 66.8469 | 786.253 | 781.135 | 721.8806 | 721.4289 | 713.3103 | 710.134 | 533.5008 | 522.1792 | 738.8623 | 753.1751 | 905.5752 | 919.5142 | 915.7431 | 925.2411 | 929.544 | 915.193 | 910.6571 | 910.25 | 910.9128 | 916.2764 | 899.1921 | 906.8713 | 915.9311 | 894.5605 | 894.766 | 922.7657 | 917.0861 | 909.1228 | 915.6148 | 910.74 | 913.124 | 911.6137 | 914.6027
2025-04-09 19:56 | 9 | 19 | 56 | 6.2817e-272 | 1 | 29.3986 | 674.7744 | 0.35598 | 0.0074999 | 157.4832 | 157.4832 | 157.4832 | 157.4832 | 12.1795 | 13.6712 | 652.1976 | 652.1976 | 652.1976 | 652.1976 | 64.5037 | 50.1324 | 15.7378 | 107.4016 | 15.6002 | 18.4206 | 66.0444 | 1 | 50.1329 | 14.0851 | 22.1 | 221 | 154840 | 237590.5957 | 3544603.2766 | 100.265 | -0.00070731 | -0.021219 | -0.021219 | -0.021219 | 7.9917 | 1024.5119 | 1022.2328 | 1022.2323 | 1024.5119 | 1065.8877 | 1065.8877 | 1065.8877 | 1065.8877 | 901.7882 | 901.7882 | 901.7882 | 12.5273 | 0 | 12.5273 | 80.6036 | 230.7909 | 230.9542 | 226.0622 | 2.1316 | 3.454 | 0 | 86 | 59.4983 | 64.5037 | 104.9184 | 7.7903 | 107.4016 | -1.2321 | 66.1817 | 62.7937 | 48.9556 | 0 | 66.8459 | 785.6147 | 780.5089 | 721.5574 | 721.1135 | 713.0521 | 709.8529 | 533.0133 | 521.667 | 738.9131 | 753.0806 | 904.295 | 918.177 | 914.6827 | 924.219 | 928.5566 | 914.0352 | 909.9425 | 909.4665 | 911.0993 | 916.0417 | 898.184 | 905.076 | 914.9073 | 894.0579 | 894.0966 | 922.7409 | 915.7823 | 908.3259 | 915.0205 | 909.5476 | 911.8637 | 910.3305 | 913.477
2025-04-09 19:57 | 9 | 19 | 57 | 6.2817e-272 | 1 | 29.3989 | 676.1442 | 0.36127 | 0.0075115 | 157.3429 | 157.3429 | 157.3429 | 157.3429 | 12.1695 | 13.7054 | 651.3843 | 651.3843 | 651.3843 | 651.3843 | 63.5444 | 50.1656 | 15.7411 | 106.5242 | 15.6004 | 18.2868 | 65.4932 | 1 | 50.1658 | 13.617 | 22.1 | 221 | 154840 | 237591.8085 | 3544621.0638 | 100.331 | 0.00073628 | 0.022089 | 0.022089 | 0.022089 | 7.9917 | 1024.6934 | 1022.4181 | 1022.4213 | 1024.6934 | 1067.0304 | 1067.0304 | 1067.0304 | 1067.0304 | 896.3738 | 896.3738 | 896.3738 | 12.2888 | 0 | 12.2922 | 80.5971 | 230.6276 | 230.7869 | 225.96 | 2.1104 | 3.4642 | 0 | 86 | 59.0195 | 63.5444 | 104.9406 | 7.3399 | 106.5242 | -1.2405 | 65.7011 | 62.7863 | 49.0017 | 0 | 66.8452 | 785.0264 | 779.9223 | 721.1641 | 720.7942 | 712.6333 | 709.5423 | 532.3573 | 521.1167 | 738.8997 | 752.8463 | 898.806 | 913.6066 | 910.0691 | 918.5631 | 922.6387 | 909.2369 | 905.2759 | 904.3507 | 903.9524 | 910.0725 | 892.8521 | 899.5361 | 910.6023 | 889.0214 | 888.9582 | 915.1541 | 910.7973 | 902.1169 | 908.5979 | 904.4109 | 905.9028 | 905.2009 | 908.3114
2025-04-09 19:58 | 9 | 19 | 58 | 6.2817e-272 | 1 | 29.3983 | 676.6438 | 0.35685 | 0.0075107 | 157.6307 | 157.6307 | 157.6307 | 157.6307 | 12.1902 | 13.7081 | 651.6659 | 651.6659 | 651.6659 | 651.6659 | 62.7751 | 50.135 | 15.7389 | 107.5093 | 15.5997 | 18.4228 | 66.0347 | 1 | 50.1354 | 15.1064 | 22.1 | 221 | 154840 | 237593.1915 | 3544638.8085 | 100.27 | -0.0018558 | -0.055674 | -0.055674 | -0.055674 | 7.9917 | 1024.3211 | 1022.0347 | 1022.0366 | 1024.3211 | 1065.747 | 1065.747 | 1065.747 | 1065.747 | 900.2824 | 900.2824 | 900.2824 | 12.4403 | 0 | 12.4392 | 80.7408 | 231.0551 | 231.223 | 225.7713 | 2.1124 | 3.4482 | 0 | 86 | 58.7687 | 62.7751 | 104.9258 | 7.4324 | 107.5093 | -1.2441 | 66.1897 | 62.7926 | 48.9978 | 0 | 66.8452 | 784.5904 | 779.5183 | 720.8633 | 720.5559 | 712.2203 | 709.0969 | 531.8385 | 520.6097 | 738.8177 | 753.2891 | 902.877 | 917.1016 | 913.3077 | 922.6705 | 926.176 | 912.4306 | 909.5518 | 908.1406 | 910.075 | 914.7577 | 896.6047 | 903.6208 | 913.4206 | 892.8037 | 892.7954 | 920.9556 | 914.2028 | 906.7004 | 913.4196 | 907.2815 | 909.7422 | 907.5277 | 911.9553
2025-04-09 19:59 | 9 | 19 | 59 | 6.2817e-272 | 1 | 29.399 | 677.0814 | 0.34788 | 0.0075047 | 157.4088 | 157.4088 | 157.4088 | 157.4088 | 12.1741 | 13.7098 | 651.157 | 651.157 | 651.157 | 651.157 | 62.2552 | 50.1142 | 15.7433 | 107.1209 | 15.6 | 18.3436 | 65.7769 | 1 | 50.1147 | 14.5957 | 22.1 | 221 | 154840 | 237594.4043 | 3544656.6596 | 100.2286 | -0.0033873 | -0.10162 | -0.10162 | -0.10162 | 7.9917 | 1024.607 | 1022.3311 | 1022.3313 | 1024.607 | 1066.2526 | 1066.2526 | 1066.2526 | 1066.2526 | 898.8955 | 898.8955 | 898.8955 | 12.3172 | 0 | 12.315 | 80.5164 | 230.6457 | 230.8111 | 225.6424 | 2.1572 | 3.465 | 0 | 86 | 58.7729 | 62.2552 | 104.9553 | 7.5139 | 107.1209 | -1.2428 | 65.9048 | 62.791 | 48.9749 | 0 | 66.845 | 784.187 | 779.2296 | 720.4773 | 720.2247 | 711.833 | 708.6537 | 531.3543 | 520.3139 | 738.6625 | 753.0506 | 901.3092 | 915.8133 | 912.3841 | 921.9983 | 925.4902 | 911.4798 | 908.069 | 906.6742 | 908.1239 | 913.1846 | 894.6966 | 902.1507 | 913.3211 | 891.5329 | 891.7362 | 917.9962 | 912.7816 | 904.7878 | 911.7644 | 905.9893 | 908.1165 | 906.8036 | 910.3634
2025-04-09 20:00 | 9 | 20 | 0 | 6.2817e-272 | 1 | 29.3959 | 678.1683 | 0.33403 | 0.0074989 | 157.6599 | 157.6599 | 157.6599 | 157.6599 | 12.1931 | 13.6984 | 651.4638 | 651.4638 | 651.4638 | 651.4638 | 61.8323 | 50.0685 | 15.7404 | 108.1222 | 15.5989 | 18.5221 | 66.4591 | 1 | 50.0689 | 15.5319 | 22.1 | 221 | 154840 | 237595.5957 | 3544674.5532 | 100.1367 | -0.00071904 | -0.021571 | -0.021571 | -0.021571 | 7.9917 | 1024.2687 | 1021.9811 | 1021.9787 | 1024.2687 | 1064.9483 | 1064.9483 | 1064.9483 | 1064.9483 | 903.7461 | 903.7461 | 903.7461 | 12.5151 | 0 | 12.5117 | 80.605 | 231.0491 | 231.2025 | 225.5221 | 2.0885 | 3.4528 | 0 | 86 | 58.6631 | 61.8323 | 104.9359 | 7.6518 | 108.1222 | -1.2343 | 66.5462 | 62.7936 | 48.9487 | 0 | 66.8446 | 783.7149 | 778.9539 | 720.1629 | 719.8904 | 711.4383 | 708.2534 | 530.9017 | 519.8914 | 738.3336 | 752.9045 | 905.6336 | 921.2908 | 917.173 | 926.6507 | 929.8241 | 915.3486 | 913.2684 | 911.1313 | 914.5605 | 918.2396 | 900.0041 | 906.8367 | 918.6719 | 896.4883 | 897.163 | 922.8898 | 916.5446 | 909.3601 | 917.1513 | 910.5378 | 913.1062 | 910.7225 | 916.3637
2025-04-09 20:01 | 9 | 20 | 1 | 6.2817e-272 | 1 | 29.3963 | 679.0433 | 0.34231 | 0.0074981 | 157.1151 | 157.1151 | 157.1151 | 157.1151 | 12.1544 | 13.7016 | 650.4709 | 650.4709 | 650.4709 | 650.4709 | 61.7171 | 50.0684 | 15.7407 | 106.7117 | 15.6007 | 18.3072 | 65.6791 | 1 | 50.0689 | 13.7447 | 22.1 | 221 | 154840 | 237596.8085 | 3544692.4043 | 100.1366 | -0.0021299 | -0.063896 | -0.063896 | -0.063896 | 7.9917 | 1024.9662 | 1022.7004 | 1022.6991 | 1024.9662 | 1066.7851 | 1066.7851 | 1066.7851 | 1066.7851 | 898.2008 | 898.2008 | 898.2008 | 12.2432 | 0 | 12.2294 | 80.2396 | 230.1277 | 230.283 | 225.3194 | 2.1235 | 3.4531 | 0 | 86 | 58.8148 | 61.7171 | 104.9378 | 7.4425 | 106.7117 | -1.1905 | 65.7743 | 62.7727 | 48.9458 | 0 | 66.8444 | 783.256 | 778.5765 | 719.8353 | 719.4231 | 711.15 | 707.8393 | 530.3548 | 519.0549 | 738.0784 | 752.4855 | 900.2988 | 915.595 | 911.6684 | 920.6656 | 924.1941 | 910.7763 | 907.5283 | 906.6826 | 906.9365 | 912.8672 | 894.4126 | 901.1571 | 911.6783 | 891.0104 | 891.1965 | 918.1125 | 912.1252 | 904.4179 | 910.3433 | 905.3942 | 906.7884 | 906.1733 | 909.792
2025-04-09 20:02 | 9 | 20 | 2 | 6.2817e-272 | 1 | 29.3951 | 680.1201 | 0.33856 | 0.0075028 | 157.3058 | 157.3058 | 157.3058 | 157.3058 | 12.1684 | 13.6954 | 650.9167 | 650.9167 | 650.9167 | 650.9167 | 61.6202 | 50.0506 | 15.741 | 107.4728 | 15.5997 | 18.4385 | 66.1146 | 1 | 50.0511 | 14.9565 | 22.1 | 221 | 154840 | 237598.1957 | 3544710 | 100.1012 | 0.00067616 | 0.020284 | 0.020284 | 0.020284 | 7.9917 | 1024.7137 | 1022.4398 | 1022.442 | 1024.7137 | 1065.7943 | 1065.7943 | 1065.7943 | 1065.7943 | 901.5423 | 901.5423 | 901.5423 | 12.3687 | 0 | 12.3749 | 80.4203 | 230.4549 | 230.6083 | 225.0586 | 2.1195 | 3.4563 | 0 | 86 | 58.8376 | 61.6202 | 104.9403 | 7.6327 | 107.4728 | -1.2204 | 66.2458 | 62.7788 | 48.9627 | 0 | 66.8442 | 782.8637 | 778.2249 | 719.8515 | 719.0952 | 711.073 | 707.4748 | 529.7393 | 518.5757 | 737.767 | 752.4098 | 904.0621 | 918.5331 | 914.4007 | 923.8498 | 927.4507 | 913.3517 | 910.8601 | 909.8193 | 911.095 | 915.9386 | 897.9212 | 904.6935 | 915.9295 | 894.3261 | 894.494 | 921.4031 | 915.1527 | 907.9121 | 914.2082 | 908.452 | 911.0982 | 908.419 | 913.8117
2025-04-09 20:03 | 9 | 20 | 3 | 6.2817e-272 | 1 | 29.397 | 681.2497 | 0.33119 | 0.0075038 | 156.9466 | 156.9466 | 156.9466 | 156.9466 | 12.1422 | 13.6863 | 649.4174 | 649.4174 | 649.4174 | 649.4174 | 62.0985 | 50.0534 | 15.7419 | 106.3191 | 15.5992 | 18.2446 | 65.4883 | 1 | 50.0537 | 13.7872 | 22.1 | 221 | 154840 | 237599.4255 | 3544727.617 | 100.1067 | 0.0055896 | 0.16769 | 0.16769 | 0.16769 | 7.9917 | 1025.1851 | 1022.9255 | 1022.9257 | 1025.1851 | 1067.297 | 1067.297 | 1067.297 | 1067.297 | 896.5784 | 896.5784 | 896.5784 | 12.1769 | 0 | 12.1738 | 80.1508 | 229.8265 | 229.9949 | 224.8793 | 2.1213 | 3.4564 | 0 | 86 | 58.4172 | 62.0985 | 104.9461 | 7.6716 | 106.3191 | -1.1675 | 65.5492 | 62.7883 | 48.9707 | 0 | 66.8438 | 782.5117 | 777.8659 | 719.7485 | 718.8202 | 710.9873 | 707.1429 | 529.1876 | 518.0024 | 737.5467 | 752.1109 | 899.2703 | 913.8818 | 909.9451 | 919.287 | 923.4819 | 909.0896 | 905.585 | 904.8672 | 904.5447 | 910.6345 | 892.8251 | 899.476 | 909.3639 | 889.5831 | 889.0784 | 916.28 | 911.183 | 902.9009 | 908.2903 | 904.3011 | 905.9798 | 904.8865 | 908.304
2025-04-09 20:04 | 9 | 20 | 4 | 6.2817e-272 | 1 | 29.3947 | 682.2363 | 0.33798 | 0.0075059 | 157.4173 | 157.4173 | 157.4173 | 157.4173 | 12.1764 | 13.6983 | 650.4072 | 650.4072 | 650.4072 | 650.4072 | 61.8545 | 50.0686 | 15.7421 | 107.5006 | 15.5983 | 18.4134 | 66.1245 | 1 | 50.0686 | 14.8085 | 22.1 | 221 | 154840 | 237600.617 | 3544745.3191 | 100.1371 | -0.00026416 | -0.0079247 | -0.0079247 | -0.0079247 | 7.9917 | 1024.5691 | 1022.2911 | 1022.29 | 1024.5691 | 1065.7583 | 1065.7583 | 1065.7583 | 1065.7583 | 900.2671 | 900.2671 | 900.2671 | 12.3794 | 0 | 12.3857 | 80.541 | 230.6562 | 230.8306 | 224.7979 | 2.0991 | 3.4367 | 0 | 86 | 58.5591 | 61.8545 | 104.9477 | 7.5824 | 107.5006 | -1.2765 | 66.1557 | 62.7841 | 48.9746 | 0 | 66.8437 | 782.221 | 777.3976 | 719.6832 | 718.6714 | 710.8512 | 707.0651 | 528.493 | 517.3754 | 737.2348 | 751.5457 | 902.9041 | 917.026 | 913.1449 | 922.0742 | 926.1581 | 911.802 | 909.4209 | 908.2976 | 909.97 | 915.0301 | 896.9121 | 903.4595 | 914.0024 | 892.605 | 892.6585 | 920.406 | 913.8497 | 906.5505 | 912.6624 | 907.6351 | 910.357 | 907.7846 | 912.5056
2025-04-09 20:05 | 9 | 20 | 5 | 6.2817e-272 | 1 | 29.3935 | 684.0414 | 0.33712 | 0.0075097 | 157.0468 | 157.0468 | 157.0468 | 157.0468 | 12.1506 | 13.7009 | 649.6847 | 649.6847 | 649.6847 | 649.6847 | 61.6306 | 50.0642 | 15.7408 | 106.5032 | 15.6009 | 18.2935 | 65.572 | 1 | 50.0644 | 13.5745 | 22.1 | 221 | 154840 | 237601.9149 | 3544763.1064 | 100.1281 | -0.00079394 | -0.023818 | -0.023818 | -0.023818 | 7.9917 | 1025.0328 | 1022.7672 | 1022.7679 | 1025.0328 | 1067.0574 | 1067.0574 | 1067.0574 | 1067.0574 | 896.7975 | 896.7975 | 896.7975 | 12.1792 | 0 | 12.1818 | 80.2235 | 230.0155 | 230.1793 | 224.7367 | 2.0757 | 3.4557 | 0 | 86 | 58.6111 | 61.6306 | 104.9385 | 7.6401 | 106.5032 | -1.2288 | 65.725 | 62.7893 | 48.99 | 0 | 66.8436 | 782.0907 | 777.1464 | 719.5566 | 718.487 | 710.7086 | 706.7318 | 527.9461 | 517.0179 | 737.1311 | 751.5136 | 899.9446 | 913.7843 | 909.8427 | 919.2404 | 923.7547 | 909.2367 | 905.8496 | 904.9014 | 904.588 | 911 | 893.4229 | 899.6574 | 910.7293 | 889.7427 | 889.682 | 916.4969 | 911.023 | 902.5019 | 908.0304 | 904.4263 | 906.4306 | 905.2514 | 908.7139
2025-04-09 20:06 | 9 | 20 | 6 | 6.2817e-272 | 1 | 29.3917 | 685.3376 | 0.33999 | 0.0075162 | 157.3643 | 157.3643 | 157.3643 | 157.3643 | 12.1739 | 13.7055 | 649.6942 | 649.6942 | 649.6942 | 649.6942 | 61.757 | 50.0805 | 15.7407 | 107.1449 | 15.5995 | 18.3692 | 65.8989 | 1 | 50.0806 | 14 | 22.1 | 221 | 154840 | 237603.2766 | 3544780.8085 | 100.1608 | 0.00046201 | 0.01386 | 0.01386 | 0.01386 | 7.9917 | 1024.6157 | 1022.3394 | 1022.3398 | 1024.6157 | 1066.2215 | 1066.2215 | 1066.2215 | 1066.2215 | 898.203 | 898.203 | 898.203 | 12.3005 | 0 | 12.3059 | 80.4897 | 230.5771 | 230.7434 | 224.5989 | 2.0647 | 3.4471 | 0 | 86 | 58.1109 | 61.757 | 104.9382 | 7.6011 | 107.1449 | -1.2447 | 65.9969 | 62.794 | 49.0143 | 0 | 66.8427 | 781.8973 | 776.6708 | 719.4448 | 718.3487 | 710.4859 | 706.5468 | 527.2562 | 516.6049 | 736.9782 | 751.2202 | 901.1734 | 914.8223 | 910.7577 | 920.352 | 924.4812 | 910.0657 | 907.6543 | 905.8387 | 906.2737 | 912.628 | 894.6013 | 901.0506 | 911.9633 | 891.2909 | 890.6607 | 918.9347 | 912.4066 | 904.2819 | 910.4191 | 905.9762 | 908.3446 | 905.8617 | 910.4578
2025-04-09 20:07 | 9 | 20 | 7 | 6.2817e-272 | 1 | 29.3926 | 685.5164 | 0.34739 | 0.0075128 | 157.3645 | 157.3645 | 157.3645 | 157.3645 | 12.1735 | 13.7104 | 649.4011 | 649.4011 | 649.4011 | 649.4011 | 61.4611 | 50.0789 | 15.7417 | 106.9703 | 15.6027 | 18.3464 | 65.7898 | 1 | 50.0788 | 14.1277 | 22.1 | 221 | 154840 | 237604.4894 | 3544798.6383 | 100.1575 | 0.0051441 | 0.15432 | 0.15432 | 0.15432 | 7.9917 | 1024.6174 | 1022.3415 | 1022.3406 | 1024.6174 | 1066.4485 | 1066.4485 | 1066.4485 | 1066.4485 | 897.2543 | 897.2543 | 897.2543 | 12.2591 | 0 | 12.2577 | 80.4874 | 230.5486 | 230.7099 | 224.5 | 2.0916 | 3.4592 | 0 | 86 | 57.8045 | 61.4611 | 104.945 | 7.4791 | 106.9703 | -1.2129 | 65.9152 | 62.7977 | 48.9987 | 0 | 66.843 | 781.8065 | 776.3874 | 719.0673 | 718.2217 | 710.0449 | 706.297 | 526.6886 | 516.3841 | 736.8671 | 750.8682 | 899.8949 | 913.7994 | 909.916 | 919.7816 | 923.814 | 909.3801 | 906.8148 | 904.9676 | 905.6627 | 912.1449 | 893.4835 | 900.2586 | 910.7139 | 890.7416 | 889.4594 | 917.4078 | 911.5803 | 902.7261 | 908.7963 | 904.905 | 906.6731 | 905.7425 | 909.9548
2025-04-09 20:08 | 9 | 20 | 8 | 6.2817e-272 | 1 | 29.3918 | 685.4974 | 0.33696 | 0.0075068 | 157.4164 | 157.4164 | 157.4164 | 157.4164 | 12.1775 | 13.6954 | 649.5704 | 649.5704 | 649.5704 | 649.5704 | 61.9541 | 50.0682 | 15.7414 | 107.2962 | 15.5991 | 18.3917 | 66.0165 | 1 | 50.0687 | 14.2553 | 22.1 | 221 | 154840 | 237605.6809 | 3544816.4255 | 100.1362 | 0.00058997 | 0.017699 | 0.017699 | 0.017699 | 7.9917 | 1024.5491 | 1022.2702 | 1022.2709 | 1024.5491 | 1066.0249 | 1066.0249 | 1066.0249 | 1066.0249 | 899.1006 | 899.1006 | 899.1006 | 12.3639 | 0 | 12.357 | 80.5437 | 230.6584 | 230.8395 | 224.3721 | 2.079 | 3.4578 | 0 | 86 | 57.5649 | 61.9541 | 104.9429 | 7.5962 | 107.2962 | -1.26 | 66.078 | 62.7857 | 48.9764 | 0 | 66.8426 | 781.6509 | 776.1335 | 718.7066 | 718.1397 | 709.6459 | 706.1706 | 526.1894 | 516.0138 | 736.6796 | 750.5526 | 901.9307 | 915.9225 | 911.884 | 921.6942 | 925.2488 | 911.0065 | 908.9285 | 906.534 | 907.5916 | 913.0253 | 895.5899 | 902.7158 | 913.4813 | 891.6771 | 891.567 | 919.0568 | 913.2938 | 904.8622 | 911.6281 | 906.9058 | 908.576 | 906.2059 | 911.4531
2025-04-09 20:09 | 9 | 20 | 9 | 6.2817e-272 | 1 | 29.3933 | 685.7955 | 0.33593 | 0.0074995 | 157.3032 | 157.3032 | 157.3032 | 157.3032 | 12.1689 | 13.6807 | 648.8995 | 648.8995 | 648.8995 | 648.8995 | 62.3254 | 50.0518 | 15.7408 | 107.078 | 15.6019 | 18.3521 | 65.8569 | 1 | 50.0518 | 14.6809 | 22.1 | 221 | 154840 | 237606.9574 | 3544834.2766 | 100.1034 | 0.0059475 | 0.17842 | 0.17842 | 0.17842 | 7.9917 | 1024.7053 | 1022.4311 | 1022.4294 | 1024.7053 | 1066.3089 | 1066.3089 | 1066.3089 | 1066.3089 | 897.9476 | 897.9476 | 897.9476 | 12.3165 | 0 | 12.3171 | 80.3893 | 230.4105 | 230.58 | 224.2863 | 2.0782 | 3.4542 | 0 | 86 | 57.4315 | 62.3254 | 104.9387 | 7.1865 | 107.078 | -1.2489 | 65.9357 | 62.7873 | 48.9467 | 0 | 66.8427 | 781.5311 | 775.9603 | 718.3766 | 718.058 | 709.2661 | 706.0238 | 525.713 | 515.6618 | 736.5235 | 750.4207 | 900.0321 | 914.274 | 910.5466 | 920.7413 | 924.3873 | 910.1961 | 907.3293 | 905.7485 | 906.3491 | 912.1773 | 893.8428 | 901.7687 | 912.417 | 890.7809 | 890.4259 | 917.6765 | 912.5134 | 903.8994 | 910.5711 | 905.6647 | 907.5688 | 905.6343 | 909.9095
2025-04-09 20:10 | 9 | 20 | 10 | 6.2817e-272 | 1 | 29.3966 | 685.5485 | 0.33624 | 0.007491 | 157.3679 | 157.3679 | 157.3679 | 157.3679 | 12.1722 | 13.6826 | 649.0127 | 649.0127 | 649.0127 | 649.0127 | 62.1175 | 50.046 | 15.7418 | 107.206 | 15.6011 | 18.3703 | 65.9628 | 1 | 50.0459 | 14.6522 | 22.1 | 221 | 154840 | 237608.1957 | 3544851.8043 | 100.0919 | 0.0027604 | 0.082812 | 0.082812 | 0.082812 | 7.9917 | 1024.6424 | 1022.3667 | 1022.367 | 1024.6424 | 1066.1417 | 1066.1417 | 1066.1417 | 1066.1417 | 898.506 | 898.506 | 898.506 | 12.362 | 0 | 12.3496 | 80.4471 | 230.537 | 230.7266 | 224.1847 | 2.1044 | 3.4488 | 0 | 86 | 57.5035 | 62.1175 | 104.9452 | 7.1287 | 107.206 | -1.2399 | 66.0009 | 62.7912 | 48.9185 | 0 | 66.8422 | 781.2478 | 775.7308 | 717.9851 | 717.9606 | 708.8998 | 705.9256 | 525.2241 | 515.1295 | 736.2186 | 750.0818 | 900.8829 | 915.0371 | 911.2073 | 921.1742 | 924.3258 | 910.7932 | 908.2186 | 905.8009 | 907.3083 | 913.0433 | 894.0406 | 901.7832 | 912.9255 | 891.399 | 890.3533 | 918.128 | 912.748 | 904.1509 | 910.6694 | 906.685 | 907.79 | 906.9252 | 910.9855
2025-04-09 20:11 | 9 | 20 | 11 | 6.2817e-272 | 1 | 29.3922 | 685.99 | 0.33326 | 0.0074849 | 157.3186 | 157.3186 | 157.3186 | 157.3186 | 12.1704 | 13.6799 | 648.8981 | 648.8981 | 648.8981 | 648.8981 | 61.9698 | 50.0329 | 15.7408 | 107.3533 | 15.6011 | 18.404 | 66.0773 | 1 | 50.0327 | 14.7234 | 22.1 | 221 | 154840 | 237609.3404 | 3544869.4043 | 100.0657 | 0.0072257 | 0.21677 | 0.21677 | 0.21677 | 7.9917 | 1024.6772 | 1022.4009 | 1022.4038 | 1024.6772 | 1065.9504 | 1065.9504 | 1065.9504 | 1065.9504 | 899.1923 | 899.1923 | 899.1923 | 12.3608 | 0 | 12.3653 | 80.4296 | 230.452 | 230.6236 | 224.1466 | 2.0633 | 3.4614 | 0 | 86 | 57.3974 | 61.9698 | 104.9384 | 7.1062 | 107.3533 | -1.2496 | 66.1222 | 62.7948 | 48.8887 | 0 | 66.8422 | 781.0046 | 775.5994 | 717.7795 | 717.8631 | 708.7007 | 705.7915 | 524.7718 | 514.7581 | 736.0375 | 749.7347 | 901.2437 | 915.7503 | 911.7598 | 921.7715 | 924.8326 | 911.5506 | 908.8906 | 906.6316 | 908.2135 | 914.0389 | 894.9237 | 903.0218 | 913.8553 | 891.7158 | 891.1752 | 919.0269 | 913.1889 | 904.8724 | 911.64 | 906.9657 | 908.3408 | 907.2122 | 911.351
2025-04-09 20:12 | 9 | 20 | 12 | 6.2817e-272 | 1 | 29.3909 | 687.0252 | 0.33741 | 0.0074798 | 157.1377 | 157.1377 | 157.1377 | 157.1377 | 12.1581 | 13.6735 | 648.4193 | 648.4193 | 648.4193 | 648.4193 | 62.5272 | 50.0447 | 15.7413 | 106.7458 | 15.6017 | 18.305 | 65.7537 | 1 | 50.0451 | 13.9574 | 22.1 | 221 | 154840 | 237610.4894 | 3544887.2128 | 100.0893 | -0.0010623 | -0.031869 | -0.031869 | -0.031869 | 7.9917 | 1024.8977 | 1022.6287 | 1022.6309 | 1024.8977 | 1066.7415 | 1066.7415 | 1066.7415 | 1066.7415 | 896.5668 | 896.5668 | 896.5668 | 12.2726 | 0 | 12.2834 | 80.3346 | 230.2168 | 230.3834 | 224.0871 | 2.0587 | 3.4599 | 0 | 86 | 57.132 | 62.5272 | 104.9419 | 6.8753 | 106.7458 | -1.2668 | 65.7664 | 62.7978 | 48.8686 | 0 | 66.8417 | 780.8795 | 775.4187 | 717.694 | 717.7325 | 708.6266 | 705.7276 | 524.3963 | 514.425 | 735.8661 | 749.5279 | 899.2722 | 913.0702 | 908.9769 | 919.3249 | 922.6177 | 909.1823 | 905.8199 | 904.2069 | 904.146 | 910.3699 | 892.3758 | 900.3741 | 911.1174 | 889.2122 | 888.4088 | 915.8639 | 911.3681 | 902.4543 | 909.2373 | 904.7432 | 906.079 | 904.5049 | 908.6084
2025-04-09 20:13 | 9 | 20 | 13 | 6.2817e-272 | 1 | 29.3877 | 688.4694 | 0.3348 | 0.0074705 | 157.1102 | 157.1102 | 157.1102 | 157.1102 | 12.1574 | 13.6674 | 648.3653 | 648.3653 | 648.3653 | 648.3653 | 62.5933 | 50.0338 | 15.743 | 106.6597 | 15.6071 | 18.3112 | 65.6515 | 1 | 50.0353 | 14.2128 | 22.1 | 221 | 154840 | 237611.6383 | 3544905.0213 | 100.0676 | -0.015958 | -0.47873 | -0.47873 | -0.47873 | 7.9917 | 1024.9111 | 1022.6426 | 1022.6419 | 1024.9111 | 1066.8532 | 1066.8532 | 1066.8532 | 1066.8532 | 896.7814 | 896.7814 | 896.7814 | 12.2695 | 0 | 12.263 | 80.2947 | 230.1296 | 230.2932 | 224.0805 | 1.9779 | 3.4422 | 0 | 86 | 57.092 | 62.5933 | 104.9532 | 7.0227 | 106.6597 | -1.2139 | 65.7884 | 62.793 | 48.8259 | 0 | 66.8411 | 780.7836 | 775.472 | 717.6839 | 717.6876 | 708.6012 | 705.5847 | 523.9701 | 513.9239 | 735.6983 | 749.4311 | 898.8409 | 913.102 | 909.2038 | 919.5437 | 923.1184 | 909.0458 | 905.4666 | 904.2478 | 905.3784 | 911.3447 | 892.4347 | 900.758 | 910.4243 | 888.9237 | 888.2468 | 917.7783 | 911.5505 | 903.3817 | 908.9439 | 904.7069 | 906.3635 | 905.1947 | 908.5439
2025-04-09 20:14 | 9 | 20 | 14 | 6.2817e-272 | 1 | 29.3913 | 688.5051 | 0.32762 | 0.0074665 | 157.3692 | 157.3692 | 157.3692 | 157.3692 | 12.1744 | 13.6657 | 648.6747 | 648.6747 | 648.6747 | 648.6747 | 62.2981 | 50.0152 | 15.7377 | 107.4637 | 15.6014 | 18.4122 | 66.1553 | 1 | 50.0149 | 15.1489 | 22.1 | 221 | 154840 | 237612.7872 | 3544922.8085 | 100.0304 | 0.022203 | 0.6661 | 0.6661 | 0.6661 | 7.9917 | 1024.6055 | 1022.3279 | 1022.3266 | 1024.6055 | 1065.8062 | 1065.8062 | 1065.8062 | 1065.8062 | 899.8 | 899.8 | 899.8 | 12.4306 | 0 | 12.424 | 80.4632 | 230.5451 | 230.7065 | 224.0561 | 2.0539 | 3.4454 | 0 | 86 | 57.5489 | 62.2981 | 104.9182 | 7.1522 | 107.4637 | -1.2249 | 66.1515 | 62.7964 | 48.8111 | 0 | 66.8413 | 780.482 | 775.2583 | 717.6308 | 717.5625 | 708.4939 | 705.5016 | 523.5426 | 513.5264 | 735.4425 | 749.4596 | 902.1461 | 916.4646 | 911.7858 | 921.9978 | 925.5044 | 911.9515 | 909.0545 | 907.1965 | 909.0481 | 914.0929 | 895.9546 | 903.8309 | 915.2908 | 891.8887 | 892.5004 | 920.4429 | 913.4971 | 905.9364 | 912.3161 | 907.3206 | 909.2074 | 907.2072 | 911.6504
2025-04-09 20:15 | 9 | 20 | 15 | 6.2817e-272 | 1 | 29.3938 | 689.0366 | 0.33001 | 0.0074706 | 157.3016 | 157.3016 | 157.3016 | 157.3016 | 12.1686 | 13.6794 | 648.5554 | 648.5554 | 648.5554 | 648.5554 | 61.9224 | 50.03 | 15.741 | 107.0977 | 15.5972 | 18.3574 | 65.9442 | 1 | 50.0302 | 13.7872 | 22.1 | 221 | 154840 | 237614.0426 | 3544940.5957 | 100.06 | 0.0026277 | 0.078832 | 0.078832 | 0.078832 | 7.9917 | 1024.7149 | 1022.4406 | 1022.4389 | 1024.7149 | 1066.2834 | 1066.2834 | 1066.2834 | 1066.2834 | 897.3586 | 897.3586 | 897.3586 | 12.298 | 0 | 12.3132 | 80.3891 | 230.3752 | 230.5575 | 224.0166 | 2.0727 | 3.4454 | 0 | 86 | 57.6532 | 61.9224 | 104.9397 | 7.1551 | 107.0977 | -1.2902 | 65.9544 | 62.7805 | 48.8339 | 0 | 66.841 | 780.1205 | 775.1151 | 717.5429 | 717.419 | 708.4386 | 705.351 | 523.0667 | 513.0438 | 735.2138 | 749.4408 | 899.6606 | 913.9804 | 909.7324 | 919.69 | 923.594 | 909.6234 | 906.0321 | 904.949 | 906.1814 | 911.8685 | 893.6802 | 900.8115 | 912.2961 | 889.3294 | 889.5411 | 918.2187 | 911.3447 | 903.6217 | 909.3315 | 904.9281 | 906.5058 | 905.7051 | 909.2758
2025-04-09 20:16 | 9 | 20 | 16 | 6.2817e-272 | 1 | 29.3906 | 689.5065 | 0.32727 | 0.0074738 | 157.35 | 157.35 | 157.35 | 157.35 | 12.1732 | 13.6828 | 647.9602 | 647.9602 | 647.9602 | 647.9602 | 61.4059 | 50.0119 | 15.7442 | 107.1411 | 15.6021 | 18.3651 | 65.9158 | 1 | 50.0133 | 14.766 | 22.1 | 221 | 154840 | 237615.2766 | 3544958.4043 | 100.0237 | -0.024567 | -0.73702 | -0.73702 | -0.73702 | 7.9917 | 1024.6238 | 1022.3483 | 1022.3466 | 1024.6238 | 1066.2257 | 1066.2257 | 1066.2257 | 1066.2257 | 897.5709 | 897.5709 | 897.5709 | 12.297 | 0 | 12.2898 | 80.4014 | 230.4259 | 230.6007 | 224.0229 | 2.001 | 3.4391 | 0 | 86 | 57.329 | 61.4059 | 104.9614 | 7.2368 | 107.1411 | -1.2175 | 65.9821 | 62.7933 | 48.8419 | 0 | 66.8401 | 779.7422 | 775.0762 | 717.4672 | 717.2646 | 708.316 | 705.1348 | 522.6421 | 512.6019 | 734.9254 | 749.344 | 900.2281 | 914.3199 | 909.8787 | 919.8643 | 924.007 | 909.5932 | 906.4327 | 905.2339 | 906.5759 | 912.2567 | 894.1733 | 901.4218 | 912.7455 | 890.0602 | 889.4823 | 916.8751 | 911.284 | 903.7266 | 909.4462 | 904.912 | 907.3228 | 905.8299 | 909.2426
2025-04-09 20:17 | 9 | 20 | 17 | 6.2817e-272 | 1 | 29.3891 | 689.6033 | 0.32931 | 0.0074791 | 157.4631 | 157.4631 | 157.4631 | 157.4631 | 12.1818 | 13.6856 | 648.1687 | 648.1687 | 648.1687 | 648.1687 | 60.8477 | 49.991 | 15.7436 | 107.6888 | 15.5967 | 18.4618 | 66.2869 | 1 | 49.9919 | 15.617 | 22.1 | 221 | 154840 | 237616.4468 | 3544976.1915 | 99.9821 | -0.014038 | -0.42115 | -0.42115 | -0.42115 | 7.9917 | 1024.4711 | 1022.1898 | 1022.1891 | 1024.4711 | 1065.513 | 1065.513 | 1065.513 | 1065.513 | 900.0009 | 900.0009 | 900.0009 | 12.3675 | 0 | 12.3709 | 80.4484 | 230.5986 | 230.7879 | 223.9988 | 1.9846 | 3.4424 | 0 | 86 | 57.5009 | 60.8477 | 104.9575 | 7.4376 | 107.6888 | -1.3174 | 66.3295 | 62.7938 | 48.8621 | 0 | 66.8404 | 779.264 | 774.8987 | 717.3914 | 716.9864 | 708.2452 | 704.8651 | 522.2578 | 511.9194 | 734.5005 | 749.1064 | 902.5289 | 916.9829 | 912.1483 | 921.9998 | 926.2734 | 911.9657 | 909.0386 | 907.7258 | 909.8566 | 914.2293 | 897.2696 | 903.7274 | 915.3528 | 891.804 | 892.0424 | 919.5733 | 913.0925 | 906.3783 | 912.4012 | 907.0787 | 910.1913 | 907.3884 | 911.6832
2025-04-09 20:18 | 9 | 20 | 18 | 6.2817e-272 | 1 | 29.3905 | 690.0655 | 0.33046 | 0.0074788 | 157.1189 | 157.1189 | 157.1189 | 157.1189 | 12.1569 | 13.693 | 647.1275 | 647.1275 | 647.1275 | 647.1275 | 60.5821 | 49.9942 | 15.7413 | 106.7062 | 15.6042 | 18.2902 | 65.7114 | 1 | 49.9964 | 13.7391 | 22.1 | 221 | 154840 | 237617.6304 | 3544993.7826 | 99.9884 | -0.033969 | -1.0191 | -1.0191 | -1.0191 | 7.9917 | 1024.9209 | 1022.6526 | 1022.652 | 1024.9209 | 1066.7933 | 1066.7933 | 1066.7933 | 1066.7933 | 895.1867 | 895.1867 | 895.1867 | 12.1398 | 0 | 12.15 | 80.2198 | 230.0476 | 230.2156 | 223.892 | 1.9959 | 3.434 | 0 | 86 | 57.5594 | 60.5821 | 104.9419 | 7.2596 | 106.7062 | -1.2443 | 65.7131 | 62.7857 | 48.863 | 0 | 66.8402 | 778.7381 | 774.6762 | 717.1426 | 716.6416 | 708.0309 | 704.5969 | 521.809 | 511.3381 | 734.1117 | 748.9789 | 897.6745 | 912.191 | 907.5952 | 917.3705 | 922.0612 | 907.9028 | 904.0395 | 903.408 | 903.5293 | 909.3333 | 892.191 | 898.229 | 910.2719 | 887.4568 | 887.708 | 915.1419 | 908.6188 | 901.4755 | 906.8835 | 902.5941 | 904.9078 | 903.44 | 905.9936
2025-04-09 20:19 | 9 | 20 | 19 | 6.2817e-272 | 1 | 29.393 | 690.1232 | 0.32196 | 0.0074828 | 157.2685 | 157.2685 | 157.2685 | 157.2685 | 12.1666 | 13.6959 | 647.7854 | 647.7854 | 647.7854 | 647.7854 | 60.6062 | 50.0032 | 15.7417 | 107.0234 | 15.6025 | 18.3427 | 65.8836 | 1 | 50.0035 | 14.5106 | 22.1 | 221 | 154840 | 237618.8085 | 3545011.3404 | 100.0064 | -0.0013198 | -0.039594 | -0.039594 | -0.039594 | 7.9917 | 1024.7447 | 1022.4728 | 1022.4713 | 1024.7447 | 1066.3794 | 1066.3794 | 1066.3794 | 1066.3794 | 896.3532 | 896.3532 | 896.3532 | 12.2219 | 0 | 12.2171 | 80.3691 | 230.347 | 230.527 | 223.7799 | 2.0419 | 3.4483 | 0 | 86 | 58.0121 | 60.6062 | 104.9448 | 7.2946 | 107.0234 | -1.2947 | 65.9016 | 62.7804 | 48.8804 | 0 | 66.8395 | 778.3428 | 774.4363 | 716.9416 | 716.447 | 707.7503 | 704.3455 | 521.2991 | 510.9495 | 733.7719 | 748.9279 | 899.2769 | 913.7954 | 908.5356 | 917.9168 | 922.4672 | 908.8602 | 905.0286 | 904.4817 | 904.7297 | 910.1176 | 893.3994 | 899.57 | 911.7313 | 888.3434 | 889.1821 | 916.2953 | 909.5417 | 902.8988 | 908.2405 | 903.6545 | 906.1386 | 904.291 | 907.1556
2025-04-09 20:20 | 9 | 20 | 20 | 6.2817e-272 | 1 | 29.3944 | 690.4381 | 0.3356 | 0.0074914 | 156.9904 | 156.9904 | 156.9904 | 156.9904 | 12.1463 | 13.6981 | 647.5214 | 647.5214 | 647.5214 | 647.5214 | 60.4313 | 50.0005 | 15.7484 | 106.3802 | 15.6004 | 18.2467 | 65.5312 | 1 | 50.0027 | 13.7872 | 22.1 | 221 | 154840 | 237620.1277 | 3545029.0851 | 100.001 | -0.054738 | -1.6421 | -1.6421 | -1.6421 | 7.9917 | 1025.1104 | 1022.8485 | 1022.8491 | 1025.1104 | 1067.2172 | 1067.2172 | 1067.2172 | 1067.2172 | 894.0529 | 894.0529 | 894.0529 | 12.0857 | 0 | 12.0781 | 80.1713 | 229.867 | 230.0264 | 223.672 | 2.0328 | 3.442 | 0 | 86 | 57.9515 | 60.4313 | 104.9896 | 7.1882 | 106.3802 | -1.2097 | 65.5568 | 62.799 | 48.9159 | 0 | 66.8398 | 777.9568 | 774.3471 | 716.7133 | 716.2399 | 707.5012 | 704.1 | 520.8083 | 510.3868 | 733.4431 | 748.8855 | 896.8687 | 911.5953 | 906.8559 | 916.2525 | 920.9104 | 906.885 | 902.7057 | 902.6049 | 901.9227 | 907.7561 | 891.2802 | 896.9935 | 909.8859 | 885.8214 | 886.6003 | 913.0345 | 907.4382 | 900.2446 | 905.5325 | 901.3084 | 903.3271 | 902.3154 | 904.7566
2025-04-09 20:21 | 9 | 20 | 21 | 6.2817e-272 | 1 | 29.3936 | 690.64 | 0.32528 | 0.0074909 | 157.1506 | 157.1506 | 157.1506 | 157.1506 | 12.158 | 13.6984 | 647.9223 | 647.9223 | 647.9223 | 647.9223 | 60.4763 | 50.0035 | 15.7395 | 106.8446 | 15.5984 | 18.3235 | 65.7989 | 1 | 50.0031 | 14.5532 | 22.1 | 221 | 154840 | 237621.3191 | 3545046.8298 | 100.007 | 0.02075 | 0.62252 | 0.62252 | 0.62252 | 7.9917 | 1024.9 | 1022.6323 | 1022.6321 | 1024.9 | 1066.6126 | 1066.6126 | 1066.6126 | 1066.6126 | 896.0007 | 896.0007 | 896.0007 | 12.1716 | 0 | 12.1849 | 80.2781 | 230.1583 | 230.325 | 223.5606 | 2.0256 | 3.4515 | 0 | 86 | 57.8558 | 60.4763 | 104.93 | 7.4116 | 106.8446 | -1.2298 | 65.8328 | 62.7963 | 48.9137 | 0 | 66.8385 | 777.6947 | 774.1349 | 716.4492 | 716.0608 | 707.2433 | 703.931 | 520.3134 | 509.842 | 733.2166 | 748.5849 | 898.5573 | 914.2085 | 909.176 | 917.9596 | 922.4978 | 908.5968 | 904.6357 | 904.2709 | 904.1816 | 909.8122 | 892.7167 | 898.8759 | 911.2226 | 887.8294 | 888.0766 | 914.9742 | 908.9317 | 902.1965 | 907.2249 | 903.7729 | 905.5286 | 904.8204 | 907.3654
2025-04-09 20:22 | 9 | 20 | 22 | 6.2817e-272 | 1 | 29.3897 | 692.015 | 0.32376 | 0.007487 | 157.16 | 157.16 | 157.16 | 157.16 | 12.1601 | 13.7133 | 647.5516 | 647.5516 | 647.5516 | 647.5516 | 60.0907 | 50.0175 | 15.7406 | 106.5277 | 15.5982 | 18.2767 | 65.6073 | 1 | 50.0174 | 13.8723 | 22.1 | 221 | 154840 | 237622.5319 | 3545064.5745 | 100.035 | 0.0060005 | 0.18001 | 0.18001 | 0.18001 | 7.9917 | 1024.8634 | 1022.594 | 1022.5915 | 1024.8634 | 1067.0245 | 1067.0245 | 1067.0245 | 1067.0245 | 894.325 | 894.325 | 894.325 | 12.1002 | 0 | 12.0932 | 80.2697 | 230.1583 | 230.3223 | 223.4474 | 1.9882 | 3.4472 | 0 | 86 | 58.0861 | 60.0907 | 104.9373 | 7.4084 | 106.5277 | -3.6608 | 65.6646 | 62.7934 | 48.8934 | 0 | 66.8388 | 777.6212 | 773.9607 | 716.2344 | 715.888 | 706.9603 | 703.6675 | 519.8848 | 509.7395 | 733.0751 | 748.373 | 897.1637 | 912.7432 | 907.8207 | 916.695 | 921.021 | 907.0346 | 903.04 | 902.3543 | 902.7248 | 908.7088 | 890.7714 | 897.0988 | 909.2607 | 886.3972 | 886.4066 | 912.9031 | 907.3979 | 900.2458 | 905.2878 | 901.7777 | 903.5349 | 902.803 | 905.8548
2025-04-09 20:23 | 9 | 20 | 23 | 6.2817e-272 | 1 | 29.3912 | 692.366 | 0.31716 | 0.0074927 | 157.3394 | 157.3394 | 157.3394 | 157.3394 | 12.1723 | 13.705 | 647.4876 | 647.4876 | 647.4876 | 647.4876 | 60.2366 | 50.0067 | 15.7371 | 107.1549 | 15.5969 | 18.3481 | 65.967 | 1 | 50.0077 | 14.6383 | 22.1 | 221 | 154840 | 237623.7234 | 3545082.3191 | 100.0134 | -0.0036532 | -0.1096 | -0.1096 | -0.1096 | 7.9917 | 1024.644 | 1022.3677 | 1022.3668 | 1024.644 | 1066.2085 | 1066.2085 | 1066.2085 | 1066.2085 | 896.4231 | 896.4231 | 896.4231 | 12.202 | 0 | 12.2157 | 80.4691 | 230.4487 | 230.6475 | 223.4577 | 1.9902 | 3.4357 | 0 | 86 | 57.7602 | 60.2366 | 104.914 | 7.3991 | 107.1549 | -4.0536 | 65.9211 | 62.7861 | 48.9184 | 0 | 66.8384 | 777.7172 | 773.8912 | 716.0231 | 715.7178 | 706.8018 | 703.4463 | 519.408 | 509.5961 | 733.0798 | 748.1741 | 898.543 | 914.3598 | 909.2408 | 918.4619 | 922.4703 | 908.7063 | 905.3567 | 904.2446 | 905.1599 | 910.7917 | 893.0206 | 899.1423 | 911.9057 | 888.354 | 889.1134 | 916.3274 | 909.3738 | 902.5068 | 907.9015 | 903.9936 | 905.5134 | 904.5012 | 908.1051
2025-04-09 20:24 | 9 | 20 | 24 | 6.2817e-272 | 1 | 29.394 | 692.9458 | 0.32548 | 0.0074845 | 157.3846 | 157.3846 | 157.3846 | 157.3846 | 12.1744 | 13.7122 | 647.0143 | 647.0143 | 647.0143 | 647.0143 | 59.9156 | 50.0086 | 15.74 | 107.0167 | 15.6003 | 18.3529 | 65.8796 | 1 | 50.0081 | 14.4255 | 22.1 | 221 | 154840 | 237625 | 3545100.0638 | 100.0173 | 0.01404 | 0.42121 | 0.42121 | 0.42121 | 7.9917 | 1024.6047 | 1022.3283 | 1022.3289 | 1024.6047 | 1066.3879 | 1066.3879 | 1066.3879 | 1066.3879 | 895.0067 | 895.0067 | 895.0067 | 12.1696 | 0 | 12.1731 | 80.4327 | 230.5158 | 230.6803 | 223.3419 | 2.0417 | 3.4284 | 0 | 86 | 57.2202 | 59.9156 | 104.9335 | 7.3442 | 107.0167 | -4.252 | 65.9383 | 62.7987 | 48.8874 | 0 | 66.838 | 777.522 | 773.5911 | 715.7933 | 715.4657 | 706.546 | 703.15 | 518.8729 | 509.1913 | 732.9744 | 747.931 | 897.4897 | 913.0054 | 908.1794 | 917.2275 | 921.2396 | 907.1414 | 904.2276 | 902.8836 | 903.2327 | 908.6026 | 891.4831 | 897.6627 | 911.0148 | 887.1894 | 888.0969 | 914.3758 | 908.0021 | 900.804 | 906.142 | 902.4314 | 904.1858 | 903.4429 | 906.9181
2025-04-09 20:25 | 9 | 20 | 25 | 6.2817e-272 | 1 | 29.3962 | 693.3032 | 0.32448 | 0.0074708 | 157.3523 | 157.3523 | 157.3523 | 157.3523 | 12.1713 | 13.7126 | 646.4553 | 646.4553 | 646.4553 | 646.4553 | 59.6265 | 49.9926 | 15.7476 | 106.7956 | 15.5966 | 18.306 | 65.7291 | 1 | 49.9932 | 14 | 22.1 | 221 | 154840 | 237626.2979 | 3545117.8936 | 99.9852 | -0.0022194 | -0.066583 | -0.066583 | -0.066583 | 7.9917 | 1024.6602 | 1022.3845 | 1022.384 | 1024.6602 | 1066.6755 | 1066.6755 | 1066.6755 | 1066.6755 | 894.5224 | 894.5224 | 894.5224 | 12.1622 | 0 | 12.1315 | 80.3661 | 230.4768 | 230.6317 | 223.2646 | 2.0369 | 3.435 | 0 | 86 | 57.3706 | 59.6265 | 104.9837 | 7.4652 | 106.7956 | -4.1306 | 65.77 | 62.7704 | 48.8347 | 0 | 66.8379 | 777.3768 | 773.3516 | 715.6492 | 715.1833 | 706.3259 | 702.8517 | 518.5052 | 508.8869 | 732.8144 | 747.6498 | 897.284 | 912.5793 | 908.1839 | 918.0324 | 921.9338 | 907.0309 | 904.0172 | 902.1841 | 902.5899 | 907.4689 | 890.8245 | 897.1747 | 910.8651 | 886.9581 | 887.8876 | 912.573 | 907.7312 | 900.1691 | 905.6429 | 901.7032 | 903.1982 | 902.4733 | 906.3954
2025-04-09 20:26 | 9 | 20 | 26 | 6.2817e-272 | 1 | 29.3954 | 693.3345 | 0.32381 | 0.0074691 | 157.5922 | 157.5922 | 157.5922 | 157.5922 | 12.1885 | 13.7269 | 646.6288 | 646.6288 | 646.6288 | 646.6288 | 59.3506 | 50.0132 | 15.7414 | 107.2045 | 15.5978 | 18.347 | 65.9795 | 1 | 50.0139 | 14.6087 | 22.1 | 221 | 154840 | 237627.4565 | 3545135.4348 | 100.0265 | 0.011443 | 0.34328 | 0.34328 | 0.34328 | 7.9917 | 1024.348 | 1022.0633 | 1022.0622 | 1024.348 | 1066.1446 | 1066.1446 | 1066.1446 | 1066.1446 | 895.0972 | 895.0972 | 895.0972 | 12.2088 | 0 | 12.2054 | 80.6466 | 230.9327 | 231.0865 | 223.111 | 2.057 | 3.4448 | 0 | 86 | 57.5074 | 59.3506 | 104.9428 | 7.2825 | 107.2045 | -4.0655 | 65.9172 | 62.7835 | 48.8271 | 0 | 66.8374 | 777.148 | 772.9937 | 715.561 | 714.9103 | 706.2487 | 702.5995 | 518.024 | 508.5723 | 732.688 | 747.4071 | 898.1009 | 912.5441 | 907.7057 | 917.5918 | 921.666 | 907.2724 | 904.599 | 902.862 | 903.747 | 908.9391 | 892.1744 | 897.957 | 910.826 | 887.4244 | 887.3205 | 914.3273 | 908.4197 | 901.348 | 906.3598 | 902.3714 | 904.4113 | 902.4455 | 906.7886
2025-04-09 20:27 | 9 | 20 | 27 | 6.2817e-272 | 1 | 29.3948 | 693.671 | 0.33553 | 0.0074734 | 157.2297 | 157.2297 | 157.2297 | 157.2297 | 12.1631 | 13.7349 | 646.5829 | 646.5829 | 646.5829 | 646.5829 | 59.2242 | 50.0264 | 15.743 | 106.4549 | 15.5994 | 18.2357 | 65.5186 | 1 | 50.0276 | 14.1702 | 22.1 | 221 | 154840 | 237628.6383 | 3545153 | 100.0527 | -0.0099969 | -0.29991 | -0.29991 | -0.29991 | 7.9917 | 1024.8143 | 1022.5438 | 1022.5434 | 1024.8143 | 1067.1204 | 1067.1204 | 1067.1204 | 1067.1204 | 891.2464 | 891.2464 | 891.2464 | 11.989 | 0 | 12.0144 | 80.4181 | 230.3722 | 230.519 | 223.0943 | 2.0554 | 3.4555 | 0 | 86 | 57.738 | 59.2242 | 104.9531 | 7.1071 | 106.4549 | -4.1202 | 65.5174 | 62.782 | 48.8433 | 0 | 66.8371 | 777.0424 | 772.8021 | 715.4769 | 714.7343 | 706.1563 | 702.4224 | 517.5398 | 507.9184 | 732.6537 | 747.1735 | 894.2545 | 909.1558 | 904.1575 | 913.3491 | 917.8404 | 903.7316 | 900.803 | 899.3656 | 898.7896 | 905.0467 | 888.0046 | 893.5352 | 906.1889 | 884.0504 | 884.2557 | 910.8546 | 905.0987 | 897.1378 | 901.7272 | 898.6993 | 900.2848 | 899.1165 | 902.586
2025-04-09 20:28 | 9 | 20 | 28 | 6.2817e-272 | 1 | 29.3917 | 694.2645 | 0.33768 | 0.0074836 | 157.4235 | 157.4235 | 157.4235 | 157.4235 | 12.178 | 13.7491 | 647.3239 | 647.3239 | 647.3239 | 647.3239 | 59.1493 | 50.0533 | 15.7433 | 106.6059 | 15.6021 | 18.2809 | 65.6078 | 1 | 50.0533 | 14.5532 | 22.1 | 221 | 154840 | 237629.7872 | 3545170.6383 | 100.1064 | 0.0071659 | 0.21498 | 0.21498 | 0.21498 | 7.9917 | 1024.5357 | 1022.2574 | 1022.2596 | 1024.5357 | 1066.9234 | 1066.9234 | 1066.9234 | 1066.9234 | 892.2656 | 892.2656 | 892.2656 | 12.0922 | 0 | 12.0806 | 80.6006 | 230.7303 | 230.8846 | 223.0561 | 2.027 | 3.4548 | 0 | 86 | 57.8063 | 59.1493 | 104.9553 | 7.0652 | 106.6059 | -4.1598 | 65.6798 | 62.7805 | 48.8829 | 0 | 66.8364 | 776.8784 | 772.5107 | 715.4668 | 714.6678 | 706.0955 | 702.3803 | 517.079 | 507.6726 | 732.5159 | 746.6104 | 895.3035 | 910.4134 | 905.6048 | 914.7324 | 919.1657 | 904.914 | 901.9558 | 900.0854 | 900.3847 | 906.3566 | 889.1236 | 894.1558 | 908.4556 | 885.212 | 884.973 | 910.4355 | 905.5346 | 897.3959 | 903.169 | 899.5453 | 901.7915 | 899.7282 | 903.454
2025-04-09 20:29 | 9 | 20 | 29 | 6.2817e-272 | 1 | 29.3886 | 695.9553 | 0.34301 | 0.0074853 | 157.1729 | 157.1729 | 157.1729 | 157.1729 | 12.1615 | 13.7682 | 646.741 | 646.741 | 646.741 | 646.741 | 59.071 | 50.0932 | 15.7426 | 105.5583 | 15.6006 | 18.1038 | 64.9362 | 1 | 50.0937 | 13.1489 | 22.1 | 221 | 154840 | 237630.9574 | 3545188.2553 | 100.1863 | -0.0068529 | -0.20559 | -0.20559 | -0.20559 | 7.9917 | 1024.8372 | 1022.5677 | 1022.5664 | 1024.8372 | 1068.2883 | 1068.2883 | 1068.2883 | 1068.2883 | 886.6065 | 886.6065 | 886.6065 | 11.835 | 0 | 11.8378 | 80.5175 | 230.333 | 230.4827 | 222.9791 | 1.991 | 3.4631 | 0 | 86 | 57.1702 | 59.071 | 104.9509 | 6.7103 | 105.5583 | -4.1218 | 65.0435 | 62.7934 | 48.8857 | 0 | 66.8363 | 776.8277 | 772.3029 | 715.4762 | 714.5942 | 705.9925 | 702.2301 | 516.5675 | 507.1996 | 732.5027 | 745.9829 | 889.7614 | 904.2831 | 899.4042 | 908.877 | 913.5426 | 899.4441 | 895.9325 | 895.0238 | 892.8468 | 900.5929 | 883.5808 | 888.0135 | 900.6851 | 879.8232 | 879.2277 | 906.5744 | 901.4077 | 892.4597 | 896.6995 | 894.4438 | 895.8526 | 894.6302 | 897.7779
2025-04-09 20:30 | 9 | 20 | 30 | 6.2817e-272 | 1 | 29.3909 | 696.6279 | 0.34014 | 0.0074713 | 157.6486 | 157.6486 | 157.6486 | 157.6486 | 12.1943 | 13.756 | 647.4463 | 647.4463 | 647.4463 | 647.4463 | 58.9197 | 50.0589 | 15.7413 | 107.0066 | 15.6023 | 18.336 | 65.775 | 1 | 50.0595 | 15.234 | 22.1 | 221 | 154840 | 237632.1489 | 3545206 | 100.1176 | 0.0018591 | 0.055774 | 0.055774 | 0.055774 | 7.9917 | 1024.2451 | 1021.957 | 1021.9555 | 1024.2451 | 1066.4009 | 1066.4009 | 1066.4009 | 1066.4009 | 893.3879 | 893.3879 | 893.3879 | 12.1408 | 0 | 12.1305 | 80.7125 | 231.0397 | 231.1976 | 222.942 | 1.9915 | 3.4432 | 0 | 86 | 56.8198 | 58.9197 | 104.9419 | 6.7749 | 107.0066 | -4.1929 | 65.8776 | 62.7907 | 48.8345 | 0 | 66.8366 | 776.7813 | 772.0885 | 715.4317 | 714.5131 | 705.8816 | 701.996 | 516.0986 | 506.9438 | 732.3716 | 746.1892 | 896.1653 | 910.4693 | 905.3753 | 914.9575 | 919.2676 | 904.7405 | 902.8578 | 901.3419 | 902.0643 | 908.2854 | 890.9888 | 895.6141 | 908.2958 | 886.0217 | 885.3767 | 913.8105 | 906.9176 | 899.3981 | 904.6907 | 900.9373 | 902.7877 | 900.9899 | 905.4167
2025-04-09 20:31 | 9 | 20 | 31 | 6.2817e-272 | 1 | 29.3925 | 696.8742 | 0.33828 | 0.0074597 | 157.6433 | 157.6433 | 157.6433 | 157.6433 | 12.1933 | 13.7682 | 647.3366 | 647.3366 | 647.3366 | 647.3366 | 58.6847 | 50.0748 | 15.7419 | 106.9263 | 15.6006 | 18.3213 | 65.7166 | 1 | 50.0753 | 14.2128 | 22.1 | 221 | 154840 | 237633.234 | 3545223.6596 | 100.1494 | -0.0045615 | -0.13685 | -0.13685 | -0.13685 | 7.9917 | 1024.2636 | 1021.976 | 1021.9794 | 1024.2636 | 1066.5066 | 1066.5066 | 1066.5066 | 1066.5066 | 891.7569 | 891.7569 | 891.7569 | 12.0763 | 0 | 12.087 | 80.751 | 231.0899 | 231.2493 | 222.8854 | 2.0251 | 3.4656 | 0 | 86 | 57.2002 | 58.6847 | 104.946 | 6.6885 | 106.9263 | -4.2156 | 65.8248 | 62.7978 | 48.7868 | 0 | 66.836 | 776.7448 | 771.9154 | 715.3523 | 714.4247 | 705.7752 | 701.8574 | 515.6816 | 506.6469 | 732.3476 | 746.128 | 894.7142 | 908.9953 | 903.9475 | 913.4221 | 917.6459 | 903.5638 | 901.3764 | 899.4308 | 899.5951 | 905.8521 | 888.9345 | 893.6639 | 907.3231 | 884.4946 | 884.7463 | 912.4674 | 905.4546 | 897.4778 | 902.756 | 899.5575 | 901.272 | 899.1395 | 903.6375
2025-04-09 20:32 | 9 | 20 | 32 | 6.2817e-272 | 1 | 29.3888 | 697.5989 | 0.33158 | 0.0074604 | 157.5855 | 157.5855 | 157.5855 | 157.5855 | 12.1906 | 13.7569 | 647.4606 | 647.4606 | 647.4606 | 647.4606 | 58.9171 | 50.0599 | 15.7421 | 106.967 | 15.5998 | 18.3204 | 65.7561 | 1 | 50.0598 | 14.1277 | 22.1 | 221 | 154840 | 237634.383 | 3545241.4468 | 100.1196 | 0.0039278 | 0.11783 | 0.11783 | 0.11783 | 7.9917 | 1024.3121 | 1022.0257 | 1022.0281 | 1024.3121 | 1066.4534 | 1066.4534 | 1066.4534 | 1066.4534 | 893.0707 | 893.0707 | 893.0707 | 12.1193 | 0 | 12.1173 | 80.7444 | 231.0095 | 231.1668 | 222.8247 | 1.9827 | 3.4631 | 0 | 86 | 56.9713 | 58.9171 | 104.9471 | 6.8769 | 106.967 | -4.1329 | 65.8216 | 62.7899 | 48.7859 | 0 | 66.8361 | 776.9433 | 771.9611 | 715.3174 | 714.3113 | 705.6834 | 701.6512 | 515.29 | 506.481 | 732.3615 | 745.9908 | 895.8 | 910.1709 | 905.0541 | 915.316 | 919.6126 | 905.1975 | 902.9419 | 900.5423 | 901.2094 | 908.0043 | 889.6881 | 895.3119 | 908.4903 | 886.119 | 885.6339 | 913.4791 | 906.8343 | 898.6705 | 903.8966 | 900.8276 | 902.7224 | 900.1815 | 904.7933
2025-04-09 20:33 | 9 | 20 | 33 | 6.2817e-272 | 1 | 29.3895 | 698.5974 | 0.34492 | 0.0074544 | 157.6492 | 157.6492 | 157.6492 | 157.6492 | 12.1949 | 13.7574 | 647.1455 | 647.1455 | 647.1455 | 647.1455 | 59.0601 | 50.0684 | 15.7417 | 106.8193 | 15.6006 | 18.2987 | 65.6725 | 1 | 50.0688 | 13.9149 | 22.1 | 221 | 154840 | 237635.4894 | 3545259.2128 | 100.1367 | 0.00051688 | 0.015507 | 0.015507 | 0.015507 | 7.9917 | 1024.2372 | 1021.9483 | 1021.9479 | 1024.2372 | 1066.646 | 1066.646 | 1066.646 | 1066.646 | 892.1841 | 892.1841 | 892.1841 | 12.1148 | 0 | 12.1122 | 80.7674 | 231.072 | 231.2279 | 222.8314 | 1.9865 | 3.476 | 0 | 86 | 56.9123 | 59.0601 | 104.9447 | 6.8062 | 106.8193 | -4.1163 | 65.7435 | 62.7874 | 48.762 | 0 | 66.8348 | 776.9874 | 771.8311 | 715.2514 | 714.2514 | 705.5916 | 701.5491 | 514.8184 | 506.1691 | 732.3723 | 745.7836 | 894.9832 | 907.781 | 903.2032 | 913.797 | 918.1732 | 903.2056 | 901.5346 | 900.0755 | 900.962 | 907.289 | 889.3609 | 894.3349 | 906.9961 | 885.0899 | 884.1784 | 913.8282 | 906.7186 | 898.4375 | 903.655 | 899.805 | 902.3914 | 899.7752 | 903.5179
2025-04-09 20:34 | 9 | 20 | 34 | 6.2817e-272 | 1 | 29.394 | 698.3318 | 0.34543 | 0.007452 | 157.61 | 157.61 | 157.61 | 157.61 | 12.1904 | 13.764 | 647.4482 | 647.4482 | 647.4482 | 647.4482 | 59.0587 | 50.0836 | 15.7418 | 106.7405 | 15.5998 | 18.289 | 65.6203 | 1 | 50.0838 | 13.6522 | 22.1 | 221 | 154840 | 237636.6087 | 3545276.7391 | 100.167 | -0.00039295 | -0.011788 | -0.011788 | -0.011788 | 7.9917 | 1024.3146 | 1022.0287 | 1022.0341 | 1024.3146 | 1066.748 | 1066.748 | 1066.748 | 1066.748 | 891.4829 | 891.4829 | 891.4829 | 12.0844 | 0 | 12.0874 | 80.8026 | 231.0728 | 231.2392 | 222.7576 | 2.0387 | 3.4718 | 0 | 86 | 57.3911 | 59.0587 | 104.9456 | 6.6916 | 106.7405 | -4.2167 | 65.709 | 62.7934 | 48.7576 | 0 | 66.8357 | 776.9396 | 771.7732 | 715.2822 | 714.1869 | 705.5578 | 701.4479 | 514.4152 | 505.9589 | 732.2478 | 745.6931 | 894.5849 | 908.4271 | 903.5615 | 913.4969 | 917.6782 | 903.5378 | 901.5039 | 899.1076 | 899.1246 | 905.8617 | 888.1014 | 893.3674 | 907.267 | 884.4838 | 883.9169 | 911.8551 | 905.7896 | 897.1688 | 902.6732 | 899.4985 | 900.8232 | 898.617 | 902.974
2025-04-09 20:35 | 9 | 20 | 35 | 6.2817e-272 | 1 | 29.3942 | 697.993 | 0.32807 | 0.007452 | 157.9516 | 157.9516 | 157.9516 | 157.9516 | 12.2144 | 13.7566 | 647.646 | 647.646 | 647.646 | 647.646 | 59.1311 | 50.0698 | 15.7415 | 107.5991 | 15.5988 | 18.4064 | 66.0498 | 1 | 50.0702 | 15.2766 | 22.1 | 221 | 154840 | 237637.6809 | 3545294.383 | 100.1395 | 0.0024262 | 0.072785 | 0.072785 | 0.072785 | 7.9917 | 1023.8828 | 1021.5843 | 1021.5815 | 1023.8828 | 1065.6298 | 1065.6298 | 1065.6298 | 1065.6298 | 895.0688 | 895.0688 | 895.0688 | 12.2636 | 0 | 12.2542 | 80.9866 | 231.59 | 231.7507 | 222.8082 | 2.0629 | 3.451 | 0 | 86 | 57.2302 | 59.1311 | 104.9436 | 6.7168 | 107.5991 | -4.1244 | 66.1304 | 62.7831 | 48.7586 | 0 | 66.8355 | 776.8861 | 771.915 | 715.3581 | 714.26 | 705.5781 | 701.4175 | 514.037 | 505.6663 | 732.0375 | 745.721 | 898.0501 | 911.3374 | 906.2152 | 917.0344 | 921.4 | 906.2291 | 904.6762 | 902.5685 | 904.4504 | 909.9982 | 891.7964 | 897.9743 | 910.0729 | 887.4278 | 887.2408 | 916.597 | 909.0003 | 901.3731 | 907.0045 | 902.5936 | 905.2189 | 901.7331 | 906.3819
2025-04-09 20:36 | 9 | 20 | 36 | 6.2817e-272 | 1 | 29.3935 | 699.0396 | 0.34014 | 0.0074458 | 157.3914 | 157.3914 | 157.3914 | 157.3914 | 12.175 | 13.7601 | 645.9589 | 645.9589 | 645.9589 | 645.9589 | 58.9608 | 50.0693 | 15.7422 | 106.0346 | 15.5994 | 18.1602 | 65.1848 | 1 | 50.0694 | 13.617 | 22.1 | 221 | 154840 | 237638.8085 | 3545312.1277 | 100.1384 | 0.0021681 | 0.065044 | 0.065044 | 0.065044 | 7.9917 | 1024.5936 | 1022.3164 | 1022.3151 | 1024.5936 | 1067.6677 | 1067.6677 | 1067.6677 | 1067.6677 | 887.3572 | 887.3572 | 887.3572 | 11.9146 | 0 | 11.92 | 80.5921 | 230.5735 | 230.7341 | 222.8338 | 2.0419 | 3.4635 | 0 | 86 | 57.0587 | 58.9608 | 104.948 | 6.6881 | 106.0346 | -4.176 | 65.2461 | 62.8011 | 48.7321 | 0 | 66.8349 | 776.4891 | 771.6843 | 715.1921 | 714.0905 | 705.4917 | 701.3661 | 513.7265 | 505.1609 | 731.8809 | 745.6651 | 891.1063 | 903.9425 | 899.0811 | 908.5195 | 913.322 | 899.1741 | 896.521 | 896.0313 | 894.0171 | 901.3763 | 884.7772 | 889.3718 | 901.8948 | 880.2456 | 879.4463 | 907.8831 | 902.1395 | 893.3775 | 897.566 | 895.4723 | 897.0435 | 896.1258 | 898.485
2025-04-09 20:37 | 9 | 20 | 37 | 6.2817e-272 | 1 | 29.3907 | 698.8752 | 0.34294 | 0.0074461 | 157.7832 | 157.7832 | 157.7832 | 157.7832 | 12.2039 | 13.7629 | 647.507 | 647.507 | 647.507 | 647.507 | 58.8799 | 50.0732 | 15.7415 | 107.2364 | 15.6 | 18.3813 | 65.9151 | 1 | 50.0734 | 14.3404 | 22.1 | 221 | 154840 | 237639.9362 | 3545329.8298 | 100.1461 | 0.0029513 | 0.088539 | 0.088539 | 0.088539 | 7.9917 | 1024.0751 | 1021.7817 | 1021.7813 | 1024.0751 | 1066.1023 | 1066.1023 | 1066.1023 | 1066.1023 | 893.359 | 893.359 | 893.359 | 12.1826 | 0 | 12.1849 | 80.8883 | 231.3306 | 231.4838 | 222.838 | 2.0226 | 3.4757 | 0 | 86 | 57.511 | 58.8799 | 104.9436 | 6.7199 | 107.2364 | -4.2101 | 66.0406 | 62.7752 | 48.7301 | 0 | 66.8344 | 776.1919 | 771.5637 | 715.2053 | 714.1336 | 705.4179 | 701.3058 | 513.3561 | 504.8342 | 731.547 | 745.4943 | 896.4885 | 910.2015 | 904.9255 | 914.8095 | 919.1836 | 904.7888 | 902.1307 | 901.0121 | 902.099 | 908.4871 | 890.2538 | 896.0483 | 908.2662 | 885.5414 | 885.3599 | 914.9747 | 906.8044 | 899.508 | 904.5545 | 901.1735 | 903.2646 | 900.9485 | 904.8131
2025-04-09 20:38 | 9 | 20 | 38 | 6.2817e-272 | 1 | 29.3872 | 699.7428 | 0.3284 | 0.0074477 | 156.2652 | 156.2652 | 156.2652 | 156.2652 | 12.0977 | 13.7657 | 644.9649 | 644.9649 | 644.9649 | 644.9649 | 58.425 | 50.0575 | 15.7452 | 103.0667 | 15.603 | 17.6758 | 63.4495 | 1 | 50.0582 | 18 | 22.1 | 221 | 154840 | 237641.0851 | 3545347.4468 | 100.1148 | -0.004535 | -0.13605 | -0.13605 | -0.13605 | 7.9917 | 1025.984 | 1023.7494 | 1023.7449 | 1025.984 | 1071.5334 | 1071.5334 | 1071.5334 | 1071.5334 | 875.7161 | 875.7161 | 875.7161 | 11.3769 | 0 | 11.3307 | 79.8788 | 228.8294 | 228.989 | 222.7853 | 2.0033 | 3.4833 | 0 | 86 | 57.4814 | 58.425 | 104.968 | 6.4529 | 103.0667 | -4.0741 | 63.5058 | 62.7714 | 48.7333 | 0 | 66.8339 | 775.6817 | 771.2883 | 714.9537 | 713.9467 | 705.2716 | 701.3698 | 513.0802 | 504.3442 | 731.3538 | 745.4773 | 879.9443 | 893.0255 | 888.7482 | 898.492 | 904.1365 | 889.5901 | 884.7415 | 885.1891 | 880.0126 | 889.0899 | 872.7045 | 876.9924 | 888.2201 | 870.297 | 869.3307 | 894.654 | 891.588 | 881.2412 | 883.4274 | 883.5976 | 885.1551 | 884.0242 | 885.6456
2025-04-09 20:39 | 9 | 20 | 39 | 6.2817e-272 | 1 | 29.3922 | 700.2199 | 0.31982 | 0.007456 | 152.3424 | 152.3424 | 152.3424 | 152.3424 | 11.8178 | 13.781 | 638.1315 | 638.1315 | 638.1315 | 638.1315 | 58.1462 | 50.0792 | 15.7458 | 92.481 | 15.6038 | 16.0792 | 57.7274 | 1 | 50.08 | 17.4894 | 22.1 | 221 | 154840 | 237642 | 3545363.6383 | 100.1582 | -0.0013874 | -0.041623 | -0.041623 | -0.041623 | 7.9917 | 1031.0296 | 1028.9485 | 1028.9481 | 1031.0296 | 1085.323 | 1085.323 | 1085.323 | 1085.323 | 825.2797 | 825.2797 | 825.2797 | 9.3104 | 0 | 9.271 | 77.9452 | 223.1008 | 223.2297 | 222.1985 | 2.0481 | 3.4775 | 0 | 86 | 57.4607 | 58.1462 | 104.9719 | 5.2387 | 92.481 | -4.0864 | 57.7694 | 62.7803 | 48.7722 | 0 | 66.8339 | 772.1664 | 767.9835 | 713.6143 | 712.7109 | 704.6831 | 701.3561 | 512.3818 | 502.3491 | 730.2336 | 744.3447 | 828.7768 | 841.8949 | 840.0286 | 847.509 | 856.671 | 842.7079 | 834.9591 | 837.9476 | 827.7739 | 836.0171 | 824.1579 | 822.519 | 830.3082 | 826.0107 | 820.5013 | 838.6701 | 844.4776 | 830.6437 | 824.1265 | 832.4621 | 837.6294 | 834.6857 | 833.9
2025-04-09 20:40 | 9 | 20 | 40 | 6.2817e-272 | 1 | 29.392 | 699.8227 | 0.3177 | 0.0074676 | 150.5947 | 150.5947 | 150.5947 | 150.5947 | 11.694 | 13.7689 | 634.7085 | 634.7085 | 634.7085 | 634.7085 | 58.4241 | 50.0635 | 15.7438 | 88.1295 | 15.6026 | 15.5078 | 55.6492 | 1 | 50.0633 | 14.6809 | 22.1 | 221 | 154840 | 237642.9574 | 3545378.5745 | 100.1269 | 0.010339 | 0.31018 | 0.31018 | 0.31018 | 7.9917 | 1033.2623 | 1031.247 | 1031.2513 | 1033.2623 | 1090.9909 | 1090.9909 | 1090.9909 | 1090.9909 | 801.647 | 801.647 | 801.647 | 8.5261 | 0 | 8.5199 | 77.138 | 220.6097 | 220.7445 | 220.9245 | 2.0636 | 3.4713 | 0 | 86 | 57.3565 | 58.4241 | 104.9587 | 4.7739 | 88.1295 | -4.1046 | 55.7166 | 62.8331 | 48.8188 | 0 | 66.8346 | 767.0562 | 762.8565 | 712.0427 | 711.1756 | 703.6055 | 700.368 | 510.7659 | 499.678 | 727.8937 | 742.6096 | 803.6856 | 818.1161 | 817.0001 | 821.0689 | 829.8369 | 818.7911 | 811.5781 | 814.8032 | 804.9558 | 812.4373 | 802.012 | 797.5037 | 805.7748 | 804.2234 | 798.3623 | 811.8854 | 819.1322 | 806.7943 | 799.2504 | 808.4473 | 816.2595 | 811.3149 | 809.9171
2025-04-09 20:41 | 9 | 20 | 41 | 6.2817e-272 | 1 | 29.3908 | 700.7339 | 0.30974 | 0.0074702 | 150.4601 | 150.4601 | 150.4601 | 150.4601 | 11.6849 | 13.7747 | 634.3017 | 634.3017 | 634.3017 | 634.3017 | 58.5781 | 50.085 | 15.7449 | 87.4043 | 15.603 | 15.4182 | 55.3092 | 1 | 50.0856 | 13.7872 | 22.1 | 221 | 154840 | 237643.7447 | 3545393.1915 | 100.1697 | -0.00067086 | -0.020127 | -0.020127 | -0.020127 | 7.9917 | 1033.4277 | 1031.4179 | 1031.4191 | 1033.4277 | 1091.9355 | 1091.9355 | 1091.9355 | 1091.9355 | 795.6054 | 795.6054 | 795.6054 | 8.4124 | 0 | 8.4087 | 77.1614 | 220.486 | 220.6393 | 219.9868 | 2.0209 | 3.4693 | 0 | 86 | 57.3934 | 58.5781 | 104.9662 | 4.5342 | 87.4043 | -4.1001 | 55.3947 | 62.8803 | 48.8271 | 0 | 66.8346 | 763.2442 | 758.8131 | 710.9138 | 710.1548 | 702.1725 | 698.8107 | 508.9439 | 497.6191 | 725.5762 | 740.0338 | 797.6558 | 812.345 | 810.9001 | 813.1517 | 820.4467 | 812.2939 | 805.1806 | 808.709 | 798.8712 | 806.4283 | 795.9229 | 791.4258 | 800.3346 | 798.4473 | 792.6959 | 805.9701 | 811.4253 | 800.7134 | 793.234 | 802.6448 | 810.7069 | 805.8678 | 803.8611
2025-04-09 20:42 | 9 | 20 | 42 | 6.2817e-272 | 1 | 29.3914 | 701.2516 | 0.30272 | 0.0074653 | 150.6939 | 150.6939 | 150.6939 | 150.6939 | 11.7013 | 13.7709 | 634.1276 | 634.1276 | 634.1276 | 634.1276 | 58.7296 | 50.0835 | 15.7439 | 87.9712 | 15.599 | 15.5272 | 55.6606 | 1 | 50.084 | 14.0851 | 22.1 | 221 | 154840 | 237644.4043 | 3545407.7872 | 100.1668 | -3.5091e-06 | -0.0001059 | -0.0001059 | -0.0001059 | 7.9917 | 1033.1321 | 1031.1153 | 1031.113 | 1033.1321 | 1091.1968 | 1091.1968 | 1091.1968 | 1091.1968 | 797.0325 | 797.0325 | 797.0325 | 8.5463 | 0 | 8.5447 | 77.3365 | 220.8763 | 221.034 | 219.4628 | 2.0261 | 3.4869 | 0 | 86 | 57.3894 | 58.7296 | 104.9592 | 4.7715 | 87.9712 | -4.0825 | 55.7862 | 62.9443 | 48.809 | 0 | 66.8347 | 760.4721 | 755.8671 | 710.1287 | 709.3962 | 700.5964 | 697.0657 | 507.1977 | 495.595 | 723.226 | 737.3719 | 799.2883 | 814.2363 | 812.54 | 813.1584 | 819.1112 | 813.5797 | 805.8257 | 810.1823 | 800.0632 | 808.1968 | 796.7904 | 793.3949 | 801.5839 | 798.808 | 794.1507 | 808.626 | 812.0786 | 802.0808 | 794.917 | 804.8737 | 812.6084 | 807.9137 | 805.4819
2025-04-09 20:43 | 9 | 20 | 43 | 6.2817e-272 | 1 | 29.3867 | 701.875 | 0.29796 | 0.0074528 | 150.6973 | 150.6973 | 150.6973 | 150.6973 | 11.7032 | 13.7636 | 634.5315 | 634.5315 | 634.5315 | 634.5315 | 58.9311 | 50.0758 | 15.7419 | 88.3348 | 15.5968 | 15.5784 | 55.8703 | 1 | 50.0757 | 14.7826 | 22.1 | 221 | 154840 | 237645.1304 | 3545422.2174 | 100.1514 | 0.0057866 | 0.1736 | 0.1736 | 0.1736 | 7.9917 | 1033.0976 | 1031.078 | 1031.0802 | 1033.0976 | 1090.7237 | 1090.7237 | 1090.7237 | 1090.7237 | 797.8003 | 797.8003 | 797.8003 | 8.5928 | 0 | 8.6083 | 77.3478 | 220.8248 | 220.9997 | 219.1157 | 1.9682 | 3.4811 | 0 | 86 | 57.3437 | 58.9311 | 104.9462 | 4.769 | 88.3348 | -4.091 | 55.9701 | 62.952 | 48.7523 | 0 | 66.8345 | 758.5984 | 753.863 | 709.4254 | 708.8018 | 699.0738 | 695.4507 | 505.6403 | 494.0442 | 720.9754 | 734.6859 | 799.3085 | 815.2856 | 813.0207 | 813.1215 | 818.1955 | 814.6502 | 806.1092 | 811.0655 | 800.9865 | 809.6232 | 797.0894 | 793.8497 | 802.7544 | 799.6179 | 794.0943 | 809.6841 | 811.93 | 802.8111 | 796.129 | 806.4917 | 812.8863 | 809.1192 | 806.724
2025-04-09 20:44 | 9 | 20 | 44 | 6.2817e-272 | 1 | 29.3841 | 703.84 | 0.30288 | 0.0074361 | 150.3139 | 150.3139 | 150.3139 | 150.3139 | 11.6771 | 13.753 | 634.4405 | 634.4405 | 634.4405 | 634.4405 | 59.7699 | 50.0928 | 15.7453 | 87.2366 | 15.6019 | 15.4133 | 55.2875 | 1 | 50.0934 | 13.7447 | 22.1 | 221 | 154840 | 237646 | 3545436.6809 | 100.1856 | -0.0039394 | -0.11818 | -0.11818 | -0.11818 | 7.9917 | 1033.5721 | 1031.5677 | 1031.5657 | 1033.5721 | 1092.1538 | 1092.1538 | 1092.1538 | 1092.1538 | 794.1202 | 794.1202 | 794.1202 | 8.4617 | 0 | 8.4631 | 77.2341 | 220.3643 | 220.5224 | 218.8782 | 1.9664 | 3.5076 | 0 | 86 | 57.4329 | 59.7699 | 104.9688 | 4.4722 | 87.2366 | -4.0786 | 55.3769 | 62.9604 | 48.6833 | 0 | 66.8333 | 757.1721 | 752.2427 | 708.7202 | 708.2241 | 697.5914 | 694.092 | 504.2899 | 492.6218 | 718.8811 | 732.2771 | 795.1033 | 811.6975 | 809.5844 | 809.1938 | 814.1254 | 810.3349 | 802.7807 | 807.4027 | 797.2586 | 805.0142 | 793.8871 | 790.129 | 799.289 | 796.3576 | 790.9432 | 805.7434 | 808.2294 | 799.0083 | 792.1283 | 802.5309 | 809.824 | 805.7181 | 803.0757
2025-04-09 20:45 | 9 | 20 | 45 | 6.2817e-272 | 1 | 29.3842 | 704.6866 | 0.29861 | 0.0074238 | 150.4795 | 150.4795 | 150.4795 | 150.4795 | 11.6888 | 13.7309 | 635.7672 | 635.7672 | 635.7672 | 635.7672 | 60.5045 | 50.0781 | 15.7437 | 88.0507 | 15.6003 | 15.5353 | 55.7408 | 1 | 50.0782 | 14.766 | 22.1 | 221 | 154840 | 237646.8511 | 3545451.2553 | 100.1561 | 0.0028289 | 0.084868 | 0.084868 | 0.084868 | 7.9917 | 1033.3572 | 1031.3462 | 1031.3468 | 1033.3572 | 1091.0938 | 1091.0938 | 1091.0938 | 1091.0938 | 798.2834 | 798.2834 | 798.2834 | 8.6702 | 0 | 8.6621 | 77.3146 | 220.6602 | 220.8422 | 218.6755 | 1.953 | 3.4936 | 0 | 86 | 57.6265 | 60.5045 | 104.9577 | 4.9697 | 88.0507 | -4.1254 | 55.8153 | 62.9604 | 48.6346 | 0 | 66.8333 | 756.297 | 751.1544 | 708.2135 | 707.8029 | 696.3286 | 692.9556 | 502.9158 | 491.1946 | 716.9926 | 730.1047 | 799.6598 | 815.8929 | 813.4964 | 812.9202 | 816.9839 | 814.8142 | 806.5873 | 811.861 | 801.2878 | 810.1296 | 797.4775 | 794.6521 | 803.5945 | 800.3931 | 794.5358 | 810.9499 | 811.9194 | 802.9933 | 796.3921 | 807.3341 | 813.3914 | 809.8114 | 807.0429
2025-04-09 20:46 | 9 | 20 | 46 | 6.2817e-272 | 1 | 29.3886 | 704.1362 | 0.28794 | 0.0074129 | 150.181 | 150.181 | 150.181 | 150.181 | 11.666 | 13.6954 | 635.6549 | 635.6549 | 635.6549 | 635.6549 | 61.7421 | 50.0563 | 15.7447 | 87.9472 | 15.5993 | 15.5371 | 55.7354 | 1 | 50.0564 | 14.5106 | 22.1 | 221 | 154840 | 237647.6383 | 3545465.9362 | 100.1126 | 0.0061666 | 0.185 | 0.185 | 0.185 | 7.9917 | 1033.7698 | 1031.7715 | 1031.7702 | 1033.7698 | 1091.2287 | 1091.2287 | 1091.2287 | 1091.2287 | 799.9264 | 799.9264 | 799.9264 | 8.7075 | 0 | 8.7049 | 77.1727 | 220.1786 | 220.3412 | 218.4995 | 2.0221 | 3.5235 | 0 | 86 | 57.3043 | 61.7421 | 104.9643 | 5.1145 | 87.9472 | -4.0692 | 55.8218 | 62.9646 | 48.5938 | 0 | 66.8332 | 755.8447 | 750.4537 | 707.7034 | 707.3624 | 695.1729 | 691.9015 | 501.6848 | 489.9352 | 715.4507 | 728.1107 | 801.133 | 817.6806 | 815.1527 | 815.0339 | 818.8443 | 816.7108 | 807.8059 | 813.0611 | 802.7427 | 811.4191 | 798.179 | 796.3686 | 805.1228 | 801.816 | 795.9805 | 812.4297 | 813.6692 | 805.126 | 798.9331 | 809.5104 | 814.729 | 811.81 | 808.9048
2025-04-09 20:47 | 9 | 20 | 47 | 6.2817e-272 | 1 | 29.3951 | 702.7837 | 0.28454 | 0.0074068 | 150.2338 | 150.2338 | 150.2338 | 150.2338 | 11.6673 | 13.6856 | 636.7499 | 636.7499 | 636.7499 | 636.7499 | 62.0012 | 50.0478 | 15.7431 | 88.3395 | 15.5978 | 15.598 | 55.9928 | 1 | 50.0482 | 14.766 | 22.1 | 221 | 154840 | 237648.4468 | 3545480.5319 | 100.0955 | 7.5687e-05 | 0.0022706 | 0.0022706 | 0.0022706 | 7.9917 | 1033.746 | 1031.747 | 1031.7449 | 1033.746 | 1090.7174 | 1090.7174 | 1090.7174 | 1090.7174 | 801.7407 | 801.7407 | 801.7407 | 8.7945 | 0 | 8.7996 | 77.0886 | 220.2449 | 220.3968 | 218.3521 | 2.0611 | 3.4639 | 0 | 86 | 58.0359 | 62.0012 | 104.9541 | 5.1299 | 88.3395 | -4.0179 | 56.0406 | 62.9616 | 48.5775 | 0 | 66.8331 | 755.6159 | 750.025 | 707.3292 | 707.035 | 694.3099 | 691.1 | 500.4413 | 489.0528 | 714.1701 | 726.4279 | 802.5386 | 819.7716 | 816.8228 | 816.1412 | 819.7028 | 818.7376 | 809.8004 | 815.2921 | 804.6172 | 813.9707 | 800.3837 | 797.8359 | 807.4161 | 803.8996 | 797.7424 | 814.9412 | 815.0919 | 806.0218 | 799.7335 | 811.4507 | 816.4831 | 813.7967 | 811.188
2025-04-09 20:48 | 9 | 20 | 48 | 6.2817e-272 | 1 | 29.3954 | 702.1699 | 0.28778 | 0.0073993 | 150.067 | 150.067 | 150.067 | 150.067 | 11.6554 | 13.6929 | 636.6709 | 636.6709 | 636.6709 | 636.6709 | 62.1002 | 50.0675 | 15.7447 | 87.532 | 15.5998 | 15.4794 | 55.5461 | 1 | 50.0674 | 13.8298 | 22.1 | 221 | 154840 | 237649.2553 | 3545495.1702 | 100.135 | 0.0076832 | 0.2305 | 0.2305 | 0.2305 | 7.9917 | 1033.9602 | 1031.967 | 1031.9687 | 1033.9602 | 1091.7694 | 1091.7694 | 1091.7694 | 1091.7694 | 798.1007 | 798.1007 | 798.1007 | 8.6618 | 0 | 8.6589 | 77.0803 | 219.9837 | 220.126 | 218.2799 | 2.1115 | 3.4833 | 0 | 86 | 58.5713 | 62.1002 | 104.9643 | 4.857 | 87.532 | -4.1176 | 55.6146 | 62.9692 | 48.5474 | 0 | 66.8325 | 755.2206 | 749.5949 | 706.9206 | 706.5575 | 693.5021 | 690.3049 | 499.2601 | 487.902 | 713.0836 | 724.7389 | 799.0185 | 815.6977 | 813.1056 | 812.857 | 816.6116 | 814.6794 | 806.1163 | 811.3603 | 801.0126 | 809.7496 | 797.0957 | 794.0996 | 803.9259 | 800.4857 | 794.8023 | 810.7052 | 811.8999 | 802.6871 | 796.0816 | 807.3669 | 813.0832 | 809.8795 | 807.321
2025-04-09 20:49 | 9 | 20 | 49 | 6.2817e-272 | 1 | 29.3959 | 701.1258 | 0.28358 | 0.0073968 | 150.0229 | 150.0229 | 150.0229 | 150.0229 | 11.6521 | 13.6812 | 636.5828 | 636.5828 | 636.5828 | 636.5828 | 62.1777 | 50.0456 | 15.7474 | 87.6715 | 15.602 | 15.4951 | 55.6084 | 1 | 50.0458 | 14.8085 | 22.1 | 221 | 154840 | 237650.1064 | 3545509.8085 | 100.0911 | -0.012728 | -0.38183 | -0.38183 | -0.38183 | 7.9917 | 1034.0181 | 1032.0268 | 1032.0274 | 1034.0181 | 1091.5881 | 1091.5881 | 1091.5881 | 1091.5881 | 798.8645 | 798.8645 | 798.8645 | 8.6688 | 0 | 8.6722 | 76.9604 | 219.8257 | 219.9739 | 218.3411 | 2.0934 | 3.4697 | 0 | 86 | 58.4242 | 62.1777 | 104.9827 | 5.1683 | 87.6715 | -4.0838 | 55.6708 | 62.9688 | 48.5367 | 0 | 66.8328 | 754.9517 | 749.2055 | 706.5851 | 706.1932 | 692.7834 | 689.6157 | 498.1249 | 487.1808 | 712.1933 | 723.4874 | 799.7382 | 816.4346 | 813.8671 | 813.8188 | 817.3103 | 815.4745 | 807.0714 | 811.9182 | 801.6754 | 810.5405 | 797.434 | 794.8212 | 804.9599 | 801.6302 | 795.814 | 811.5703 | 812.5267 | 803.1325 | 796.7716 | 808.25 | 813.8454 | 810.6099 | 807.9504
2025-04-09 20:50 | 9 | 20 | 50 | 6.2817e-272 | 1 | 29.3941 | 701.3282 | 0.29292 | 0.0073935 | 150.365 | 150.365 | 150.365 | 150.365 | 11.677 | 13.6994 | 636.5309 | 636.5309 | 636.5309 | 636.5309 | 61.6146 | 50.06 | 15.7427 | 87.9955 | 15.6 | 15.5456 | 55.7626 | 1 | 50.0604 | 14.2553 | 22.1 | 221 | 154840 | 237651 | 3545524.3617 | 100.1199 | 0.0033939 | 0.10182 | 0.10182 | 0.10182 | 7.9917 | 1033.5719 | 1031.5664 | 1031.566 | 1033.5719 | 1091.1655 | 1091.1655 | 1091.1655 | 1091.1655 | 798.9669 | 798.9669 | 798.9669 | 8.747 | 0 | 8.7263 | 77.2109 | 220.4117 | 220.5523 | 218.2887 | 2.0777 | 3.4755 | 0 | 86 | 58.3212 | 61.6146 | 104.9511 | 4.9273 | 87.9955 | -4.1092 | 55.8524 | 62.9694 | 48.5219 | 0 | 66.8325 | 754.5293 | 748.7115 | 706.194 | 705.8513 | 692.177 | 689.0262 | 497.0337 | 486.064 | 711.4173 | 722.3802 | 800.4473 | 816.6904 | 814.2154 | 813.542 | 816.9869 | 815.6006 | 807.2448 | 812.2437 | 801.8229 | 811.0814 | 797.4264 | 794.9484 | 804.6109 | 801.412 | 795.4133 | 812.5499 | 812.4326 | 803.1613 | 796.8087 | 808.4003 | 813.3124 | 810.7722 | 808.1077
2025-04-09 20:51 | 9 | 20 | 51 | 6.2817e-272 | 1 | 29.3933 | 701.5041 | 0.28424 | 0.0073875 | 150.3695 | 150.3695 | 150.3695 | 150.3695 | 11.6776 | 13.7049 | 635.9681 | 635.9681 | 635.9681 | 635.9681 | 61.339 | 50.0572 | 15.7427 | 88.192 | 15.5993 | 15.5786 | 55.9089 | 1 | 50.0579 | 14.3478 | 22.1 | 221 | 154840 | 237651.8913 | 3545538.8261 | 100.1143 | -0.0070772 | -0.21232 | -0.21232 | -0.21232 | 7.9917 | 1033.56 | 1031.5554 | 1031.5552 | 1033.56 | 1090.9098 | 1090.9098 | 1090.9098 | 1090.9098 | 798.7788 | 798.7788 | 798.7788 | 8.7106 | 0 | 8.7328 | 77.2693 | 220.4314 | 220.5872 | 218.3135 | 2.0826 | 3.4838 | 0 | 86 | 58.1145 | 61.339 | 104.9517 | 4.8836 | 88.192 | -4.1305 | 55.9709 | 62.9711 | 48.4974 | 0 | 66.8322 | 754.1358 | 748.1609 | 705.8513 | 705.4705 | 691.6302 | 688.4148 | 495.9649 | 485.4655 | 710.825 | 721.4709 | 799.7974 | 816.4333 | 813.6413 | 812.9075 | 816.2746 | 815.3839 | 807.4688 | 812.347 | 801.9657 | 811.0985 | 797.3285 | 794.6874 | 804.1976 | 801.1163 | 794.8129 | 812.4585 | 812.4783 | 802.8246 | 796.5716 | 808.508 | 813.418 | 810.5222 | 807.9472
2025-04-09 20:52 | 9 | 20 | 52 | 6.2817e-272 | 1 | 29.3966 | 698.9129 | 0.27453 | 0.0073838 | 150.1513 | 150.1513 | 150.1513 | 150.1513 | 11.6609 | 13.6684 | 637.0616 | 637.0616 | 637.0616 | 637.0616 | 62.6596 | 50.0387 | 15.7445 | 88.2604 | 15.6006 | 15.6023 | 55.985 | 1 | 50.0394 | 14.6383 | 22.1 | 221 | 154840 | 237652.6809 | 3545553.3617 | 100.0774 | -0.00081618 | -0.024486 | -0.024486 | -0.024486 | 7.9917 | 1033.8566 | 1031.8613 | 1031.8632 | 1033.8566 | 1090.8202 | 1090.8202 | 1090.8202 | 1090.8202 | 803.038 | 803.038 | 803.038 | 8.8582 | 0 | 8.8443 | 77.0689 | 220.0334 | 220.2056 | 218.3833 | 2.1444 | 3.4854 | 0 | 86 | 58.4144 | 62.6596 | 104.963 | 5.0939 | 88.2604 | -4.127 | 56.0561 | 62.9612 | 48.4861 | 0 | 66.8318 | 754.5148 | 748.3008 | 705.6721 | 705.3009 | 691.1937 | 688.0116 | 494.9418 | 484.8692 | 710.4287 | 720.7774 | 803.9462 | 821.0818 | 818.2193 | 817.803 | 820.5466 | 819.6623 | 811.1029 | 816.3578 | 805.5691 | 815.4876 | 801.0806 | 798.9896 | 808.6894 | 805.3943 | 798.8061 | 816.8556 | 816.6168 | 807.2168 | 801.115 | 813.4357 | 817.2232 | 815.2906 | 812.9313
2025-04-09 20:53 | 9 | 20 | 53 | 6.2817e-272 | 1 | 29.3985 | 697.7821 | 0.28819 | 0.0073708 | 149.868 | 149.868 | 149.868 | 149.868 | 11.6401 | 13.6487 | 637.4174 | 637.4174 | 637.4174 | 637.4174 | 63.5767 | 50.0389 | 15.7435 | 87.9579 | 15.599 | 15.5485 | 55.8109 | 1 | 50.0393 | 14 | 22.1 | 221 | 154840 | 237653.5106 | 3545568.0426 | 100.0778 | -0.0011704 | -0.035111 | -0.035111 | -0.035111 | 7.9917 | 1034.2338 | 1032.2491 | 1032.2479 | 1034.2338 | 1091.214 | 1091.214 | 1091.214 | 1091.214 | 802.5784 | 802.5784 | 802.5784 | 8.808 | 0 | 8.8154 | 76.9974 | 219.6894 | 219.8471 | 218.3203 | 2.1539 | 3.5044 | 0 | 86 | 58.7058 | 63.5767 | 104.9569 | 5.2003 | 87.9579 | -4.152 | 55.8628 | 62.9636 | 48.4358 | 0 | 66.8309 | 754.9385 | 748.5224 | 705.5521 | 705.1879 | 690.926 | 687.8057 | 493.975 | 484.2326 | 710.1894 | 720.2259 | 803.2681 | 820.4499 | 817.3381 | 817.5401 | 820.3889 | 819.2005 | 810.9805 | 815.9061 | 805.3796 | 815.0416 | 800.4746 | 798.3805 | 808.0182 | 805.096 | 798.6777 | 815.9226 | 816.5366 | 807.1387 | 800.6389 | 812.8141 | 816.7823 | 814.5344 | 812.3021
2025-04-09 20:54 | 9 | 20 | 54 | 6.2817e-272 | 1 | 29.3985 | 697.6214 | 0.28396 | 0.0073596 | 149.7987 | 149.7987 | 149.7987 | 149.7987 | 11.6352 | 13.6316 | 637.6387 | 637.6387 | 637.6387 | 637.6387 | 64.1622 | 50.0288 | 15.7482 | 87.9164 | 15.6018 | 15.5554 | 55.8251 | 1 | 50.0298 | 14.4681 | 22.1 | 221 | 154840 | 237654.383 | 3545582.6383 | 100.0575 | -0.026715 | -0.80145 | -0.80145 | -0.80145 | 7.9917 | 1034.3243 | 1032.3423 | 1032.3394 | 1034.3243 | 1091.2685 | 1091.2685 | 1091.2685 | 1091.2685 | 802.9991 | 802.9991 | 802.9991 | 8.8543 | 0 | 8.8467 | 76.9 | 219.5555 | 219.7004 | 218.2913 | 2.1445 | 3.5134 | 0 | 86 | 58.7978 | 64.1622 | 104.9879 | 5.2944 | 87.9164 | -4.0134 | 55.8874 | 62.962 | 48.3899 | 0 | 66.8288 | 755.1633 | 748.5552 | 705.3804 | 705.0759 | 690.7274 | 687.587 | 493.0117 | 483.5491 | 709.872 | 719.7219 | 803.8091 | 820.6319 | 817.4276 | 817.947 | 820.774 | 819.6488 | 811.0609 | 816.1402 | 805.809 | 815.5175 | 800.9078 | 798.8305 | 808.1797 | 805.5573 | 799.0638 | 816.6603 | 817.0668 | 807.11 | 801.3837 | 813.6823 | 817.2731 | 814.9115 | 813.1706
2025-04-09 20:55 | 9 | 20 | 55 | 6.2817e-272 | 1 | 29.3917 | 699.5356 | 0.28909 | 0.0073447 | 149.9937 | 149.9937 | 149.9937 | 149.9937 | 11.6515 | 13.6269 | 637.4468 | 637.4468 | 637.4468 | 637.4468 | 64.1763 | 50.0187 | 15.741 | 88.3733 | 15.6012 | 15.6223 | 56.0868 | 1 | 50.0185 | 14.9787 | 22.1 | 221 | 154840 | 237655.234 | 3545597.2979 | 100.0373 | -0.0023806 | -0.071418 | -0.071418 | -0.071418 | 7.9917 | 1034.0272 | 1032.0372 | 1032.0368 | 1034.0272 | 1090.6732 | 1090.6732 | 1090.6732 | 1090.6732 | 804.3787 | 804.3787 | 804.3787 | 8.9355 | 0 | 8.9333 | 76.9695 | 219.8015 | 219.9372 | 218.2512 | 2.0291 | 3.492 | 0 | 86 | 58.4878 | 64.1763 | 104.9403 | 5.3348 | 88.3733 | -4.1413 | 56.1279 | 62.9649 | 48.3232 | 0 | 66.8289 | 755.1633 | 748.5153 | 705.1888 | 704.8656 | 690.4776 | 687.3643 | 492.0383 | 483.03 | 709.5923 | 719.2517 | 804.9576 | 822.3309 | 819.4194 | 819.2029 | 821.6028 | 821.0347 | 812.6993 | 817.5532 | 806.6935 | 817.0418 | 802.1842 | 800.1973 | 809.7288 | 806.9626 | 799.956 | 818.2934 | 818.5317 | 808.7342 | 802.7821 | 815.2311 | 818.2423 | 816.367 | 814.3239
2025-04-09 20:56 | 9 | 20 | 56 | 6.2817e-272 | 1 | 29.3951 | 699.5855 | 0.28358 | 0.0073334 | 149.8717 | 149.8717 | 149.8717 | 149.8717 | 11.6417 | 13.6275 | 636.3924 | 636.3924 | 636.3924 | 636.3924 | 64.1582 | 50.017 | 15.743 | 87.8639 | 15.5977 | 15.5372 | 55.8008 | 1 | 50.0191 | 14.2979 | 22.1 | 221 | 154840 | 237656.1277 | 3545611.9149 | 100.0341 | -0.023128 | -0.69383 | -0.69383 | -0.69383 | 7.9917 | 1034.2085 | 1032.2236 | 1032.2217 | 1034.2085 | 1091.3368 | 1091.3368 | 1091.3368 | 1091.3368 | 800.9107 | 800.9107 | 800.9107 | 8.8071 | 0 | 8.8225 | 76.9375 | 219.6183 | 219.749 | 218.193 | 2.0864 | 3.4897 | 0 | 86 | 58.4054 | 64.1582 | 104.9532 | 5.2744 | 87.8639 | -4.1004 | 55.8222 | 62.9516 | 48.2828 | 0 | 66.8286 | 754.9106 | 748.2216 | 704.9611 | 704.583 | 690.3077 | 687.0727 | 491.1324 | 482.269 | 709.239 | 718.8283 | 801.2323 | 818.4507 | 815.9055 | 815.7941 | 818.5431 | 817.0582 | 809.14 | 814.1207 | 803.3174 | 813.0743 | 799.242 | 796.3597 | 806.1029 | 803.4544 | 796.856 | 814.4372 | 815.3281 | 805.274 | 799.1047 | 811.5906 | 815.4817 | 812.9891 | 810.9146
2025-04-09 20:57 | 9 | 20 | 57 | 6.2817e-272 | 1 | 29.3913 | 699.87 | 0.27935 | 0.0073247 | 149.8577 | 149.8577 | 149.8577 | 149.8577 | 11.6421 | 13.623 | 635.8468 | 635.8468 | 635.8468 | 635.8468 | 63.5182 | 49.9776 | 15.7481 | 88.0126 | 15.5975 | 15.5391 | 55.8337 | 1 | 49.9783 | 14.766 | 22.1 | 221 | 154840 | 237657.0213 | 3545626.6383 | 99.9552 | -0.026134 | -0.78402 | -0.78402 | -0.78402 | 7.9917 | 1034.2002 | 1032.2151 | 1032.2157 | 1034.2002 | 1091.1443 | 1091.1443 | 1091.1443 | 1091.1443 | 802.122 | 802.122 | 802.122 | 8.8353 | 0 | 8.8243 | 76.7797 | 219.5151 | 219.6331 | 218.159 | 2.0068 | 3.46 | 0 | 86 | 57.6807 | 63.5182 | 104.9874 | 5.3578 | 88.0126 | -4.0348 | 55.829 | 62.9638 | 48.2412 | 0 | 66.828 | 754.6253 | 747.9546 | 704.7468 | 704.2705 | 690.0745 | 686.7598 | 490.2978 | 481.6355 | 708.8363 | 718.4334 | 802.7554 | 819.8441 | 817.2771 | 817.7454 | 820.5424 | 818.6229 | 810.2518 | 815.338 | 804.8068 | 814.3859 | 800.1518 | 797.7645 | 807.1996 | 804.4936 | 798.2608 | 815.5601 | 816.1722 | 806.32 | 800.2931 | 812.5808 | 816.1127 | 813.9938 | 811.8638
2025-04-09 20:58 | 9 | 20 | 58 | 6.2817e-272 | 1 | 29.3917 | 700.1956 | 0.28052 | 0.0073118 | 149.619 | 149.619 | 149.619 | 149.619 | 11.625 | 13.629 | 635.3436 | 635.3436 | 635.3436 | 635.3436 | 63.141 | 49.9728 | 15.7445 | 87.6151 | 15.6004 | 15.4693 | 55.711 | 1 | 49.9725 | 14.4255 | 22.1 | 221 | 154840 | 237658 | 3545641.1702 | 99.9457 | 0.020195 | 0.60585 | 0.60585 | 0.60585 | 7.9917 | 1034.5077 | 1032.5315 | 1032.5347 | 1034.5077 | 1091.6615 | 1091.6615 | 1091.6615 | 1091.6615 | 800.6297 | 800.6297 | 800.6297 | 8.7579 | 0 | 8.7519 | 76.5994 | 219.1391 | 219.2643 | 217.9889 | 2.0226 | 3.4738 | 0 | 86 | 57.643 | 63.141 | 104.9632 | 5.3688 | 87.6151 | -4.1329 | 55.5783 | 62.9593 | 48.1892 | 0 | 66.8284 | 753.9314 | 747.3837 | 704.3847 | 703.854 | 689.8146 | 686.4158 | 489.4356 | 480.8105 | 708.4409 | 717.9243 | 801.2449 | 818.288 | 815.7275 | 815.5274 | 818.5719 | 816.9349 | 808.8964 | 813.9699 | 803.4413 | 812.7975 | 799.1619 | 796.3445 | 805.5622 | 802.8817 | 796.7726 | 813.3878 | 814.8152 | 805.2389 | 798.9625 | 811.2048 | 815.0259 | 812.6476 | 810.4861
2025-04-09 20:59 | 9 | 20 | 59 | 6.2817e-272 | 1 | 29.3953 | 698.8666 | 0.28295 | 0.007304 | 149.5906 | 149.5906 | 149.5906 | 149.5906 | 11.6216 | 13.6201 | 635.7641 | 635.7641 | 635.7641 | 635.7641 | 63.4922 | 49.9699 | 15.747 | 87.768 | 15.5989 | 15.5149 | 55.8128 | 1 | 49.9695 | 13.913 | 22.1 | 221 | 154840 | 237658.8913 | 3545655.6304 | 99.9399 | 0.0099811 | 0.29943 | 0.29943 | 0.29943 | 7.9917 | 1034.5711 | 1032.5972 | 1032.5983 | 1034.5711 | 1091.4615 | 1091.4615 | 1091.4615 | 1091.4615 | 801.7603 | 801.7603 | 801.7603 | 8.7813 | 0 | 8.7954 | 76.605 | 219.0872 | 219.1885 | 217.8033 | 2.1186 | 3.4818 | 0 | 86 | 58.326 | 63.4922 | 104.9801 | 5.4502 | 87.768 | -4.0973 | 55.7422 | 62.9645 | 48.1633 | 0 | 66.8274 | 753.7713 | 747.2766 | 704.2667 | 703.6355 | 689.6476 | 686.1028 | 488.595 | 480.0187 | 708.1156 | 717.5507 | 802.6557 | 819.6586 | 816.8725 | 816.6802 | 819.6846 | 818.1951 | 809.9354 | 815.0979 | 804.4825 | 813.9659 | 800.3607 | 797.0668 | 806.895 | 803.896 | 797.941 | 814.9373 | 815.5706 | 805.8129 | 800.2156 | 812.6831 | 815.8366 | 813.8078 | 811.6372
2025-04-09 21:00 | 9 | 21 | 0 | 6.2817e-272 | 1 | 29.3932 | 699.3686 | 0.28446 | 0.0073032 | 149.7958 | 149.7958 | 149.7958 | 149.7958 | 11.637 | 13.6106 | 636.2953 | 636.2953 | 636.2953 | 636.2953 | 63.7597 | 49.9597 | 15.7425 | 88.3036 | 15.6018 | 15.6079 | 56.1164 | 1 | 49.9605 | 14.4255 | 22.1 | 221 | 154840 | 237659.7872 | 3545670.1064 | 99.9194 | -0.0070009 | -0.21003 | -0.21003 | -0.21003 | 7.9917 | 1034.2936 | 1032.3123 | 1032.3109 | 1034.2936 | 1090.7636 | 1090.7636 | 1090.7636 | 1090.7636 | 804.5123 | 804.5123 | 804.5123 | 8.9185 | 0 | 8.9181 | 76.8018 | 219.4305 | 219.5491 | 217.7347 | 2.0901 | 3.4799 | 0 | 86 | 58.4464 | 63.7597 | 104.9498 | 5.5179 | 88.3036 | -4.0809 | 56.0762 | 62.9581 | 48.1584 | 0 | 66.8275 | 753.7667 | 747.3488 | 704.2392 | 703.5705 | 689.6056 | 685.9721 | 487.777 | 479.4204 | 707.8733 | 717.2761 | 805.575 | 822.137 | 819.0821 | 819.5614 | 822.4085 | 821.2954 | 812.3759 | 817.6948 | 806.9759 | 816.9731 | 802.2419 | 800.1749 | 809.9183 | 806.5511 | 800.5528 | 818.535 | 818.2718 | 808.5953 | 803.158 | 815.699 | 818.8452 | 816.4297 | 814.5323
2025-04-09 21:01 | 9 | 21 | 1 | 6.2817e-272 | 1 | 29.3937 | 699.6059 | 0.28643 | 0.0073041 | 149.7413 | 149.7413 | 149.7413 | 149.7413 | 11.6329 | 13.6118 | 636.4413 | 636.4413 | 636.4413 | 636.4413 | 63.7414 | 49.9622 | 15.7417 | 88.1357 | 15.6009 | 15.5777 | 55.9986 | 1 | 49.9622 | 14.5532 | 22.1 | 221 | 154840 | 237660.6809 | 3545684.766 | 99.9245 | 0.0060003 | 0.18001 | 0.18001 | 0.18001 | 7.9917 | 1034.3651 | 1032.3836 | 1032.3832 | 1034.3651 | 1090.9828 | 1090.9828 | 1090.9828 | 1090.9828 | 803.6973 | 803.6973 | 803.6973 | 8.8746 | 0 | 8.8746 | 76.6916 | 219.3269 | 219.4393 | 217.7961 | 2.0778 | 3.4894 | 0 | 86 | 58.4821 | 63.7414 | 104.9445 | 5.4715 | 88.1357 | -4.2338 | 55.9676 | 62.9575 | 48.1615 | 0 | 66.8274 | 753.6124 | 747.2327 | 704.1071 | 703.4527 | 689.4658 | 685.874 | 487.0193 | 478.9066 | 707.6262 | 717.0096 | 804.6186 | 821.1979 | 818.5784 | 818.6656 | 821.8377 | 820.1917 | 811.3684 | 817.1102 | 806.256 | 816.1673 | 802.324 | 799.4779 | 809.2272 | 805.7909 | 799.5831 | 817.3249 | 817.6502 | 808.0134 | 802.0529 | 814.4129 | 817.864 | 815.7641 | 813.159
2025-04-09 21:02 | 9 | 21 | 2 | 6.2817e-272 | 1 | 29.3967 | 699.8505 | 0.28582 | 0.007304 | 149.6592 | 149.6592 | 149.6592 | 149.6592 | 11.626 | 13.6167 | 636.004 | 636.004 | 636.004 | 636.004 | 63.9199 | 49.982 | 15.7428 | 87.7814 | 15.6028 | 15.5457 | 55.8233 | 1 | 49.9814 | 13.9149 | 22.1 | 221 | 154840 | 237661.5957 | 3545699.383 | 99.9641 | 0.025448 | 0.76343 | 0.76343 | 0.76343 | 7.9917 | 1034.4894 | 1032.5126 | 1032.5132 | 1034.4894 | 1091.4438 | 1091.4438 | 1091.4438 | 1091.4438 | 802.2402 | 802.2402 | 802.2402 | 8.8527 | 0 | 8.8367 | 76.7434 | 219.2439 | 219.3512 | 217.7104 | 2.0779 | 3.4684 | 0 | 86 | 58.3852 | 63.9199 | 104.9522 | 5.4733 | 87.7814 | -4.0988 | 55.8527 | 62.9608 | 48.1636 | 0 | 66.8276 | 753.4817 | 747.1482 | 703.9938 | 703.3408 | 689.3796 | 685.8266 | 486.2018 | 478.0469 | 707.4313 | 716.7993 | 803.1311 | 819.9709 | 817.3095 | 817.3243 | 820.647 | 819.0286 | 810.2712 | 815.1364 | 805.071 | 814.499 | 800.1938 | 797.9233 | 807.6664 | 804.4634 | 798.3996 | 815.4557 | 816.1439 | 806.2761 | 800.548 | 812.9906 | 816.7157 | 814.5985 | 811.7735
2025-04-09 21:03 | 9 | 21 | 3 | 6.2817e-272 | 1 | 29.4014 | 697.9292 | 0.28031 | 0.0073004 | 149.6721 | 149.6721 | 149.6721 | 149.6721 | 11.6252 | 13.5999 | 637.2535 | 637.2535 | 637.2535 | 637.2535 | 64.5913 | 49.9756 | 15.7434 | 88.3782 | 15.5955 | 15.6521 | 56.1807 | 1 | 49.9748 | 14.8936 | 22.1 | 221 | 154840 | 237662.5106 | 3545714 | 99.9512 | 0.020744 | 0.62233 | 0.62233 | 0.62233 | 7.9917 | 1034.5049 | 1032.5285 | 1032.5317 | 1034.5049 | 1090.6664 | 1090.6664 | 1090.6664 | 1090.6664 | 805.8849 | 805.8849 | 805.8849 | 8.9612 | 0 | 8.9698 | 76.6853 | 219.2272 | 219.3168 | 217.7505 | 2.1448 | 3.4735 | 0 | 86 | 59.066 | 64.5913 | 104.9561 | 5.4695 | 88.3782 | -4.1725 | 56.2351 | 62.958 | 48.1555 | 0 | 66.8267 | 753.712 | 747.4328 | 704.1079 | 703.4774 | 689.4888 | 685.8737 | 485.4343 | 477.5136 | 707.3506 | 716.7602 | 807.0209 | 823.9551 | 821.0183 | 820.7473 | 823.5286 | 822.6067 | 813.2784 | 818.8764 | 808.3188 | 818.7227 | 803.901 | 801.6734 | 811.2413 | 807.5171 | 801.5713 | 819.9061 | 819.5518 | 810.1245 | 804.6139 | 817.2824 | 820.1176 | 818.5156 | 815.5322
2025-04-09 21:04 | 9 | 21 | 4 | 6.2817e-272 | 1 | 29.4058 | 693.885 | 0.2844 | 0.0072985 | 149.168 | 149.168 | 149.168 | 149.168 | 11.5878 | 13.5982 | 637.7568 | 637.7568 | 637.7568 | 637.7568 | 65.0399 | 49.9927 | 15.7429 | 87.17 | 15.6021 | 15.4447 | 55.5339 | 1 | 49.9922 | 13.3191 | 22.1 | 221 | 154840 | 237663.4043 | 3545728.617 | 99.9855 | 0.014257 | 0.42772 | 0.42772 | 0.42772 | 7.9917 | 1035.1774 | 1033.2213 | 1033.2191 | 1035.1774 | 1092.2406 | 1092.2406 | 1092.2406 | 1092.2406 | 802.3894 | 802.3894 | 802.3894 | 8.7629 | 0 | 8.7736 | 76.5042 | 218.556 | 218.6532 | 217.7223 | 2.242 | 3.4831 | 0 | 86 | 59.5775 | 65.0399 | 104.9525 | 5.4059 | 87.17 | -4.1351 | 55.4897 | 62.9736 | 48.1529 | 0 | 66.8264 | 754.0339 | 747.9514 | 704.2508 | 703.6638 | 689.6327 | 686.0951 | 484.6296 | 476.9329 | 707.3567 | 716.7937 | 802.7263 | 820.4391 | 817.6649 | 818.0694 | 821.4171 | 819.4661 | 810.5305 | 815.6112 | 805.4538 | 814.7296 | 800.9686 | 797.5868 | 807.8407 | 804.6855 | 798.0503 | 814.988 | 815.8128 | 806.0556 | 800.222 | 813.102 | 816.6849 | 815.0068 | 811.9219
2025-04-09 21:05 | 9 | 21 | 5 | 6.2817e-272 | 1 | 29.4042 | 691.3378 | 0.28013 | 0.0072992 | 149.3992 | 149.3992 | 149.3992 | 149.3992 | 11.6048 | 13.5997 | 639.0949 | 639.0949 | 639.0949 | 639.0949 | 65.436 | 50.0143 | 15.7468 | 87.8166 | 15.6051 | 15.5505 | 55.856 | 1 | 50.0133 | 13.7447 | 22.1 | 221 | 154840 | 237664.2979 | 3545743.1915 | 100.0287 | 0.025906 | 0.77717 | 0.77717 | 0.77717 | 7.9917 | 1034.8685 | 1032.9045 | 1032.9034 | 1034.8685 | 1091.3983 | 1091.3983 | 1091.3983 | 1091.3983 | 805.7957 | 805.7957 | 805.7957 | 8.9283 | 0 | 8.9247 | 76.6615 | 218.9629 | 219.0662 | 217.8132 | 2.2219 | 3.4822 | 0 | 86 | 60.0105 | 65.436 | 104.9785 | 5.3622 | 87.8166 | -4.1208 | 55.8698 | 62.9742 | 48.155 | 0 | 66.8264 | 754.4434 | 748.5025 | 704.6256 | 704.0467 | 689.9517 | 686.4444 | 483.9733 | 476.4101 | 707.4526 | 716.9224 | 806.5741 | 823.8753 | 820.9409 | 821.3189 | 824.5749 | 823.3111 | 813.3536 | 819.078 | 808.8233 | 818.3775 | 803.9116 | 801.4145 | 811.2806 | 807.5132 | 801.6987 | 819.0085 | 819.1027 | 809.5929 | 804.0344 | 816.6728 | 819.9224 | 818.3626 | 815.1113
2025-04-09 21:06 | 9 | 21 | 6 | 6.2817e-272 | 1 | 29.4059 | 689.805 | 0.28646 | 0.0072976 | 149.4207 | 149.4207 | 149.4207 | 149.4207 | 11.6057 | 13.6057 | 639.6249 | 639.6249 | 639.6249 | 639.6249 | 65.4847 | 50.0317 | 15.7467 | 87.5894 | 15.6 | 15.5143 | 55.7052 | 1 | 50.031 | 13.9574 | 22.1 | 221 | 154840 | 237665.1702 | 3545757.8085 | 100.0633 | 0.018569 | 0.55706 | 0.55706 | 0.55706 | 7.9917 | 1034.8606 | 1032.8955 | 1032.8934 | 1034.8606 | 1091.6949 | 1091.6949 | 1091.6949 | 1091.6949 | 804.3347 | 804.3347 | 804.3347 | 8.8725 | 0 | 8.8727 | 76.7641 | 218.998 | 219.0954 | 217.9897 | 2.2252 | 3.4799 | 0 | 86 | 60.4362 | 65.4847 | 104.9779 | 5.2816 | 87.5894 | -4.1832 | 55.7398 | 62.9759 | 48.1478 | 0 | 66.8263 | 754.8036 | 749.0397 | 704.9021 | 704.4389 | 690.2579 | 686.8305 | 483.2578 | 475.8606 | 707.6858 | 717.1609 | 805.0194 | 822.2016 | 819.2048 | 819.6263 | 823.0929 | 821.5836 | 812.2715 | 817.7726 | 807.4547 | 816.886 | 802.8223 | 799.8988 | 810.2922 | 806.4813 | 800.5746 | 817.2567 | 817.6472 | 808.0649 | 802.2581 | 814.7666 | 818.6662 | 816.7857 | 813.4518
2025-04-09 21:07 | 9 | 21 | 7 | 6.2817e-272 | 1 | 29.4031 | 688.6958 | 0.27796 | 0.007291 | 149.6333 | 149.6333 | 149.6333 | 149.6333 | 11.6218 | 13.6062 | 639.6782 | 639.6782 | 639.6782 | 639.6782 | 65.6734 | 50.0405 | 15.7444 | 87.9026 | 15.5953 | 15.5715 | 55.8716 | 1 | 50.0402 | 14.2609 | 22.1 | 221 | 154840 | 237666 | 3545772.1957 | 100.0809 | 0.012897 | 0.38692 | 0.38692 | 0.38692 | 7.9917 | 1034.5663 | 1032.5922 | 1032.5904 | 1034.5663 | 1091.2859 | 1091.2859 | 1091.2859 | 1091.2859 | 805.2753 | 805.2753 | 805.2753 | 8.9564 | 0 | 8.9518 | 76.8568 | 219.3321 | 219.4355 | 218.1651 | 2.2311 | 3.4778 | 0 | 86 | 60.4626 | 65.6734 | 104.9628 | 5.1453 | 87.9026 | -4.1491 | 55.9453 | 62.9762 | 48.1194 | 0 | 66.8262 | 755.0029 | 749.2353 | 705.099 | 704.7525 | 690.4298 | 687.156 | 482.612 | 475.4561 | 707.923 | 717.3296 | 806.2377 | 823.1567 | 820.278 | 820.204 | 823.5945 | 822.6262 | 812.7473 | 818.6857 | 808.171 | 817.6698 | 803.6753 | 800.9517 | 811.4664 | 807.2563 | 801.7373 | 818.5669 | 818.3849 | 809.2501 | 803.441 | 815.895 | 819.3252 | 817.9568 | 814.2982
2025-04-09 21:08 | 9 | 21 | 8 | 6.2817e-272 | 1 | 29.4001 | 688.7223 | 0.28836 | 0.0072866 | 149.7107 | 149.7107 | 149.7107 | 149.7107 | 11.6284 | 13.6052 | 639.5775 | 639.5775 | 639.5775 | 639.5775 | 65.7848 | 50.0437 | 15.743 | 87.9497 | 15.6 | 15.555 | 55.8585 | 1 | 50.045 | 14.5532 | 22.1 | 221 | 154840 | 237666.9787 | 3545786.6809 | 100.0874 | -0.0086094 | -0.25828 | -0.25828 | -0.25828 | 7.9917 | 1034.4451 | 1032.4668 | 1032.4672 | 1034.4451 | 1091.226 | 1091.226 | 1091.226 | 1091.226 | 804.8408 | 804.8408 | 804.8408 | 8.9522 | 0 | 8.9522 | 76.9246 | 219.4686 | 219.5758 | 218.3085 | 2.1392 | 3.4737 | 0 | 86 | 60.3241 | 65.7848 | 104.9533 | 5.2235 | 87.9497 | -4.1072 | 55.8863 | 62.9833 | 48.099 | 0 | 66.826 | 755.3233 | 749.4589 | 705.2402 | 705.022 | 690.5972 | 687.3856 | 482.1264 | 474.9432 | 708.1122 | 717.4977 | 805.6544 | 822.747 | 820.0893 | 819.9007 | 823.2902 | 822.1184 | 812.5189 | 817.7039 | 807.8015 | 817.2184 | 802.9722 | 800.5929 | 810.6518 | 806.676 | 801.0464 | 817.8244 | 818.1097 | 808.7596 | 803.1198 | 815.5026 | 819.3055 | 817.7263 | 814.2862
2025-04-09 21:09 | 9 | 21 | 9 | 6.2817e-272 | 1 | 29.3955 | 688.7472 | 0.28831 | 0.007283 | 149.7051 | 149.7051 | 149.7051 | 149.7051 | 11.6297 | 13.6082 | 639.2734 | 639.2734 | 639.2734 | 639.2734 | 65.7409 | 50.0496 | 15.7454 | 87.7083 | 15.6021 | 15.5208 | 55.7069 | 1 | 50.0499 | 13.7021 | 22.1 | 221 | 154840 | 237667.8298 | 3545801.2766 | 100.0991 | 0.0009856 | 0.029568 | 0.029568 | 0.029568 | 7.9917 | 1034.4253 | 1032.4457 | 1032.4445 | 1034.4253 | 1091.5389 | 1091.5389 | 1091.5389 | 1091.5389 | 803.5838 | 803.5838 | 803.5838 | 8.9027 | 0 | 8.9038 | 76.898 | 219.4703 | 219.5725 | 218.4473 | 2.1279 | 3.4923 | 0 | 86 | 59.9504 | 65.7409 | 104.9693 | 5.3256 | 87.7083 | -4.0536 | 55.7631 | 62.9784 | 48.0797 | 0 | 66.826 | 755.5109 | 749.5833 | 705.3796 | 705.1711 | 690.7168 | 687.5473 | 481.5026 | 474.4314 | 708.3056 | 717.6127 | 804.6044 | 821.3602 | 818.7367 | 818.8303 | 822.3627 | 820.6007 | 810.944 | 816.9883 | 806.8204 | 815.7417 | 801.8266 | 799.3508 | 809.4586 | 805.4318 | 799.917 | 816.5878 | 816.9848 | 807.3419 | 801.4508 | 813.8352 | 818.0285 | 816.3854 | 813.09
2025-04-09 21:10 | 9 | 21 | 10 | 6.2817e-272 | 1 | 29.3931 | 690.6609 | 0.28111 | 0.0072768 | 149.9441 | 149.9441 | 149.9441 | 149.9441 | 11.6475 | 13.6143 | 638.9633 | 638.9633 | 638.9633 | 638.9633 | 65.4543 | 50.05 | 15.7437 | 88.1821 | 15.5983 | 15.6018 | 55.9701 | 1 | 50.0504 | 14.3404 | 22.1 | 221 | 154840 | 237668.7021 | 3545815.9149 | 100.1 | 0.0015078 | 0.045234 | 0.045234 | 0.045234 | 7.9917 | 1034.1028 | 1032.1145 | 1032.1145 | 1034.1028 | 1090.9226 | 1090.9226 | 1090.9226 | 1090.9226 | 804.932 | 804.932 | 804.932 | 8.9968 | 0 | 8.9876 | 77.0251 | 219.7957 | 219.8977 | 218.5039 | 2.0765 | 3.4793 | 0 | 86 | 59.8413 | 65.4543 | 104.9582 | 5.309 | 88.1821 | -4.1007 | 56.0542 | 62.977 | 48.0517 | 0 | 66.8256 | 755.4446 | 749.4658 | 705.301 | 705.2173 | 690.6875 | 687.5943 | 480.964 | 473.9485 | 708.4075 | 717.7082 | 806.1603 | 822.8236 | 820.0317 | 819.4547 | 822.8335 | 821.9314 | 812.4689 | 818.2184 | 807.8056 | 817.1289 | 803.2352 | 800.8545 | 810.8103 | 806.6745 | 801.324 | 818.2135 | 818.3655 | 808.9921 | 803.28 | 815.6278 | 819.2062 | 817.6926 | 814.2537
2025-04-09 21:11 | 9 | 21 | 11 | 6.2817e-272 | 1 | 29.3942 | 691.4943 | 0.2817 | 0.0072663 | 149.8294 | 149.8294 | 149.8294 | 149.8294 | 11.639 | 13.6104 | 638.411 | 638.411 | 638.411 | 638.411 | 65.6728 | 50.0499 | 15.7444 | 87.7761 | 15.6007 | 15.5348 | 55.7961 | 1 | 50.05 | 14 | 22.1 | 221 | 154840 | 237669.5745 | 3545830.4894 | 100.0997 | 0.00079627 | 0.023888 | 0.023888 | 0.023888 | 7.9917 | 1034.2568 | 1032.2723 | 1032.273 | 1034.2568 | 1091.4513 | 1091.4513 | 1091.4513 | 1091.4513 | 802.9323 | 802.9323 | 802.9323 | 8.936 | 0 | 8.9311 | 77.0116 | 219.6467 | 219.7508 | 218.5448 | 2.0639 | 3.471 | 0 | 86 | 59.917 | 65.6728 | 104.9626 | 5.3541 | 87.7761 | -4.1153 | 55.8135 | 62.9689 | 48.0106 | 0 | 66.8259 | 755.436 | 749.3608 | 705.3053 | 705.245 | 690.6581 | 687.6011 | 480.3157 | 473.4985 | 708.4938 | 717.7428 | 803.9929 | 821.1341 | 818.5829 | 817.929 | 821.2138 | 820.2545 | 810.866 | 815.6336 | 805.8411 | 814.8448 | 800.5279 | 798.9151 | 808.5692 | 804.8265 | 799.2162 | 816.2353 | 816.5897 | 807.0941 | 800.9206 | 813.2315 | 817.3374 | 816.0316 | 812.4029
2025-04-09 21:12 | 9 | 21 | 12 | 6.2817e-272 | 1 | 29.3924 | 693.5195 | 0.28893 | 0.0072548 | 150.1065 | 150.1065 | 150.1065 | 150.1065 | 11.6593 | 13.6354 | 637.7252 | 637.7252 | 637.7252 | 637.7252 | 64.542 | 50.0538 | 15.743 | 88.1604 | 15.5956 | 15.5843 | 55.9352 | 1 | 50.054 | 14.383 | 22.1 | 221 | 154840 | 237670.4468 | 3545845.1064 | 100.1075 | 0.0032935 | 0.098807 | 0.098807 | 0.098807 | 7.9917 | 1033.8896 | 1031.8949 | 1031.8945 | 1033.8896 | 1090.9502 | 1090.9502 | 1090.9502 | 1090.9502 | 802.1127 | 802.1127 | 802.1127 | 8.902 | 0 | 8.9229 | 77.1004 | 220.0123 | 220.1161 | 218.5878 | 2.0319 | 3.4804 | 0 | 86 | 58.9982 | 64.542 | 104.9534 | 5.2445 | 88.1604 | -4.1715 | 55.9913 | 62.9778 | 47.9624 | 0 | 66.826 | 755.1157 | 749.095 | 705.1926 | 705.1326 | 690.5088 | 687.4471 | 479.6054 | 472.8833 | 708.504 | 717.7197 | 802.9612 | 820.2823 | 817.694 | 817.0768 | 820.3304 | 819.3368 | 810.045 | 815.1807 | 805.0385 | 814.0994 | 799.9661 | 798.0328 | 807.6639 | 803.8594 | 798.2782 | 815.0304 | 815.9174 | 806.3451 | 800.0383 | 812.3985 | 816.5429 | 814.9504 | 811.4858
2025-04-09 21:13 | 9 | 21 | 13 | 6.2817e-272 | 1 | 29.3917 | 694.8182 | 0.2895 | 0.0072559 | 149.8108 | 149.8108 | 149.8108 | 149.8108 | 11.6386 | 13.644 | 636.8516 | 636.8516 | 636.8516 | 636.8516 | 64.274 | 50.0607 | 15.7449 | 87.1936 | 15.6008 | 15.4452 | 55.3884 | 1 | 50.0612 | 13.3617 | 22.1 | 221 | 154840 | 237671.2979 | 3545859.7872 | 100.1212 | 0.0024164 | 0.072493 | 0.072493 | 0.072493 | 7.9917 | 1034.2619 | 1032.2789 | 1032.2768 | 1034.2619 | 1092.2098 | 1092.2098 | 1092.2098 | 1092.2098 | 798.9298 | 798.9298 | 798.9298 | 8.7551 | 0 | 8.7422 | 77.0043 | 219.6068 | 219.7105 | 218.5628 | 2.0244 | 3.4821 | 0 | 86 | 58.6401 | 64.274 | 104.9658 | 5.131 | 87.1936 | -4.0945 | 55.4918 | 62.969 | 47.9664 | 0 | 66.8254 | 754.8019 | 748.8371 | 704.9805 | 704.8414 | 690.3019 | 687.1584 | 478.9493 | 472.5479 | 708.4643 | 717.6425 | 799.2559 | 816.8737 | 814.2345 | 814.346 | 817.9195 | 815.8411 | 806.9798 | 812.3479 | 802.0394 | 810.4014 | 797.7061 | 794.5076 | 804.5315 | 801.0985 | 794.8166 | 811.1903 | 812.8561 | 803.0494 | 796.7895 | 808.8284 | 813.7242 | 811.6136 | 808.4349
2025-04-09 21:14 | 9 | 21 | 14 | 6.2817e-272 | 1 | 29.3925 | 695.6451 | 0.28629 | 0.0072533 | 150.3496 | 150.3496 | 150.3496 | 150.3496 | 11.6765 | 13.6416 | 637.6375 | 637.6375 | 637.6375 | 637.6375 | 64.3101 | 50.0576 | 15.7455 | 88.6857 | 15.5981 | 15.6741 | 56.2092 | 1 | 50.0571 | 15.5319 | 22.1 | 221 | 154840 | 237672.0851 | 3545874.3404 | 100.1151 | 0.0081227 | 0.24368 | 0.24368 | 0.24368 | 7.9917 | 1033.58 | 1031.5757 | 1031.5726 | 1033.58 | 1090.2662 | 1090.2662 | 1090.2662 | 1090.2662 | 804.0787 | 804.0787 | 804.0787 | 9.0317 | 0 | 9.0296 | 77.2689 | 220.416 | 220.5363 | 218.4601 | 2.073 | 3.4668 | 0 | 86 | 58.8184 | 64.3101 | 104.9697 | 5.1023 | 88.6857 | -4.1079 | 56.3141 | 62.978 | 47.9566 | 0 | 66.8256 | 754.6137 | 748.6482 | 704.9166 | 704.7386 | 690.2334 | 686.9556 | 478.2272 | 471.8233 | 708.3637 | 717.5484 | 804.8706 | 822.2686 | 819.352 | 818.4419 | 821.4862 | 821.2919 | 811.8435 | 817.5164 | 806.9349 | 816.4033 | 801.7687 | 799.8752 | 809.6727 | 805.5231 | 799.7795 | 818.0941 | 817.4426 | 808.4533 | 802.6713 | 814.9416 | 818.2723 | 817.0729 | 813.8744
2025-04-09 21:15 | 9 | 21 | 15 | 6.2817e-272 | 1 | 29.3931 | 696.9544 | 0.2845 | 0.0072365 | 149.9803 | 149.9803 | 149.9803 | 149.9803 | 11.6501 | 13.6401 | 636.6142 | 636.6142 | 636.6142 | 636.6142 | 64.3232 | 50.0533 | 15.7454 | 87.7002 | 15.602 | 15.5078 | 55.667 | 1 | 50.0539 | 13.6087 | 22.1 | 221 | 154840 | 237673 | 3545888.8913 | 100.1065 | -0.0021655 | -0.064966 | -0.064966 | -0.064966 | 7.9917 | 1034.0539 | 1032.0639 | 1032.0646 | 1034.0539 | 1091.5507 | 1091.5507 | 1091.5507 | 1091.5507 | 800.5012 | 800.5012 | 800.5012 | 8.8406 | 0 | 8.839 | 77.0258 | 219.8819 | 219.9958 | 218.4712 | 2.0691 | 3.4784 | 0 | 86 | 58.6667 | 64.3232 | 104.9692 | 5.0188 | 87.7002 | -4.0976 | 55.7165 | 62.971 | 47.8887 | 0 | 66.8249 | 754.511 | 748.58 | 704.7907 | 704.5264 | 690.0742 | 686.7278 | 477.6742 | 471.227 | 708.2658 | 717.4912 | 801.3087 | 818.3305 | 815.3774 | 815.5536 | 819.1207 | 817.518 | 808.3472 | 813.8026 | 803.4971 | 811.9343 | 798.2876 | 796.2804 | 805.7008 | 802.4259 | 797.1843 | 812.9609 | 814.3244 | 805.114 | 798.9962 | 810.8223 | 815.004 | 812.986 | 810.1314
2025-04-09 21:16 | 9 | 21 | 16 | 6.2817e-272 | 1 | 29.3974 | 695.5793 | 0.28434 | 0.0072321 | 150.2706 | 150.2706 | 150.2706 | 150.2706 | 11.669 | 13.623 | 637.0521 | 637.0521 | 637.0521 | 637.0521 | 64.5737 | 50.0265 | 15.7446 | 88.7454 | 15.6016 | 15.6432 | 56.2367 | 1 | 50.0265 | 15.234 | 22.1 | 221 | 154840 | 237673.8723 | 3545903.4043 | 100.053 | 0.010115 | 0.30346 | 0.30346 | 0.30346 | 7.9917 | 1033.7138 | 1031.714 | 1031.7119 | 1033.7138 | 1090.1883 | 1090.1883 | 1090.1883 | 1090.1883 | 804.7072 | 804.7072 | 804.7072 | 9.0488 | 0 | 9.0444 | 77.0706 | 220.1665 | 220.2746 | 218.4574 | 2.1363 | 3.4824 | 0 | 86 | 58.8267 | 64.5737 | 104.9637 | 5.4032 | 88.7454 | -4.0631 | 56.203 | 62.9703 | 47.8769 | 0 | 66.825 | 754.4529 | 748.4852 | 704.6805 | 704.4748 | 689.8895 | 686.6008 | 477.0979 | 470.9226 | 708.1792 | 717.3508 | 805.8943 | 823.0773 | 820.0012 | 819.2745 | 822.3903 | 821.6429 | 812.6819 | 817.725 | 807.2712 | 816.6819 | 801.5938 | 800.7674 | 810.1585 | 805.9689 | 801.0805 | 818.5966 | 818.4511 | 809.0107 | 803.3753 | 815.6955 | 818.8644 | 817.4564 | 814.7505
2025-04-09 21:17 | 9 | 21 | 17 | 6.2817e-272 | 1 | 29.3972 | 695.5003 | 0.28469 | 0.0072317 | 149.8223 | 149.8223 | 149.8223 | 149.8223 | 11.6374 | 13.6336 | 636.606 | 636.606 | 636.606 | 636.606 | 64.7696 | 50.0593 | 15.7432 | 87.2615 | 15.6015 | 15.4578 | 55.4536 | 1 | 50.0599 | 13.6596 | 22.1 | 221 | 154840 | 237674.7447 | 3545917.9574 | 100.1185 | -0.003692 | -0.11076 | -0.11076 | -0.11076 | 7.9917 | 1034.2877 | 1032.3045 | 1032.3028 | 1034.2877 | 1092.1221 | 1092.1221 | 1092.1221 | 1092.1221 | 798.1413 | 798.1413 | 798.1413 | 8.7821 | 0 | 8.7853 | 76.9942 | 219.688 | 219.7835 | 218.3684 | 2.1376 | 3.4965 | 0 | 86 | 59.0153 | 64.7696 | 104.9547 | 5.0928 | 87.2615 | -4.128 | 55.5369 | 62.9702 | 47.8751 | 0 | 66.8251 | 754.1128 | 748.0415 | 704.4227 | 704.2953 | 689.714 | 686.4632 | 476.5639 | 470.2831 | 708.1135 | 717.1271 | 798.4201 | 816.0729 | 813.5479 | 812.9607 | 816.5678 | 814.9983 | 806.4796 | 811.2964 | 801.2219 | 809.361 | 796.0075 | 793.2314 | 803.2873 | 800.2362 | 794.8255 | 810.6283 | 812.1014 | 802.401 | 796.351 | 808.4853 | 812.7204 | 810.8216 | 808.0667
2025-04-09 21:18 | 9 | 21 | 18 | 6.2817e-272 | 1 | 29.3929 | 696.1113 | 0.28475 | 0.0072323 | 150.0363 | 150.0363 | 150.0363 | 150.0363 | 11.6541 | 13.6324 | 637.0959 | 637.0959 | 637.0959 | 637.0959 | 65.0735 | 50.0731 | 15.7437 | 87.7622 | 15.5996 | 15.5539 | 55.7499 | 1 | 50.0733 | 14.2979 | 22.1 | 221 | 154840 | 237675.5532 | 3545932.4894 | 100.146 | 0.0056002 | 0.16801 | 0.16801 | 0.16801 | 7.9917 | 1033.9843 | 1031.9919 | 1031.9915 | 1033.9843 | 1091.4685 | 1091.4685 | 1091.4685 | 1091.4685 | 800.0631 | 800.0631 | 800.0631 | 8.9005 | 0 | 8.9038 | 77.1086 | 220.001 | 220.1 | 218.23 | 2.1121 | 3.5007 | 0 | 86 | 58.8273 | 65.0735 | 104.9577 | 4.8978 | 87.7622 | -4.1309 | 55.8821 | 62.9714 | 47.8735 | 0 | 66.8242 | 753.911 | 747.859 | 704.3498 | 704.2981 | 689.5662 | 686.3714 | 475.8549 | 469.6314 | 707.8891 | 716.904 | 800.0836 | 818.3613 | 815.8944 | 814.6635 | 817.6977 | 817.1724 | 808.0557 | 813.5497 | 803.3262 | 811.8073 | 797.9641 | 795.5249 | 805.3004 | 801.6756 | 796.1877 | 812.8952 | 813.8151 | 804.4624 | 798.6151 | 810.8457 | 814.2181 | 813.1354 | 809.8421
2025-04-09 21:19 | 9 | 21 | 19 | 6.2817e-272 | 1 | 29.3941 | 696.6177 | 0.29168 | 0.0072303 | 150.0266 | 150.0266 | 150.0266 | 150.0266 | 11.653 | 13.633 | 637.4687 | 637.4687 | 637.4687 | 637.4687 | 65.2525 | 50.0823 | 15.7444 | 87.7581 | 15.5999 | 15.518 | 55.6909 | 1 | 50.0826 | 13.5319 | 22.1 | 221 | 154840 | 237676.2979 | 3545947.1064 | 100.1644 | -8.3867e-05 | -0.0025164 | -0.0025164 | -0.0025164 | 7.9917 | 1034.0038 | 1032.0132 | 1032.0126 | 1034.0038 | 1091.4747 | 1091.4747 | 1091.4747 | 1091.4747 | 800.1521 | 800.1521 | 800.1521 | 8.8815 | 0 | 8.894 | 77.1512 | 220.0168 | 220.1289 | 218.0984 | 2.11 | 3.5203 | 0 | 86 | 58.6433 | 65.2525 | 104.9626 | 4.3869 | 87.7581 | -4.091 | 55.7531 | 62.9718 | 47.8662 | 0 | 66.8244 | 753.9245 | 747.9198 | 704.3599 | 704.2945 | 689.4488 | 686.2888 | 475.2801 | 469.144 | 707.7623 | 716.7845 | 800.5109 | 818.4481 | 815.9872 | 815.1858 | 818.2067 | 817.3923 | 808.3153 | 813.6107 | 803.4111 | 811.748 | 797.6026 | 795.5778 | 805.0894 | 801.8064 | 796.4377 | 812.6959 | 813.8314 | 804.5331 | 798.3677 | 810.6802 | 814.5979 | 813.077 | 809.7861
2025-04-09 21:20 | 9 | 21 | 20 | 6.2817e-272 | 1 | 29.3945 | 696.7156 | 0.28819 | 0.007229 | 150.1223 | 150.1223 | 150.1223 | 150.1223 | 11.6596 | 13.6296 | 637.7302 | 637.7302 | 637.7302 | 637.7302 | 64.9984 | 50.0629 | 15.7464 | 88.1114 | 15.5977 | 15.5716 | 55.8914 | 1 | 50.0637 | 14.4255 | 22.1 | 221 | 154840 | 237677.0638 | 3545961.766 | 100.1257 | -0.0081375 | -0.24412 | -0.24412 | -0.24412 | 7.9917 | 1033.8832 | 1031.8887 | 1031.8894 | 1033.8832 | 1091.014 | 1091.014 | 1091.014 | 1091.014 | 801.8912 | 801.8912 | 801.8912 | 8.9487 | 0 | 8.9506 | 77.1527 | 220.1041 | 220.2246 | 218.0854 | 2.1013 | 3.4835 | 0 | 86 | 58.8615 | 64.9984 | 104.9757 | 4.839 | 88.1114 | -4.1208 | 55.9457 | 62.9751 | 47.862 | 0 | 66.824 | 753.9921 | 747.9926 | 704.2729 | 704.2444 | 689.2955 | 686.1879 | 474.7278 | 468.6711 | 707.6436 | 716.6742 | 802.2524 | 819.91 | 816.9548 | 816.6325 | 819.7474 | 819.1356 | 809.5661 | 815.2013 | 805.3096 | 814.0037 | 799.3259 | 797.2023 | 807.3242 | 803.6425 | 798.3692 | 815.4776 | 815.3387 | 806.0667 | 800.3863 | 812.6966 | 816.0513 | 814.5819 | 811.7914
2025-04-09 21:21 | 9 | 21 | 21 | 6.2817e-272 | 1 | 29.3946 | 696.608 | 0.28927 | 0.0072228 | 150.2354 | 150.2354 | 150.2354 | 150.2354 | 11.6676 | 13.6374 | 638.0575 | 638.0575 | 638.0575 | 638.0575 | 65.0775 | 50.0835 | 15.7447 | 88.3214 | 15.6001 | 15.6106 | 55.9718 | 1 | 50.0839 | 14.4255 | 22.1 | 221 | 154840 | 237678 | 3545976.4043 | 100.1669 | -0.00073505 | -0.022052 | -0.022052 | -0.022052 | 7.9917 | 1033.7381 | 1031.7383 | 1031.7385 | 1033.7381 | 1090.7409 | 1090.7409 | 1090.7409 | 1090.7409 | 802.6464 | 802.6464 | 802.6464 | 9.0169 | 0 | 9.006 | 77.3494 | 220.4119 | 220.5533 | 218.012 | 2.1081 | 3.4947 | 0 | 86 | 58.9206 | 65.0775 | 104.9645 | 4.8259 | 88.3214 | -4.0579 | 56.0858 | 62.9738 | 47.8355 | 0 | 66.8237 | 753.9581 | 748.0075 | 704.2474 | 704.2576 | 689.2168 | 686.1544 | 474.0652 | 468.2522 | 707.5372 | 716.5701 | 803.13 | 821.1272 | 818.2203 | 817.221 | 820.1447 | 819.5945 | 810.0711 | 816.2309 | 805.8365 | 814.8213 | 800.0961 | 798.2335 | 807.9973 | 804.1291 | 798.9634 | 816.3595 | 816.0397 | 806.7649 | 801.146 | 813.611 | 816.398 | 815.7862 | 812.7806
2025-04-09 21:22 | 9 | 21 | 22 | 6.2817e-272 | 1 | 29.3945 | 697.2787 | 0.2956 | 0.007217 | 150.0071 | 150.0071 | 150.0071 | 150.0071 | 11.6514 | 13.6474 | 637.4587 | 637.4587 | 637.4587 | 637.4587 | 65.2027 | 50.1119 | 15.7446 | 87.3022 | 15.601 | 15.4573 | 55.4364 | 1 | 50.1124 | 13.5319 | 22.1 | 221 | 154840 | 237678.7872 | 3545991 | 100.224 | 0.0025753 | 0.077258 | 0.077258 | 0.077258 | 7.9917 | 1034.0309 | 1032.04 | 1032.0404 | 1034.0309 | 1092.0679 | 1092.0679 | 1092.0679 | 1092.0679 | 797.8464 | 797.8464 | 797.8464 | 8.8103 | 0 | 8.8163 | 77.209 | 220.0477 | 220.1645 | 218.0128 | 2.0659 | 3.4859 | 0 | 86 | 58.9857 | 65.2027 | 104.9636 | 4.1653 | 87.3022 | -4.1173 | 55.5352 | 62.9743 | 47.8118 | 0 | 66.8237 | 753.9401 | 748.0304 | 704.3493 | 704.2055 | 689.2885 | 686.03 | 473.4856 | 468.0255 | 707.5865 | 716.5827 | 798.318 | 815.688 | 813.0964 | 812.9187 | 816.2674 | 814.7153 | 805.5621 | 811.515 | 801.0034 | 809.2734 | 796.1915 | 793.1073 | 803.0101 | 799.8769 | 794.7316 | 810.17 | 811.6943 | 802.3462 | 795.9004 | 808.0231 | 812.2343 | 810.4159 | 807.184
2025-04-09 21:23 | 9 | 21 | 23 | 6.2817e-272 | 1 | 29.3931 | 696.8432 | 0.29108 | 0.0072067 | 150.2035 | 150.2035 | 150.2035 | 150.2035 | 11.6659 | 13.6425 | 636.6542 | 636.6542 | 636.6542 | 636.6542 | 65.0099 | 50.0921 | 15.745 | 87.8558 | 15.601 | 15.5405 | 55.7213 | 1 | 50.0922 | 14.5217 | 22.1 | 221 | 154840 | 237679.3478 | 3546005.4783 | 100.1841 | 0.0072946 | 0.21884 | 0.21884 | 0.21884 | 7.9917 | 1033.7689 | 1031.77 | 1031.7704 | 1033.7689 | 1091.3478 | 1091.3478 | 1091.3478 | 1091.3478 | 800.178 | 800.178 | 800.178 | 8.9395 | 0 | 8.9238 | 77.2436 | 220.28 | 220.406 | 218.1053 | 2.0661 | 3.4992 | 0 | 86 | 58.5872 | 65.0099 | 104.9668 | 4.3766 | 87.8558 | -4.1156 | 55.834 | 62.9799 | 47.7696 | 0 | 66.8234 | 753.8937 | 747.9365 | 704.4348 | 704.0024 | 689.3117 | 685.7919 | 472.753 | 467.5008 | 707.5013 | 716.5175 | 800.5554 | 818.5528 | 815.6137 | 815.4465 | 818.6392 | 817.2454 | 807.7697 | 813.2685 | 803.29 | 811.9549 | 797.5211 | 795.4094 | 804.8467 | 801.8261 | 796.1702 | 813.3062 | 813.9795 | 804.7401 | 798.5012 | 811.1763 | 814.7855 | 813.0791 | 810.1087
2025-04-09 21:24 | 9 | 21 | 24 | 6.2817e-272 | 1 | 29.3933 | 696.879 | 0.30168 | 0.0071951 | 150.2147 | 150.2147 | 150.2147 | 150.2147 | 11.6666 | 13.672 | 636.4047 | 636.4047 | 636.4047 | 636.4047 | 64.7153 | 50.1456 | 15.7468 | 87.3319 | 15.5996 | 15.47 | 55.4245 | 1 | 50.1457 | 13.3617 | 22.1 | 221 | 154840 | 237680 | 3546019.8511 | 100.2911 | -0.0017924 | -0.053772 | -0.053772 | -0.053772 | 7.9917 | 1033.7572 | 1031.7591 | 1031.7621 | 1033.7572 | 1092.0304 | 1092.0304 | 1092.0304 | 1092.0304 | 795.7142 | 795.7142 | 795.7142 | 8.7927 | 0 | 8.8029 | 77.4842 | 220.473 | 220.5971 | 218.2001 | 2.0449 | 3.5133 | 0 | 86 | 57.991 | 64.7153 | 104.9787 | 3.1102 | 87.3319 | -4.1618 | 55.5807 | 62.9851 | 47.7226 | 0 | 66.8234 | 753.5013 | 747.6421 | 704.4754 | 703.787 | 689.3455 | 685.5837 | 472.048 | 467.1869 | 707.4014 | 716.4247 | 796.118 | 814.124 | 810.7255 | 810.6778 | 814.2911 | 812.4553 | 803.6663 | 809.0995 | 798.6553 | 807.0676 | 793.8594 | 790.6912 | 800.2719 | 797.402 | 791.9117 | 808.0141 | 809.8713 | 800.6518 | 793.6206 | 806.0802 | 811.3944 | 808.2127 | 805.4839
2025-04-09 21:25 | 9 | 21 | 25 | 6.2817e-272 | 1 | 29.3942 | 695.5172 | 0.2967 | 0.0071975 | 150.6855 | 150.6855 | 150.6855 | 150.6855 | 11.6996 | 13.6727 | 636.6496 | 636.6496 | 636.6496 | 636.6496 | 64.5107 | 50.1372 | 15.7452 | 88.4421 | 15.5993 | 15.6233 | 55.9821 | 1 | 50.1378 | 14.2553 | 22.1 | 221 | 154840 | 237680.1915 | 3546034.4894 | 100.2746 | 0.00065569 | 0.019671 | 0.019671 | 0.019671 | 7.9917 | 1033.1626 | 1031.1457 | 1031.1455 | 1033.1626 | 1090.5834 | 1090.5834 | 1090.5834 | 1090.5834 | 800.1331 | 800.1331 | 800.1331 | 8.9954 | 0 | 9.001 | 77.6403 | 221.1215 | 221.2427 | 218.3108 | 2.0549 | 3.4832 | 0 | 86 | 57.6243 | 64.5107 | 104.9683 | 1.8102 | 88.4421 | -4.1588 | 56.1317 | 62.9782 | 47.7335 | 0 | 66.8232 | 753.5104 | 747.6814 | 704.7222 | 703.736 | 689.414 | 685.4129 | 471.4416 | 466.6881 | 707.3143 | 716.3812 | 800.5668 | 818.8286 | 815.4762 | 815.1671 | 818.5088 | 816.9989 | 807.8575 | 813.8199 | 802.8025 | 812.3428 | 797.7731 | 795.3334 | 804.6613 | 801.4928 | 795.3961 | 813.5911 | 813.8958 | 804.7607 | 798.1197 | 811.1047 | 815.232 | 812.7552 | 809.7542
2025-04-09 21:26 | 9 | 21 | 26 | 6.2817e-272 | 1 | 29.3919 | 695.3145 | 0.29651 | 0.0071957 | 150.7579 | 150.7579 | 150.7579 | 150.7579 | 11.7056 | 13.7147 | 635.8444 | 635.8444 | 635.8444 | 635.8444 | 62.7817 | 50.1507 | 15.7458 | 87.9769 | 15.6035 | 15.5422 | 55.666 | 1 | 50.151 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3546049.1489 | 100.3015 | 0.0020945 | 0.062836 | 0.062836 | 0.062836 | 7.9917 | 1033.0532 | 1031.0334 | 1031.0319 | 1033.0532 | 1091.1898 | 1091.1898 | 1091.1898 | 1091.1898 | 796.6958 | 796.6958 | 796.6958 | 8.8408 | 0 | 8.8286 | 77.7216 | 221.2409 | 221.3638 | 218.3697 | 2.022 | 3.4764 | 0 | 86 | 57.0773 | 62.7817 | 104.9718 | 1.4466 | 87.9769 | -4.1494 | 55.8401 | 62.9813 | 47.7225 | 0 | 66.8227 | 753.1073 | 747.3959 | 704.6199 | 703.615 | 689.3374 | 685.2702 | 470.9118 | 466.3963 | 707.204 | 716.2616 | 797.2822 | 814.7443 | 811.6296 | 812.0516 | 815.8275 | 813.3689 | 804.4065 | 810.4009 | 799.5632 | 808.7356 | 795.0209 | 791.5074 | 801.5866 | 798.4593 | 792.5615 | 809.6379 | 810.2588 | 801.1364 | 794.2579 | 807.0756 | 811.762 | 809.0706 | 806.0266
2025-04-09 21:27 | 9 | 21 | 27 | 6.2817e-272 | 1 | 29.3939 | 693.9334 | 0.30814 | 0.0071877 | 150.8327 | 150.8327 | 150.8327 | 150.8327 | 11.7102 | 13.7403 | 635.4386 | 635.4386 | 635.4386 | 635.4386 | 61.6152 | 50.1534 | 15.7435 | 88.0918 | 15.5989 | 15.5528 | 55.731 | 1 | 50.1539 | 14 | 22.1 | 221 | 154840 | 237681 | 3546063.7447 | 100.3068 | -0.0018479 | -0.055438 | -0.055438 | -0.055438 | 7.9917 | 1032.973 | 1030.9504 | 1030.9521 | 1032.973 | 1091.0398 | 1091.0398 | 1091.0398 | 1091.0398 | 795.7095 | 795.7095 | 795.7095 | 8.7917 | 0 | 8.7928 | 77.8099 | 221.4316 | 221.5482 | 218.2872 | 2.0451 | 3.496 | 0 | 86 | 57.0127 | 61.6152 | 104.9566 | 1.8111 | 88.0918 | -4.1208 | 55.8783 | 62.9869 | 47.6934 | 0 | 66.8237 | 752.3936 | 746.809 | 704.4051 | 703.5788 | 689.0965 | 685.2179 | 470.4647 | 465.7491 | 706.976 | 716.0061 | 796.4887 | 813.8622 | 810.645 | 810.5287 | 814.2839 | 812.7303 | 803.5117 | 809.5862 | 798.7691 | 807.8437 | 794.3349 | 790.4815 | 800.9322 | 797.2974 | 791.1586 | 808.9448 | 808.9547 | 800.4309 | 793.4613 | 806.015 | 810.5184 | 807.9666 | 805.1116
2025-04-09 21:28 | 9 | 21 | 28 | 6.2817e-272 | 1 | 29.3925 | 692.5594 | 0.30798 | 0.007178 | 150.8359 | 150.8359 | 150.8359 | 150.8359 | 11.7109 | 13.7531 | 635.6344 | 635.6344 | 635.6344 | 635.6344 | 61.4379 | 50.1725 | 15.7466 | 87.816 | 15.6015 | 15.5124 | 55.5643 | 1 | 50.1731 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3546078.3617 | 100.3449 | 0.0051999 | 0.156 | 0.156 | 0.156 | 7.9917 | 1032.96 | 1030.9374 | 1030.9355 | 1032.96 | 1091.3989 | 1091.3989 | 1091.3989 | 1091.3989 | 794.254 | 794.254 | 794.254 | 8.734 | 0 | 8.7376 | 77.8293 | 221.4473 | 221.5667 | 218.1549 | 2.0247 | 3.4965 | 0 | 86 | 56.7863 | 61.4379 | 104.9775 | 0.54828 | 87.816 | -4.1351 | 55.7332 | 62.9868 | 47.6536 | 0 | 66.824 | 751.9846 | 746.4029 | 704.2711 | 703.686 | 688.8831 | 685.1899 | 470.0429 | 465.327 | 706.794 | 715.6988 | 795.0122 | 812.3182 | 809.4415 | 809.2326 | 812.9929 | 811.2426 | 802.398 | 807.9433 | 797.3401 | 806.0887 | 792.9946 | 788.9817 | 799.6672 | 796.1649 | 790.4579 | 807.0445 | 807.3733 | 798.4721 | 791.6677 | 804.1333 | 809.1749 | 806.6748 | 803.3103
2025-04-09 21:29 | 9 | 21 | 29 | 6.2817e-272 | 1 | 29.3944 | 690.8243 | 0.30817 | 0.0071775 | 150.9896 | 150.9896 | 150.9896 | 150.9896 | 11.7211 | 13.7555 | 635.0113 | 635.0113 | 635.0113 | 635.0113 | 60.7161 | 50.1432 | 15.7471 | 88.2825 | 15.5992 | 15.5665 | 55.7616 | 1 | 50.1436 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3546093.0426 | 100.2864 | 0.00047181 | 0.014154 | 0.014154 | 0.014154 | 7.9917 | 1032.7768 | 1030.7472 | 1030.7477 | 1032.7768 | 1090.7921 | 1090.7921 | 1090.7921 | 1090.7921 | 794.9031 | 794.9031 | 794.9031 | 8.7661 | 0 | 8.7651 | 77.8459 | 221.6059 | 221.7544 | 217.9884 | 2.0528 | 3.4832 | 0 | 86 | 56.2855 | 60.7161 | 104.9805 | -0.056237 | 88.2825 | -4.0819 | 55.9275 | 62.9868 | 47.6535 | 0 | 66.8248 | 751.4859 | 745.9218 | 704.0317 | 703.6439 | 688.5565 | 685.0987 | 469.5747 | 464.9986 | 706.5426 | 715.3753 | 795.8662 | 812.7147 | 809.9708 | 809.9941 | 813.5827 | 812.1789 | 802.7395 | 808.3564 | 797.973 | 807.1973 | 793.2344 | 789.9224 | 800.5362 | 796.5528 | 790.8297 | 808.4669 | 807.8849 | 798.9695 | 792.2014 | 804.7364 | 809.6288 | 807.466 | 804.0504
2025-04-09 21:30 | 9 | 21 | 30 | 6.2817e-272 | 1 | 29.392 | 689.3932 | 0.3012 | 0.0071841 | 150.8822 | 150.8822 | 150.8822 | 150.8822 | 11.7144 | 13.7623 | 634.5688 | 634.5688 | 634.5688 | 634.5688 | 60.6695 | 50.157 | 15.745 | 87.8004 | 15.5992 | 15.5102 | 55.543 | 1 | 50.1571 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3546107.6383 | 100.314 | 0.0043912 | 0.13173 | 0.13173 | 0.13173 | 7.9917 | 1032.8974 | 1030.8726 | 1030.8738 | 1032.8974 | 1091.4185 | 1091.4185 | 1091.4185 | 1091.4185 | 792.5548 | 792.5548 | 792.5548 | 8.685 | 0 | 8.6896 | 77.8794 | 221.509 | 221.6597 | 217.7369 | 2.0192 | 3.4795 | 0 | 86 | 56.2442 | 60.6695 | 104.9666 | -0.3075 | 87.7994 | -4.1195 | 55.725 | 62.9869 | 47.6771 | 0 | 66.8243 | 750.9841 | 745.2844 | 703.8004 | 703.5528 | 688.2726 | 685.0173 | 469.2159 | 464.6486 | 706.3343 | 715.0053 | 793.1842 | 810.385 | 807.9689 | 807.4089 | 810.9531 | 809.973 | 800.7971 | 805.727 | 795.7877 | 804.502 | 790.7659 | 787.6218 | 798.2579 | 794.2207 | 788.9531 | 805.4098 | 805.6457 | 796.569 | 789.8223 | 802.2851 | 807.701 | 805.2517 | 801.6472
2025-04-09 21:31 | 9 | 21 | 31 | 6.2817e-272 | 1 | 29.3928 | 688.1243 | 0.30904 | 0.0071791 | 150.8707 | 150.8707 | 150.8707 | 150.8707 | 11.7133 | 13.7641 | 634.7856 | 634.7856 | 634.7856 | 634.7856 | 60.5246 | 50.1541 | 15.7446 | 87.6889 | 15.6002 | 15.4728 | 55.4329 | 1 | 50.1545 | 14.4348 | 22.1 | 221 | 154840 | 237681 | 3546122.1087 | 100.3082 | 0.003455 | 0.10365 | 0.10365 | 0.10365 | 7.9917 | 1032.9161 | 1030.8924 | 1030.8924 | 1032.9161 | 1091.5646 | 1091.5646 | 1091.5646 | 1091.5646 | 792.175 | 792.175 | 792.175 | 8.6629 | 0 | 8.6539 | 77.8373 | 221.4612 | 221.6329 | 217.6378 | 1.9998 | 3.4751 | 0 | 86 | 56.2056 | 60.5246 | 104.9642 | -0.40962 | 87.6889 | -4.1053 | 55.5908 | 62.9724 | 47.6582 | 0 | 66.8238 | 750.6967 | 745.0343 | 703.7344 | 703.5979 | 688.1001 | 684.9868 | 468.8445 | 464.034 | 706.1805 | 714.7742 | 792.9715 | 809.5554 | 807.0941 | 807.1327 | 810.8946 | 809.6307 | 800.3286 | 805.356 | 795.4546 | 804.0198 | 790.7966 | 787.3129 | 798.1346 | 794.2158 | 788.7937 | 805.1249 | 805.1729 | 796.1426 | 789.6895 | 801.6976 | 807.0258 | 804.7319 | 800.8209
2025-04-09 21:32 | 9 | 21 | 32 | 6.2817e-272 | 1 | 29.393 | 686.8371 | 0.30755 | 0.0071773 | 150.8621 | 150.8621 | 150.8621 | 150.8621 | 11.7126 | 13.7802 | 634.5236 | 634.5236 | 634.5236 | 634.5236 | 60.1369 | 50.1718 | 15.7446 | 87.4015 | 15.5998 | 15.4425 | 55.2712 | 1 | 50.1723 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3546136.4681 | 100.3435 | -1.0076e-05 | -0.00030172 | -0.00030172 | -0.00030172 | 7.9917 | 1032.9298 | 1030.9066 | 1030.9068 | 1032.9298 | 1091.9387 | 1091.9387 | 1091.9387 | 1091.9387 | 789.1878 | 789.1878 | 789.1878 | 8.5731 | 0 | 8.5735 | 77.898 | 221.4971 | 221.6411 | 217.5444 | 2.0061 | 3.4743 | 0 | 86 | 56.213 | 60.1369 | 104.964 | -0.68215 | 87.4015 | -4.1497 | 55.482 | 62.97 | 47.6517 | 0 | 66.8236 | 750.056 | 744.4719 | 703.5867 | 703.5034 | 687.9453 | 684.9214 | 468.454 | 463.7281 | 705.9073 | 714.5059 | 789.936 | 806.5597 | 804.4039 | 804.0483 | 807.819 | 806.5095 | 797.1586 | 802.2874 | 792.3206 | 800.7559 | 788.4584 | 784.3474 | 795.2749 | 791.5385 | 785.8182 | 801.6782 | 802.1872 | 793.3267 | 786.757 | 798.4136 | 803.9021 | 801.8269 | 797.7239
2025-04-09 21:33 | 9 | 21 | 33 | 6.2817e-272 | 1 | 29.3918 | 685.3374 | 0.30208 | 0.0071843 | 151.0902 | 151.0902 | 151.0902 | 151.0902 | 11.7292 | 13.7949 | 634.3977 | 634.3977 | 634.3977 | 634.3977 | 59.5522 | 50.1774 | 15.7446 | 87.7828 | 15.6 | 15.4986 | 55.6702 | 1 | 50.178 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3546151.0426 | 100.3547 | -0.00084929 | -0.025478 | -0.025478 | -0.025478 | 7.9917 | 1032.6287 | 1030.5962 | 1030.5983 | 1032.6287 | 1091.4426 | 1091.4426 | 1091.4426 | 1091.4426 | 789.9021 | 789.9021 | 789.9021 | 8.6098 | 0 | 8.6149 | 78.0835 | 221.9096 | 222.0534 | 217.3214 | 2.0114 | 3.4752 | 0 | 86 | 56.1819 | 59.5522 | 104.9642 | -0.81442 | 87.7828 | -3.5936 | 55.6834 | 62.973 | 47.679 | 0 | 66.8234 | 749.588 | 744.0547 | 703.5084 | 703.2329 | 687.718 | 684.5057 | 467.8956 | 463.2676 | 705.6359 | 714.1777 | 790.9333 | 807.1898 | 804.845 | 804.492 | 808.1723 | 807.4161 | 797.8779 | 803.1676 | 793.3513 | 802.1707 | 789.0417 | 784.803 | 796.0395 | 792.2592 | 786.0429 | 802.7755 | 802.472 | 793.5428 | 786.7453 | 799.2391 | 805.0934 | 802.5489 | 798.8168
2025-04-09 21:34 | 9 | 21 | 34 | 6.2817e-272 | 1 | 29.3909 | 683.8466 | 0.30171 | 0.0071924 | 151.2872 | 151.2872 | 151.2872 | 151.2872 | 11.7435 | 13.8038 | 634.7088 | 634.7088 | 634.7088 | 634.7088 | 59.1385 | 50.1776 | 15.7475 | 88.2521 | 15.5999 | 15.5457 | 55.8283 | 1 | 50.1783 | 14.766 | 22.1 | 221 | 154840 | 237681 | 3546165.6809 | 100.3553 | -0.0057547 | -0.17264 | -0.17264 | -0.17264 | 7.9917 | 1032.3717 | 1030.3311 | 1030.3296 | 1032.3717 | 1090.8313 | 1090.8313 | 1090.8313 | 1090.8313 | 791.6144 | 791.6144 | 791.6144 | 8.6774 | 0 | 8.6767 | 78.2922 | 222.2727 | 222.431 | 216.9016 | 1.9822 | 3.474 | 0 | 86 | 55.8328 | 59.1385 | 104.983 | -0.9791 | 88.2521 | -2.2515 | 55.8527 | 62.9737 | 47.7096 | 0 | 66.8238 | 749.3445 | 743.8974 | 703.4525 | 702.9619 | 687.5822 | 684.0952 | 467.3485 | 462.6224 | 705.4037 | 713.9202 | 792.9314 | 809.0693 | 806.3347 | 806.0716 | 809.8664 | 808.9171 | 799.8216 | 805.1794 | 794.7039 | 803.9957 | 790.6639 | 786.33 | 797.8231 | 793.6667 | 787.6047 | 804.8772 | 804.2429 | 795.5973 | 788.7751 | 800.9731 | 806.9552 | 803.8894 | 800.3499
2025-04-09 21:35 | 9 | 21 | 35 | 6.2817e-272 | 1 | 29.387 | 682.2554 | 0.30634 | 0.0072013 | 151.0832 | 151.0832 | 151.0832 | 151.0832 | 11.7305 | 13.7985 | 634.4042 | 634.4042 | 634.4042 | 634.4042 | 58.9474 | 50.1557 | 15.7471 | 87.9627 | 15.599 | 15.5039 | 55.551 | 1 | 50.1557 | 14.2979 | 22.1 | 221 | 154840 | 237681 | 3546180.3404 | 100.3115 | -0.00088879 | -0.026664 | -0.026664 | -0.026664 | 7.9917 | 1032.6032 | 1030.5691 | 1030.57 | 1032.6032 | 1091.2077 | 1091.2077 | 1091.2077 | 1091.2077 | 791.2714 | 791.2714 | 791.2714 | 8.5985 | 0 | 8.6059 | 78.0984 | 221.9567 | 222.0963 | 216.5698 | 1.9412 | 3.4662 | 0 | 86 | 55.8045 | 58.9474 | 104.9806 | -0.82029 | 87.9627 | -2.1788 | 55.7024 | 62.9869 | 47.7412 | 0 | 66.823 | 749.173 | 743.9038 | 703.3303 | 702.5945 | 687.3385 | 683.6625 | 466.7438 | 462.1952 | 705.166 | 713.7941 | 792.338 | 808.8095 | 806.0789 | 806.2025 | 809.9275 | 808.2711 | 799.5176 | 804.9775 | 794.3119 | 803.5956 | 790.7448 | 785.811 | 797.3252 | 793.7523 | 787.4878 | 804.2599 | 803.8498 | 795.0559 | 787.8594 | 800.3205 | 806.3994 | 803.368 | 800.269
2025-04-09 21:36 | 9 | 21 | 36 | 6.2817e-272 | 1 | 29.3868 | 680.8745 | 0.30183 | 0.0072018 | 151.4168 | 151.4168 | 151.4168 | 151.4168 | 11.7542 | 13.7925 | 634.17 | 634.17 | 634.17 | 634.17 | 58.5214 | 50.1227 | 15.7458 | 89.0001 | 15.5991 | 15.6737 | 56.1394 | 1 | 50.1232 | 15.5319 | 22.1 | 221 | 154840 | 237681 | 3546194.9787 | 100.2456 | -0.002249 | -0.067472 | -0.067472 | -0.067472 | 7.9917 | 1032.1777 | 1030.1315 | 1030.1328 | 1032.1777 | 1089.8568 | 1089.8568 | 1089.8568 | 1089.8568 | 795.2335 | 795.2335 | 795.2335 | 8.7934 | 0 | 8.7935 | 78.199 | 222.3592 | 222.5276 | 216.4311 | 1.9348 | 3.4691 | 0 | 86 | 55.7573 | 58.5214 | 104.9723 | -0.87959 | 89.0001 | -2.2086 | 56.3127 | 62.9764 | 47.7447 | 0 | 66.8229 | 748.8602 | 743.7282 | 703.0936 | 702.1031 | 687.089 | 683.1606 | 466.0616 | 461.873 | 704.93 | 713.6229 | 796.7011 | 813.2024 | 809.7424 | 809.3308 | 812.7909 | 812.2201 | 803.1116 | 809.0971 | 798.1776 | 808.3083 | 793.9146 | 789.9614 | 801.1119 | 797.2536 | 790.9566 | 809.6748 | 807.5871 | 799.2429 | 792.6299 | 805.335 | 809.5996 | 807.0293 | 804.348
2025-04-09 21:37 | 9 | 21 | 37 | 6.2817e-272 | 1 | 29.39 | 679.2358 | 0.30262 | 0.0072087 | 150.83 | 150.83 | 150.83 | 150.83 | 11.7114 | 13.7991 | 633.3448 | 633.3448 | 633.3448 | 633.3448 | 58.2683 | 50.1248 | 15.7476 | 87.4269 | 15.6023 | 15.4426 | 55.3283 | 1 | 50.1248 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3546209.7021 | 100.2496 | 0.0083764 | 0.25129 | 0.25129 | 0.25129 | 7.9917 | 1032.9509 | 1030.9279 | 1030.9245 | 1032.9509 | 1091.9057 | 1091.9057 | 1091.9057 | 1091.9057 | 789.8035 | 789.8035 | 789.8035 | 8.506 | 0 | 8.4929 | 77.8872 | 221.4491 | 221.6193 | 216.4007 | 1.9713 | 3.4816 | 0 | 86 | 55.7641 | 58.2683 | 104.9842 | -0.89074 | 87.4269 | -2.2635 | 55.4822 | 62.973 | 47.7736 | 0 | 66.8228 | 748.6323 | 743.6959 | 702.8748 | 701.6267 | 686.838 | 682.7079 | 465.3929 | 461.532 | 704.7775 | 713.5407 | 791.0343 | 807.6311 | 804.5102 | 804.5756 | 808.4933 | 805.9868 | 797.9383 | 803.7617 | 792.967 | 802.1078 | 789.9251 | 783.8436 | 795.3038 | 792.6496 | 786.2246 | 802.3816 | 802.5899 | 793.9142 | 786.3991 | 798.7523 | 804.332 | 801.4833 | 798.7265
2025-04-09 21:38 | 9 | 21 | 38 | 6.2817e-272 | 1 | 29.3908 | 677.6362 | 0.30245 | 0.0072105 | 151.0874 | 151.0874 | 151.0874 | 151.0874 | 11.7294 | 13.8051 | 633.3202 | 633.3202 | 633.3202 | 633.3202 | 58.0761 | 50.127 | 15.7479 | 88.0493 | 15.6035 | 15.527 | 55.6009 | 1 | 50.1277 | 14.5957 | 22.1 | 221 | 154840 | 237681 | 3546224.2766 | 100.254 | -0.0031813 | -0.09544 | -0.09544 | -0.09544 | 7.9917 | 1032.6262 | 1030.5932 | 1030.5902 | 1032.6262 | 1091.0951 | 1091.0951 | 1091.0951 | 1091.0951 | 791.5216 | 791.5216 | 791.5216 | 8.595 | 0 | 8.5916 | 78.0124 | 221.8266 | 222.0061 | 216.3276 | 2.0181 | 3.4905 | 0 | 86 | 55.6531 | 58.0761 | 104.9857 | -1.0444 | 88.0493 | -2.1862 | 55.7854 | 62.9674 | 47.7822 | 0 | 66.8229 | 748.3799 | 743.3707 | 702.6365 | 701.1772 | 686.5623 | 682.2413 | 464.7408 | 461.0361 | 704.563 | 713.2843 | 793.1453 | 809.325 | 805.8147 | 806.5801 | 810.1966 | 808.291 | 800.0797 | 805.321 | 794.4676 | 804.2436 | 790.2807 | 785.6627 | 796.8452 | 794.0298 | 787.4794 | 804.7042 | 804.5059 | 796.0404 | 788.3365 | 800.8484 | 806.2921 | 802.7226 | 800.3547
2025-04-09 21:39 | 9 | 21 | 39 | 6.2817e-272 | 1 | 29.3847 | 676.9858 | 0.30056 | 0.007214 | 150.9742 | 150.9742 | 150.9742 | 150.9742 | 11.7236 | 13.8018 | 633.2382 | 633.2382 | 633.2382 | 633.2382 | 57.9808 | 50.1161 | 15.7448 | 88.003 | 15.5979 | 15.5198 | 55.6565 | 1 | 50.1162 | 13.9574 | 22.1 | 221 | 154840 | 237681 | 3546238.9574 | 100.2321 | 0.0018646 | 0.055939 | 0.055939 | 0.055939 | 7.9917 | 1032.7296 | 1030.6989 | 1030.6983 | 1032.7296 | 1091.1557 | 1091.1557 | 1091.1557 | 1091.1557 | 791.8099 | 791.8099 | 791.8099 | 8.5799 | 0 | 8.5851 | 77.9167 | 221.6776 | 221.8524 | 216.288 | 1.9558 | 3.4977 | 0 | 86 | 55.6643 | 57.9808 | 104.9654 | -1.2057 | 88.003 | -2.1807 | 55.7597 | 62.97 | 47.7908 | 0 | 66.8224 | 748.2725 | 743.2461 | 702.2946 | 700.8609 | 686.2144 | 681.8966 | 464.1647 | 460.6571 | 704.4796 | 713.0269 | 792.9959 | 809.8803 | 806.5086 | 807.0601 | 810.5268 | 808.5768 | 800.3612 | 805.8282 | 794.7843 | 804.6561 | 790.7277 | 785.5446 | 797.1958 | 794.4289 | 787.5556 | 805.4139 | 804.5746 | 795.9148 | 787.98 | 801.2341 | 805.961 | 803.282 | 800.9698
2025-04-09 21:40 | 9 | 21 | 40 | 6.2817e-272 | 1 | 29.3839 | 676.4941 | 0.30123 | 0.007223 | 150.9992 | 150.9992 | 150.9992 | 150.9992 | 11.7257 | 13.8004 | 633.3429 | 633.3429 | 633.3429 | 633.3429 | 57.8137 | 50.1057 | 15.747 | 88.2461 | 15.6 | 15.5517 | 55.7233 | 1 | 50.1061 | 14.6087 | 22.1 | 221 | 154840 | 237681 | 3546253.4565 | 100.2113 | 0.0018151 | 0.054452 | 0.054452 | 0.054452 | 7.9917 | 1032.6909 | 1030.66 | 1030.6626 | 1032.6909 | 1090.8396 | 1090.8396 | 1090.8396 | 1090.8396 | 792.5404 | 792.5404 | 792.5404 | 8.6095 | 0 | 8.6085 | 77.9497 | 221.7569 | 221.9324 | 216.188 | 1.9268 | 3.5035 | 0 | 86 | 56.0645 | 57.8137 | 104.9799 | -1.2925 | 88.2461 | -2.1886 | 55.8744 | 62.9815 | 47.8265 | 0 | 66.8216 | 748.1717 | 743.0688 | 702.0041 | 700.7054 | 685.8602 | 681.7442 | 463.6576 | 460.3197 | 704.303 | 712.7849 | 793.9797 | 810.6064 | 806.9492 | 807.5525 | 810.9082 | 809.3022 | 801.1352 | 806.532 | 795.4483 | 805.5365 | 791.0925 | 786.5181 | 797.8192 | 795.1831 | 788.4323 | 806.4257 | 805.5463 | 796.7119 | 789.1187 | 802.077 | 806.6024 | 803.6385 | 801.5482
2025-04-09 21:41 | 9 | 21 | 41 | 6.2817e-272 | 1 | 29.384 | 675.9086 | 0.29467 | 0.007231 | 150.7309 | 150.7309 | 150.7309 | 150.7309 | 11.7067 | 13.7978 | 633.3452 | 633.3452 | 633.3452 | 633.3452 | 58.0079 | 50.1085 | 15.7454 | 87.6211 | 15.5992 | 15.4589 | 55.4635 | 1 | 50.1092 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3546267.9149 | 100.2171 | -0.0055541 | -0.16662 | -0.16662 | -0.16662 | 7.9917 | 1033.0374 | 1031.0166 | 1031.0162 | 1033.0374 | 1091.653 | 1091.653 | 1091.653 | 1091.653 | 790.6809 | 790.6809 | 790.6809 | 8.5057 | 0 | 8.5039 | 77.8062 | 221.3441 | 221.5183 | 216.1104 | 1.9253 | 3.5025 | 0 | 86 | 56.1619 | 58.0079 | 104.9693 | -1.4646 | 87.6211 | -2.1934 | 55.5408 | 62.9713 | 47.8563 | 0 | 66.822 | 748.0662 | 742.9353 | 701.6651 | 700.6175 | 685.5867 | 681.6203 | 463.2451 | 459.8663 | 704.1568 | 712.5958 | 791.8247 | 808.4544 | 805.0786 | 805.6564 | 809.2199 | 807.5071 | 799.6492 | 804.736 | 793.7753 | 803.3571 | 789.5718 | 784.2834 | 796.1584 | 793.7302 | 786.8486 | 803.7325 | 803.5754 | 794.9571 | 786.9576 | 799.9653 | 804.9208 | 801.969 | 799.5761
2025-04-09 21:42 | 9 | 21 | 42 | 6.2817e-272 | 1 | 29.387 | 674.3689 | 0.29162 | 0.0072397 | 150.7756 | 150.7756 | 150.7756 | 150.7756 | 11.7087 | 13.7817 | 633.7506 | 633.7506 | 633.7506 | 633.7506 | 58.3727 | 50.0899 | 15.7459 | 87.8902 | 15.6018 | 15.5066 | 55.6356 | 1 | 50.0902 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3546282.5745 | 100.1795 | 0.0032461 | 0.097384 | 0.097384 | 0.097384 | 7.9917 | 1033.0019 | 1030.9796 | 1030.9774 | 1033.0019 | 1091.303 | 1091.303 | 1091.303 | 1091.303 | 792.6656 | 792.6656 | 792.6656 | 8.587 | 0 | 8.5838 | 77.8068 | 221.3448 | 221.5155 | 216.0501 | 1.9526 | 3.492 | 0 | 86 | 56.0602 | 58.3727 | 104.9727 | -1.427 | 87.8902 | -2.1989 | 55.7122 | 62.9725 | 47.8971 | 0 | 66.8218 | 748.0647 | 742.8445 | 701.4773 | 700.6322 | 685.3183 | 681.6122 | 462.836 | 459.6474 | 704.0099 | 712.3678 | 793.7636 | 810.5328 | 807.035 | 807.6371 | 810.9301 | 809.8406 | 801.445 | 806.6946 | 795.7339 | 805.5449 | 790.9831 | 786.6512 | 798.2842 | 795.5148 | 788.8719 | 806.3 | 805.5101 | 796.7904 | 788.9743 | 802.0717 | 806.665 | 804.0443 | 801.8223
2025-04-09 21:43 | 9 | 21 | 43 | 6.2817e-272 | 1 | 29.3917 | 673.5794 | 0.29503 | 0.0072469 | 150.8419 | 150.8419 | 150.8419 | 150.8419 | 11.7116 | 13.7851 | 633.8242 | 633.8242 | 633.8242 | 633.8242 | 58.4607 | 50.1023 | 15.7476 | 87.9973 | 15.5996 | 15.5256 | 55.6319 | 1 | 50.1028 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3546297.1277 | 100.2045 | -0.0027837 | -0.083512 | -0.083512 | -0.083512 | 7.9917 | 1032.9457 | 1030.9211 | 1030.9217 | 1032.9457 | 1091.163 | 1091.163 | 1091.163 | 1091.163 | 792.077 | 792.077 | 792.077 | 8.588 | 0 | 8.5881 | 77.8613 | 221.4736 | 221.652 | 216.071 | 1.9809 | 3.4901 | 0 | 86 | 56.257 | 58.4607 | 104.984 | -1.5713 | 87.9973 | -2.159 | 55.7804 | 62.9769 | 47.9294 | 0 | 66.8217 | 747.8833 | 742.7193 | 701.2679 | 700.598 | 685.1399 | 681.5879 | 462.5284 | 459.3301 | 703.7989 | 712.2231 | 792.6116 | 810.0615 | 806.8073 | 806.637 | 809.964 | 809.0552 | 800.6209 | 806.062 | 795.0729 | 804.9407 | 790.6647 | 785.9409 | 798.117 | 795.0469 | 787.9645 | 805.6269 | 804.8581 | 796.2419 | 788.5774 | 801.6683 | 805.7595 | 803.8716 | 801.2131
2025-04-09 21:44 | 9 | 21 | 44 | 6.2817e-272 | 1 | 29.3935 | 672.4639 | 0.2972 | 0.0072472 | 150.7659 | 150.7659 | 150.7659 | 150.7659 | 11.7056 | 13.7822 | 634.0279 | 634.0279 | 634.0279 | 634.0279 | 58.6103 | 50.1023 | 15.7471 | 87.8255 | 15.5995 | 15.5036 | 55.5605 | 1 | 50.1028 | 14 | 22.1 | 221 | 154840 | 237681 | 3546311.8085 | 100.2043 | -0.0035827 | -0.10748 | -0.10748 | -0.10748 | 7.9917 | 1033.0532 | 1031.034 | 1031.0351 | 1033.0532 | 1091.387 | 1091.387 | 1091.387 | 1091.387 | 792.0624 | 792.0624 | 792.0624 | 8.5684 | 0 | 8.5708 | 77.8046 | 221.3503 | 221.5365 | 216.1753 | 1.9934 | 3.4942 | 0 | 86 | 56.3079 | 58.6103 | 104.9805 | -1.7266 | 87.8255 | -2.0856 | 55.7015 | 62.9745 | 47.9311 | 0 | 66.8214 | 747.7867 | 742.7637 | 701.1903 | 700.64 | 684.996 | 681.5885 | 462.2251 | 458.8966 | 703.5724 | 712.1478 | 792.6888 | 809.9719 | 806.6814 | 806.8344 | 810.1288 | 809.2393 | 800.575 | 806.1816 | 795.1719 | 804.742 | 790.8319 | 785.9649 | 798.1835 | 794.9615 | 788.1393 | 805.3166 | 804.6495 | 796.464 | 788.8945 | 801.3476 | 805.5885 | 803.7109 | 800.6794
2025-04-09 21:45 | 9 | 21 | 45 | 6.2817e-272 | 1 | 29.3984 | 669.5729 | 0.29523 | 0.0072487 | 150.7008 | 150.7008 | 150.7008 | 150.7008 | 11.6992 | 13.7759 | 634.8895 | 634.8895 | 634.8895 | 634.8895 | 58.8681 | 50.1001 | 15.748 | 87.9598 | 15.599 | 15.5176 | 55.6416 | 1 | 50.1005 | 14 | 22.1 | 221 | 154840 | 237681 | 3546326.4255 | 100.2001 | 0.0021239 | 0.063718 | 0.063718 | 0.063718 | 7.9917 | 1033.1728 | 1031.156 | 1031.156 | 1033.1728 | 1091.2119 | 1091.2119 | 1091.2119 | 1091.2119 | 793.5103 | 793.5103 | 793.5103 | 8.5934 | 0 | 8.6028 | 77.7926 | 221.2631 | 221.4156 | 216.2524 | 2.0715 | 3.4992 | 0 | 86 | 56.8877 | 58.8681 | 104.9868 | -1.874 | 87.9598 | -2.1064 | 55.7518 | 62.9764 | 47.9446 | 0 | 66.8214 | 747.832 | 742.9991 | 701.1606 | 700.8163 | 684.9321 | 681.6928 | 461.8932 | 458.6335 | 703.4296 | 712.1224 | 794.1764 | 811.5622 | 808.191 | 808.5094 | 811.6241 | 810.8932 | 802.0296 | 807.7247 | 796.7328 | 806.5004 | 791.9936 | 787.464 | 799.7852 | 796.3148 | 789.5187 | 807.3304 | 805.8515 | 797.5939 | 789.9791 | 802.8193 | 807.0312 | 805.2197 | 802.0133
2025-04-09 21:46 | 9 | 21 | 46 | 6.2817e-272 | 1 | 29.3997 | 667.8936 | 0.29933 | 0.0072558 | 150.7572 | 150.7572 | 150.7572 | 150.7572 | 11.7027 | 13.7663 | 635.328 | 635.328 | 635.328 | 635.328 | 59.4305 | 50.1071 | 15.7485 | 87.9924 | 15.5995 | 15.5342 | 55.6841 | 1 | 50.1073 | 14.2979 | 22.1 | 221 | 154840 | 237681 | 3546341 | 100.2143 | 0.0068752 | 0.20626 | 0.20626 | 0.20626 | 7.9917 | 1033.1057 | 1031.087 | 1031.0879 | 1033.1057 | 1091.1691 | 1091.1691 | 1091.1691 | 1091.1691 | 794.2856 | 794.2856 | 794.2856 | 8.657 | 0 | 8.6515 | 77.7756 | 221.3236 | 221.4651 | 216.3632 | 2.1077 | 3.4964 | 0 | 86 | 57.2698 | 59.4305 | 104.9899 | -2.0504 | 87.9924 | -2.1057 | 55.8114 | 62.979 | 47.9745 | 0 | 66.8213 | 747.9634 | 743.2664 | 701.1551 | 700.9384 | 684.9249 | 681.8239 | 461.5578 | 458.3357 | 703.2994 | 712.0902 | 795.0523 | 812.4155 | 808.7602 | 808.9801 | 812.1003 | 811.3644 | 802.2379 | 808.4455 | 797.4344 | 807.1491 | 792.6136 | 788.5819 | 800.7663 | 797.1985 | 790.8253 | 807.8548 | 806.6852 | 798.6569 | 791.2002 | 803.5423 | 807.7099 | 806.1501 | 803.079
2025-04-09 21:47 | 9 | 21 | 47 | 6.2817e-272 | 1 | 29.3993 | 666.1775 | 0.29928 | 0.0072579 | 150.5923 | 150.5923 | 150.5923 | 150.5923 | 11.6911 | 13.7675 | 635.4025 | 635.4025 | 635.4025 | 635.4025 | 59.5923 | 50.1163 | 15.7495 | 87.5102 | 15.6007 | 15.463 | 55.4231 | 1 | 50.1164 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3546355.6596 | 100.2328 | 0.0034437 | 0.10331 | 0.10331 | 0.10331 | 7.9917 | 1033.3187 | 1031.3064 | 1031.3064 | 1033.3187 | 1091.7977 | 1091.7977 | 1091.7977 | 1091.7977 | 792.2037 | 792.2037 | 792.2037 | 8.5678 | 0 | 8.5644 | 77.7651 | 221.1283 | 221.2877 | 216.3805 | 2.1004 | 3.4921 | 0 | 86 | 57.5309 | 59.5923 | 104.9967 | -2.0778 | 87.5102 | -2.1206 | 55.5557 | 62.9795 | 47.9828 | 0 | 66.8208 | 748.081 | 743.447 | 701.1873 | 700.9914 | 684.9448 | 681.8637 | 461.1924 | 458.014 | 703.2527 | 712.0566 | 792.769 | 809.9859 | 806.4846 | 807.0796 | 810.4006 | 809.4805 | 800.2213 | 806.4267 | 795.3059 | 804.9573 | 790.7359 | 786.1639 | 798.679 | 794.9373 | 788.4379 | 805.6558 | 804.7936 | 796.5482 | 788.8132 | 801.5669 | 806.1575 | 803.8718 | 800.6524
2025-04-09 21:48 | 9 | 21 | 48 | 6.2817e-272 | 1 | 29.3995 | 664.4171 | 0.30327 | 0.0072698 | 150.8717 | 150.8717 | 150.8717 | 150.8717 | 11.7109 | 13.7644 | 635.7616 | 635.7616 | 635.7616 | 635.7616 | 59.8112 | 50.1194 | 15.7462 | 88.2676 | 15.6002 | 15.5717 | 55.8256 | 1 | 50.1199 | 14.4348 | 22.1 | 221 | 154840 | 237681 | 3546370.087 | 100.2389 | -0.001217 | -0.036509 | -0.036509 | -0.036509 | 7.9917 | 1032.9617 | 1030.9393 | 1030.9413 | 1032.9617 | 1090.8117 | 1090.8117 | 1090.8117 | 1090.8117 | 794.6197 | 794.6197 | 794.6197 | 8.7013 | 0 | 8.706 | 77.8915 | 221.4997 | 221.6578 | 216.3882 | 2.1077 | 3.496 | 0 | 86 | 57.5882 | 59.8112 | 104.9749 | -2.041 | 88.2676 | -2.1936 | 55.9463 | 62.9783 | 48.031 | 0 | 66.8212 | 748.0941 | 743.4645 | 701.2255 | 701.0903 | 685.004 | 681.9595 | 460.8044 | 457.5482 | 703.1405 | 711.9545 | 795.4703 | 812.6804 | 808.7749 | 809.078 | 812.0399 | 811.7956 | 802.2626 | 808.7566 | 797.8216 | 807.8874 | 793.1587 | 788.967 | 801.1611 | 797.0868 | 790.8462 | 808.4734 | 806.8803 | 799.1021 | 791.5265 | 804.2664 | 808.2114 | 806.5307 | 803.4387
2025-04-09 21:49 | 9 | 21 | 49 | 6.2817e-272 | 1 | 29.3994 | 663.7931 | 0.30592 | 0.0072795 | 150.758 | 150.758 | 150.758 | 150.758 | 11.7029 | 13.7756 | 635.1977 | 635.1977 | 635.1977 | 635.1977 | 59.7472 | 50.143 | 15.7496 | 87.5637 | 15.5995 | 15.4505 | 55.3987 | 1 | 50.1432 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3546384.5532 | 100.286 | 0.00074932 | 0.02248 | 0.02248 | 0.02248 | 7.9917 | 1033.1053 | 1031.0872 | 1031.086 | 1033.1053 | 1091.7274 | 1091.7274 | 1091.7274 | 1091.7274 | 791.3077 | 791.3077 | 791.3077 | 8.5668 | 0 | 8.5678 | 77.8838 | 221.3901 | 221.5369 | 216.5301 | 2.1225 | 3.5047 | 0 | 86 | 57.5979 | 59.7472 | 104.9971 | -2.1665 | 87.5637 | -2.1963 | 55.5105 | 62.9852 | 48.0696 | 0 | 66.8206 | 748.0825 | 743.4614 | 701.2664 | 701.0989 | 685.0183 | 681.9678 | 460.3745 | 457.4601 | 703.084 | 711.9166 | 792.2607 | 809.3231 | 805.6649 | 806.0708 | 809.454 | 808.2286 | 799.3678 | 805.3615 | 794.5088 | 804.1799 | 790.3608 | 785.8186 | 797.8235 | 794.0463 | 787.7801 | 804.6013 | 803.8562 | 795.6191 | 787.7934 | 800.3254 | 805.1338 | 803.1856 | 799.866
2025-04-09 21:50 | 9 | 21 | 50 | 6.2817e-272 | 1 | 29.3994 | 662.5303 | 0.29801 | 0.0072902 | 150.759 | 150.759 | 150.759 | 150.759 | 11.7029 | 13.7749 | 635.9438 | 635.9438 | 635.9438 | 635.9438 | 59.6855 | 50.1386 | 15.7467 | 87.6925 | 15.5993 | 15.4925 | 55.4814 | 1 | 50.1387 | 16.3404 | 22.1 | 221 | 154840 | 237681 | 3546399.1489 | 100.2771 | 0.0021846 | 0.065538 | 0.065538 | 0.065538 | 7.9917 | 1033.1036 | 1031.0843 | 1031.0819 | 1033.1036 | 1091.5606 | 1091.5606 | 1091.5606 | 1091.5606 | 792.3142 | 792.3142 | 792.3142 | 8.6074 | 0 | 8.5926 | 77.8483 | 221.3598 | 221.4931 | 216.6424 | 2.0931 | 3.4855 | 0 | 86 | 57.7952 | 59.6855 | 104.9778 | -2.2875 | 87.6925 | -2.1966 | 55.6614 | 62.9825 | 48.1134 | 0 | 66.8206 | 747.9968 | 743.4799 | 701.2785 | 701.1821 | 685.0499 | 682.0424 | 459.9978 | 456.8673 | 703.0411 | 711.8178 | 793.3073 | 810.0839 | 806.7586 | 807.059 | 810.2164 | 809.5775 | 800.2751 | 806.4234 | 795.6062 | 805.2339 | 790.9638 | 786.4017 | 799.26 | 795.1147 | 788.9276 | 805.9737 | 804.4247 | 796.6571 | 788.8329 | 801.2006 | 805.8937 | 804.1759 | 800.5245
2025-04-09 21:51 | 9 | 21 | 51 | 6.2817e-272 | 1 | 29.3993 | 660.754 | 0.28933 | 0.0073163 | 147.4619 | 147.4619 | 147.4619 | 147.4619 | 11.4693 | 13.7771 | 630.9197 | 630.9197 | 630.9197 | 630.9197 | 59.6822 | 50.1431 | 15.7514 | 79.0113 | 15.6034 | 14.1883 | 50.8195 | 1 | 50.1436 | 18 | 22.1 | 221 | 154840 | 237681 | 3546413.1915 | 100.2861 | -0.0020109 | -0.060327 | -0.060327 | -0.060327 | 7.9917 | 1037.3106 | 1035.4194 | 1035.4136 | 1037.3106 | 1102.8681 | 1102.8681 | 1102.8681 | 1102.8681 | 755.6733 | 755.6733 | 755.6733 | 7.0111 | 0 | 6.9572 | 74.3625 | 214.4244 | 214.5367 | 216.5732 | 2.1166 | 3.4904 | 0 | 86 | 58.0931 | 59.6822 | 105.0094 | -2.6473 | 79.0113 | -2.1593 | 50.9758 | 62.9821 | 48.2171 | 0 | 66.82 | 746.6768 | 742.2922 | 700.7421 | 700.683 | 684.9046 | 681.958 | 459.5345 | 455.7213 | 702.8136 | 711.6291 | 755.6025 | 771.8102 | 769.4644 | 772.7404 | 779.1972 | 771.2515 | 766.36 | 768.5312 | 759.7758 | 763.4015 | 759.387 | 749.2793 | 762.2724 | 761.8745 | 756.4401 | 761.0483 | 768.0162 | 760.8037 | 752.8607 | 760.0269 | 770.397 | 764.77 | 764.4083
2025-04-09 21:52 | 9 | 21 | 52 | 6.2817e-272 | 1 | 29.4005 | 659.3839 | 0.28497 | 0.0073535 | 144.1804 | 144.1804 | 144.1804 | 144.1804 | 11.2365 | 13.7729 | 624.0614 | 624.0614 | 624.0614 | 624.0614 | 59.6736 | 50.1339 | 15.7513 | 70.5012 | 15.604 | 12.9945 | 46.56 | 1 | 50.1341 | 16.5532 | 22.1 | 221 | 154840 | 237681 | 3546425.5957 | 100.2679 | 0.0052425 | 0.15728 | 0.15728 | 0.15728 | 7.9917 | 1041.5098 | 1039.7464 | 1039.7449 | 1041.5098 | 1113.9538 | 1113.9538 | 1113.9538 | 1113.9538 | 715.6445 | 715.6445 | 715.6445 | 5.4583 | 0 | 5.4137 | 70.0915 | 206.6031 | 206.7329 | 216.653 | 2.1215 | 3.5005 | 0 | 86 | 57.8281 | 59.6736 | 105.0083 | -3.0964 | 70.5012 | -2.219 | 46.6868 | 62.9839 | 48.3675 | 0 | 66.8193 | 742.2096 | 737.8791 | 699.2711 | 699.321 | 684.2601 | 681.6357 | 458.6662 | 452.4902 | 701.6084 | 710.8544 | 717.3297 | 729.0221 | 728.0389 | 731.2878 | 740.9992 | 730.4234 | 727.2722 | 727.1278 | 719.2429 | 720.5174 | 720.5868 | 715.5749 | 720.9478 | 721.712 | 720.2234 | 718.6275 | 727.9586 | 719.9808 | 717.2512 | 719.2231 | 729.336 | 723.4828 | 724.8736
2025-04-09 21:53 | 9 | 21 | 53 | 6.2817e-272 | 1 | 29.3976 | 658.4365 | 0.28263 | 0.0073697 | 143.2127 | 143.2127 | 143.2127 | 143.2127 | 11.169 | 13.7652 | 620.51 | 620.51 | 620.51 | 620.51 | 59.8433 | 50.1366 | 15.7481 | 68.1228 | 15.5997 | 12.6937 | 45.4877 | 0.44681 | 50.1372 | 14.3404 | 22.1 | 221 | 154840 | 237681 | 3546436.9574 | 100.2735 | -0.0031135 | -0.093404 | -0.093404 | -0.093404 | 7.9917 | 1043.4938 | 1042.1066 | 1042.1083 | 1042.7268 | 1117.0511 | 1117.0511 | 1117.0511 | 1117.0511 | 700.8129 | 700.8129 | 700.8129 | 5.0054 | 0 | 5.0114 | 69.2715 | 204.5971 | 204.7451 | 216.7325 | 2.0305 | 3.4801 | 0 | 85.7444 | 57.4421 | 59.8433 | 104.9869 | -3.5077 | 68.1228 | -2.2096 | 45.606 | 63.0372 | 48.4292 | 0 | 66.8194 | 737.2367 | 732.7145 | 697.8538 | 697.9111 | 683.0385 | 680.3228 | 457.2974 | 449.7163 | 699.7706 | 709.4994 | 702.9969 | 713.334 | 713.0066 | 713.8413 | 722.0083 | 714.322 | 712.5069 | 712.1174 | 704.4328 | 704.6797 | 705.091 | 702.6442 | 705.7312 | 705.9742 | 705.3266 | 703.7364 | 713.1473 | 706.2864 | 703.0624 | 707.5907 | 714.3609 | 709.1966 | 710.4224
2025-04-09 21:54 | 9 | 21 | 54 | 6.2817e-272 | 1 | 29.397 | 655.2865 | 0.28355 | 0.0073548 | 142.6681 | 142.6681 | 142.6681 | 142.6681 | 11.1306 | 13.7439 | 618.4854 | 618.4854 | 618.4854 | 618.4854 | 59.9085 | 50.149 | 15.7502 | 67.6282 | 15.6006 | 12.6266 | 45.2735 | 0.021277 | 50.1492 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3546448.2766 | 100.298 | 0.0017834 | 0.053503 | 0.053503 | 0.053503 | 7.9917 | 1047.1117 | 1043.6711 | 1043.6694 | 1043.4196 | 1117.6957 | 1117.6957 | 1117.6957 | 1117.6957 | 698.5376 | 698.5376 | 698.5376 | 4.9599 | 0 | 4.941 | 68.998 | 203.7986 | 203.936 | 216.5885 | 2.0214 | 3.4742 | 0 | 84.7668 | 57.2871 | 59.9085 | 105.0013 | -3.5764 | 67.6282 | -2.194 | 45.3648 | 63.1286 | 48.37 | 0 | 66.8196 | 733.486 | 728.7599 | 696.7161 | 696.8545 | 681.5014 | 678.7117 | 456.0311 | 447.6261 | 697.9074 | 707.2816 | 700.734 | 711.123 | 711.2842 | 711.1997 | 716.9757 | 711.3951 | 709.9574 | 709.7958 | 702.6104 | 702.4596 | 702.7082 | 700.5377 | 703.2957 | 703.4022 | 702.8447 | 701.3222 | 709.3326 | 704.2316 | 702.0738 | 705.9111 | 711.9286 | 707.5046 | 708.4487
2025-04-09 21:55 | 9 | 21 | 55 | 6.2817e-272 | 1 | 29.397 | 650.4967 | 0.28026 | 0.0073345 | 141.9121 | 141.9121 | 141.9121 | 141.9121 | 11.077 | 13.7082 | 615.0724 | 615.0724 | 615.0724 | 615.0724 | 59.6327 | 50.1585 | 15.749 | 67.7065 | 15.6001 | 12.6136 | 45.2093 | 0 | 50.1589 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3546459.5745 | 100.317 | -0.00059083 | -0.017725 | -0.017725 | -0.017725 | 7.9917 | 1052.3711 | 1044.71 | 1044.7089 | 1044.3857 | 1117.5938 | 1117.5938 | 1117.5938 | 1117.5938 | 699.0823 | 699.0823 | 699.0823 | 4.9119 | 0 | 4.9196 | 68.7583 | 202.8596 | 202.9738 | 216.1806 | 1.9995 | 3.4204 | 0 | 83.3369 | 57.2797 | 59.6327 | 104.9936 | -3.874 | 67.7065 | -2.3336 | 45.3181 | 63.1964 | 48.2875 | 0 | 66.8198 | 730.2319 | 725.2644 | 695.5003 | 695.7064 | 679.7547 | 676.9766 | 454.6011 | 445.9867 | 696.0723 | 704.8399 | 701.0722 | 711.7701 | 712.2622 | 711.2352 | 714.9693 | 711.4838 | 710.7371 | 710.6251 | 703.759 | 703.2078 | 703.1724 | 700.967 | 703.6856 | 703.845 | 703.153 | 701.5253 | 708.7764 | 704.938 | 703.5594 | 706.9989 | 712.3836 | 708.3373 | 709.1609
2025-04-09 21:56 | 9 | 21 | 56 | 6.2817e-272 | 1 | 29.3953 | 647.6538 | 0.27819 | 0.0073266 | 141.6232 | 141.6232 | 141.6232 | 141.6232 | 11.0572 | 13.6904 | 612.7804 | 612.7804 | 612.7804 | 612.7804 | 59.2481 | 50.1693 | 15.7486 | 67.9 | 15.5984 | 12.6569 | 45.2612 | 0 | 50.1697 | 14.5217 | 22.1 | 221 | 154840 | 237681 | 3546470.6522 | 100.3387 | 0.00082175 | 0.024653 | 0.024653 | 0.024653 | 7.9917 | 1054.963 | 1045.078 | 1045.0791 | 1044.7437 | 1117.342 | 1117.342 | 1117.342 | 1117.342 | 700.8498 | 700.8498 | 700.8498 | 4.9515 | 0 | 4.9516 | 68.796 | 202.5842 | 202.7182 | 215.6556 | 1.9524 | 3.3996 | 0 | 82.5937 | 56.9533 | 59.2481 | 104.9903 | -4.3006 | 67.9 | -2.0417 | 45.4739 | 63.2223 | 48.2542 | 0 | 66.8192 | 727.3838 | 722.1458 | 694.2364 | 694.395 | 677.9058 | 675.0589 | 453.1454 | 444.7155 | 694.1187 | 702.2976 | 702.4875 | 714.0653 | 713.7434 | 713.0518 | 715.7711 | 713.7676 | 712.9817 | 712.8602 | 706.3793 | 705.4949 | 704.8647 | 702.754 | 705.1654 | 705.1766 | 704.5756 | 702.7475 | 709.8547 | 706.5724 | 705.3248 | 708.6508 | 714.0682 | 710.6321 | 711.3422
2025-04-09 21:57 | 9 | 21 | 57 | 6.2817e-272 | 1 | 29.3949 | 646.3434 | 0.28111 | 0.0073168 | 141.327 | 141.327 | 141.327 | 141.327 | 11.0363 | 13.6882 | 611.4803 | 611.4803 | 611.4803 | 611.4803 | 58.9135 | 50.1849 | 15.7483 | 67.5552 | 15.6012 | 12.6191 | 45.1545 | 0 | 50.1853 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3546481.8085 | 100.3696 | 0.0037985 | 0.11395 | 0.11395 | 0.11395 | 7.9917 | 1056.614 | 1045.4662 | 1045.4662 | 1045.12 | 1117.7906 | 1117.7906 | 1117.7906 | 1117.7906 | 699.3647 | 699.3647 | 699.3647 | 4.8575 | 0 | 4.8798 | 68.6829 | 202.1927 | 202.3175 | 215.2089 | 1.9363 | 3.383 | 0 | 82.1695 | 56.3552 | 58.9135 | 104.9887 | -4.3041 | 67.5552 | -2.0853 | 45.3378 | 63.234 | 48.2148 | 0 | 66.8191 | 725.2485 | 719.8308 | 693.1955 | 693.2308 | 676.202 | 673.1926 | 451.7595 | 443.5919 | 692.1745 | 699.7803 | 700.7824 | 712.6657 | 712.1719 | 711.8538 | 713.9714 | 712.29 | 711.5244 | 711.3603 | 705.05 | 704.1379 | 703.4667 | 700.7994 | 703.413 | 703.3784 | 702.6541 | 700.9094 | 707.8629 | 704.9661 | 704.423 | 707.597 | 712.8645 | 709.3216 | 710.3839
2025-04-09 21:58 | 9 | 21 | 58 | 6.2817e-272 | 1 | 29.3949 | 646.6636 | 0.28114 | 0.0073107 | 141.6565 | 141.6565 | 141.6565 | 141.6565 | 11.0597 | 13.7024 | 611.87 | 611.87 | 611.87 | 611.87 | 58.5154 | 50.1613 | 15.7515 | 67.9093 | 15.5989 | 12.6512 | 45.3151 | 0 | 50.1617 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3546493.1489 | 100.3225 | -0.0015246 | -0.045738 | -0.045738 | -0.045738 | 7.9917 | 1054.9432 | 1045.0319 | 1045.034 | 1044.697 | 1117.3304 | 1117.3304 | 1117.3304 | 1117.3304 | 699.5415 | 699.5415 | 699.5415 | 4.9539 | 0 | 4.9341 | 68.9127 | 202.8144 | 202.9334 | 214.8865 | 1.9458 | 3.4104 | 0 | 82.5838 | 56.061 | 58.5154 | 105.0101 | -4.2881 | 67.9093 | -2.0934 | 45.4533 | 63.2664 | 48.1906 | 0 | 66.8192 | 723.4647 | 717.9545 | 692.1651 | 692.0634 | 674.6803 | 671.4003 | 450.419 | 442.2587 | 690.2456 | 697.531 | 701.1974 | 712.8268 | 712.7513 | 711.7701 | 714.0308 | 711.8192 | 711.4734 | 711.4295 | 704.9447 | 704.3021 | 703.8975 | 700.9726 | 703.8043 | 704.0852 | 702.9266 | 701.2119 | 707.8686 | 705.2046 | 704.0781 | 707.7774 | 713.2292 | 709.3485 | 710.3889
2025-04-09 21:59 | 9 | 21 | 59 | 6.2817e-272 | 1 | 29.3926 | 646.3407 | 0.28179 | 0.0073124 | 141.6731 | 141.6731 | 141.6731 | 141.6731 | 11.0617 | 13.7045 | 610.9467 | 610.9467 | 610.9467 | 610.9467 | 58.2281 | 50.1737 | 15.7472 | 68.2425 | 15.6006 | 12.7242 | 45.5315 | 0 | 50.1739 | 13.7447 | 22.1 | 221 | 154840 | 237681 | 3546504.4468 | 100.3473 | 0.0037917 | 0.11375 | 0.11375 | 0.11375 | 7.9917 | 1055.6998 | 1044.9964 | 1045.0002 | 1044.6634 | 1116.8949 | 1116.8949 | 1116.8949 | 1116.8949 | 700.792 | 700.792 | 700.792 | 4.9663 | 0 | 4.9832 | 69.1228 | 202.9801 | 203.1141 | 214.5768 | 1.8942 | 3.3881 | 0 | 82.3221 | 55.8116 | 58.2281 | 104.9813 | -4.4271 | 68.2425 | -2.0223 | 45.7156 | 63.2484 | 48.1941 | 0 | 66.8189 | 721.9193 | 716.299 | 691.2152 | 690.9067 | 673.1972 | 669.7517 | 449.0048 | 441.2251 | 688.5075 | 695.5068 | 702.124 | 714.6223 | 713.7889 | 713.1204 | 714.7344 | 713.0485 | 712.7746 | 712.8279 | 706.7683 | 705.9615 | 705.0928 | 701.8453 | 704.559 | 705.0554 | 703.999 | 702.1683 | 708.7655 | 706.5581 | 705.5209 | 709.2515 | 714.5827 | 710.6756 | 712.0798
2025-04-09 22:00 | 9 | 22 | 0 | 6.2817e-272 | 1 | 29.3927 | 648.8297 | 0.27954 | 0.0073176 | 142.4404 | 142.4404 | 142.4404 | 142.4404 | 11.116 | 13.7365 | 612.7048 | 612.7048 | 612.7048 | 612.7048 | 57.9426 | 50.1392 | 15.7513 | 68.6956 | 15.6006 | 12.7663 | 45.7088 | 0 | 50.1397 | 15.5319 | 22.1 | 221 | 154840 | 237681 | 3546515.8723 | 100.2785 | -0.0020795 | -0.062385 | -0.062385 | -0.062385 | 7.9917 | 1051.643 | 1043.9847 | 1043.9823 | 1043.6823 | 1116.306 | 1116.306 | 1116.306 | 1116.306 | 699.7821 | 699.7821 | 699.7821 | 5.0778 | 0 | 5.0521 | 69.4177 | 204.0657 | 204.2169 | 214.3721 | 1.9215 | 3.4159 | 0 | 83.3452 | 55.664 | 57.9426 | 105.0088 | -4.6446 | 68.6956 | -2.0466 | 45.867 | 63.2725 | 48.216 | 0 | 66.8203 | 721.0163 | 715.4584 | 690.5584 | 690.0236 | 671.9952 | 668.3019 | 447.7524 | 439.6855 | 686.7624 | 693.7236 | 701.4101 | 713.5009 | 713.5047 | 711.7913 | 713.8434 | 711.4587 | 711.7549 | 712.0244 | 705.2239 | 704.7593 | 704.4123 | 700.6736 | 704.1235 | 704.958 | 703.1658 | 701.4729 | 707.7923 | 705.1065 | 702.963 | 707.6612 | 714.2015 | 709.4077 | 710.7479
2025-04-09 22:01 | 9 | 22 | 1 | 6.2817e-272 | 1 | 29.3935 | 643.0749 | 0.27872 | 0.007318 | 140.7303 | 140.7303 | 140.7303 | 140.7303 | 10.9945 | 13.6699 | 608.8145 | 608.8145 | 608.8145 | 608.8145 | 57.897 | 50.1543 | 15.7497 | 67.327 | 15.6011 | 12.5903 | 45.0336 | 0 | 50.1551 | 13.5745 | 22.1 | 221 | 154840 | 237681 | 3546527.1702 | 100.3087 | -0.001861 | -0.055829 | -0.055829 | -0.055829 | 7.9917 | 1059.317 | 1046.243 | 1046.2428 | 1045.874 | 1118.0885 | 1118.0885 | 1118.0885 | 1118.0885 | 699.1644 | 699.1644 | 699.1644 | 4.786 | 0 | 4.8044 | 68.4636 | 201.4074 | 201.5572 | 214.2043 | 1.8899 | 3.3675 | 0 | 81.5182 | 55.5565 | 57.897 | 104.9979 | -5.1108 | 67.327 | -1.8804 | 45.2345 | 63.2688 | 48.2181 | 0 | 66.8183 | 719.6254 | 714.1534 | 689.6667 | 688.987 | 670.8598 | 667.0838 | 446.4872 | 438.9092 | 685.2962 | 692.2033 | 700.579 | 712.882 | 711.6348 | 711.3931 | 713.2408 | 711.2891 | 711.1526 | 711.2304 | 705.2255 | 704.4507 | 703.895 | 700.0867 | 702.7681 | 703.0484 | 701.9403 | 700.2545 | 707.0749 | 705.2812 | 704.6187 | 707.6998 | 713.177 | 709.0015 | 710.5199
2025-04-09 22:02 | 9 | 22 | 2 | 6.2817e-272 | 1 | 29.3948 | 642.7684 | 0.27825 | 0.0073195 | 141.3755 | 141.3755 | 141.3755 | 141.3755 | 11.0398 | 13.6917 | 609.8033 | 609.8033 | 609.8033 | 609.8033 | 57.6956 | 50.1438 | 15.7518 | 68.1501 | 15.5974 | 12.688 | 45.4381 | 0 | 50.144 | 14.5957 | 22.1 | 221 | 154840 | 237681 | 3546538.4468 | 100.2877 | -0.00093305 | -0.027992 | -0.027992 | -0.027992 | 7.9917 | 1056.8606 | 1045.4015 | 1045.4032 | 1045.0562 | 1117.0157 | 1117.0157 | 1117.0157 | 1117.0157 | 700.2945 | 700.2945 | 700.2945 | 4.9476 | 0 | 4.9348 | 68.9291 | 202.5355 | 202.6771 | 213.7494 | 1.9135 | 3.3966 | 0 | 82.0659 | 55.6819 | 57.6956 | 105.0117 | -5.302 | 68.1501 | -1.809 | 45.5856 | 63.2547 | 48.2256 | 0 | 66.8171 | 718.3161 | 713.0514 | 688.8134 | 688.0568 | 669.7734 | 665.8718 | 445.4193 | 437.5257 | 683.7788 | 690.7583 | 702.1973 | 713.8906 | 713.5761 | 712.2391 | 714.3204 | 712.1763 | 712.0858 | 712.5753 | 706.0221 | 705.2273 | 705.1132 | 701.365 | 704.3112 | 704.9115 | 703.6784 | 701.8331 | 707.8574 | 706.1393 | 705.0295 | 708.3445 | 714.2886 | 709.7137 | 711.0511
2025-04-09 22:03 | 9 | 22 | 3 | 6.2817e-272 | 1 | 29.3932 | 642.3017 | 0.27145 | 0.0073297 | 141.5867 | 141.5867 | 141.5867 | 141.5867 | 11.0553 | 13.6951 | 610.4387 | 610.4387 | 610.4387 | 610.4387 | 57.8205 | 50.1233 | 15.7512 | 68.3934 | 15.5989 | 12.7181 | 45.5971 | 0 | 50.1237 | 14.3404 | 22.1 | 221 | 154840 | 237681 | 3546549.8085 | 100.2468 | -0.001337 | -0.040109 | -0.040109 | -0.040109 | 7.9917 | 1055.443 | 1045.1119 | 1045.1126 | 1044.7762 | 1116.6989 | 1116.6989 | 1116.6989 | 1116.6989 | 700.4614 | 700.4614 | 700.4614 | 4.9742 | 0 | 4.9761 | 69.0286 | 202.8405 | 203.0057 | 213.5573 | 1.8935 | 3.4124 | 0 | 82.4447 | 55.6836 | 57.8205 | 105.008 | -5.3489 | 68.3934 | -1.8986 | 45.6938 | 63.2623 | 48.2662 | 0 | 66.8156 | 717.6002 | 712.445 | 688.107 | 687.3141 | 668.8071 | 664.8989 | 444.3827 | 436.4548 | 682.4595 | 689.4348 | 702.2731 | 714.3132 | 713.8897 | 712.3338 | 714.4047 | 712.2962 | 712.3944 | 712.9502 | 706.371 | 705.4031 | 705.3904 | 701.3521 | 704.3922 | 704.9341 | 703.6167 | 701.6649 | 707.9904 | 706.3378 | 705.102 | 708.6721 | 714.5989 | 709.9034 | 711.1447
2025-04-09 22:04 | 9 | 22 | 4 | 6.2817e-272 | 1 | 29.3922 | 640.6115 | 0.28059 | 0.0073398 | 140.8785 | 140.8785 | 140.8785 | 140.8785 | 11.0055 | 13.6746 | 609.1209 | 609.1209 | 609.1209 | 609.1209 | 57.8498 | 50.1534 | 15.7519 | 67.5145 | 15.6007 | 12.6101 | 45.2553 | 0 | 50.1535 | 13.4348 | 22.1 | 221 | 154840 | 237681 | 3546561.0217 | 100.3068 | 0.0037893 | 0.11368 | 0.11368 | 0.11368 | 7.9917 | 1058.7796 | 1046.0396 | 1046.0391 | 1045.6765 | 1117.8446 | 1117.8446 | 1117.8446 | 1117.8446 | 699.5123 | 699.5123 | 699.5123 | 4.8266 | 0 | 4.8435 | 68.6766 | 201.7291 | 201.8847 | 213.4296 | 1.8663 | 3.3798 | 0 | 81.6326 | 55.5389 | 57.8498 | 105.0123 | -5.6397 | 67.5145 | -2.0301 | 45.3055 | 63.2575 | 48.3041 | 0 | 66.8179 | 716.9046 | 711.8542 | 687.3783 | 686.6165 | 667.9245 | 664.0928 | 443.3496 | 435.7159 | 681.4304 | 688.2892 | 701.2798 | 713.0887 | 712.2177 | 711.3399 | 713.4408 | 711.4805 | 711.3921 | 711.999 | 705.6933 | 704.6337 | 704.4807 | 700.5662 | 703.261 | 703.5861 | 702.5598 | 700.6487 | 707.1844 | 705.6395 | 704.6766 | 707.8809 | 713.7579 | 709.2041 | 710.4474
2025-04-09 22:05 | 9 | 22 | 5 | 6.2817e-272 | 1 | 29.392 | 642.3413 | 0.2785 | 0.0073533 | 141.2922 | 141.2922 | 141.2922 | 141.2922 | 11.0349 | 13.696 | 609.9546 | 609.9546 | 609.9546 | 609.9546 | 57.8237 | 50.1673 | 15.7528 | 67.7535 | 15.6025 | 12.6458 | 45.2974 | 0 | 50.1674 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3546572.234 | 100.3345 | 0.0058805 | 0.17642 | 0.17642 | 0.17642 | 7.9917 | 1057.2268 | 1045.4911 | 1045.4894 | 1045.1432 | 1117.533 | 1117.533 | 1117.533 | 1117.533 | 699.5317 | 699.5317 | 699.5317 | 4.9067 | 0 | 4.8866 | 68.936 | 202.3836 | 202.5512 | 213.3773 | 1.8818 | 3.3883 | 0 | 81.9711 | 55.586 | 57.8237 | 105.0183 | -5.6753 | 67.7535 | -2.132 | 45.434 | 63.2635 | 48.3584 | 0 | 66.8174 | 716.374 | 711.2638 | 686.731 | 686.0314 | 667.1424 | 663.3844 | 442.3705 | 434.8049 | 680.5541 | 687.2784 | 701.2307 | 713.2591 | 712.6851 | 711.2254 | 713.2619 | 711.3737 | 711.2684 | 711.8889 | 705.4345 | 704.434 | 704.4815 | 700.6252 | 703.3687 | 703.8118 | 702.5966 | 700.6879 | 707.2611 | 705.7253 | 704.6397 | 707.9247 | 713.786 | 709.1887 | 710.4897
2025-04-09 22:06 | 9 | 22 | 6 | 6.2817e-272 | 1 | 29.3925 | 640.9221 | 0.27753 | 0.0073662 | 141.5213 | 141.5213 | 141.5213 | 141.5213 | 11.0509 | 13.7011 | 610.3347 | 610.3347 | 610.3347 | 610.3347 | 57.7507 | 50.1649 | 15.7503 | 68.5637 | 15.5983 | 12.7479 | 45.6282 | 0 | 50.1653 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3546583.5319 | 100.3299 | -0.0035269 | -0.10581 | -0.10581 | -0.10581 | 7.9917 | 1056.6496 | 1045.1968 | 1045.1989 | 1044.8591 | 1116.477 | 1116.477 | 1116.477 | 1116.477 | 701.026 | 701.026 | 701.026 | 4.9687 | 0 | 4.9866 | 69.1707 | 202.8565 | 202.9933 | 213.2275 | 1.8964 | 3.3919 | 0 | 82.0701 | 55.7774 | 57.7507 | 105.0016 | -5.9123 | 68.5637 | -2.1138 | 45.8007 | 63.2671 | 48.4106 | 0 | 66.8172 | 715.9761 | 710.7909 | 686.1437 | 685.5383 | 666.4604 | 662.7899 | 441.4413 | 434.3041 | 679.8345 | 686.3919 | 702.3655 | 714.7683 | 714.6145 | 712.678 | 714.2957 | 712.7328 | 713.0679 | 713.7802 | 707.1448 | 706.2869 | 705.9851 | 701.7634 | 705.1214 | 705.7729 | 703.9475 | 702.1091 | 708.4588 | 706.9796 | 705.7142 | 709.4173 | 715.0871 | 710.7024 | 711.8501
2025-04-09 22:07 | 9 | 22 | 7 | 6.2817e-272 | 1 | 29.3925 | 643.0711 | 0.27026 | 0.0073626 | 142.0819 | 142.0819 | 142.0819 | 142.0819 | 11.0906 | 13.7251 | 612.1122 | 612.1122 | 612.1122 | 612.1122 | 57.6244 | 50.1334 | 15.7527 | 68.7356 | 15.5977 | 12.7703 | 45.7505 | 0 | 50.1337 | 15.0213 | 22.1 | 221 | 154840 | 237681 | 3546595 | 100.2669 | 0.0028949 | 0.086845 | 0.086845 | 0.086845 | 7.9917 | 1053.3336 | 1044.4572 | 1044.457 | 1044.1391 | 1116.2536 | 1116.2536 | 1116.2536 | 1116.2536 | 700.284 | 700.284 | 700.284 | 5.0232 | 0 | 5.029 | 69.2889 | 203.5855 | 203.7192 | 213.2401 | 1.9152 | 3.4308 | 0 | 82.9367 | 55.9929 | 57.6244 | 105.0178 | -5.8912 | 68.7356 | -2.1051 | 45.8813 | 63.2594 | 48.3974 | 0 | 66.8174 | 716.0711 | 710.808 | 685.7505 | 685.2359 | 665.8787 | 662.3551 | 440.665 | 433.3198 | 679.2516 | 685.5996 | 701.7942 | 713.8742 | 713.9843 | 711.8781 | 713.4663 | 711.7913 | 712.2644 | 712.8582 | 706.0425 | 705.3067 | 704.992 | 701.137 | 704.5916 | 705.3894 | 703.5474 | 701.7333 | 708.1021 | 706.1613 | 704.2185 | 708.8749 | 714.2686 | 709.7578 | 710.977
2025-04-09 22:08 | 9 | 22 | 8 | 6.2817e-272 | 1 | 29.3936 | 641.5972 | 0.27211 | 0.0073531 | 141.728 | 141.728 | 141.728 | 141.728 | 11.0652 | 13.6985 | 611.1465 | 611.1465 | 611.1465 | 611.1465 | 57.8715 | 50.1082 | 15.751 | 68.4967 | 15.6009 | 12.7235 | 45.6259 | 0 | 50.1086 | 14.5957 | 22.1 | 221 | 154840 | 237681 | 3546606.4255 | 100.2164 | -0.0050421 | -0.15126 | -0.15126 | -0.15126 | 7.9917 | 1054.4638 | 1044.9268 | 1044.9274 | 1044.5955 | 1116.5649 | 1116.5649 | 1116.5649 | 1116.5649 | 700.0476 | 700.0476 | 700.0476 | 4.9892 | 0 | 4.9875 | 69.0755 | 203.0593 | 203.2104 | 213.3055 | 1.9568 | 3.3947 | 0 | 82.7114 | 55.9655 | 57.8715 | 105.0068 | -5.7808 | 68.4967 | -2.1609 | 45.7131 | 63.2669 | 48.3592 | 0 | 66.8206 | 716.0162 | 710.6104 | 685.1858 | 684.8177 | 665.3639 | 661.9241 | 439.7568 | 432.6614 | 678.762 | 684.934 | 701.2414 | 713.6573 | 713.4139 | 711.691 | 713.2111 | 711.7196 | 712.1162 | 712.5355 | 705.7911 | 705.1241 | 704.6971 | 700.8203 | 704.2526 | 705.0961 | 703.137 | 701.3809 | 707.8434 | 705.9982 | 704.4524 | 708.9008 | 714.1009 | 709.5921 | 710.9738
2025-04-09 22:09 | 9 | 22 | 9 | 6.2817e-272 | 1 | 29.3929 | 642.9706 | 0.26835 | 0.007346 | 141.8347 | 141.8347 | 141.8347 | 141.8347 | 11.073 | 13.7029 | 611.9759 | 611.9759 | 611.9759 | 611.9759 | 57.9561 | 50.0893 | 15.7515 | 68.2689 | 15.5991 | 12.6925 | 45.5459 | 0 | 50.0895 | 14.4255 | 22.1 | 221 | 154840 | 237681 | 3546617.8085 | 100.1782 | 0.0079252 | 0.23776 | 0.23776 | 0.23776 | 7.9917 | 1053.2498 | 1044.784 | 1044.7845 | 1044.4581 | 1116.8613 | 1116.8613 | 1116.8613 | 1116.8613 | 699.0044 | 699.0044 | 699.0044 | 4.9852 | 0 | 4.9609 | 69.043 | 203.121 | 203.2599 | 213.3111 | 1.9373 | 3.4007 | 0 | 83.0683 | 56.0257 | 57.9561 | 105.0098 | -5.8445 | 68.2689 | -2.1385 | 45.6016 | 63.2484 | 48.3297 | 0 | 66.821 | 716.0757 | 710.5938 | 684.7824 | 684.4826 | 664.8904 | 661.5889 | 438.9231 | 432.1032 | 678.3443 | 684.3376 | 700.2132 | 712.597 | 712.4764 | 710.7517 | 712.2326 | 710.4753 | 711.0104 | 711.3448 | 704.4277 | 704.1668 | 703.572 | 699.8246 | 703.2552 | 704.2893 | 702.1501 | 700.541 | 707.0805 | 704.811 | 703.0441 | 707.6134 | 712.7717 | 708.398 | 709.9697
2025-04-09 22:10 | 9 | 22 | 10 | 6.2817e-272 | 1 | 29.3946 | 641.5115 | 0.26245 | 0.0073385 | 141.6175 | 141.6175 | 141.6175 | 141.6175 | 11.057 | 13.6836 | 611.8164 | 611.8164 | 611.8164 | 611.8164 | 57.9554 | 50.053 | 15.7506 | 68.6085 | 15.5979 | 12.7527 | 45.7564 | 0 | 50.053 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3546629.1915 | 100.1059 | 0.0071629 | 0.21489 | 0.21489 | 0.21489 | 7.9917 | 1053.7206 | 1045.0804 | 1045.0834 | 1044.7451 | 1116.4196 | 1116.4196 | 1116.4196 | 1116.4196 | 701.1521 | 701.1521 | 701.1521 | 4.9987 | 0 | 5.0146 | 68.928 | 202.8278 | 202.9635 | 213.2228 | 1.9488 | 3.3839 | 0 | 83.0094 | 56.1073 | 57.9554 | 105.0038 | -6.1309 | 68.6085 | -2.1281 | 45.8179 | 63.2698 | 48.301 | 0 | 66.8203 | 715.8054 | 710.3444 | 684.2134 | 684.0672 | 664.4488 | 661.2811 | 438.1212 | 431.616 | 677.9502 | 683.8573 | 702.3566 | 714.9212 | 714.6763 | 712.7761 | 713.8641 | 712.6711 | 713.1754 | 713.553 | 706.9282 | 706.5745 | 705.8098 | 702.1714 | 705.6407 | 706.4951 | 704.183 | 702.6364 | 708.996 | 706.8836 | 705.1231 | 709.8336 | 714.859 | 710.6461 | 712.3102
2025-04-09 22:11 | 9 | 22 | 11 | 6.2817e-272 | 1 | 29.397 | 645.2722 | 0.26399 | 0.0073469 | 142.664 | 142.664 | 142.664 | 142.664 | 11.1303 | 13.7091 | 615.1008 | 615.1008 | 615.1008 | 615.1008 | 57.8351 | 49.9717 | 15.7504 | 69.2462 | 15.6021 | 12.8478 | 46.1404 | 0.17021 | 49.9723 | 15.8723 | 22.1 | 221 | 154840 | 237681 | 3546640.7234 | 99.9434 | -0.0072094 | -0.21628 | -0.21628 | -0.21628 | 7.9917 | 1047.0634 | 1043.3821 | 1043.3821 | 1043.4283 | 1115.5885 | 1115.5885 | 1115.5885 | 1115.5885 | 700.8458 | 700.8458 | 700.8458 | 5.1291 | 0 | 5.131 | 69.3846 | 204.2694 | 204.4021 | 213.3046 | 2.0156 | 3.4243 | 0 | 84.7881 | 56.0141 | 57.8351 | 105.0024 | -5.6967 | 69.2462 | -2.0362 | 46.1597 | 63.245 | 48.3381 | 0 | 66.8176 | 716.0502 | 710.744 | 683.9773 | 684.002 | 664.078 | 661.0861 | 437.4695 | 430.7492 | 677.3929 | 683.4535 | 702.0968 | 714.9865 | 714.4234 | 712.3557 | 713.8589 | 712.369 | 712.6155 | 713.2945 | 706.5308 | 706.5147 | 705.7873 | 701.4968 | 706.0467 | 706.8321 | 704.6477 | 702.7113 | 708.7254 | 705.6321 | 702.9038 | 708.1304 | 714.8966 | 710.37 | 711.7777
2025-04-09 22:12 | 9 | 22 | 12 | 6.2817e-272 | 1 | 29.3957 | 640.8019 | 0.26179 | 0.007361 | 141.4048 | 141.4048 | 141.4048 | 141.4048 | 11.0416 | 13.6607 | 611.7939 | 611.7939 | 611.7939 | 611.7939 | 57.8223 | 49.9712 | 15.7496 | 68.1806 | 15.5968 | 12.6462 | 45.5788 | 0 | 49.9706 | 14.087 | 22.1 | 221 | 154840 | 237681 | 3546651.9783 | 99.9425 | 0.011331 | 0.33994 | 0.33994 | 0.33994 | 7.9917 | 1052.9515 | 1045.3665 | 1045.3689 | 1045.0239 | 1116.9761 | 1116.9761 | 1116.9761 | 1116.9761 | 698.9839 | 698.9839 | 698.9839 | 4.8954 | 0 | 4.91 | 68.4926 | 202.2067 | 202.3317 | 213.4027 | 1.9687 | 3.3645 | 0 | 83.3571 | 55.85 | 57.8223 | 104.9969 | -5.4831 | 68.1806 | -2.0613 | 45.4355 | 63.2599 | 48.3937 | 0 | 66.8163 | 715.6425 | 710.568 | 683.4678 | 683.6275 | 663.7301 | 660.8827 | 436.615 | 429.9977 | 676.902 | 683.0962 | 699.9772 | 712.8861 | 712.4695 | 710.6622 | 712.1547 | 710.6849 | 710.849 | 711.4813 | 704.8267 | 704.3295 | 703.6049 | 699.7615 | 703.5553 | 704.1833 | 702.3348 | 700.3597 | 706.538 | 704.6063 | 702.836 | 707.3444 | 712.6123 | 708.6717 | 709.8123
2025-04-09 22:13 | 9 | 22 | 13 | 6.2817e-272 | 1 | 29.3947 | 640.2436 | 0.26119 | 0.0073729 | 141.6178 | 141.6178 | 141.6178 | 141.6178 | 11.057 | 13.6601 | 611.9209 | 611.9209 | 611.9209 | 611.9209 | 57.8498 | 49.9566 | 15.752 | 68.5552 | 15.5997 | 12.7223 | 45.7521 | 0 | 49.9575 | 14.5106 | 22.1 | 221 | 154840 | 237681 | 3546663.2553 | 99.9133 | -0.011382 | -0.34147 | -0.34147 | -0.34147 | 7.9917 | 1052.2796 | 1045.0809 | 1045.08 | 1044.746 | 1116.4883 | 1116.4883 | 1116.4883 | 1116.4883 | 700.3479 | 700.3479 | 700.3479 | 4.9967 | 0 | 4.977 | 68.7732 | 202.6539 | 202.7757 | 213.1364 | 1.9731 | 3.3722 | 0 | 83.4884 | 55.7821 | 57.8498 | 105.0133 | -5.3482 | 68.5552 | -2.1164 | 45.7087 | 63.2519 | 48.44 | 0 | 66.8162 | 715.1126 | 710.1996 | 682.9385 | 683.2035 | 663.2943 | 660.5463 | 435.8601 | 429.282 | 676.4174 | 682.7429 | 701.4796 | 714.3292 | 714.3074 | 712.1183 | 713.5293 | 712.1369 | 711.9289 | 712.6292 | 706.1512 | 705.4479 | 704.9155 | 701.3696 | 705.2558 | 705.8576 | 703.8707 | 701.756 | 707.7437 | 705.9836 | 704.1572 | 708.2515 | 713.8056 | 709.972 | 711.0642
2025-04-09 22:14 | 9 | 22 | 14 | 6.2817e-272 | 1 | 29.3941 | 639.9463 | 0.25876 | 0.007395 | 141.418 | 141.418 | 141.418 | 141.418 | 11.043 | 13.6494 | 611.7155 | 611.7155 | 611.7155 | 611.7155 | 57.846 | 49.9347 | 15.7516 | 68.1449 | 15.6024 | 12.7049 | 45.5797 | 0 | 49.9352 | 14.4255 | 22.1 | 221 | 154840 | 237681 | 3546674.6809 | 99.8694 | -0.0079615 | -0.23885 | -0.23885 | -0.23885 | 7.9917 | 1052.3794 | 1045.3445 | 1045.3389 | 1045.0009 | 1117.0232 | 1117.0232 | 1117.0232 | 1117.0232 | 699.1434 | 699.1434 | 699.1434 | 4.9206 | 0 | 4.9168 | 68.5006 | 202.1773 | 202.3081 | 212.9633 | 1.9678 | 3.3777 | 0 | 83.5387 | 55.659 | 57.846 | 105.0104 | -5.3055 | 68.1449 | -2.0632 | 45.6462 | 63.2484 | 48.5284 | 0 | 66.8162 | 714.7997 | 710.0229 | 682.5019 | 682.8833 | 662.8584 | 660.2294 | 435.1003 | 428.7001 | 675.8998 | 682.2541 | 700.4414 | 713.1806 | 713.2119 | 710.8953 | 712.3607 | 711.2088 | 710.8726 | 711.6859 | 704.8112 | 704.0163 | 703.4903 | 700.3261 | 703.962 | 704.3134 | 702.6977 | 700.566 | 706.6618 | 704.7031 | 702.8568 | 706.7571 | 712.7258 | 708.9342 | 709.8171
2025-04-09 22:15 | 9 | 22 | 15 | 6.2817e-272 | 1 | 29.3925 | 638.2524 | 0.25904 | 0.0074138 | 140.999 | 140.999 | 140.999 | 140.999 | 11.0139 | 13.6279 | 610.5055 | 610.5055 | 610.5055 | 610.5055 | 57.9099 | 49.9332 | 15.751 | 68.1425 | 15.5963 | 12.6368 | 45.5619 | 0 | 49.9335 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3546686.0213 | 99.8665 | 0.0015971 | 0.047913 | 0.047913 | 0.047913 | 7.9917 | 1054.4891 | 1045.8821 | 1045.8813 | 1045.5228 | 1117.0264 | 1117.0264 | 1117.0264 | 1117.0264 | 700.247 | 700.247 | 700.247 | 4.8819 | 0 | 4.8865 | 68.351 | 201.6355 | 201.7725 | 212.7804 | 1.9358 | 3.3608 | 0 | 83.0119 | 55.6378 | 57.9099 | 105.0065 | -5.3443 | 68.1425 | -2.0986 | 45.4015 | 63.2484 | 48.6034 | 0 | 66.8156 | 714.2401 | 709.5561 | 681.9836 | 682.4327 | 662.4314 | 659.9033 | 434.3527 | 428.0479 | 675.3767 | 681.8829 | 701.2311 | 714.2964 | 714.1524 | 711.8383 | 713.0551 | 712.2926 | 711.7366 | 712.8404 | 705.9949 | 704.9324 | 704.5504 | 701.4804 | 705.1034 | 705.1477 | 703.5068 | 701.2442 | 707.6085 | 706.3249 | 705.022 | 708.6652 | 713.9454 | 710.1656 | 711.1071
2025-04-09 22:16 | 9 | 22 | 16 | 6.2817e-272 | 1 | 29.3913 | 639.5399 | 0.25536 | 0.0074211 | 141.3986 | 141.3986 | 141.3986 | 141.3986 | 11.0427 | 13.6377 | 611.602 | 611.602 | 611.602 | 611.602 | 58.049 | 49.9123 | 15.749 | 68.4527 | 15.6003 | 12.6868 | 45.7943 | 0 | 49.9127 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3546697.383 | 99.8247 | 0.00059008 | 0.017703 | 0.017703 | 0.017703 | 7.9917 | 1052.2806 | 1045.3464 | 1045.3504 | 1045.0032 | 1116.6221 | 1116.6221 | 1116.6221 | 1116.6221 | 700.9459 | 700.9459 | 700.9459 | 4.9792 | 0 | 4.9669 | 68.6026 | 202.2586 | 202.4069 | 212.5736 | 1.9267 | 3.3893 | 0 | 83.5746 | 55.7759 | 58.049 | 104.9933 | -5.1444 | 68.4527 | -2.1226 | 45.5813 | 63.2445 | 48.6297 | 0 | 66.8154 | 713.888 | 709.361 | 681.5937 | 682.1197 | 662.0659 | 659.595 | 433.6682 | 427.0259 | 674.8343 | 681.4548 | 702.0254 | 715.1628 | 715.026 | 712.2541 | 713.8692 | 712.9527 | 712.415 | 713.7484 | 706.9492 | 705.6457 | 705.449 | 702.1352 | 706.0982 | 705.9827 | 704.4994 | 701.9951 | 708.0514 | 706.8625 | 705.2194 | 708.9576 | 714.708 | 710.8356 | 711.3709
2025-04-09 22:17 | 9 | 22 | 17 | 6.2817e-272 | 1 | 29.3926 | 637.9631 | 0.25465 | 0.007419 | 140.7079 | 140.7079 | 140.7079 | 140.7079 | 10.9933 | 13.605 | 610.1486 | 610.1486 | 610.1486 | 610.1486 | 58.0922 | 49.9065 | 15.7499 | 67.9809 | 15.5996 | 12.6535 | 45.4873 | 0 | 49.9067 | 14 | 22.1 | 221 | 154840 | 237681 | 3546708.7021 | 99.813 | 0.0042942 | 0.12883 | 0.12883 | 0.12883 | 7.9917 | 1055.34 | 1046.2653 | 1046.2651 | 1045.8947 | 1117.2368 | 1117.2368 | 1117.2368 | 1117.2368 | 700.0229 | 700.0229 | 700.0229 | 4.8382 | 0 | 4.8569 | 68.1564 | 201.1943 | 201.3444 | 212.5058 | 1.9149 | 3.3526 | 0 | 82.8521 | 55.9762 | 58.0922 | 104.9992 | -4.9283 | 67.9809 | -2.1372 | 45.4614 | 63.2171 | 48.6233 | 0 | 66.8151 | 713.4723 | 709.1544 | 681.2041 | 681.8327 | 661.7699 | 659.3544 | 432.9001 | 426.3084 | 674.3529 | 681.1084 | 701.0976 | 714.2904 | 714.0683 | 711.0618 | 712.5665 | 711.9422 | 711.3104 | 712.6846 | 705.9531 | 704.4891 | 704.4212 | 701.4212 | 704.8913 | 704.6854 | 703.4684 | 700.8219 | 707.2561 | 706.3986 | 705.193 | 708.2299 | 713.7187 | 710.1362 | 710.832
2025-04-09 22:18 | 9 | 22 | 18 | 6.2817e-272 | 1 | 29.3911 | 642.651 | 0.26058 | 0.0074232 | 142.1044 | 142.1044 | 142.1044 | 142.1044 | 11.0927 | 13.6555 | 614.2018 | 614.2018 | 614.2018 | 614.2018 | 58.252 | 49.8706 | 15.7501 | 68.8286 | 15.602 | 12.7798 | 46.0845 | 0 | 49.8705 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3546720.1277 | 99.7411 | 0.0024537 | 0.073611 | 0.073611 | 0.073611 | 7.9917 | 1047.6853 | 1044.4189 | 1044.4181 | 1044.103 | 1116.1321 | 1116.1321 | 1116.1321 | 1116.1321 | 700.8091 | 700.8091 | 700.8091 | 5.074 | 0 | 5.0574 | 68.8678 | 203.264 | 203.4138 | 212.4166 | 1.9109 | 3.4211 | 0 | 84.8065 | 55.9809 | 58.252 | 105.0007 | -4.6614 | 68.8286 | -2.1869 | 45.9153 | 63.2487 | 48.6389 | 0 | 66.8152 | 713.6363 | 709.3005 | 681.0693 | 681.7417 | 661.5293 | 659.1794 | 432.3157 | 425.6142 | 673.9965 | 680.6604 | 701.8463 | 715.3432 | 714.9688 | 712.0166 | 714.0277 | 712.7778 | 711.9142 | 713.5135 | 706.838 | 705.4971 | 705.4886 | 702.0427 | 706.3608 | 705.9723 | 704.7526 | 701.8117 | 708.0774 | 706.4735 | 703.689 | 708.1936 | 714.9419 | 710.9024 | 711.153
2025-04-09 22:19 | 9 | 22 | 19 | 6.2817e-272 | 1 | 29.3877 | 640.6279 | 0.26095 | 0.0074296 | 141.3342 | 141.3342 | 141.3342 | 141.3342 | 11.0393 | 13.6237 | 612.2881 | 612.2881 | 612.2881 | 612.2881 | 58.343 | 49.875 | 15.7504 | 68.3187 | 15.6014 | 12.699 | 45.7726 | 0 | 49.8752 | 14.5532 | 22.1 | 221 | 154840 | 237681 | 3546731.4681 | 99.7499 | -0.00056738 | -0.017021 | -0.017021 | -0.017021 | 7.9917 | 1051.4721 | 1045.4089 | 1045.4083 | 1045.0634 | 1116.7964 | 1116.7964 | 1116.7964 | 1116.7964 | 699.9883 | 699.9883 | 699.9883 | 4.9209 | 0 | 4.9474 | 68.4137 | 202.0796 | 202.2241 | 212.5339 | 1.8848 | 3.3977 | 0 | 83.8644 | 55.997 | 58.343 | 105.0027 | -4.8074 | 68.3187 | -2.2336 | 45.625 | 63.2241 | 48.6611 | 0 | 66.8142 | 713.6583 | 709.2057 | 680.913 | 681.5057 | 661.3896 | 659.0023 | 431.5834 | 424.9356 | 673.7595 | 680.3163 | 700.9571 | 714.081 | 714.0462 | 711.1818 | 713.0458 | 712.0529 | 711.1511 | 712.4117 | 705.8829 | 704.5147 | 704.537 | 701.0648 | 705.1372 | 704.9133 | 703.774 | 700.7869 | 707.1116 | 705.9941 | 704.5614 | 708.1565 | 713.8456 | 709.9535 | 710.597
2025-04-09 22:20 | 9 | 22 | 20 | 6.2817e-272 | 1 | 29.3887 | 640.8553 | 0.26335 | 0.0074281 | 141.013 | 141.013 | 141.013 | 141.013 | 11.0162 | 13.6087 | 611.8259 | 611.8259 | 611.8259 | 611.8259 | 58.4164 | 49.8718 | 15.7507 | 67.7131 | 15.5997 | 12.6229 | 45.3569 | 0 | 49.8716 | 13.8696 | 22.1 | 221 | 154840 | 237681 | 3546742.7391 | 99.7437 | 0.0091772 | 0.27532 | 0.27532 | 0.27532 | 7.9917 | 1052.5859 | 1045.835 | 1045.8326 | 1045.4776 | 1117.5854 | 1117.5854 | 1117.5854 | 1117.5854 | 698.8518 | 698.8518 | 698.8518 | 4.8704 | 0 | 4.8554 | 68.1478 | 201.496 | 201.6353 | 212.4699 | 1.8859 | 3.3867 | 0 | 83.6278 | 55.9987 | 58.4164 | 105.0044 | -4.8302 | 67.7131 | -2.0128 | 45.3517 | 63.2152 | 48.6567 | 0 | 66.8143 | 713.6163 | 709.0214 | 680.6858 | 681.1814 | 661.2073 | 658.8091 | 430.8835 | 424.6165 | 673.542 | 679.9895 | 699.947 | 712.8153 | 712.8157 | 710.1645 | 712.1639 | 710.9626 | 710.2542 | 711.2553 | 704.7733 | 703.2314 | 703.2408 | 699.9492 | 703.7854 | 703.6779 | 702.6974 | 699.7939 | 706.1249 | 704.7038 | 703.6174 | 706.6756 | 712.7924 | 708.7585 | 709.4635
2025-04-09 22:21 | 9 | 22 | 21 | 6.2817e-272 | 1 | 29.3895 | 638.0317 | 0.25711 | 0.0074306 | 140.1974 | 140.1974 | 140.1974 | 140.1974 | 10.9582 | 13.5762 | 609.4235 | 609.4235 | 609.4235 | 609.4235 | 58.4158 | 49.9038 | 15.7529 | 67.2007 | 15.6 | 12.5264 | 45.1608 | 0 | 49.9039 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3546753.8511 | 99.8076 | 0.0046918 | 0.14075 | 0.14075 | 0.14075 | 7.9917 | 1057.3287 | 1046.917 | 1046.9151 | 1046.5289 | 1118.2528 | 1118.2528 | 1118.2528 | 1118.2528 | 699.1781 | 699.1781 | 699.1781 | 4.7857 | 0 | 4.765 | 67.8495 | 200.3691 | 200.4947 | 212.1441 | 1.8768 | 3.3518 | 0 | 82.3983 | 56.0238 | 58.4158 | 105.0191 | -4.8114 | 67.2007 | -1.9181 | 45.0049 | 63.2226 | 48.6666 | 0 | 66.8139 | 712.9843 | 708.2852 | 680.1565 | 680.6287 | 660.9197 | 658.3749 | 430.123 | 424.3943 | 673.3125 | 679.6489 | 700.3161 | 713.1599 | 713.3973 | 711.0268 | 712.5731 | 711.4974 | 710.7695 | 711.5505 | 705.3717 | 703.4358 | 703.3439 | 700.4122 | 703.6785 | 703.6196 | 702.7627 | 700.153 | 706.303 | 705.1463 | 704.7932 | 707.0668 | 712.5546 | 709.0425 | 710.0597
2025-04-09 22:22 | 9 | 22 | 22 | 6.2817e-272 | 1 | 29.3892 | 638.7477 | 0.26008 | 0.007433 | 140.4841 | 140.4841 | 140.4841 | 140.4841 | 10.9786 | 13.5899 | 609.6899 | 609.6899 | 609.6899 | 609.6899 | 58.4083 | 49.9305 | 15.7507 | 67.76 | 15.5981 | 12.5811 | 45.4157 | 0 | 49.9304 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3546765.1064 | 99.8609 | 0.0047056 | 0.14117 | 0.14117 | 0.14117 | 7.9917 | 1056.897 | 1046.5419 | 1046.5391 | 1046.1634 | 1117.5243 | 1117.5243 | 1117.5243 | 1117.5243 | 700.5024 | 700.5024 | 700.5024 | 4.8482 | 0 | 4.8666 | 68.1765 | 200.9667 | 201.1117 | 211.7299 | 1.9015 | 3.3619 | 0 | 82.4226 | 55.9989 | 58.4083 | 105.0047 | -4.8729 | 67.76 | -1.8668 | 45.2013 | 63.2284 | 48.6761 | 0 | 66.8135 | 712.5044 | 707.7196 | 679.8264 | 680.2416 | 660.5963 | 657.9921 | 429.3855 | 423.6287 | 673.0377 | 679.2548 | 701.3852 | 714.3676 | 714.6943 | 712.0158 | 713.4551 | 712.5655 | 712.0407 | 712.9868 | 706.8565 | 705.1883 | 704.9707 | 701.3674 | 705.359 | 705.4069 | 704.1422 | 701.2573 | 707.3412 | 706.2319 | 706.0167 | 708.6339 | 714.0754 | 710.4887 | 711.4535
2025-04-09 22:23 | 9 | 22 | 23 | 6.2817e-272 | 1 | 29.389 | 638.3198 | 0.26044 | 0.0074287 | 139.9107 | 139.9107 | 139.9107 | 139.9107 | 10.938 | 13.5741 | 608.403 | 608.403 | 608.403 | 608.403 | 58.3338 | 49.9553 | 15.7505 | 67.1874 | 15.6011 | 12.5244 | 45.1013 | 0 | 49.9564 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3546776.3404 | 99.9107 | -0.0087402 | -0.26221 | -0.26221 | -0.26221 | 7.9917 | 1059.6932 | 1047.2915 | 1047.2915 | 1046.8915 | 1118.2706 | 1118.2706 | 1118.2706 | 1118.2706 | 699.404 | 699.404 | 699.404 | 4.7328 | 0 | 4.7408 | 67.9042 | 200.094 | 200.2276 | 211.5518 | 1.8823 | 3.345 | 0 | 81.7329 | 55.9644 | 58.3338 | 105.003 | -4.9482 | 67.1874 | -2.0898 | 44.9977 | 63.2282 | 48.6589 | 0 | 66.814 | 712.1953 | 707.2931 | 679.5205 | 679.8677 | 660.2834 | 657.6223 | 428.6757 | 423.3824 | 672.8138 | 678.9103 | 700.5636 | 712.9343 | 713.6973 | 711.1078 | 712.3592 | 711.4945 | 711.2599 | 711.8961 | 705.7426 | 703.8469 | 703.5717 | 700.5619 | 703.9167 | 703.9384 | 702.8862 | 700.347 | 706.6283 | 705.3309 | 705.1199 | 707.6363 | 713.0716 | 709.2344 | 710.3064
2025-04-09 22:24 | 9 | 22 | 24 | 6.2817e-272 | 1 | 29.3874 | 639.74 | 0.2663 | 0.0074247 | 140.4527 | 140.4527 | 140.4527 | 140.4527 | 10.977 | 13.5967 | 609.4318 | 609.4318 | 609.4318 | 609.4318 | 58.4454 | 49.9606 | 15.7515 | 67.7339 | 15.5997 | 12.6156 | 45.3651 | 0 | 49.9608 | 14 | 22.1 | 221 | 154840 | 237681 | 3546787.5957 | 99.9213 | 0.0034674 | 0.10402 | 0.10402 | 0.10402 | 7.9917 | 1057.4209 | 1046.5687 | 1046.5702 | 1046.1904 | 1117.5583 | 1117.5583 | 1117.5583 | 1117.5583 | 700.1824 | 700.1824 | 700.1824 | 4.8442 | 0 | 4.8485 | 68.2077 | 200.9294 | 201.0898 | 211.3385 | 1.9184 | 3.3671 | 0 | 82.2569 | 55.9032 | 58.4454 | 105.0101 | -4.7705 | 67.7339 | -2.0771 | 45.3255 | 63.239 | 48.6411 | 0 | 66.8136 | 712.0133 | 706.9656 | 679.3163 | 679.5625 | 660.0134 | 657.2982 | 428.0264 | 422.798 | 672.5658 | 678.5534 | 701.3591 | 713.9778 | 714.8301 | 711.9781 | 713.0596 | 712.1044 | 712.0359 | 712.5193 | 706.3117 | 704.6765 | 704.4667 | 701.2847 | 704.7175 | 704.9997 | 703.7031 | 701.1956 | 707.3596 | 705.8892 | 705.5507 | 708.4663 | 713.9009 | 710.1039 | 711.2291
2025-04-09 22:25 | 9 | 22 | 25 | 6.2817e-272 | 1 | 29.3863 | 640.2053 | 0.26345 | 0.0074247 | 140.4064 | 140.4064 | 140.4064 | 140.4064 | 10.9741 | 13.6061 | 609.7524 | 609.7524 | 609.7524 | 609.7524 | 58.5733 | 49.9944 | 15.7499 | 67.3426 | 15.5986 | 12.5898 | 45.2277 | 0 | 49.9935 | 13.0638 | 22.1 | 221 | 154840 | 237681 | 3546798.8511 | 99.9888 | 0.023779 | 0.71336 | 0.71336 | 0.71336 | 7.9917 | 1057.746 | 1046.6215 | 1046.6196 | 1046.2406 | 1118.0681 | 1118.0681 | 1118.0681 | 1118.0681 | 699.5331 | 699.5331 | 699.5331 | 4.8247 | 0 | 4.8133 | 68.2206 | 200.9064 | 201.0698 | 211.3383 | 1.9214 | 3.3622 | 0 | 82.1643 | 55.9516 | 58.5733 | 104.999 | -4.8727 | 67.3426 | -2.1853 | 45.2329 | 63.2411 | 48.64 | 0 | 66.8132 | 712.0359 | 706.866 | 679.2207 | 679.3822 | 659.8494 | 657.0508 | 427.3483 | 422.3094 | 672.3856 | 678.2235 | 700.5665 | 713.1164 | 713.234 | 711.3094 | 712.7704 | 711.5017 | 711.3834 | 711.7413 | 705.8235 | 704.4648 | 703.9921 | 700.4351 | 703.9634 | 704.209 | 703.0055 | 700.6365 | 706.9407 | 705.2955 | 705.0659 | 707.8932 | 713.0726 | 709.2077 | 710.4567
2025-04-09 22:26 | 9 | 22 | 26 | 6.2817e-272 | 1 | 29.387 | 640.2961 | 0.26381 | 0.0074256 | 140.4797 | 140.4797 | 140.4797 | 140.4797 | 10.979 | 13.6154 | 609.7474 | 609.7474 | 609.7474 | 609.7474 | 58.6263 | 50.0382 | 15.751 | 67.4583 | 15.5995 | 12.5918 | 45.2337 | 0 | 50.0396 | 13.9149 | 22.1 | 221 | 154840 | 237681 | 3546810.0851 | 100.0764 | -0.0072865 | -0.2186 | -0.2186 | -0.2186 | 7.9917 | 1058.3413 | 1046.5332 | 1046.5328 | 1046.1557 | 1117.9162 | 1117.9162 | 1117.9162 | 1117.9162 | 699.9797 | 699.9797 | 699.9797 | 4.8444 | 0 | 4.8348 | 68.4067 | 201.1523 | 201.3072 | 211.3496 | 1.9157 | 3.3736 | 0 | 81.9375 | 55.9027 | 58.6263 | 105.0064 | -5.1124 | 67.4583 | -2.069 | 45.2401 | 63.2288 | 48.6447 | 0 | 66.813 | 712.0352 | 706.7877 | 679.1577 | 679.275 | 659.789 | 656.9487 | 426.6451 | 422.0232 | 672.3332 | 677.9364 | 700.8612 | 713.5131 | 713.802 | 711.8851 | 713.1509 | 711.9104 | 711.7781 | 711.9767 | 706.1887 | 704.7721 | 704.4454 | 700.9645 | 704.4476 | 704.756 | 703.1692 | 700.7584 | 707.4926 | 705.8383 | 705.562 | 708.6031 | 713.874 | 709.8047 | 711.0682
2025-04-09 22:27 | 9 | 22 | 27 | 6.2817e-272 | 1 | 29.3862 | 639.4211 | 0.26582 | 0.007428 | 140.1101 | 140.1101 | 140.1101 | 140.1101 | 10.9531 | 13.6129 | 608.9066 | 608.9066 | 608.9066 | 608.9066 | 58.6224 | 50.0878 | 15.7517 | 67.1396 | 15.5984 | 12.5577 | 45.0697 | 0 | 50.0882 | 13.1489 | 22.1 | 221 | 154840 | 237681 | 3546821.2766 | 100.1754 | 0.0030445 | 0.091334 | 0.091334 | 0.091334 | 7.9917 | 1060.6211 | 1047.0113 | 1047.0128 | 1046.6194 | 1118.3328 | 1118.3328 | 1118.3328 | 1118.3328 | 700.1779 | 700.1779 | 700.1779 | 4.7619 | 0 | 4.7821 | 68.317 | 200.6807 | 200.8514 | 211.3355 | 1.9085 | 3.3695 | 0 | 81.333 | 55.8786 | 58.6224 | 105.011 | -5.5541 | 67.1396 | -2.0739 | 45.1172 | 63.2544 | 48.654 | 0 | 66.8133 | 711.9076 | 706.5191 | 679.0758 | 679.0705 | 659.7085 | 656.7361 | 425.8535 | 421.7324 | 672.2496 | 677.6379 | 701.2834 | 713.6061 | 713.1214 | 711.9366 | 713.2472 | 712.2065 | 712.1494 | 712.1729 | 706.6816 | 705.4163 | 704.8379 | 701.4632 | 704.2803 | 704.5343 | 703.2346 | 701.1179 | 707.9351 | 706.1961 | 706.0508 | 708.7065 | 713.9746 | 710.0999 | 711.4364
2025-04-09 22:28 | 9 | 22 | 28 | 6.2817e-272 | 1 | 29.3851 | 642.1334 | 0.26737 | 0.0074252 | 141.0629 | 141.0629 | 141.0629 | 141.0629 | 11.021 | 13.659 | 611.2557 | 611.2557 | 611.2557 | 611.2557 | 58.7606 | 50.1072 | 15.7523 | 67.7118 | 15.6003 | 12.6363 | 45.3146 | 0 | 50.1074 | 14 | 22.1 | 221 | 154840 | 237681 | 3546832.5319 | 100.2142 | 0.0013129 | 0.039388 | 0.039388 | 0.039388 | 7.9917 | 1056.5823 | 1045.7483 | 1045.7479 | 1045.394 | 1117.5866 | 1117.5866 | 1117.5866 | 1117.5866 | 699.8144 | 699.8144 | 699.8144 | 4.9272 | 0 | 4.8998 | 68.8427 | 202.1305 | 202.2929 | 211.461 | 1.909 | 3.3988 | 0 | 82.2701 | 55.9228 | 58.7606 | 105.0152 | -5.7011 | 67.7118 | -2.0544 | 45.3998 | 63.2278 | 48.6404 | 0 | 66.8127 | 712.253 | 706.8007 | 679.2879 | 679.1553 | 659.7235 | 656.6336 | 425.2386 | 421.2435 | 672.213 | 677.4276 | 700.9894 | 713.1994 | 713.5369 | 711.6838 | 713.1501 | 711.7887 | 711.842 | 712.0522 | 705.872 | 704.7443 | 704.3022 | 700.8636 | 703.9684 | 704.6949 | 703.0695 | 700.938 | 707.5797 | 705.491 | 704.9439 | 708.3566 | 713.6278 | 709.4023 | 710.821
2025-04-09 22:29 | 9 | 22 | 29 | 6.2817e-272 | 1 | 29.3851 | 641.6612 | 0.27514 | 0.0074199 | 140.8751 | 140.8751 | 140.8751 | 140.8751 | 11.0077 | 13.6542 | 610.7851 | 610.7851 | 610.7851 | 610.7851 | 59.027 | 50.1492 | 15.7509 | 67.9306 | 15.6 | 12.6737 | 45.4085 | 0 | 50.1494 | 13.6957 | 22.1 | 221 | 154840 | 237681 | 3546843.6304 | 100.2986 | 0.00027656 | 0.0082963 | 0.0082963 | 0.0082963 | 7.9917 | 1058.1287 | 1045.9972 | 1045.9993 | 1045.6352 | 1117.302 | 1117.302 | 1117.302 | 1117.302 | 701.2762 | 701.2762 | 701.2762 | 4.904 | 0 | 4.9351 | 68.9177 | 201.9608 | 202.1193 | 211.6286 | 1.9001 | 3.383 | 0 | 81.8366 | 56.0376 | 59.027 | 105.0058 | -5.8784 | 67.9306 | -2.0978 | 45.534 | 63.2479 | 48.6181 | 0 | 66.8128 | 712.4464 | 706.8387 | 679.3843 | 679.1551 | 659.776 | 656.5852 | 424.6176 | 420.9982 | 672.2681 | 677.3306 | 702.2934 | 714.9102 | 714.4844 | 713.3136 | 714.461 | 713.068 | 713.3402 | 713.4017 | 707.594 | 706.7936 | 706.0021 | 702.1545 | 705.3508 | 706.0571 | 704.3898 | 702.2623 | 709.0258 | 707.1067 | 706.4574 | 709.8703 | 715.1477 | 710.9137 | 712.4983
2025-04-09 22:30 | 9 | 22 | 30 | 6.2817e-272 | 1 | 29.3833 | 642.6902 | 0.27352 | 0.0074153 | 140.9422 | 140.9422 | 140.9422 | 140.9422 | 11.0131 | 13.6706 | 611.5287 | 611.5287 | 611.5287 | 611.5287 | 59.1315 | 50.1853 | 15.7519 | 67.3891 | 15.6 | 12.6076 | 45.1366 | 0 | 50.1854 | 13.4043 | 22.1 | 221 | 154840 | 237681 | 3546854.7872 | 100.3703 | 0.0055574 | 0.16672 | 0.16672 | 0.16672 | 7.9917 | 1057.9077 | 1045.897 | 1045.8972 | 1045.5381 | 1118.0066 | 1118.0066 | 1118.0066 | 1118.0066 | 699.3484 | 699.3484 | 699.3484 | 4.8795 | 0 | 4.8674 | 68.8853 | 202.0029 | 202.1435 | 211.7936 | 1.8812 | 3.3976 | 0 | 81.8762 | 56.1815 | 59.1315 | 105.0125 | -5.9236 | 67.3891 | -2.1112 | 45.2965 | 63.2607 | 48.601 | 0 | 66.8122 | 712.887 | 707.2727 | 679.6348 | 679.3334 | 659.9233 | 656.6067 | 424.0101 | 420.6761 | 672.3216 | 677.2539 | 700.5436 | 712.7372 | 712.6071 | 711.6494 | 712.8441 | 711.1274 | 711.4897 | 711.3204 | 705.3435 | 704.6649 | 704.011 | 700.1423 | 703.2157 | 704.2559 | 702.3318 | 700.4993 | 707.1695 | 705.0151 | 704.4336 | 707.8644 | 713.2569 | 708.937 | 710.6893
2025-04-09 22:31 | 9 | 22 | 31 | 6.2817e-272 | 1 | 29.3845 | 644.1886 | 0.26809 | 0.0074052 | 141.5018 | 141.5018 | 141.5018 | 141.5018 | 11.0523 | 13.6943 | 612.6982 | 612.6982 | 612.6982 | 612.6982 | 59.0825 | 50.1785 | 15.7511 | 68.0191 | 15.602 | 12.6801 | 45.3807 | 0 | 50.1789 | 14.6383 | 22.1 | 221 | 154840 | 237681 | 3546866.1489 | 100.357 | 0.00087251 | 0.026176 | 0.026176 | 0.026176 | 7.9917 | 1055.3894 | 1045.1672 | 1045.1677 | 1044.8291 | 1117.1862 | 1117.1862 | 1117.1862 | 1117.1862 | 699.8023 | 699.8023 | 699.8023 | 4.9736 | 0 | 4.964 | 69.252 | 202.9307 | 203.0927 | 211.9635 | 1.9007 | 3.4075 | 0 | 82.479 | 56.2122 | 59.0825 | 105.0074 | -5.9524 | 68.0191 | -2.031 | 45.5573 | 63.2512 | 48.5604 | 0 | 66.8117 | 713.2127 | 707.5679 | 679.789 | 679.4966 | 659.953 | 656.6498 | 423.4729 | 420.0594 | 672.3157 | 677.207 | 701.0967 | 713.1714 | 713.2301 | 711.6187 | 713.1543 | 711.4204 | 711.9613 | 711.8703 | 705.5979 | 705.0005 | 704.6288 | 700.5404 | 704.118 | 705.0827 | 702.9881 | 701.1671 | 707.5671 | 705.2781 | 704.4796 | 708.3273 | 713.6889 | 709.2944 | 710.8685
2025-04-09 22:32 | 9 | 22 | 32 | 6.2817e-272 | 1 | 29.3861 | 643.4708 | 0.26937 | 0.0073907 | 141.418 | 141.418 | 141.418 | 141.418 | 11.0458 | 13.689 | 612.4034 | 612.4034 | 612.4034 | 612.4034 | 58.933 | 50.1686 | 15.7506 | 68.1962 | 15.5997 | 12.7168 | 45.4849 | 0 | 50.1689 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3546877.4681 | 100.3373 | -0.0011625 | -0.034874 | -0.034874 | -0.034874 | 7.9917 | 1055.7911 | 1045.2915 | 1045.2904 | 1044.9498 | 1116.9564 | 1116.9564 | 1116.9564 | 1116.9564 | 700.8641 | 700.8641 | 700.8641 | 4.9828 | 0 | 4.9917 | 69.2375 | 202.8792 | 203.0271 | 212.1539 | 1.9201 | 3.4079 | 0 | 82.3868 | 56.2646 | 58.933 | 105.0036 | -5.9381 | 68.1962 | -1.8924 | 45.6891 | 63.2656 | 48.5033 | 0 | 66.8121 | 713.27 | 707.6873 | 679.7531 | 679.5331 | 659.9301 | 656.7014 | 422.8526 | 419.5191 | 672.2607 | 677.1736 | 702.0664 | 714.3983 | 713.8767 | 712.6945 | 714.0658 | 712.5313 | 712.86 | 712.8946 | 706.9789 | 706.3262 | 705.6374 | 701.8846 | 705.0032 | 706.005 | 704.1006 | 702.1017 | 708.7731 | 706.6811 | 705.7197 | 709.4873 | 714.7039 | 710.3357 | 711.9234
2025-04-09 22:33 | 9 | 22 | 33 | 6.2817e-272 | 1 | 29.3856 | 642.1604 | 0.2734 | 0.007381 | 140.847 | 140.847 | 140.847 | 140.847 | 11.0055 | 13.6702 | 611.0953 | 611.0953 | 611.0953 | 611.0953 | 58.7507 | 50.1802 | 15.7533 | 67.4637 | 15.6004 | 12.6012 | 45.1001 | 0 | 50.1804 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3546888.7234 | 100.3601 | 0.00040063 | 0.012019 | 0.012019 | 0.012019 | 7.9917 | 1058.5377 | 1046.0377 | 1046.0351 | 1045.673 | 1117.91 | 1117.91 | 1117.91 | 1117.91 | 698.7668 | 698.7668 | 698.7668 | 4.8461 | 0 | 4.8469 | 68.7873 | 201.8406 | 201.9807 | 212.1742 | 1.9106 | 3.3929 | 0 | 81.711 | 56.2708 | 58.7507 | 105.0216 | -6.0099 | 67.4637 | -1.8567 | 45.2738 | 63.2503 | 48.4629 | 0 | 66.8122 | 713.1671 | 707.7475 | 679.7523 | 679.6384 | 659.8822 | 656.7806 | 422.2947 | 418.9969 | 672.1337 | 677.129 | 700.318 | 711.9534 | 711.8437 | 710.431 | 711.85 | 710.4361 | 710.8392 | 710.9929 | 704.7026 | 703.7735 | 703.4538 | 700.1373 | 702.9658 | 703.7746 | 702.0477 | 700.1258 | 706.7396 | 704.5824 | 703.813 | 707.1039 | 712.4123 | 708.2139 | 709.8491
2025-04-09 22:34 | 9 | 22 | 34 | 6.2817e-272 | 1 | 29.3862 | 642.9596 | 0.26881 | 0.0073767 | 141.3146 | 141.3146 | 141.3146 | 141.3146 | 11.0385 | 13.6803 | 611.7107 | 611.7107 | 611.7107 | 611.7107 | 58.7239 | 50.1527 | 15.7524 | 68.1561 | 15.5978 | 12.6833 | 45.4434 | 0 | 50.153 | 14.6809 | 22.1 | 221 | 154840 | 237681 | 3546900.0426 | 100.3055 | -0.004492 | -0.13476 | -0.13476 | -0.13476 | 7.9917 | 1056.3379 | 1045.427 | 1045.4277 | 1045.0826 | 1117.0079 | 1117.0079 | 1117.0079 | 1117.0079 | 700.1769 | 700.1769 | 700.1769 | 4.9666 | 0 | 4.9606 | 69.0724 | 202.5771 | 202.7408 | 212.1169 | 1.9213 | 3.4061 | 0 | 82.2476 | 56.2174 | 58.7239 | 105.0159 | -5.8435 | 68.1561 | -1.8979 | 45.5685 | 63.2489 | 48.4466 | 0 | 66.8118 | 712.9933 | 707.668 | 679.6626 | 679.689 | 659.81 | 656.8074 | 421.7105 | 418.4937 | 671.9493 | 677.0771 | 701.4636 | 713.6174 | 713.9544 | 711.807 | 713.1523 | 712.0797 | 712.2709 | 712.6457 | 706.1275 | 705.1779 | 704.7824 | 701.2128 | 704.7894 | 705.5345 | 703.3949 | 701.4338 | 707.7567 | 705.6976 | 704.7602 | 708.3349 | 713.8329 | 709.9214 | 711.1026
2025-04-09 22:35 | 9 | 22 | 35 | 6.2817e-272 | 1 | 29.3862 | 643.7809 | 0.26682 | 0.0073745 | 141.8245 | 141.8245 | 141.8245 | 141.8245 | 11.0746 | 13.6839 | 612.8098 | 612.8098 | 612.8098 | 612.8098 | 58.9681 | 50.1081 | 15.7496 | 69.0237 | 15.5989 | 12.8111 | 45.9174 | 0 | 50.1084 | 15.5319 | 22.1 | 221 | 154840 | 237681 | 3546911.4468 | 100.2163 | -0.0012838 | -0.038512 | -0.038512 | -0.038512 | 7.9917 | 1053.4753 | 1044.76 | 1044.7615 | 1044.4334 | 1115.8785 | 1115.8785 | 1115.8785 | 1115.8785 | 701.9097 | 701.9097 | 701.9097 | 5.0753 | 0 | 5.1097 | 69.4257 | 203.3953 | 203.5691 | 212.2249 | 1.936 | 3.4208 | 0 | 82.9889 | 56.2842 | 58.9681 | 104.9973 | -5.8143 | 69.0237 | -1.8973 | 46.0279 | 63.2531 | 48.4389 | 0 | 66.8115 | 713.1146 | 707.8787 | 679.6833 | 679.8671 | 659.7397 | 656.8617 | 421.1308 | 417.8798 | 671.784 | 677.0327 | 703.0028 | 715.7447 | 715.6929 | 713.1034 | 714.5788 | 713.8671 | 713.9058 | 714.4205 | 708.0302 | 707.1171 | 706.7652 | 702.953 | 706.9831 | 707.2201 | 705.0492 | 702.8617 | 709.5619 | 707.4581 | 705.9771 | 710.0077 | 715.8939 | 711.9557 | 712.9475
2025-04-09 22:36 | 9 | 22 | 36 | 6.2817e-272 | 1 | 29.3871 | 649.8777 | 0.26449 | 0.0073718 | 142.7239 | 142.7239 | 142.7239 | 142.7239 | 11.1381 | 13.7153 | 616.7443 | 616.7443 | 616.7443 | 616.7443 | 58.924 | 50.0393 | 15.7501 | 68.5011 | 15.6047 | 12.783 | 45.8694 | 0.17021 | 50.0392 | 15.3191 | 22.1 | 221 | 154840 | 237681 | 3546922.9574 | 100.0785 | 0.012215 | 0.36644 | 0.36644 | 0.36644 | 7.9917 | 1046.6128 | 1043.2343 | 1043.2313 | 1043.2834 | 1116.5589 | 1116.5589 | 1116.5589 | 1116.5589 | 699.058 | 699.058 | 699.058 | 5.138 | 0 | 5.0939 | 69.495 | 204.4136 | 204.5499 | 212.4631 | 1.9471 | 3.4524 | 0 | 84.889 | 56.3518 | 58.924 | 105.0003 | -4.7944 | 68.5011 | -1.8742 | 45.9268 | 63.2489 | 48.4282 | 0 | 66.8111 | 713.8406 | 708.7552 | 679.9697 | 680.299 | 659.8185 | 657.108 | 420.5207 | 417.2624 | 671.6365 | 677.0501 | 700.4881 | 712.8902 | 712.491 | 710.5566 | 712.8424 | 711.2495 | 710.6799 | 711.1511 | 704.6534 | 704.0971 | 703.9862 | 700.3173 | 704.3368 | 704.6298 | 702.9095 | 700.5693 | 707.2188 | 703.9529 | 701.3981 | 706.037 | 713.6387 | 708.9693 | 709.6586
2025-04-09 22:37 | 9 | 22 | 37 | 6.2817e-272 | 1 | 29.39 | 642.1266 | 0.26666 | 0.0073625 | 141.1319 | 141.1319 | 141.1319 | 141.1319 | 11.0242 | 13.647 | 611.6485 | 611.6485 | 611.6485 | 611.6485 | 58.8652 | 50.0552 | 15.751 | 68.0527 | 15.5992 | 12.6766 | 45.4663 | 0 | 50.0551 | 14.2174 | 22.1 | 221 | 154840 | 237681 | 3546934.1522 | 100.1102 | 0.0048088 | 0.14426 | 0.14426 | 0.14426 | 7.9917 | 1055.4435 | 1045.6913 | 1045.69 | 1045.338 | 1117.1426 | 1117.1426 | 1117.1426 | 1117.1426 | 700.1729 | 700.1729 | 700.1729 | 4.9513 | 0 | 4.9519 | 68.7373 | 202.149 | 202.2864 | 212.5749 | 1.964 | 3.3878 | 0 | 82.6315 | 56.4298 | 58.8652 | 105.0067 | -4.8422 | 68.0527 | -1.9432 | 45.5444 | 63.2343 | 48.393 | 0 | 66.8111 | 713.3303 | 708.4486 | 679.6871 | 680.0458 | 659.8062 | 657.0905 | 419.8691 | 416.7207 | 671.5632 | 677.1334 | 701.4323 | 713.7833 | 714.012 | 711.5142 | 713.0696 | 712.342 | 712.0745 | 712.7521 | 706.0657 | 704.7178 | 704.6483 | 701.4942 | 704.9766 | 705.1363 | 703.5591 | 701.2124 | 707.6019 | 705.9776 | 704.9433 | 708.2831 | 713.814 | 710.2285 | 710.9433
2025-04-09 22:38 | 9 | 22 | 38 | 6.2817e-272 | 1 | 29.3903 | 640.8963 | 0.26567 | 0.0073581 | 140.8766 | 140.8766 | 140.8766 | 140.8766 | 11.006 | 13.6374 | 610.9212 | 610.9212 | 610.9212 | 610.9212 | 58.7976 | 50.0579 | 15.7501 | 67.8688 | 15.5989 | 12.6448 | 45.3764 | 0 | 50.0578 | 14.1702 | 22.1 | 221 | 154840 | 237681 | 3546945.383 | 100.1156 | 0.0059872 | 0.17962 | 0.17962 | 0.17962 | 7.9917 | 1056.6643 | 1046.0289 | 1046.0268 | 1045.6655 | 1117.383 | 1117.383 | 1117.383 | 1117.383 | 699.6927 | 699.6927 | 699.6927 | 4.8874 | 0 | 4.9056 | 68.6412 | 201.7223 | 201.8719 | 212.336 | 1.9734 | 3.3869 | 0 | 82.3336 | 56.3646 | 58.7976 | 105.0007 | -4.6591 | 67.8688 | -1.8392 | 45.4303 | 63.2401 | 48.3769 | 0 | 66.8111 | 712.9538 | 708.1986 | 679.4283 | 679.8543 | 659.5648 | 656.9329 | 419.2775 | 416.3098 | 671.4007 | 677.0913 | 700.8883 | 713.308 | 713.8465 | 711.3354 | 712.7472 | 712.0018 | 711.5096 | 712.2219 | 705.5811 | 704.1502 | 704.1323 | 701.0337 | 704.5253 | 704.5514 | 703.0442 | 700.7059 | 707.1136 | 705.57 | 704.6659 | 707.6044 | 713.1473 | 709.658 | 710.3634
2025-04-09 22:39 | 9 | 22 | 39 | 6.2817e-272 | 1 | 29.3894 | 640.3713 | 0.27213 | 0.0073485 | 140.5086 | 140.5086 | 140.5086 | 140.5086 | 10.9802 | 13.6327 | 609.9402 | 609.9402 | 609.9402 | 609.9402 | 58.708 | 50.0932 | 15.7518 | 67.342 | 15.6015 | 12.5756 | 45.1239 | 0 | 50.0935 | 13.4468 | 22.1 | 221 | 154840 | 237681 | 3546956.617 | 100.1862 | -0.00014722 | -0.004417 | -0.004417 | -0.004417 | 7.9917 | 1058.8628 | 1046.5098 | 1046.5087 | 1046.1328 | 1118.0687 | 1118.0687 | 1118.0687 | 1118.0687 | 699.4488 | 699.4488 | 699.4488 | 4.8459 | 0 | 4.8352 | 68.4828 | 201.1873 | 201.3351 | 212.1663 | 1.9497 | 3.3779 | 0 | 81.7552 | 56.2643 | 58.708 | 105.0116 | -4.9235 | 67.3407 | -1.8697 | 45.1817 | 63.2354 | 48.3364 | 0 | 66.8108 | 712.5592 | 707.8511 | 679.2253 | 679.6153 | 659.3954 | 656.7355 | 418.7441 | 416.2029 | 671.2806 | 677.0025 | 700.6024 | 713.2423 | 712.8404 | 710.9738 | 712.4767 | 711.5731 | 711.152 | 711.8126 | 705.6303 | 704.1423 | 703.936 | 701.0895 | 704.1057 | 703.9789 | 702.7415 | 700.4486 | 706.9022 | 705.5135 | 704.6842 | 707.4527 | 712.9606 | 709.5561 | 710.3014
2025-04-09 22:40 | 9 | 22 | 40 | 6.2817e-272 | 1 | 29.3895 | 640.956 | 0.26529 | 0.0073386 | 140.8552 | 140.8552 | 140.8552 | 140.8552 | 11.0047 | 13.6446 | 610.2751 | 610.2751 | 610.2751 | 610.2751 | 58.63 | 50.0915 | 15.7511 | 68.0086 | 15.6018 | 12.6463 | 45.3898 | 0 | 50.0916 | 14.2553 | 22.1 | 221 | 154840 | 237681 | 3546967.8936 | 100.1827 | 0.00073974 | 0.022193 | 0.022193 | 0.022193 | 7.9917 | 1057.6191 | 1046.054 | 1046.0549 | 1045.6896 | 1117.2004 | 1117.2004 | 1117.2004 | 1117.2004 | 700.5538 | 700.5538 | 700.5538 | 4.9175 | 0 | 4.9252 | 68.7351 | 201.8173 | 201.9699 | 212.026 | 1.9459 | 3.3692 | 0 | 82.0242 | 56.1869 | 58.63 | 105.0072 | -4.965 | 68.0086 | -1.8203 | 45.4356 | 63.2514 | 48.2963 | 0 | 66.8108 | 712.2864 | 707.6426 | 679.0529 | 679.4449 | 659.1615 | 656.5626 | 418.2408 | 415.5076 | 671.1573 | 676.9209 | 701.6375 | 714.4982 | 714.2227 | 712.0481 | 713.4303 | 712.7349 | 712.3586 | 713.2329 | 706.7959 | 705.3939 | 704.9066 | 701.9231 | 705.2219 | 705.2286 | 703.9638 | 701.5103 | 707.7623 | 706.3802 | 705.5136 | 708.5634 | 714.0211 | 710.7899 | 711.5849
2025-04-09 22:41 | 9 | 22 | 41 | 6.2817e-272 | 1 | 29.3898 | 641.7027 | 0.26628 | 0.0073344 | 141.3043 | 141.3043 | 141.3043 | 141.3043 | 11.0365 | 13.6634 | 611.4024 | 611.4024 | 611.4024 | 611.4024 | 58.6994 | 50.0929 | 15.7494 | 68.3306 | 15.6001 | 12.7078 | 45.5843 | 0 | 50.0934 | 14.3404 | 22.1 | 221 | 154840 | 237681 | 3546979.2128 | 100.1857 | -0.0048882 | -0.14665 | -0.14665 | -0.14665 | 7.9917 | 1055.6602 | 1045.4626 | 1045.4609 | 1045.1151 | 1116.7804 | 1116.7804 | 1116.7804 | 1116.7804 | 700.3539 | 700.3539 | 700.3539 | 4.9909 | 0 | 4.9915 | 68.9783 | 202.5343 | 202.6921 | 211.9982 | 1.9779 | 3.4004 | 0 | 82.4852 | 56.1289 | 58.6994 | 104.9957 | -5.033 | 68.3306 | -1.8512 | 45.6566 | 63.2685 | 48.2809 | 0 | 66.8104 | 712.2409 | 707.5882 | 678.9263 | 679.4046 | 658.971 | 656.4198 | 417.7557 | 414.9854 | 670.9619 | 676.7663 | 701.1113 | 714.2709 | 714.2557 | 711.9098 | 713.611 | 712.7869 | 712.3382 | 713.0713 | 706.6379 | 705.1162 | 704.6543 | 701.472 | 705.2012 | 705.2001 | 703.59 | 701.2048 | 707.4998 | 706.0642 | 705.1151 | 708.3146 | 713.6476 | 710.4721 | 711.1599
2025-04-09 22:42 | 9 | 22 | 42 | 6.2817e-272 | 1 | 29.3887 | 642.6941 | 0.26844 | 0.0073332 | 141.4377 | 141.4377 | 141.4377 | 141.4377 | 11.0464 | 13.6722 | 612.4656 | 612.4656 | 612.4656 | 612.4656 | 58.7047 | 50.0763 | 15.7528 | 68.1462 | 15.6003 | 12.6795 | 45.5 | 0 | 50.077 | 14.2553 | 22.1 | 221 | 154840 | 237681 | 3546990.617 | 100.1525 | 0.00020605 | 0.0061816 | 0.0061816 | 0.0061816 | 7.9917 | 1054.2891 | 1045.2777 | 1045.2791 | 1044.9366 | 1117.0219 | 1117.0219 | 1117.0219 | 1117.0219 | 699.6055 | 699.6055 | 699.6055 | 4.9743 | 0 | 4.9719 | 68.991 | 202.6015 | 202.7492 | 212.0505 | 1.9664 | 3.4188 | 0 | 82.8815 | 56.1068 | 58.7047 | 105.0184 | -5.4303 | 68.1462 | -1.9145 | 45.5549 | 63.2571 | 48.2747 | 0 | 66.8101 | 712.5211 | 707.8819 | 679.0318 | 679.5448 | 658.9714 | 656.3806 | 417.2303 | 414.5756 | 670.8922 | 676.7221 | 700.6313 | 713.2758 | 713.4645 | 710.8941 | 712.6687 | 711.7717 | 711.298 | 712.3346 | 705.7154 | 704.15 | 703.9222 | 700.8696 | 704.3517 | 704.5507 | 703.2248 | 700.8029 | 707.0171 | 705.4224 | 704.4081 | 707.7574 | 712.9588 | 709.493 | 710.2576
2025-04-09 22:43 | 9 | 22 | 43 | 6.2817e-272 | 1 | 29.3865 | 642.1382 | 0.26427 | 0.0073282 | 141.234 | 141.234 | 141.234 | 141.234 | 11.0327 | 13.6551 | 612.3243 | 612.3243 | 612.3243 | 612.3243 | 58.7349 | 50.0512 | 15.7523 | 68.0069 | 15.6004 | 12.6703 | 45.4794 | 0 | 50.0517 | 14.6383 | 22.1 | 221 | 154840 | 237681 | 3547001.9787 | 100.1022 | -0.0004054 | -0.012162 | -0.012162 | -0.012162 | 7.9917 | 1054.7743 | 1045.5315 | 1045.5304 | 1045.1823 | 1117.2026 | 1117.2026 | 1117.2026 | 1117.2026 | 699.6315 | 699.6315 | 699.6315 | 4.9498 | 0 | 4.95 | 68.7797 | 202.2569 | 202.3872 | 212.1088 | 1.9566 | 3.4126 | 0 | 82.8025 | 56.1129 | 58.7349 | 105.0151 | -5.5213 | 68.0069 | -1.8996 | 45.522 | 63.2536 | 48.2518 | 0 | 66.8104 | 712.5476 | 707.9508 | 678.9836 | 679.4928 | 658.9029 | 656.3751 | 416.7905 | 414.3573 | 670.8111 | 676.6583 | 700.6664 | 713.2599 | 713.4267 | 710.724 | 712.4954 | 711.7427 | 711.2134 | 712.1766 | 705.6697 | 704.3031 | 704.0462 | 701.0323 | 704.6533 | 704.6446 | 703.2252 | 700.6073 | 707.2097 | 705.6968 | 704.4442 | 707.6904 | 713.116 | 709.5026 | 710.2173
2025-04-09 22:44 | 9 | 22 | 44 | 6.2817e-272 | 1 | 29.3879 | 641.9 | 0.26851 | 0.0073228 | 141.2365 | 141.2365 | 141.2365 | 141.2365 | 11.0323 | 13.6552 | 612.0439 | 612.0439 | 612.0439 | 612.0439 | 58.7183 | 50.0617 | 15.7525 | 68.3026 | 15.6006 | 12.721 | 45.613 | 0 | 50.0622 | 15.1064 | 22.1 | 221 | 154840 | 237681 | 3547013.2553 | 100.1234 | -0.0037413 | -0.11224 | -0.11224 | -0.11224 | 7.9917 | 1055.1679 | 1045.5413 | 1045.5434 | 1045.1917 | 1116.8172 | 1116.8172 | 1116.8172 | 1116.8172 | 701.0694 | 701.0694 | 701.0694 | 4.9989 | 0 | 4.9992 | 68.9024 | 202.3792 | 202.5162 | 212.1077 | 1.9516 | 3.4112 | 0 | 82.6757 | 56.0889 | 58.7183 | 105.0163 | -5.5092 | 68.3026 | -1.9041 | 45.7041 | 63.2572 | 48.2317 | 0 | 66.8098 | 712.2824 | 707.8715 | 678.9461 | 679.3586 | 658.9228 | 656.33 | 416.4388 | 414.045 | 670.7503 | 676.6892 | 701.9477 | 714.9936 | 714.6255 | 712.5376 | 714.2887 | 713.3488 | 712.6609 | 713.6575 | 707.456 | 705.9455 | 705.6332 | 702.2011 | 706.0401 | 706.0094 | 704.728 | 701.8969 | 708.2635 | 706.8689 | 705.6731 | 708.9478 | 714.5693 | 711.0672 | 711.6663
2025-04-09 22:45 | 9 | 22 | 45 | 6.2817e-272 | 1 | 29.3901 | 641.3846 | 0.26649 | 0.0073277 | 141.4108 | 141.4108 | 141.4108 | 141.4108 | 11.0439 | 13.6519 | 612.4908 | 612.4908 | 612.4908 | 612.4908 | 58.8995 | 50.037 | 15.7463 | 68.4548 | 15.5977 | 12.7236 | 45.3092 | 0 | 50.0392 | 14.8261 | 22.1 | 221 | 154840 | 237681 | 3547024.5652 | 100.0739 | -0.016667 | -0.50002 | -0.50002 | -0.50002 | 7.9917 | 1054.0626 | 1045.3248 | 1045.3263 | 1044.9824 | 1116.6196 | 1116.6196 | 1116.6196 | 1116.6196 | 700.6204 | 700.6204 | 700.6204 | 4.9944 | 0 | 5.0145 | 68.9677 | 202.566 | 202.6991 | 212.3367 | 2.0057 | 3.3938 | 0 | 82.9736 | 56.311 | 58.8995 | 104.9755 | -4.501 | 68.4548 | -1.2207 | 45.7134 | 63.254 | 48.2531 | 0 | 66.8099 | 712.4543 | 708.2486 | 679.1362 | 679.4597 | 659.0147 | 656.3694 | 416.0519 | 413.5428 | 670.6934 | 676.8128 | 701.6459 | 714.6006 | 714.8446 | 711.7803 | 713.6054 | 712.808 | 712.3318 | 713.5631 | 706.8929 | 705.2197 | 705.0772 | 701.5555 | 705.6622 | 705.7627 | 704.3805 | 701.5764 | 707.8001 | 706.506 | 705.0931 | 708.3683 | 713.992 | 710.524 | 711.0322
2025-04-09 22:46 | 9 | 22 | 46 | 6.2817e-272 | 1 | 29.3926 | 638.5513 | 0.26885 | 0.0073456 | 140.2246 | 140.2246 | 140.2246 | 140.2246 | 10.959 | 13.6163 | 610.1445 | 610.1445 | 610.1445 | 610.1445 | 58.9478 | 50.0761 | 15.7513 | 66.9269 | 15.6008 | 12.4924 | 44.7975 | 0 | 50.0761 | 13.2766 | 22.1 | 221 | 154840 | 237681 | 3547035.6596 | 100.1519 | 0.0058014 | 0.17404 | 0.17404 | 0.17404 | 7.9917 | 1059.4664 | 1046.9 | 1046.8977 | 1046.5111 | 1118.6096 | 1118.6096 | 1118.6096 | 1118.6096 | 698.0508 | 698.0508 | 698.0508 | 4.7717 | 0 | 4.7444 | 68.1708 | 200.6451 | 200.7582 | 212.4788 | 1.9816 | 3.3836 | 0 | 81.6792 | 56.318 | 58.9478 | 105.0086 | -4.5076 | 66.9269 | -0.90416 | 44.8828 | 63.262 | 48.3285 | 0 | 66.8098 | 712.2464 | 708.1761 | 679.1638 | 679.3636 | 659.1264 | 656.3332 | 415.6216 | 413.5223 | 670.7309 | 676.9095 | 699.3979 | 712.0211 | 711.6409 | 709.8775 | 711.639 | 710.4039 | 709.7811 | 710.6697 | 704.2791 | 702.4414 | 702.3576 | 699.5644 | 702.1407 | 702.0904 | 701.7323 | 699.0333 | 705.3883 | 704.289 | 703.4104 | 705.737 | 711.5334 | 707.781 | 708.6926
2025-04-09 22:47 | 9 | 22 | 47 | 6.2817e-272 | 1 | 29.3896 | 638.4262 | 0.27008 | 0.0073612 | 140.6525 | 140.6525 | 140.6525 | 140.6525 | 10.9904 | 13.6262 | 610.2977 | 610.2977 | 610.2977 | 610.2977 | 58.9499 | 50.0863 | 15.7481 | 67.9028 | 15.6015 | 12.6355 | 45.3104 | 0 | 50.0867 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3547046.9149 | 100.1723 | -0.004299 | -0.12897 | -0.12897 | -0.12897 | 7.9917 | 1058.5077 | 1046.3187 | 1046.3198 | 1045.9477 | 1117.3377 | 1117.3377 | 1117.3377 | 1117.3377 | 700.1058 | 700.1058 | 700.1058 | 4.8804 | 0 | 4.8957 | 68.6425 | 201.5006 | 201.6361 | 212.3832 | 1.9622 | 3.3813 | 0 | 81.8137 | 56.2432 | 58.9499 | 104.9873 | -4.9267 | 67.9028 | -0.88111 | 45.397 | 63.2675 | 48.3886 | 0 | 66.8099 | 711.8899 | 707.8829 | 679.1171 | 679.2073 | 659.0886 | 656.1884 | 415.306 | 413.2356 | 670.6584 | 676.9913 | 701.4321 | 714.2401 | 714.4256 | 711.871 | 713.5671 | 712.512 | 711.8612 | 713.1367 | 706.3626 | 704.242 | 704.29 | 701.4045 | 704.3637 | 704.4185 | 703.6841 | 700.9026 | 707.1911 | 706.2748 | 705.2203 | 707.6459 | 713.513 | 709.9221 | 710.8271
2025-04-09 22:48 | 9 | 22 | 48 | 6.2817e-272 | 1 | 29.3861 | 640.4777 | 0.27191 | 0.0073634 | 141.1889 | 141.1889 | 141.1889 | 141.1889 | 11.0296 | 13.6431 | 610.9287 | 610.9287 | 610.9287 | 610.9287 | 58.8791 | 50.086 | 15.7472 | 68.4402 | 15.6005 | 12.7241 | 45.6563 | 0 | 50.0866 | 15.4894 | 22.1 | 221 | 154840 | 237681 | 3547058.2128 | 100.172 | 0.00053723 | 0.016117 | 0.016117 | 0.016117 | 7.9917 | 1056.5906 | 1045.5923 | 1045.5962 | 1045.2423 | 1116.6383 | 1116.6383 | 1116.6383 | 1116.6383 | 701.9457 | 701.9457 | 701.9457 | 5.0195 | 0 | 5.0216 | 69.0299 | 202.4284 | 202.5712 | 212.2689 | 1.9271 | 3.3779 | 0 | 82.2187 | 56.1046 | 58.8791 | 104.9811 | -5.1944 | 68.4402 | -0.84053 | 45.7152 | 63.2571 | 48.3936 | 0 | 66.81 | 711.7633 | 707.62 | 679.0602 | 679.174 | 658.9506 | 656.0473 | 414.9077 | 412.7988 | 670.6029 | 676.8275 | 703.0185 | 716.3831 | 715.5296 | 713.1099 | 714.9369 | 713.8558 | 713.2448 | 714.6571 | 708.5718 | 706.8598 | 706.6431 | 703.1434 | 706.6422 | 706.5771 | 705.8034 | 702.599 | 709.1849 | 708.1046 | 706.5155 | 709.5395 | 715.9319 | 712.0428 | 712.6056
2025-04-09 22:49 | 9 | 22 | 49 | 6.2817e-272 | 1 | 29.3856 | 643.1513 | 0.26756 | 0.0073518 | 141.3924 | 141.3924 | 141.3924 | 141.3924 | 11.0442 | 13.658 | 612.2322 | 612.2322 | 612.2322 | 612.2322 | 58.701 | 50.0378 | 15.7507 | 67.9839 | 15.6028 | 12.6413 | 45.3711 | 0 | 50.038 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3547069.6596 | 100.0754 | -0.0096504 | -0.28951 | -0.28951 | -0.28951 | 7.9917 | 1054.0109 | 1045.3179 | 1045.3166 | 1044.9757 | 1117.2328 | 1117.2328 | 1117.2328 | 1117.2328 | 698.1331 | 698.1331 | 698.1331 | 4.9172 | 0 | 4.9056 | 68.7485 | 202.3993 | 202.5319 | 212.1884 | 1.9408 | 3.4002 | 0 | 82.9863 | 56.0391 | 58.701 | 105.0047 | -4.5802 | 67.9839 | -0.88144 | 45.4177 | 63.2794 | 48.347 | 0 | 66.8102 | 712.1516 | 707.8484 | 679.1128 | 679.2556 | 658.8109 | 655.9545 | 414.4313 | 412.5439 | 670.5572 | 676.6126 | 699.1973 | 712.196 | 711.7848 | 709.6758 | 711.9437 | 710.2179 | 709.7597 | 710.808 | 704.439 | 702.8043 | 702.7115 | 699.0988 | 702.8776 | 702.9435 | 701.9082 | 699.1002 | 705.4793 | 703.9206 | 702.798 | 705.8548 | 711.4478 | 707.5493 | 708.4945
2025-04-09 22:50 | 9 | 22 | 50 | 6.2817e-272 | 1 | 29.3837 | 639.5855 | 0.27055 | 0.0073459 | 140.4015 | 140.4015 | 140.4015 | 140.4015 | 10.9746 | 13.6165 | 609.201 | 609.201 | 609.201 | 609.201 | 58.6431 | 50.0777 | 15.7491 | 67.7278 | 15.6018 | 12.6202 | 45.2592 | 0 | 50.0779 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3547080.8936 | 100.1551 | -0.0021329 | -0.063987 | -0.063987 | -0.063987 | 7.9917 | 1059.6943 | 1046.6136 | 1046.6123 | 1046.2328 | 1117.5666 | 1117.5666 | 1117.5666 | 1117.5666 | 700.4676 | 700.4676 | 700.4676 | 4.858 | 0 | 4.8678 | 68.4756 | 201.1001 | 201.2363 | 211.9899 | 1.8906 | 3.3507 | 0 | 81.5136 | 56.0208 | 58.6431 | 104.9938 | -4.7847 | 67.7278 | -0.91812 | 45.3419 | 63.2676 | 48.3213 | 0 | 66.81 | 711.6826 | 707.1613 | 678.6932 | 678.8373 | 658.5666 | 655.6506 | 413.8632 | 412.4476 | 670.5698 | 676.3589 | 701.4131 | 714.3533 | 713.766 | 712.1425 | 713.5776 | 712.4761 | 712.193 | 712.9585 | 707.0547 | 705.3973 | 704.9008 | 701.5354 | 704.68 | 704.8074 | 703.9134 | 701.1725 | 707.8709 | 706.8224 | 706.0741 | 708.8189 | 714.1062 | 710.3058 | 711.2494
2025-04-09 22:51 | 9 | 22 | 51 | 6.2817e-272 | 1 | 29.3824 | 642.336 | 0.26846 | 0.0073486 | 141.4505 | 141.4505 | 141.4505 | 141.4505 | 11.0495 | 13.6526 | 611.2099 | 611.2099 | 611.2099 | 611.2099 | 58.5536 | 50.0468 | 15.7463 | 68.7526 | 15.5978 | 12.7699 | 45.8153 | 0 | 50.0478 | 15.4468 | 22.1 | 221 | 154840 | 237681 | 3547092.2553 | 100.0935 | -0.0053912 | -0.16174 | -0.16174 | -0.16174 | 7.9917 | 1054.8566 | 1045.223 | 1045.2253 | 1044.8836 | 1116.2313 | 1116.2313 | 1116.2313 | 1116.2313 | 701.2506 | 701.2506 | 701.2506 | 5.0249 | 0 | 5.0461 | 69.0802 | 202.7477 | 202.8887 | 211.7628 | 1.8966 | 3.3914 | 0 | 82.6775 | 55.992 | 58.5536 | 104.9752 | -4.9137 | 68.7526 | -0.92397 | 45.8797 | 63.2563 | 48.3299 | 0 | 66.8098 | 711.813 | 706.9838 | 678.5687 | 678.7109 | 658.3384 | 655.4266 | 413.381 | 412.0629 | 670.4838 | 676.0326 | 702.5537 | 715.154 | 715.2482 | 712.4295 | 714.0457 | 712.9429 | 713.0658 | 713.8731 | 707.7851 | 706.2491 | 705.6281 | 702.5355 | 705.6716 | 706.3183 | 705.042 | 702.5371 | 708.8592 | 707.0816 | 705.7644 | 709.3015 | 714.7891 | 711.0276 | 711.9807
2025-04-09 22:52 | 9 | 22 | 52 | 6.2817e-272 | 1 | 29.381 | 644.4159 | 0.26674 | 0.0073509 | 141.5293 | 141.5293 | 141.5293 | 141.5293 | 11.0555 | 13.6574 | 612.7474 | 612.7474 | 612.7474 | 612.7474 | 58.4318 | 49.9967 | 15.7483 | 68.1764 | 15.6025 | 12.6588 | 45.4882 | 0 | 49.9978 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3547103.7447 | 99.9934 | -0.019572 | -0.58717 | -0.58717 | -0.58717 | 7.9917 | 1052.5345 | 1045.1064 | 1045.1026 | 1044.7717 | 1116.9819 | 1116.9819 | 1116.9819 | 1116.9819 | 698.4631 | 698.4631 | 698.4631 | 4.9649 | 0 | 4.9313 | 68.781 | 202.5904 | 202.7141 | 211.6983 | 1.9101 | 3.4131 | 0 | 83.4105 | 56.0135 | 58.4318 | 104.9888 | -4.9127 | 68.1764 | -0.92007 | 45.4806 | 63.2773 | 48.338 | 0 | 66.8093 | 712.193 | 707.189 | 678.606 | 678.7073 | 658.2169 | 655.2575 | 412.7593 | 411.6381 | 670.3617 | 675.695 | 699.6721 | 712.0941 | 712.3017 | 710.1459 | 711.9496 | 710.2719 | 710.1502 | 710.5858 | 704.3556 | 703.3954 | 703.0962 | 699.2216 | 703.2814 | 704.1146 | 702.4434 | 700.0013 | 706.2174 | 703.6961 | 701.9033 | 705.8887 | 712.2067 | 708.0602 | 709.2074
2025-04-09 22:53 | 9 | 22 | 53 | 6.2817e-272 | 1 | 29.3847 | 641.9305 | 0.26233 | 0.0073601 | 141.0075 | 141.0075 | 141.0075 | 141.0075 | 11.0172 | 13.6261 | 610.2862 | 610.2862 | 610.2862 | 610.2862 | 58.2259 | 49.9854 | 15.7471 | 68.4377 | 15.5948 | 12.7075 | 45.6172 | 0 | 49.9854 | 14.9565 | 22.1 | 221 | 154840 | 237681 | 3547114.9348 | 99.9709 | 0.01689 | 0.5067 | 0.5067 | 0.5067 | 7.9917 | 1055.7902 | 1045.822 | 1045.8196 | 1045.4646 | 1116.6411 | 1116.6411 | 1116.6411 | 1116.6411 | 700.4909 | 700.4909 | 700.4909 | 4.9384 | 0 | 4.9465 | 68.628 | 201.8939 | 202.0181 | 211.5482 | 1.9003 | 3.3726 | 0 | 82.5588 | 55.9772 | 58.2259 | 104.9804 | -4.8832 | 68.4377 | -1.0267 | 45.6557 | 63.26 | 48.3782 | 0 | 66.8096 | 711.779 | 706.6865 | 678.3207 | 678.3263 | 658.0712 | 655.0086 | 412.1575 | 411.3856 | 670.2942 | 675.4858 | 701.6802 | 714.0898 | 714.344 | 711.9625 | 713.342 | 712.1251 | 712.4609 | 712.9285 | 706.7142 | 705.5976 | 705.1478 | 701.1971 | 705.2785 | 706.0343 | 704.0134 | 701.789 | 707.8733 | 705.9558 | 704.7311 | 708.4818 | 714.1057 | 710.1856 | 711.5952
2025-04-09 22:54 | 9 | 22 | 54 | 6.2817e-272 | 1 | 29.3892 | 640.5028 | 0.26486 | 0.0073689 | 140.734 | 140.734 | 140.734 | 140.734 | 10.9963 | 13.61 | 608.9763 | 608.9763 | 608.9763 | 608.9763 | 58.0039 | 49.9736 | 15.7443 | 68.3288 | 15.599 | 12.6677 | 45.5816 | 0 | 49.975 | 15.0213 | 22.1 | 221 | 154840 | 237681 | 3547126.1915 | 99.9472 | -0.0055064 | -0.16519 | -0.16519 | -0.16519 | 7.9917 | 1057.2968 | 1046.2096 | 1046.2113 | 1045.8409 | 1116.783 | 1116.783 | 1116.783 | 1116.783 | 700.6707 | 700.6707 | 700.6707 | 4.9108 | 0 | 4.9244 | 68.4917 | 201.5433 | 201.669 | 211.2884 | 1.9491 | 3.3531 | 0 | 82.1816 | 55.8835 | 58.0039 | 104.9619 | -4.7767 | 68.3288 | -0.90319 | 45.5124 | 63.2586 | 48.4183 | 0 | 66.8094 | 711.3818 | 706.2077 | 678.0886 | 677.939 | 657.8934 | 654.7002 | 411.6256 | 411.0344 | 670.1235 | 675.2174 | 701.95 | 714.2128 | 714.261 | 711.8648 | 713.2534 | 712.1376 | 712.6737 | 713.1552 | 706.8766 | 705.7974 | 705.3405 | 701.52 | 705.2411 | 706.0972 | 703.9359 | 701.93 | 708.3579 | 706.3844 | 705.2344 | 709.1643 | 714.569 | 710.3019 | 711.8219
2025-04-09 22:55 | 9 | 22 | 55 | 6.2817e-272 | 1 | 29.3864 | 642.5033 | 0.26127 | 0.0073758 | 141.1201 | 141.1201 | 141.1201 | 141.1201 | 11.0246 | 13.6248 | 610.1925 | 610.1925 | 610.1925 | 610.1925 | 57.9205 | 49.9277 | 15.7492 | 68.2498 | 15.5987 | 12.6087 | 45.5385 | 0 | 49.928 | 14.383 | 22.1 | 221 | 154840 | 237681 | 3547137.5957 | 99.8554 | 0.0035288 | 0.10586 | 0.10586 | 0.10586 | 7.9917 | 1054.343 | 1045.6823 | 1045.6813 | 1045.3289 | 1116.887 | 1116.887 | 1116.887 | 1116.887 | 698.6366 | 698.6366 | 698.6366 | 4.9136 | 0 | 4.894 | 68.5081 | 201.9323 | 202.0576 | 211.252 | 1.9435 | 3.3709 | 0 | 82.9939 | 55.7614 | 57.9205 | 104.9949 | -4.477 | 68.2498 | -0.8954 | 45.3006 | 63.2425 | 48.4431 | 0 | 66.8092 | 711.3582 | 706.1247 | 677.974 | 677.7152 | 657.7735 | 654.4077 | 411.1011 | 410.4816 | 669.8902 | 674.9156 | 700.282 | 712.0314 | 712.1285 | 710.1806 | 712.2959 | 710.1962 | 710.5362 | 710.9118 | 704.4377 | 703.6722 | 703.4287 | 699.262 | 703.3129 | 704.271 | 702.2271 | 700.541 | 706.267 | 703.8835 | 702.6186 | 706.6931 | 711.9931 | 707.7564 | 709.3796
2025-04-09 22:56 | 9 | 22 | 56 | 6.2817e-272 | 1 | 29.3849 | 641.5674 | 0.26665 | 0.0073748 | 140.9004 | 140.9004 | 140.9004 | 140.9004 | 11.0096 | 13.6105 | 608.6349 | 608.6349 | 608.6349 | 608.6349 | 57.7243 | 49.9348 | 15.7483 | 68.6911 | 15.5996 | 12.7105 | 45.7929 | 0 | 49.9351 | 14.766 | 22.1 | 221 | 154840 | 237681 | 3547148.9787 | 99.8696 | -0.00075819 | -0.022746 | -0.022746 | -0.022746 | 7.9917 | 1056.1764 | 1045.9623 | 1045.9655 | 1045.6013 | 1116.3111 | 1116.3111 | 1116.3111 | 1116.3111 | 701.3381 | 701.3381 | 701.3381 | 4.9526 | 0 | 4.9628 | 68.6365 | 201.797 | 201.9481 | 211.1974 | 1.885 | 3.3581 | 0 | 82.4768 | 55.5821 | 57.7243 | 104.9888 | -4.5351 | 68.6911 | -1.0801 | 45.6665 | 63.241 | 48.4381 | 0 | 66.8091 | 710.9837 | 705.7344 | 677.8149 | 677.3977 | 657.6967 | 654.1738 | 410.6252 | 410.305 | 669.7237 | 674.7221 | 702.9709 | 714.8234 | 714.8285 | 712.4824 | 714.2573 | 712.6486 | 713.3374 | 713.9126 | 707.367 | 706.5893 | 706.2232 | 702.0182 | 705.8033 | 707.0894 | 704.9513 | 703.0044 | 708.9306 | 706.7249 | 705.4474 | 709.548 | 714.9351 | 710.6906 | 712.4131
2025-04-09 22:57 | 9 | 22 | 57 | 6.2817e-272 | 1 | 29.3854 | 643.0842 | 0.26438 | 0.0073616 | 141.2247 | 141.2247 | 141.2247 | 141.2247 | 11.0324 | 13.6248 | 609.8562 | 609.8562 | 609.8562 | 609.8562 | 57.66 | 49.9114 | 15.749 | 68.6635 | 15.6026 | 12.7418 | 45.8243 | 0 | 49.9117 | 15.3191 | 22.1 | 221 | 154840 | 237681 | 3547160.383 | 99.8227 | -0.00012138 | -0.0036404 | -0.0036404 | -0.0036404 | 7.9917 | 1053.7666 | 1045.5396 | 1045.5404 | 1045.1902 | 1116.3468 | 1116.3468 | 1116.3468 | 1116.3468 | 700.907 | 700.907 | 700.907 | 4.9989 | 0 | 4.9845 | 68.6284 | 202.1845 | 202.3482 | 211.126 | 1.9257 | 3.3637 | 0 | 83.1418 | 55.5083 | 57.66 | 104.9929 | -4.3259 | 68.6635 | -1.0035 | 45.7787 | 63.2365 | 48.3866 | 0 | 66.8092 | 710.8832 | 705.6792 | 677.7527 | 677.2623 | 657.5874 | 653.9806 | 410.1797 | 409.9843 | 669.6379 | 674.6078 | 702.5496 | 714.6124 | 713.9968 | 712.4569 | 714.507 | 712.592 | 712.9322 | 713.2038 | 706.954 | 706.3349 | 706.113 | 701.3744 | 705.6004 | 706.6688 | 704.6153 | 702.5666 | 708.6823 | 705.7655 | 703.7458 | 708.389 | 715.3593 | 710.4265 | 711.7669
2025-04-09 22:58 | 9 | 22 | 58 | 6.2817e-272 | 1 | 29.3874 | 641.9583 | 0.26033 | 0.0073522 | 140.755 | 140.755 | 140.755 | 140.755 | 10.9984 | 13.609 | 609.5034 | 609.5034 | 609.5034 | 609.5034 | 57.7088 | 49.9002 | 15.7503 | 67.9376 | 15.599 | 12.6168 | 45.4642 | 0 | 49.9005 | 13.6596 | 22.1 | 221 | 154840 | 237681 | 3547171.7234 | 99.8004 | 0.0025426 | 0.076278 | 0.076278 | 0.076278 | 7.9917 | 1055.2468 | 1046.1679 | 1046.1679 | 1045.8004 | 1117.2926 | 1117.2926 | 1117.2926 | 1117.2926 | 698.6739 | 698.6739 | 698.6739 | 4.8513 | 0 | 4.8495 | 68.2478 | 201.3139 | 201.4703 | 211.3697 | 1.9297 | 3.3594 | 0 | 82.8497 | 55.6312 | 57.7088 | 105.0017 | -4.1564 | 67.9376 | -1.0123 | 45.3298 | 63.2494 | 48.3488 | 0 | 66.8088 | 710.9848 | 705.9806 | 677.8765 | 677.2424 | 657.6416 | 653.9009 | 409.7447 | 409.8673 | 669.453 | 674.5654 | 700.5522 | 712.1735 | 711.915 | 710.0573 | 712.3821 | 709.9035 | 710.5754 | 710.9699 | 704.2258 | 703.6956 | 703.865 | 699.2186 | 703.2489 | 704.2194 | 702.0604 | 700.3994 | 706.4085 | 704.1577 | 702.6473 | 706.5995 | 712.3342 | 707.8173 | 709.6682
2025-04-09 22:59 | 9 | 22 | 59 | 6.2817e-272 | 1 | 29.3875 | 640.2616 | 0.26412 | 0.0073537 | 140.186 | 140.186 | 140.186 | 140.186 | 10.958 | 13.5945 | 608.5967 | 608.5967 | 608.5967 | 608.5967 | 57.8054 | 49.9311 | 15.749 | 67.2929 | 15.6002 | 12.5822 | 45.1826 | 0 | 49.9313 | 13.6596 | 22.1 | 221 | 154840 | 237681 | 3547183.0638 | 99.8622 | 0.0062575 | 0.18772 | 0.18772 | 0.18772 | 7.9917 | 1057.9887 | 1046.9189 | 1046.9189 | 1046.5298 | 1118.1332 | 1118.1332 | 1118.1332 | 1118.1332 | 698.7567 | 698.7567 | 698.7567 | 4.7684 | 0 | 4.7695 | 68.0137 | 200.4775 | 200.6059 | 211.3684 | 1.9211 | 3.3413 | 0 | 82.1794 | 55.8037 | 57.8054 | 104.9931 | -4.3423 | 67.2929 | -1.0116 | 45.2053 | 63.2501 | 48.3538 | 0 | 66.8087 | 710.7416 | 705.9091 | 677.7084 | 677.0794 | 657.6354 | 653.7931 | 409.3352 | 409.5524 | 669.3571 | 674.6063 | 700.6561 | 712.495 | 711.4147 | 710.3192 | 712.6933 | 710.2846 | 710.7104 | 711.151 | 704.6023 | 703.9415 | 703.9451 | 699.4527 | 702.9382 | 703.9761 | 702.1765 | 700.2781 | 706.4854 | 704.4866 | 702.6894 | 706.553 | 712.5862 | 708.0991 | 709.8039
2025-04-09 23:00 | 9 | 23 | 0 | 6.2817e-272 | 1 | 29.3878 | 641.036 | 0.26652 | 0.0073619 | 141.304 | 141.304 | 141.304 | 141.304 | 11.0371 | 13.6248 | 610.4667 | 610.4667 | 610.4667 | 610.4667 | 57.8468 | 49.9061 | 15.7468 | 69.019 | 15.6018 | 12.7696 | 45.9917 | 0 | 49.9065 | 15.8723 | 22.1 | 221 | 154840 | 237681 | 3547194.383 | 99.8123 | -0.0042491 | -0.12748 | -0.12748 | -0.12748 | 7.9917 | 1053.3747 | 1045.4526 | 1045.4534 | 1045.1066 | 1115.8849 | 1115.8849 | 1115.8849 | 1115.8849 | 702.3473 | 702.3473 | 702.3473 | 5.0516 | 0 | 5.0576 | 68.7691 | 202.3944 | 202.5441 | 211.2057 | 1.9692 | 3.3764 | 0 | 83.2453 | 55.9469 | 57.8468 | 104.9789 | -4.3377 | 69.019 | -0.91066 | 45.8787 | 63.2469 | 48.388 | 0 | 66.8085 | 710.516 | 705.8411 | 677.5827 | 676.9393 | 657.4834 | 653.6767 | 409.012 | 408.9807 | 669.1738 | 674.5698 | 704.2087 | 716.3536 | 715.5482 | 713.5017 | 715.9206 | 713.7739 | 714.0147 | 715.137 | 708.1546 | 707.5363 | 707.725 | 702.7508 | 707.1609 | 708.4923 | 705.9993 | 703.9765 | 709.5448 | 707.7318 | 705.4253 | 709.9221 | 716.0021 | 711.5693 | 713.1451
2025-04-09 23:01 | 9 | 23 | 1 | 6.2817e-272 | 1 | 29.3868 | 641.7364 | 0.26661 | 0.0073607 | 141.2593 | 141.2593 | 141.2593 | 141.2593 | 11.0344 | 13.624 | 610.9964 | 610.9964 | 610.9964 | 610.9964 | 57.8564 | 49.8639 | 15.7475 | 68.598 | 15.6009 | 12.7076 | 45.8266 | 0 | 49.864 | 14.5217 | 22.1 | 221 | 154840 | 237681 | 3547205.6739 | 99.7277 | 0.00011984 | 0.0035954 | 0.0035954 | 0.0035954 | 7.9917 | 1052.1943 | 1045.5013 | 1045.5028 | 1045.1537 | 1116.433 | 1116.433 | 1116.433 | 1116.433 | 699.847 | 699.847 | 699.847 | 4.9436 | 0 | 4.9627 | 68.545 | 202.104 | 202.2578 | 211.4 | 1.9548 | 3.3741 | 0 | 83.6531 | 56.0398 | 57.8564 | 104.983 | -4.1058 | 68.598 | -1.0094 | 45.656 | 63.2511 | 48.3831 | 0 | 66.8083 | 710.8505 | 706.2817 | 677.6596 | 677.1018 | 657.4127 | 653.7113 | 408.6711 | 408.5869 | 669.1533 | 674.5068 | 701.5754 | 713.7285 | 712.8703 | 710.8908 | 713.7309 | 711.3917 | 711.6506 | 712.5747 | 705.2949 | 704.6723 | 704.8687 | 700.2864 | 704.5401 | 705.6522 | 703.3589 | 701.209 | 707.4491 | 705.7224 | 703.3982 | 707.7992 | 713.5716 | 708.9515 | 710.6248
2025-04-09 23:02 | 9 | 23 | 2 | 6.2817e-272 | 1 | 29.3859 | 639.2595 | 0.26315 | 0.0073565 | 140.0328 | 140.0328 | 140.0328 | 140.0328 | 10.9477 | 13.5742 | 608.8557 | 608.8557 | 608.8557 | 608.8557 | 57.9772 | 49.8819 | 15.7519 | 67.0338 | 15.6022 | 12.5079 | 45.0523 | 0 | 49.8821 | 13.5745 | 22.1 | 221 | 154840 | 237681 | 3547216.8723 | 99.7638 | 0.0037841 | 0.11352 | 0.11352 | 0.11352 | 7.9917 | 1057.6013 | 1047.1121 | 1047.1091 | 1046.7155 | 1118.4702 | 1118.4702 | 1118.4702 | 1118.4702 | 697.759 | 697.759 | 697.759 | 4.7598 | 0 | 4.7258 | 67.6993 | 200.0909 | 200.2201 | 211.4064 | 1.9238 | 3.3369 | 0 | 82.3691 | 56.2261 | 57.9772 | 105.0129 | -4.2472 | 67.0338 | -0.95416 | 44.9386 | 63.2392 | 48.3658 | 0 | 66.8084 | 710.6946 | 706.223 | 677.4172 | 677.0199 | 657.3047 | 653.7797 | 408.3751 | 408.4688 | 668.9986 | 674.4664 | 699.7379 | 711.4835 | 710.9305 | 709.2807 | 711.7404 | 709.4612 | 709.5541 | 710.3054 | 703.1116 | 702.0808 | 702.4372 | 698.8482 | 702.0346 | 702.9455 | 701.0869 | 699.205 | 705.5732 | 703.7978 | 702.0083 | 705.3677 | 711.6469 | 707.0816 | 708.7356
2025-04-09 23:03 | 9 | 23 | 3 | 6.2817e-272 | 1 | 29.3876 | 639.0234 | 0.26264 | 0.0073592 | 140.7093 | 140.7093 | 140.7093 | 140.7093 | 10.9951 | 13.5925 | 609.6076 | 609.6076 | 609.6076 | 609.6076 | 58.0092 | 49.8806 | 15.7472 | 68.3385 | 15.6004 | 12.6953 | 45.7053 | 0 | 49.8808 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3547228.1489 | 99.7611 | 0.00045052 | 0.013516 | 0.013516 | 0.013516 | 7.9917 | 1055.4332 | 1046.2338 | 1046.2343 | 1045.8634 | 1116.7698 | 1116.7698 | 1116.7698 | 1116.7698 | 701.5671 | 701.5671 | 701.5671 | 4.9408 | 0 | 4.9475 | 68.3882 | 201.392 | 201.5476 | 211.068 | 1.9388 | 3.3476 | 0 | 82.8114 | 56.4139 | 58.0092 | 104.981 | -4.0362 | 68.3385 | -1.0538 | 45.6118 | 63.2479 | 48.3792 | 0 | 66.8079 | 710.2954 | 705.825 | 677.0492 | 676.8268 | 657.0117 | 653.6281 | 408.157 | 408.173 | 668.8564 | 674.3416 | 703.2367 | 715.4552 | 714.846 | 712.6657 | 714.8616 | 713.1935 | 713.3785 | 714.4591 | 707.5703 | 706.4048 | 706.4551 | 702.3629 | 706.379 | 707.1457 | 705.0088 | 702.8629 | 708.878 | 707.39 | 705.661 | 709.271 | 715.113 | 711.0966 | 712.5275
2025-04-09 23:04 | 9 | 23 | 4 | 6.2817e-272 | 1 | 29.3894 | 638.616 | 0.26185 | 0.0073648 | 140.6767 | 140.6767 | 140.6767 | 140.6767 | 10.9921 | 13.5914 | 610.0102 | 610.0102 | 610.0102 | 610.0102 | 58.0181 | 49.8693 | 15.7489 | 68.1411 | 15.6012 | 12.6591 | 45.619 | 0 | 49.8697 | 14.1277 | 22.1 | 221 | 154840 | 237681 | 3547239.4894 | 99.7386 | 0.0034385 | 0.10316 | 0.10316 | 0.10316 | 7.9917 | 1055.1519 | 1046.2855 | 1046.2883 | 1045.9151 | 1117.0281 | 1117.0281 | 1117.0281 | 1117.0281 | 700.0192 | 700.0192 | 700.0192 | 4.8709 | 0 | 4.8965 | 68.2176 | 201.2083 | 201.3512 | 211.1312 | 1.9796 | 3.3545 | 0 | 82.9221 | 56.4973 | 58.0181 | 104.9928 | -4.0026 | 68.1411 | -0.97624 | 45.4816 | 63.2638 | 48.4006 | 0 | 66.8078 | 710.477 | 705.9675 | 676.9583 | 676.9132 | 656.7936 | 653.6266 | 407.8864 | 407.7894 | 668.8324 | 674.2188 | 701.2847 | 713.9196 | 713.494 | 710.929 | 713.1832 | 711.5095 | 711.8195 | 712.8076 | 705.9659 | 704.7522 | 704.8651 | 700.5748 | 704.9374 | 705.6851 | 703.4 | 701.1949 | 707.469 | 705.9787 | 704.2817 | 707.8748 | 713.4864 | 709.4821 | 710.9407
2025-04-09 23:05 | 9 | 23 | 5 | 6.2817e-272 | 1 | 29.3866 | 636.9195 | 0.26439 | 0.0073689 | 139.9302 | 139.9302 | 139.9302 | 139.9302 | 10.9402 | 13.5661 | 608.6569 | 608.6569 | 608.6569 | 608.6569 | 58.0612 | 49.8985 | 15.7468 | 67.2582 | 15.6015 | 12.5318 | 45.1418 | 0 | 49.899 | 13.6596 | 22.1 | 221 | 154840 | 237681 | 3547250.766 | 99.797 | 0.0047886 | 0.14366 | 0.14366 | 0.14366 | 7.9917 | 1058.7849 | 1047.2504 | 1047.2509 | 1046.8509 | 1118.1777 | 1118.1777 | 1118.1777 | 1118.1777 | 698.9245 | 698.9245 | 698.9245 | 4.7653 | 0 | 4.7511 | 67.7779 | 200.0604 | 200.1999 | 211.0482 | 1.9175 | 3.3234 | 0 | 82.0205 | 56.5306 | 58.0612 | 104.9785 | -4.2584 | 67.2582 | -0.99961 | 45.0244 | 63.2505 | 48.4168 | 0 | 66.8072 | 710.3021 | 705.691 | 676.668 | 676.7608 | 656.5973 | 653.6137 | 407.5654 | 407.5432 | 668.6869 | 674.043 | 700.4191 | 712.4149 | 712.5681 | 710.1543 | 712.0887 | 710.6107 | 710.789 | 711.5257 | 704.8843 | 703.3754 | 703.3557 | 700.0684 | 703.4727 | 704.3578 | 702.5522 | 700.3157 | 706.5171 | 704.8471 | 703.6603 | 706.5691 | 712.1658 | 708.5419 | 709.9149
2025-04-09 23:06 | 9 | 23 | 6 | 6.2817e-272 | 1 | 29.3877 | 636.3021 | 0.26648 | 0.0073686 | 139.8044 | 139.8044 | 139.8044 | 139.8044 | 10.9309 | 13.5616 | 607.9681 | 607.9681 | 607.9681 | 607.9681 | 58.0882 | 49.9221 | 15.7486 | 67.3159 | 15.603 | 12.5028 | 45.1414 | 0 | 49.9223 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3547261.9787 | 99.8442 | 5.8956e-05 | 0.0017685 | 0.0017685 | 0.0017685 | 7.9917 | 1060.0477 | 1047.4221 | 1047.4211 | 1047.0183 | 1118.1028 | 1118.1028 | 1118.1028 | 1118.1028 | 699.6806 | 699.6806 | 699.6806 | 4.7813 | 0 | 4.7558 | 67.884 | 199.9872 | 200.136 | 210.8274 | 1.9209 | 3.3223 | 0 | 81.6558 | 56.5245 | 58.0882 | 104.9902 | -4.0083 | 67.3159 | -1.0331 | 44.9201 | 63.2434 | 48.4151 | 0 | 66.8072 | 709.9677 | 705.2157 | 676.3567 | 676.5853 | 656.3393 | 653.4799 | 407.3119 | 407.3844 | 668.5562 | 673.8307 | 701.1909 | 713.1738 | 713.4895 | 710.9051 | 712.5584 | 711.4422 | 711.7402 | 712.3052 | 705.7334 | 703.8509 | 703.6793 | 701.0208 | 704.0567 | 705.0983 | 703.3586 | 701.0236 | 707.4238 | 705.6602 | 704.7962 | 707.4698 | 712.9361 | 709.286 | 710.8207
2025-04-09 23:07 | 9 | 23 | 7 | 6.2817e-272 | 1 | 29.387 | 637.1337 | 0.26435 | 0.0073661 | 140.1502 | 140.1502 | 140.1502 | 140.1502 | 10.9557 | 13.5849 | 608.6857 | 608.6857 | 608.6857 | 608.6857 | 58.1855 | 49.9664 | 15.7501 | 67.861 | 15.6008 | 12.6392 | 45.4558 | 0 | 49.9653 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3547273.1915 | 99.9329 | 0.023899 | 0.71697 | 0.71697 | 0.71697 | 7.9917 | 1059.247 | 1046.9679 | 1046.9666 | 1046.5774 | 1117.3928 | 1117.3928 | 1117.3928 | 1117.3928 | 701.6856 | 701.6856 | 701.6856 | 4.8595 | 0 | 4.8745 | 68.2639 | 200.6648 | 200.8133 | 210.6676 | 1.9077 | 3.3341 | 0 | 81.7784 | 56.5085 | 58.1855 | 105.0005 | -4.31 | 67.861 | -1.1473 | 45.4101 | 63.2501 | 48.4055 | 0 | 66.8069 | 709.6569 | 704.8228 | 676.1932 | 676.57 | 656.1269 | 653.3942 | 407.0304 | 407.3074 | 668.502 | 673.6816 | 702.7332 | 715.395 | 714.7652 | 712.8596 | 714.458 | 713.5729 | 713.5877 | 714.1915 | 708.2917 | 706.7757 | 706.2386 | 702.8962 | 706.4398 | 706.9665 | 705.4596 | 702.6244 | 709.2657 | 707.5729 | 706.4297 | 709.4777 | 714.9532 | 711.551 | 712.8457
2025-04-09 23:08 | 9 | 23 | 8 | 6.2817e-272 | 1 | 29.3849 | 638.9594 | 0.26753 | 0.0073686 | 140.4994 | 140.4994 | 140.4994 | 140.4994 | 10.9812 | 13.6053 | 610.0067 | 610.0067 | 610.0067 | 610.0067 | 58.063 | 49.9667 | 15.7488 | 67.7015 | 15.6024 | 12.6109 | 45.3542 | 0 | 49.9669 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3547284.4681 | 99.9334 | 0.0036294 | 0.10888 | 0.10888 | 0.10888 | 7.9917 | 1057.5049 | 1046.4894 | 1046.4904 | 1046.1128 | 1117.6002 | 1117.6002 | 1117.6002 | 1117.6002 | 699.3763 | 699.3763 | 699.3763 | 4.8481 | 0 | 4.8366 | 68.2819 | 201.0881 | 201.2364 | 210.8136 | 1.9076 | 3.3425 | 0 | 82.2018 | 56.7347 | 58.063 | 104.9922 | -4.0958 | 67.7015 | -1.0636 | 45.3087 | 63.2594 | 48.4125 | 0 | 66.8068 | 709.9593 | 705.1169 | 676.3321 | 676.779 | 656.0742 | 653.4846 | 406.7724 | 406.9114 | 668.3962 | 673.5141 | 700.6309 | 712.5653 | 712.9394 | 710.5201 | 712.4636 | 711.4804 | 711.4638 | 711.9167 | 705.4664 | 703.7603 | 703.5463 | 700.5411 | 704.1468 | 704.9825 | 703.301 | 700.6756 | 707.0524 | 705.1989 | 704.3182 | 707.1141 | 712.4446 | 708.8305 | 710.2054
2025-04-09 23:09 | 9 | 23 | 9 | 6.2817e-272 | 1 | 29.3849 | 639.0396 | 0.26472 | 0.0073739 | 140.3671 | 140.3671 | 140.3671 | 140.3671 | 10.9718 | 13.6022 | 609.8388 | 609.8388 | 609.8388 | 609.8388 | 58.1704 | 49.973 | 15.7455 | 67.6648 | 15.5985 | 12.6033 | 45.3288 | 0 | 49.9734 | 13.6522 | 22.1 | 221 | 154840 | 237681 | 3547295.6739 | 99.9459 | 0.0065081 | 0.19524 | 0.19524 | 0.19524 | 7.9917 | 1057.9396 | 1046.665 | 1046.6633 | 1046.2828 | 1117.6478 | 1117.6478 | 1117.6478 | 1117.6478 | 699.4935 | 699.4935 | 699.4935 | 4.8119 | 0 | 4.8311 | 68.275 | 200.9172 | 201.0573 | 210.9089 | 1.9099 | 3.3499 | 0 | 82.1144 | 56.7134 | 58.1704 | 104.9699 | -3.8702 | 67.6648 | -1.0708 | 45.2812 | 63.2695 | 48.4359 | 0 | 66.8065 | 710.1288 | 705.2088 | 676.3059 | 676.8832 | 656.0378 | 653.4963 | 406.3981 | 406.8667 | 668.3663 | 673.4086 | 700.6636 | 712.6778 | 713.1321 | 710.4932 | 712.1368 | 711.3883 | 711.777 | 712.1468 | 705.7225 | 704.1816 | 703.8077 | 700.7008 | 704.36 | 705.0492 | 703.1195 | 700.6585 | 707.2199 | 705.2993 | 704.4483 | 707.3189 | 712.5343 | 709.1314 | 710.4172
2025-04-09 23:10 | 9 | 23 | 10 | 6.2817e-272 | 1 | 29.3862 | 639.6049 | 0.26443 | 0.0073745 | 140.6654 | 140.6654 | 140.6654 | 140.6654 | 10.9924 | 13.6186 | 609.8839 | 609.8839 | 609.8839 | 609.8839 | 58.1352 | 50.0052 | 15.7479 | 68.1818 | 15.6022 | 12.6623 | 45.4893 | 0 | 50.0051 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3547306.8085 | 100.0104 | 0.00064129 | 0.019239 | 0.019239 | 0.019239 | 7.9917 | 1057.5787 | 1046.2813 | 1046.2813 | 1045.9106 | 1116.9749 | 1116.9749 | 1116.9749 | 1116.9749 | 700.6462 | 700.6462 | 700.6462 | 4.9025 | 0 | 4.9065 | 68.5744 | 201.4939 | 201.6205 | 210.9032 | 1.9325 | 3.3569 | 0 | 82.111 | 56.6112 | 58.1352 | 104.9862 | -4.0482 | 68.1818 | -1.0805 | 45.4931 | 63.2533 | 48.4387 | 0 | 66.807 | 710.1139 | 705.1384 | 676.3283 | 676.9529 | 656.0196 | 653.5787 | 406.0373 | 406.5539 | 668.3804 | 673.3285 | 701.8391 | 714.1174 | 714.0793 | 711.8163 | 713.494 | 712.7049 | 712.6579 | 713.0701 | 707.0814 | 705.5969 | 704.928 | 701.9584 | 705.5793 | 706.2867 | 704.4721 | 701.9479 | 708.2396 | 706.3281 | 705.2736 | 708.3244 | 713.5783 | 710.3518 | 711.5664
2025-04-09 23:11 | 9 | 23 | 11 | 6.2817e-272 | 1 | 29.3847 | 641.4016 | 0.26638 | 0.0073682 | 141.0497 | 141.0497 | 141.0497 | 141.0497 | 11.0202 | 13.6363 | 611.1685 | 611.1685 | 611.1685 | 611.1685 | 58.0973 | 49.98 | 15.7489 | 68.1532 | 15.601 | 12.6683 | 45.5238 | 0 | 49.9792 | 14.8936 | 22.1 | 221 | 154840 | 237681 | 3547318.234 | 99.96 | 0.018529 | 0.55588 | 0.55588 | 0.55588 | 7.9917 | 1054.9977 | 1045.764 | 1045.7638 | 1045.4081 | 1117.0123 | 1117.0123 | 1117.0123 | 1117.0123 | 699.438 | 699.438 | 699.438 | 4.915 | 0 | 4.911 | 68.6269 | 201.9593 | 202.0688 | 211.0501 | 1.9431 | 3.3681 | 0 | 82.8027 | 56.6429 | 58.0973 | 104.9923 | -3.8537 | 68.1532 | -1.1415 | 45.5148 | 63.2539 | 48.4122 | 0 | 66.8065 | 710.5462 | 705.4634 | 676.4581 | 677.2014 | 656.0277 | 653.6614 | 405.6813 | 406.2432 | 668.3713 | 673.2607 | 700.612 | 712.8785 | 713.2641 | 710.8403 | 712.4791 | 711.6365 | 711.5753 | 711.9596 | 705.5671 | 704.1147 | 703.6715 | 700.6113 | 704.5242 | 705.2159 | 703.2669 | 700.9569 | 707.147 | 704.6699 | 703.1159 | 706.8281 | 712.5606 | 709.2526 | 710.4061
2025-04-09 23:12 | 9 | 23 | 12 | 6.2817e-272 | 1 | 29.3845 | 637.0174 | 0.27123 | 0.0073667 | 138.7851 | 138.7851 | 138.7851 | 138.7851 | 10.8598 | 13.5202 | 606.6534 | 606.6534 | 606.6534 | 606.6534 | 58.0519 | 49.9602 | 15.7518 | 65.4659 | 15.604 | 12.2962 | 44.202 | 0 | 49.9608 | 17.8298 | 22.1 | 221 | 154840 | 237681 | 3547329.4468 | 99.9204 | -0.0041282 | -0.12385 | -0.12385 | -0.12385 | 7.9917 | 1064.0423 | 1048.7383 | 1048.7311 | 1048.2957 | 1120.5123 | 1120.5123 | 1120.5123 | 1120.5123 | 696.328 | 696.328 | 696.328 | 4.5452 | 0 | 4.476 | 67.1108 | 198.3079 | 198.4116 | 210.9609 | 1.8823 | 3.2981 | 0 | 80.7271 | 56.4673 | 58.0519 | 105.0121 | -3.7922 | 65.4659 | -1.049 | 44.1777 | 63.2583 | 48.4046 | 0 | 66.8065 | 710.1585 | 705.0857 | 676.2376 | 676.8344 | 655.9911 | 653.5073 | 405.2192 | 406.2766 | 668.3591 | 673.1752 | 697.5769 | 709.4955 | 709.2165 | 707.8574 | 709.6248 | 708.8167 | 708.8523 | 708.938 | 702.5298 | 701.0697 | 700.5754 | 697.707 | 700.6234 | 701.0084 | 699.6511 | 697.6415 | 704.1448 | 701.7488 | 701.1787 | 703.9431 | 709.5817 | 706.5579 | 707.6208
2025-04-09 23:13 | 9 | 23 | 13 | 6.2817e-272 | 1 | 29.3824 | 556.309 | 0.25933 | 0.0073672 | 122.5359 | 122.5359 | 122.5359 | 122.5359 | 9.7087 | 12.3792 | 578.0517 | 578.0517 | 578.0517 | 578.0517 | 58.0079 | 50.0424 | 15.7534 | 51.7325 | 15.6039 | 10.5268 | 37.8463 | 0 | 50.0429 | 17.1489 | 22.1 | 221 | 154840 | 237681 | 3547339.1489 | 100.0847 | -0.0056041 | -0.16812 | -0.16812 | -0.16812 | 7.9917 | 1099.0379 | 1070.1117 | 1070.0996 | 1069.0379 | 1138.4023 | 1138.4023 | 1138.4023 | 1138.4023 | 691.3956 | 691.3956 | 691.3956 | 2.3038 | 0 | 2.2639 | 58.767 | 174.2196 | 174.3286 | 209.2239 | 1.5495 | 2.7294 | 0 | 66.6765 | 56.4778 | 58.0079 | 105.0225 | -4.8336 | 51.7325 | -1.0668 | 37.8207 | 63.2683 | 48.4063 | 0 | 66.8068 | 705.6181 | 700.4563 | 673.4103 | 673.8543 | 655.0249 | 652.2619 | 403.8115 | 405.6236 | 668.2743 | 673.0923 | 691.22 | 703.4543 | 700.6727 | 702.3712 | 705.5023 | 705.8511 | 707.2311 | 706.1065 | 700.1997 | 698.0253 | 695.5139 | 693.8401 | 693.7003 | 691.5439 | 691.2109 | 690.5927 | 699.5377 | 697.822 | 697.477 | 700.5623 | 707.014 | 703.4723 | 703.8535
2025-04-09 23:14 | 9 | 23 | 14 | 6.2817e-272 | 1 | 29.3815 | 498.4128 | 0.2599 | 0.0073726 | 117.3432 | 117.3432 | 117.3432 | 117.3432 | 9.3409 | 11.9196 | 566.4037 | 566.4037 | 566.4037 | 566.4037 | 57.9061 | 50.028 | 15.7518 | 48.6331 | 15.6016 | 10.2052 | 36.6273 | 0 | 50.0269 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3547347.4681 | 100.056 | 0.027213 | 0.81638 | 0.81638 | 0.81638 | 7.9917 | 1105.6802 | 1076.9557 | 1076.9519 | 1075.6802 | 1142.4391 | 1142.4391 | 1142.4391 | 1142.4391 | 699.3191 | 699.3191 | 699.3191 | 2.0255 | 0 | 2.022 | 56.7036 | 167.1123 | 167.272 | 205.2241 | 1.4114 | 2.5564 | 0 | 62.7993 | 56.3787 | 57.9061 | 105.0116 | -4.9506 | 48.6331 | -1.1136 | 36.6653 | 63.2677 | 48.4261 | 0 | 66.8091 | 699.3167 | 693.8371 | 669.6672 | 669.9975 | 652.8835 | 649.8187 | 402.8158 | 404.8138 | 667.4695 | 672.1667 | 699.4298 | 711.1537 | 708.2823 | 710.354 | 713.5323 | 713.8453 | 715.4134 | 713.9147 | 709.1467 | 706.8524 | 704.3766 | 702.7519 | 702.5886 | 700.4024 | 699.4248 | 699.2418 | 705.9771 | 705.5886 | 704.5919 | 707.5604 | 714.4274 | 710.8525 | 711.6862
2025-04-09 23:15 | 9 | 23 | 15 | 6.2817e-272 | 1 | 29.379 | 486.5735 | 0.25766 | 0.0073747 | 117.9547 | 117.9547 | 117.9547 | 117.9547 | 9.385 | 11.9758 | 566.4781 | 566.4781 | 566.4781 | 566.4781 | 57.861 | 50.0352 | 15.751 | 49.4668 | 15.5988 | 10.2984 | 36.9947 | 0 | 50.0359 | 15.1064 | 22.1 | 221 | 154840 | 237681 | 3547355.5957 | 100.0704 | -0.02151 | -0.6453 | -0.6453 | -0.6453 | 7.9917 | 1104.8857 | 1076.1372 | 1076.1379 | 1074.8857 | 1141.3534 | 1141.3534 | 1141.3534 | 1141.3534 | 700.4809 | 700.4809 | 700.4809 | 2.0368 | 0 | 2.0314 | 57.273 | 168.2341 | 168.3993 | 202.1897 | 1.3965 | 2.5677 | 0 | 63.1913 | 56.2482 | 57.861 | 105.0066 | -5.0315 | 49.4668 | -1.1093 | 37.0001 | 63.347 | 48.4327 | 0 | 66.8097 | 694.5853 | 688.9523 | 667.1137 | 667.3511 | 650.6091 | 647.271 | 402.2087 | 404.5353 | 665.9258 | 670.4953 | 700.6167 | 712.0284 | 709.3775 | 711.7868 | 715.1151 | 715.3214 | 717.1623 | 715.4318 | 710.5506 | 708.4407 | 705.9536 | 703.7973 | 704.2338 | 702.1622 | 700.7467 | 700.4451 | 706.8952 | 706.2469 | 705.2491 | 708.1994 | 715.0453 | 711.5087 | 712.4735
2025-04-09 23:16 | 9 | 23 | 16 | 6.2817e-272 | 1 | 29.3796 | 479.4006 | 0.26514 | 0.0073743 | 116.7211 | 116.7211 | 116.7211 | 116.7211 | 9.2974 | 11.8656 | 564.3131 | 564.3131 | 564.3131 | 564.3131 | 57.8771 | 50.0604 | 15.7486 | 48.3805 | 15.5986 | 10.2074 | 36.6186 | 0 | 50.0604 | 13.5745 | 22.1 | 221 | 154840 | 237681 | 3547363.7234 | 100.1206 | 0.0088128 | 0.26438 | 0.26438 | 0.26438 | 7.9917 | 1106.4672 | 1077.7668 | 1077.7698 | 1076.4672 | 1142.7674 | 1142.7674 | 1142.7674 | 1142.7674 | 700.1751 | 700.1751 | 700.1751 | 2.027 | 0 | 2.0408 | 56.8553 | 166.5764 | 166.7347 | 200.2838 | 1.4119 | 2.5368 | 0 | 62.3417 | 56.1394 | 57.8771 | 104.9906 | -5.0428 | 48.3805 | -1.1356 | 36.6732 | 63.4446 | 48.4307 | 0 | 66.8086 | 690.9326 | 685.1244 | 664.933 | 665.0898 | 648.3832 | 644.9811 | 401.6058 | 404.0831 | 664.2963 | 668.5998 | 700.0007 | 711.646 | 708.8631 | 711.2914 | 714.8004 | 715.1648 | 716.9933 | 714.9633 | 710.137 | 708.3607 | 706.0075 | 703.1774 | 704.5466 | 702.3651 | 700.2959 | 700.135 | 706.5241 | 705.8748 | 704.8234 | 707.772 | 714.6696 | 710.9446 | 711.9834
2025-04-09 23:17 | 9 | 23 | 17 | 6.2817e-272 | 1 | 29.3796 | 484.6479 | 0.26774 | 0.0073744 | 117.6647 | 117.6647 | 117.6647 | 117.6647 | 9.3642 | 11.9463 | 565.5877 | 565.5877 | 565.5877 | 565.5877 | 57.8272 | 50.0504 | 15.7472 | 49.0119 | 15.6015 | 10.2583 | 36.7934 | 0 | 50.0509 | 14.3478 | 22.1 | 221 | 154840 | 237681 | 3547371.8261 | 100.1008 | 0.0003316 | 0.0099478 | 0.0099478 | 0.0099478 | 7.9917 | 1105.2578 | 1076.5204 | 1076.5185 | 1075.2578 | 1141.9459 | 1141.9459 | 1141.9459 | 1141.9459 | 699.3351 | 699.3351 | 699.3351 | 2.086 | 0 | 2.0657 | 57.3604 | 168.0222 | 168.183 | 198.9721 | 1.4168 | 2.5615 | 0 | 62.9447 | 55.9733 | 57.8272 | 104.9813 | -4.9348 | 49.0119 | -1.0621 | 36.8561 | 63.5264 | 48.4317 | 0 | 66.808 | 688.1593 | 682.1269 | 663.1042 | 663.2012 | 646.4208 | 642.8475 | 401.0998 | 403.7662 | 662.529 | 666.5316 | 699.1939 | 710.9362 | 708.4989 | 710.8783 | 714.324 | 714.5282 | 716.6026 | 714.5482 | 709.5704 | 707.5587 | 705.1927 | 702.1467 | 703.2568 | 701.118 | 699.2263 | 699.0299 | 705.5683 | 704.4032 | 703.653 | 706.8292 | 713.8447 | 710.3521 | 711.3913
2025-04-09 23:18 | 9 | 23 | 18 | 6.2817e-272 | 1 | 29.3753 | 482.6635 | 0.26423 | 0.0073729 | 117.4697 | 117.4697 | 117.4697 | 117.4697 | 9.3517 | 11.9273 | 565.0269 | 565.0269 | 565.0269 | 565.0269 | 57.8788 | 50.0127 | 15.7501 | 48.7842 | 15.6007 | 10.2431 | 36.7716 | 0 | 50.013 | 15.1489 | 22.1 | 221 | 154840 | 237681 | 3547380 | 100.0254 | 0.0073407 | 0.22022 | 0.22022 | 0.22022 | 7.9917 | 1105.4847 | 1076.7547 | 1076.7519 | 1075.4847 | 1142.2419 | 1142.2419 | 1142.2419 | 1142.2419 | 698.7753 | 698.7753 | 698.7753 | 2.0945 | 0 | 2.1121 | 57.2174 | 167.732 | 167.8795 | 198.1641 | 1.378 | 2.5724 | 0 | 62.8921 | 55.8167 | 57.8788 | 105.0006 | -4.5356 | 48.7842 | -0.97267 | 36.8014 | 63.5587 | 48.4197 | 0 | 66.8086 | 685.8706 | 679.7659 | 661.2079 | 661.3697 | 644.5052 | 640.8588 | 400.662 | 403.4925 | 660.5677 | 664.5666 | 698.4809 | 710.3746 | 707.9579 | 710.3991 | 713.9099 | 714.1718 | 716.2479 | 714.1081 | 709.0595 | 707.0738 | 704.75 | 701.3177 | 702.8813 | 700.6677 | 698.7877 | 698.5334 | 704.9097 | 703.6146 | 702.8121 | 706.146 | 713.0767 | 709.6617 | 710.7908
2025-04-09 23:19 | 9 | 23 | 19 | 6.2817e-272 | 1 | 29.3728 | 464.0528 | 0.26608 | 0.0073676 | 116.5714 | 116.5714 | 116.5714 | 116.5714 | 9.2887 | 11.8483 | 563.1939 | 563.1939 | 563.1939 | 563.1939 | 57.9455 | 50.0702 | 15.7494 | 48.3855 | 15.5998 | 10.2154 | 36.6304 | 0 | 50.0701 | 13.7447 | 22.1 | 221 | 154840 | 237681 | 3547387.9787 | 100.1401 | 0.0035629 | 0.10689 | 0.10689 | 0.10689 | 7.9917 | 1106.6217 | 1077.9255 | 1077.9266 | 1076.6217 | 1142.7623 | 1142.7623 | 1142.7623 | 1142.7623 | 700.8518 | 700.8518 | 700.8518 | 2.0202 | 0 | 2.022 | 57.0324 | 166.602 | 166.7671 | 197.2089 | 1.3128 | 2.5294 | 0 | 62.2066 | 55.6383 | 57.9455 | 104.996 | -5.095 | 48.3855 | -1.0038 | 36.7019 | 63.5861 | 48.3958 | 0 | 66.8091 | 683.5342 | 677.4075 | 659.3011 | 659.4835 | 642.7764 | 639.122 | 400.0822 | 402.9557 | 659.3415 | 662.97 | 700.481 | 712.3313 | 709.5252 | 712.0922 | 715.6006 | 715.949 | 717.9821 | 715.9515 | 711.1476 | 709.3993 | 707.0157 | 703.6678 | 705.363 | 703.2467 | 700.9322 | 700.7488 | 706.8018 | 705.9951 | 705.0289 | 708.2373 | 715.1881 | 711.5926 | 712.8627
2025-04-09 23:20 | 9 | 23 | 20 | 6.2817e-272 | 1 | 29.3747 | 469.1441 | 0.26297 | 0.0073631 | 117.5839 | 117.5839 | 117.5839 | 117.5839 | 9.3599 | 11.9321 | 564.5494 | 564.5494 | 564.5494 | 564.5494 | 57.9231 | 50.0366 | 15.7494 | 49.3876 | 15.5994 | 10.3181 | 37.0692 | 0 | 50.037 | 14.7234 | 22.1 | 221 | 154840 | 237681 | 3547396.1277 | 100.0731 | -0.00098146 | -0.029444 | -0.029444 | -0.029444 | 7.9917 | 1105.3391 | 1076.6038 | 1076.6068 | 1075.3391 | 1141.4564 | 1141.4564 | 1141.4564 | 1141.4564 | 700.5703 | 700.5703 | 700.5703 | 2.0497 | 0 | 2.0525 | 57.5244 | 168.1008 | 168.2581 | 196.7924 | 1.3639 | 2.5544 | 0 | 62.8809 | 55.4853 | 57.9231 | 104.9962 | -4.8124 | 49.3876 | -0.96942 | 37.0708 | 63.5831 | 48.3802 | 0 | 66.8083 | 681.8423 | 675.8556 | 657.7764 | 657.8966 | 641.1329 | 637.4104 | 399.6548 | 402.6861 | 657.5184 | 661.2311 | 699.9087 | 712.2047 | 709.4146 | 712.056 | 715.5157 | 715.7498 | 717.8645 | 715.9085 | 710.829 | 709.0664 | 706.651 | 703.0705 | 704.96 | 702.7475 | 700.6829 | 700.1701 | 706.492 | 705.8125 | 704.7171 | 707.98 | 714.9025 | 711.3079 | 712.5111
2025-04-09 23:21 | 9 | 23 | 21 | 6.2817e-272 | 1 | 29.3777 | 468.1668 | 0.26709 | 0.007364 | 117.0027 | 117.0027 | 117.0027 | 117.0027 | 9.3179 | 11.8799 | 563.7675 | 563.7675 | 563.7675 | 563.7675 | 57.93 | 50.0575 | 15.751 | 48.6182 | 15.6016 | 10.2345 | 36.7186 | 0 | 50.0577 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3547404.2979 | 100.1148 | 0.0070107 | 0.21032 | 0.21032 | 0.21032 | 7.9917 | 1106.093 | 1077.3815 | 1077.3826 | 1076.093 | 1142.4585 | 1142.4585 | 1142.4585 | 1142.4585 | 699.6302 | 699.6302 | 699.6302 | 2.0344 | 0 | 2.022 | 57.2386 | 167.2528 | 167.4261 | 196.5324 | 1.3623 | 2.5531 | 0 | 62.4509 | 55.5344 | 57.93 | 105.0066 | -4.77 | 48.6182 | -1.0012 | 36.7705 | 63.5896 | 48.3865 | 0 | 66.8081 | 680.4225 | 674.514 | 656.3018 | 656.3671 | 639.7035 | 635.9144 | 399.2352 | 402.323 | 656.1312 | 659.7342 | 699.2279 | 711.4836 | 708.564 | 711.0035 | 714.4853 | 714.6809 | 716.8561 | 715.0265 | 709.7602 | 707.8297 | 705.6027 | 702.2221 | 703.8062 | 701.7413 | 699.8114 | 699.3953 | 705.6664 | 704.9423 | 703.7472 | 706.9088 | 713.9371 | 710.3359 | 711.6237
2025-04-09 23:22 | 9 | 23 | 22 | 6.2817e-272 | 1 | 29.3777 | 475.4739 | 0.26323 | 0.0073621 | 118.6263 | 118.6263 | 118.6263 | 118.6263 | 9.433 | 12.016 | 565.9793 | 565.9793 | 565.9793 | 565.9793 | 58.0005 | 49.9959 | 15.7496 | 50.2443 | 15.5968 | 10.4096 | 37.4295 | 0 | 49.9966 | 15.6596 | 22.1 | 221 | 154840 | 237681 | 3547412.5745 | 99.9918 | -0.0056645 | -0.16993 | -0.16993 | -0.16993 | 7.9917 | 1104.0202 | 1075.2438 | 1075.2451 | 1074.0202 | 1140.3402 | 1140.3402 | 1140.3402 | 1140.3402 | 699.8816 | 699.8816 | 699.8816 | 2.2012 | 0 | 2.2119 | 57.9703 | 169.5556 | 169.6949 | 196.4058 | 1.4102 | 2.6257 | 0 | 63.5998 | 55.5702 | 58.0005 | 104.9973 | -4.258 | 50.2443 | -1.0665 | 37.3996 | 63.6021 | 48.3791 | 0 | 66.8082 | 679.467 | 673.6437 | 655.0577 | 655.0815 | 638.3475 | 634.4649 | 398.9566 | 402.1125 | 654.3094 | 658.2757 | 699.2357 | 712.1953 | 709.466 | 711.9722 | 715.295 | 715.2437 | 717.3748 | 715.7731 | 710.1781 | 708.0413 | 705.689 | 701.9467 | 703.5637 | 701.4296 | 699.6091 | 699.1153 | 705.7923 | 705.0928 | 703.9 | 707.0425 | 714.1145 | 710.6326 | 712.0287
2025-04-09 23:23 | 9 | 23 | 23 | 6.2817e-272 | 1 | 29.3732 | 470.3044 | 0.26622 | 0.0073604 | 117.1543 | 117.1543 | 117.1543 | 117.1543 | 9.3299 | 11.8921 | 563.6325 | 563.6325 | 563.6325 | 563.6325 | 57.9465 | 50.0369 | 15.7484 | 48.9206 | 15.5982 | 10.2723 | 36.8519 | 0 | 50.0369 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3547420.7234 | 100.0737 | 0.010131 | 0.30392 | 0.30392 | 0.30392 | 7.9917 | 1105.877 | 1077.1594 | 1077.1579 | 1075.877 | 1142.0645 | 1142.0645 | 1142.0645 | 1142.0645 | 700.4173 | 700.4173 | 700.4173 | 2.0596 | 0 | 2.0623 | 57.3811 | 167.5191 | 167.6619 | 196.1575 | 1.3376 | 2.5622 | 0 | 62.5887 | 55.5796 | 57.9465 | 104.9893 | -4.3883 | 48.9206 | -1.011 | 36.9063 | 63.6045 | 48.3683 | 0 | 66.8086 | 678.2893 | 672.5185 | 653.6827 | 653.6834 | 637.1932 | 633.2439 | 398.451 | 401.6394 | 653.3354 | 657.1185 | 699.945 | 712.6272 | 709.6387 | 712.0343 | 715.513 | 715.4998 | 717.6601 | 716.1238 | 710.6607 | 708.6498 | 706.4016 | 702.8064 | 704.5174 | 702.444 | 700.5712 | 700.0611 | 706.1609 | 705.7035 | 704.3621 | 707.4916 | 714.5947 | 710.9488 | 712.378
2025-04-09 23:24 | 9 | 23 | 24 | 6.2817e-272 | 1 | 29.372 | 467.5068 | 0.26712 | 0.0073602 | 116.192 | 116.192 | 116.192 | 116.192 | 9.262 | 11.815 | 562.5186 | 562.5186 | 562.5186 | 562.5186 | 58.0353 | 50.0632 | 15.7482 | 48.1195 | 15.6 | 10.1905 | 36.5741 | 0 | 50.0637 | 13.4043 | 22.1 | 221 | 154840 | 237681 | 3547428.8085 | 100.1264 | -0.0005505 | -0.016515 | -0.016515 | -0.016515 | 7.9917 | 1107.1045 | 1078.4236 | 1078.4251 | 1077.1045 | 1143.1081 | 1143.1081 | 1143.1081 | 1143.1081 | 700.1621 | 700.1621 | 700.1621 | 2.0374 | 0 | 2.0306 | 56.9667 | 166.1817 | 166.3363 | 195.8566 | 1.3141 | 2.5227 | 0 | 61.9819 | 55.7245 | 58.0353 | 104.9878 | -4.4773 | 48.1195 | -1.0321 | 36.6125 | 63.5965 | 48.3667 | 0 | 66.8082 | 677.3058 | 671.5996 | 652.4569 | 652.4258 | 636.0604 | 632.1233 | 398.0619 | 401.4282 | 652.3191 | 655.9634 | 699.6832 | 712.2887 | 708.9693 | 711.3776 | 714.9278 | 715.03 | 717.2693 | 715.7057 | 710.3621 | 708.5919 | 706.3007 | 702.4931 | 704.471 | 702.4179 | 700.2658 | 699.8971 | 705.986 | 705.7598 | 704.2736 | 707.3696 | 714.3719 | 710.5801 | 712.0175
2025-04-09 23:25 | 9 | 23 | 25 | 6.2817e-272 | 1 | 29.3734 | 473.5743 | 0.27105 | 0.007363 | 117.7173 | 117.7173 | 117.7173 | 117.7173 | 9.3698 | 11.9378 | 564.9022 | 564.9022 | 564.9022 | 564.9022 | 58.0283 | 50.0552 | 15.7512 | 49.2969 | 15.6006 | 10.3002 | 36.9898 | 0 | 50.0554 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3547436.9787 | 100.1102 | 0.0013961 | 0.041883 | 0.041883 | 0.041883 | 7.9917 | 1105.1606 | 1076.42 | 1076.4177 | 1075.1606 | 1141.5747 | 1141.5747 | 1141.5747 | 1141.5747 | 699.6442 | 699.6442 | 699.6442 | 2.0317 | 0 | 2.0249 | 57.7207 | 168.3997 | 168.5595 | 195.6649 | 1.351 | 2.5647 | 0 | 62.8889 | 55.8172 | 58.0283 | 105.0077 | -4.5984 | 49.2969 | -0.99474 | 37.0067 | 63.6208 | 48.3792 | 0 | 66.8077 | 676.6584 | 670.7879 | 651.4048 | 651.4087 | 634.9717 | 631.0975 | 397.6665 | 401.261 | 651.247 | 654.617 | 698.8011 | 711.885 | 708.9687 | 711.3983 | 714.7238 | 714.6819 | 717.1432 | 715.5303 | 709.9345 | 707.729 | 705.2282 | 701.7462 | 703.4339 | 701.4935 | 699.7937 | 699.1466 | 705.4129 | 704.8596 | 703.7942 | 707.0922 | 713.994 | 710.3426 | 711.7493
2025-04-09 23:26 | 9 | 23 | 26 | 6.2817e-272 | 1 | 29.3741 | 469.3018 | 0.26794 | 0.0073671 | 116.521 | 116.521 | 116.521 | 116.521 | 9.2848 | 11.8435 | 563.3552 | 563.3552 | 563.3552 | 563.3552 | 58.0754 | 50.075 | 15.7482 | 48.3105 | 15.6011 | 10.2044 | 36.6035 | 0 | 50.0756 | 13.913 | 22.1 | 221 | 154840 | 237681 | 3547445.0217 | 100.1499 | -0.0024274 | -0.072823 | -0.072823 | -0.072823 | 7.9917 | 1106.6937 | 1077.9991 | 1077.9985 | 1076.6937 | 1142.8593 | 1142.8593 | 1142.8593 | 1142.8593 | 699.7792 | 699.7792 | 699.7792 | 2.0291 | 0 | 2.022 | 57.2148 | 166.7854 | 166.949 | 195.472 | 1.3414 | 2.5383 | 0 | 62.164 | 55.8903 | 58.0754 | 104.9879 | -4.7643 | 48.3105 | -0.99945 | 36.6626 | 63.6023 | 48.3951 | 0 | 66.8076 | 676.0107 | 669.8345 | 650.2051 | 650.4194 | 633.8793 | 630.1969 | 397.2258 | 400.9697 | 650.2456 | 653.3123 | 698.9975 | 711.7859 | 709.0608 | 711.403 | 714.5437 | 714.8018 | 717.1351 | 715.1657 | 709.9954 | 708.0541 | 705.4638 | 702.1107 | 703.908 | 702.0138 | 699.9933 | 699.5113 | 705.6733 | 704.8904 | 704.0528 | 707.1761 | 713.9318 | 710.3915 | 711.8484
2025-04-09 23:27 | 9 | 23 | 27 | 6.2817e-272 | 1 | 29.3742 | 469.5064 | 0.26981 | 0.0073676 | 116.5541 | 116.5541 | 116.5541 | 116.5541 | 9.2871 | 11.8434 | 563.3297 | 563.3297 | 563.3297 | 563.3297 | 58.1835 | 50.0825 | 15.7492 | 48.335 | 15.6011 | 10.2077 | 36.6199 | 0 | 50.0825 | 13.4894 | 22.1 | 221 | 154840 | 237681 | 3547453 | 100.1648 | 0.0053083 | 0.15925 | 0.15925 | 0.15925 | 7.9917 | 1106.6509 | 1077.9551 | 1077.956 | 1076.6509 | 1142.8274 | 1142.8274 | 1142.8274 | 1142.8274 | 699.8491 | 699.8491 | 699.8491 | 2.0332 | 0 | 2.022 | 57.2667 | 166.8331 | 166.9876 | 195.0668 | 1.3594 | 2.5489 | 0 | 62.1637 | 55.8479 | 58.1835 | 104.9944 | -4.8151 | 48.335 | -0.98598 | 36.6743 | 63.6321 | 48.3982 | 0 | 66.8078 | 675.3209 | 668.8367 | 649.0409 | 649.4645 | 632.8646 | 629.3528 | 396.8591 | 400.6763 | 649.3001 | 652.0705 | 698.994 | 711.6113 | 709.1542 | 711.4893 | 714.493 | 714.931 | 717.2762 | 715.051 | 710.2316 | 708.1887 | 705.4961 | 702.4395 | 704.0713 | 702.167 | 700.0187 | 699.6684 | 705.8123 | 704.7879 | 704.1809 | 707.2933 | 713.8376 | 710.4879 | 712.0034
2025-04-09 23:28 | 9 | 23 | 28 | 6.2817e-272 | 1 | 29.3763 | 473.177 | 0.26959 | 0.0073638 | 117.4751 | 117.4751 | 117.4751 | 117.4751 | 9.3518 | 11.9194 | 564.7888 | 564.7888 | 564.7888 | 564.7888 | 58.2786 | 50.0826 | 15.7495 | 49.3388 | 15.6002 | 10.3172 | 37.0352 | 0 | 50.0829 | 14.5957 | 22.1 | 221 | 154840 | 237681 | 3547461.1277 | 100.1649 | -0.0056603 | -0.16981 | -0.16981 | -0.16981 | 7.9917 | 1105.4864 | 1076.7557 | 1076.7589 | 1075.4864 | 1141.5198 | 1141.5198 | 1141.5198 | 1141.5198 | 700.4245 | 700.4245 | 700.4245 | 2.0356 | 0 | 2.0352 | 57.7307 | 168.1506 | 168.3047 | 194.8269 | 1.388 | 2.57 | 0 | 62.7254 | 55.871 | 58.2786 | 104.9968 | -4.8039 | 49.3388 | -0.98793 | 37.0678 | 63.627 | 48.3848 | 0 | 66.8072 | 674.9295 | 668.1614 | 648.0911 | 648.6661 | 631.8974 | 628.5756 | 396.4513 | 400.3854 | 648.3918 | 650.8266 | 699.345 | 712.0243 | 709.91 | 712.3131 | 715.0172 | 715.5513 | 717.9867 | 715.4191 | 710.8508 | 708.8072 | 705.8273 | 702.9296 | 704.6338 | 702.718 | 700.6813 | 700.0789 | 706.477 | 705.3599 | 704.9394 | 708.1698 | 714.4122 | 711.1758 | 712.692
2025-04-09 23:29 | 9 | 23 | 29 | 6.2817e-272 | 1 | 29.3764 | 474.0394 | 0.2686 | 0.0073651 | 117.6138 | 117.6138 | 117.6138 | 117.6138 | 9.3616 | 11.9314 | 564.921 | 564.921 | 564.921 | 564.921 | 58.2352 | 50.0714 | 15.749 | 49.4729 | 15.6003 | 10.3407 | 37.1053 | 0 | 50.0719 | 15.234 | 22.1 | 221 | 154840 | 237681 | 3547469.3191 | 100.1427 | -0.00086219 | -0.025865 | -0.025865 | -0.025865 | 7.9917 | 1105.3083 | 1076.5723 | 1076.574 | 1075.3083 | 1141.3451 | 1141.3451 | 1141.3451 | 1141.3451 | 700.9223 | 700.9223 | 700.9223 | 2.0728 | 0 | 2.0845 | 57.805 | 168.3905 | 168.5429 | 194.7063 | 1.4001 | 2.5767 | 0 | 62.8353 | 55.8792 | 58.2352 | 104.993 | -4.7049 | 49.4729 | -0.9691 | 37.1522 | 63.6127 | 48.3908 | 0 | 66.8071 | 674.4766 | 667.5931 | 647.1577 | 647.8707 | 631.0453 | 627.9008 | 396.0737 | 399.9685 | 647.4448 | 649.7864 | 699.8385 | 712.5991 | 710.8331 | 713.0631 | 715.5445 | 716.1289 | 718.4162 | 715.773 | 711.431 | 709.3084 | 706.197 | 703.5053 | 705.0616 | 703.1057 | 701.3371 | 700.6833 | 706.7017 | 705.4973 | 705.4688 | 708.531 | 714.8395 | 711.784 | 713.3421
2025-04-09 23:30 | 9 | 23 | 30 | 6.2817e-272 | 1 | 29.3779 | 473.0688 | 0.27161 | 0.007367 | 117.0336 | 117.0336 | 117.0336 | 117.0336 | 9.32 | 11.8831 | 564.3812 | 564.3812 | 564.3812 | 564.3812 | 58.3626 | 50.0475 | 15.7505 | 48.7193 | 15.6009 | 10.2438 | 36.7812 | 0 | 50.0472 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3547477.5532 | 100.0949 | 0.0063534 | 0.1906 | 0.1906 | 0.1906 | 7.9917 | 1106.0557 | 1077.3428 | 1077.3389 | 1076.0557 | 1142.3274 | 1142.3274 | 1142.3274 | 1142.3274 | 698.8991 | 698.8991 | 698.8991 | 2.0263 | 0 | 2.0223 | 57.4097 | 167.4471 | 167.6079 | 194.7632 | 1.4141 | 2.5722 | 0 | 62.538 | 55.9243 | 58.3626 | 105.0029 | -4.319 | 48.7193 | -1.0178 | 36.804 | 63.6182 | 48.4005 | 0 | 66.8072 | 674.0841 | 667.2581 | 646.3409 | 647.0568 | 630.3143 | 627.1627 | 395.7427 | 399.5823 | 646.5677 | 648.8714 | 697.4555 | 710.5205 | 708.5988 | 710.7426 | 713.5033 | 714.3174 | 716.6442 | 714.1396 | 709.6731 | 707.325 | 704.2566 | 701.2371 | 703.1203 | 700.9843 | 699.2723 | 698.433 | 704.87 | 703.47 | 703.3479 | 706.4215 | 712.6943 | 709.7452 | 711.1305
2025-04-09 23:31 | 9 | 23 | 31 | 6.2817e-272 | 1 | 29.377 | 471.7711 | 0.27002 | 0.0073674 | 116.7205 | 116.7205 | 116.7205 | 116.7205 | 9.2981 | 11.8535 | 563.6149 | 563.6149 | 563.6149 | 563.6149 | 58.3372 | 50.0585 | 15.7501 | 48.5745 | 15.5971 | 10.2432 | 36.7487 | 0 | 50.0585 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3547485.6596 | 100.1168 | 0.0092789 | 0.27837 | 0.27837 | 0.27837 | 7.9917 | 1106.4528 | 1077.7526 | 1077.7521 | 1076.4528 | 1142.5153 | 1142.5153 | 1142.5153 | 1142.5153 | 700.0253 | 700.0253 | 700.0253 | 2.0418 | 0 | 2.0267 | 57.3104 | 167.0198 | 167.1843 | 194.598 | 1.3953 | 2.5633 | 0 | 62.2965 | 55.9309 | 58.3372 | 105.0006 | -4.534 | 48.5745 | -1.0181 | 36.8019 | 63.6207 | 48.3993 | 0 | 66.8068 | 673.4552 | 666.7435 | 645.5637 | 646.1973 | 629.656 | 626.5139 | 395.2469 | 399.107 | 645.7972 | 648.1664 | 698.9407 | 711.7634 | 709.8086 | 711.7307 | 714.6434 | 715.2821 | 717.3969 | 715.0123 | 710.7675 | 708.2901 | 705.4096 | 702.5456 | 704.2147 | 702.0359 | 700.4247 | 699.6631 | 705.7916 | 704.8933 | 704.6455 | 707.5206 | 713.9728 | 710.8516 | 712.2661
2025-04-09 23:32 | 9 | 23 | 32 | 6.2817e-272 | 1 | 29.3779 | 474.5428 | 0.27157 | 0.00737 | 117.5 | 117.5 | 117.5 | 117.5 | 9.3531 | 11.9208 | 564.6699 | 564.6699 | 564.6699 | 564.6699 | 58.2912 | 50.0556 | 15.7502 | 49.3988 | 15.6 | 10.3473 | 37.1013 | 0 | 50.0565 | 14.3404 | 22.1 | 221 | 154840 | 237681 | 3547493.8085 | 100.1112 | -0.0087193 | -0.26158 | -0.26158 | -0.26158 | 7.9917 | 1105.4619 | 1076.7319 | 1076.7311 | 1075.4619 | 1141.4415 | 1141.4415 | 1141.4415 | 1141.4415 | 700.7052 | 700.7052 | 700.7052 | 2.0157 | 0 | 2.0432 | 57.7282 | 168.1815 | 168.3499 | 194.5468 | 1.4242 | 2.5802 | 0 | 62.7912 | 55.9134 | 58.2912 | 105.0009 | -4.4989 | 49.3988 | -1.0421 | 37.1759 | 63.6129 | 48.4113 | 0 | 66.8063 | 672.867 | 666.4883 | 644.934 | 645.4511 | 629.1353 | 625.8507 | 394.8369 | 398.5876 | 644.9101 | 647.5161 | 699.3758 | 712.6844 | 710.7002 | 712.6073 | 715.7037 | 716.1198 | 718.1383 | 715.9589 | 711.5685 | 708.9169 | 706.209 | 702.8315 | 704.7831 | 702.5466 | 701.1965 | 700.0413 | 706.0286 | 705.4257 | 705.2384 | 708.1041 | 714.816 | 711.6485 | 712.8963
2025-04-09 23:33 | 9 | 23 | 33 | 6.2817e-272 | 1 | 29.3778 | 474.2253 | 0.27025 | 0.0073728 | 117.1067 | 117.1067 | 117.1067 | 117.1067 | 9.3252 | 11.8889 | 564.2516 | 564.2516 | 564.2516 | 564.2516 | 58.1808 | 50.0564 | 15.7523 | 48.7667 | 15.6003 | 10.2459 | 36.8046 | 0 | 50.057 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3547502 | 100.1127 | 0.0051572 | 0.15472 | 0.15472 | 0.15472 | 7.9917 | 1105.9619 | 1077.2457 | 1077.244 | 1075.9619 | 1142.2647 | 1142.2647 | 1142.2647 | 1142.2647 | 699.1235 | 699.1235 | 699.1235 | 2.0253 | 0 | 2.0298 | 57.5038 | 167.5983 | 167.7522 | 194.6628 | 1.4003 | 2.5792 | 0 | 62.5423 | 55.9053 | 58.1808 | 105.0154 | -4.6114 | 48.7667 | -0.99831 | 36.8115 | 63.635 | 48.4237 | 0 | 66.8059 | 672.4592 | 666.3723 | 644.4366 | 644.8001 | 628.6559 | 625.226 | 394.3266 | 398.1577 | 644.0963 | 646.8644 | 698.0992 | 711.1696 | 708.9632 | 710.889 | 714.2203 | 714.557 | 716.4842 | 714.6678 | 709.8401 | 707.2004 | 704.7746 | 701.3586 | 703.1958 | 700.7423 | 699.4613 | 698.4406 | 704.4851 | 703.8867 | 703.5184 | 706.4287 | 713.3544 | 710.0606 | 711.0896
2025-04-09 23:34 | 9 | 23 | 34 | 6.2817e-272 | 1 | 29.3763 | 475.1177 | 0.27139 | 0.0073812 | 117.317 | 117.317 | 117.317 | 117.317 | 9.3405 | 11.9046 | 563.9695 | 563.9695 | 563.9695 | 563.9695 | 58.0641 | 50.0492 | 15.7504 | 49.2843 | 15.6004 | 10.3115 | 37.0015 | 0 | 50.0497 | 14.3478 | 22.1 | 221 | 154840 | 237681 | 3547510.1087 | 100.0984 | -0.0055845 | -0.16754 | -0.16754 | -0.16754 | 7.9917 | 1105.6859 | 1076.962 | 1076.9622 | 1075.6859 | 1141.5907 | 1141.5907 | 1141.5907 | 1141.5907 | 700.2894 | 700.2894 | 700.2894 | 2.0148 | 0 | 2.0297 | 57.6353 | 167.9123 | 168.0681 | 194.6558 | 1.3694 | 2.5722 | 0 | 62.6646 | 55.8174 | 58.0641 | 105.0029 | -4.847 | 49.2843 | -1.0276 | 37.0473 | 63.61 | 48.4557 | 0 | 66.8057 | 672.065 | 666.1476 | 643.8871 | 644.0677 | 628.2442 | 624.6228 | 393.8713 | 397.8299 | 643.4127 | 646.3603 | 699.4225 | 712.5999 | 710.1087 | 712.1823 | 715.5729 | 715.6494 | 717.4534 | 715.8304 | 710.8695 | 708.4221 | 706.06 | 702.5402 | 704.2282 | 701.7863 | 700.4681 | 699.5434 | 705.5228 | 705.2921 | 704.5277 | 707.6445 | 714.727 | 711.1048 | 712.2373
2025-04-09 23:35 | 9 | 23 | 35 | 6.2817e-272 | 1 | 29.3785 | 475.2199 | 0.26887 | 0.0073888 | 117.4317 | 117.4317 | 117.4317 | 117.4317 | 9.348 | 11.9193 | 564.0888 | 564.0888 | 564.0888 | 564.0888 | 57.8881 | 50.0487 | 15.7502 | 49.4391 | 15.6018 | 10.3311 | 37.1173 | 0 | 50.0485 | 14.2979 | 22.1 | 221 | 154840 | 237681 | 3547518.1915 | 100.0973 | 0.011615 | 0.34846 | 0.34846 | 0.34846 | 7.9917 | 1105.5521 | 1076.8238 | 1076.8272 | 1075.5521 | 1141.3891 | 1141.3891 | 1141.3891 | 1141.3891 | 700.6463 | 700.6463 | 700.6463 | 2.0543 | 0 | 2.0418 | 57.6261 | 167.9956 | 168.1523 | 194.7423 | 1.4112 | 2.5746 | 0 | 62.7564 | 55.8244 | 57.8881 | 105.0012 | -5.0427 | 49.4391 | -1.0353 | 37.1176 | 63.6054 | 48.4881 | 0 | 66.8056 | 671.6552 | 666.0703 | 643.4841 | 643.4977 | 627.9032 | 624.0729 | 393.2784 | 397.5772 | 642.7606 | 645.9131 | 699.9482 | 712.967 | 710.1373 | 712.4488 | 715.9593 | 715.789 | 717.6196 | 716.2953 | 711.079 | 708.8438 | 706.5251 | 702.974 | 704.6084 | 702.1057 | 700.7743 | 699.9001 | 705.8486 | 705.957 | 704.877 | 707.997 | 715.1849 | 711.3821 | 712.503
2025-04-09 23:36 | 9 | 23 | 36 | 6.2817e-272 | 1 | 29.378 | 473.5614 | 0.26986 | 0.0073909 | 116.8035 | 116.8035 | 116.8035 | 116.8035 | 9.3037 | 11.868 | 563.4162 | 563.4162 | 563.4162 | 563.4162 | 57.7468 | 50.0523 | 15.7492 | 48.6349 | 15.6022 | 10.2284 | 36.7224 | 0 | 50.0523 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3547526.4043 | 100.1045 | 0.0051171 | 0.15351 | 0.15351 | 0.15351 | 7.9917 | 1106.3509 | 1077.646 | 1077.6436 | 1076.3509 | 1142.4364 | 1142.4364 | 1142.4364 | 1142.4364 | 699.039 | 699.039 | 699.039 | 2.021 | 0 | 2.0221 | 57.3824 | 167.1901 | 167.3388 | 194.8425 | 1.3934 | 2.5611 | 0 | 62.3595 | 55.7809 | 57.7468 | 104.9949 | -4.9843 | 48.6349 | -1.0149 | 36.7486 | 63.6135 | 48.4964 | 0 | 66.8057 | 671.3586 | 665.99 | 643.0777 | 642.9349 | 627.5638 | 623.5744 | 392.9006 | 397.2599 | 642.1995 | 645.4882 | 698.4732 | 711.5126 | 708.4403 | 710.6748 | 714.4329 | 714.2329 | 716.0126 | 714.8754 | 709.2403 | 707.071 | 704.9941 | 701.3032 | 702.9916 | 700.475 | 699.038 | 698.4357 | 704.2501 | 704.2231 | 703.0659 | 706.3609 | 713.6516 | 709.8247 | 710.7318
2025-04-09 23:37 | 9 | 23 | 37 | 6.2817e-272 | 1 | 29.3775 | 475.2101 | 0.27355 | 0.0073953 | 117.6569 | 117.6569 | 117.6569 | 117.6569 | 9.3643 | 11.9414 | 564.675 | 564.675 | 564.675 | 564.675 | 57.7527 | 50.0528 | 15.7503 | 49.5946 | 15.5984 | 10.3508 | 37.144 | 0 | 50.0532 | 14 | 22.1 | 221 | 154840 | 237681 | 3547534.5957 | 100.1055 | -0.002635 | -0.079049 | -0.079049 | -0.079049 | 7.9917 | 1105.2598 | 1076.5228 | 1076.5219 | 1075.2598 | 1141.1868 | 1141.1868 | 1141.1868 | 1141.1868 | 700.629 | 700.629 | 700.629 | 2.018 | 0 | 2.0261 | 57.8151 | 168.3969 | 168.5554 | 194.8084 | 1.4142 | 2.5812 | 0 | 62.8994 | 55.6989 | 57.7527 | 105.0016 | -4.9544 | 49.5946 | -1.0295 | 37.1885 | 63.61 | 48.5128 | 0 | 66.8054 | 671.1243 | 665.9111 | 642.7297 | 642.51 | 627.3044 | 623.2123 | 392.5487 | 396.944 | 641.8251 | 645.0681 | 700.1002 | 713.1112 | 710.0462 | 712.5069 | 716.2461 | 715.8399 | 717.451 | 716.4401 | 710.8248 | 708.8373 | 706.6562 | 702.754 | 704.5885 | 701.9917 | 700.6763 | 699.9404 | 705.6419 | 706.0453 | 704.6063 | 707.9883 | 715.3231 | 711.2873 | 712.1605
2025-04-09 23:38 | 9 | 23 | 38 | 6.2817e-272 | 1 | 29.3783 | 473.9341 | 0.27349 | 0.0073951 | 117.2188 | 117.2188 | 117.2188 | 117.2188 | 9.333 | 11.9084 | 564.3239 | 564.3239 | 564.3239 | 564.3239 | 57.9919 | 50.0629 | 15.7518 | 48.9881 | 15.6019 | 10.292 | 36.8943 | 0 | 50.063 | 14 | 22.1 | 221 | 154840 | 237681 | 3547542.7872 | 100.1256 | 0.00034443 | 0.010333 | 0.010333 | 0.010333 | 7.9917 | 1105.8262 | 1077.106 | 1077.1038 | 1075.8262 | 1141.977 | 1141.977 | 1141.977 | 1141.977 | 699.8529 | 699.8529 | 699.8529 | 2.0398 | 0 | 2.0325 | 57.5948 | 167.7814 | 167.9334 | 195.0587 | 1.4205 | 2.5762 | 0 | 62.6557 | 55.7774 | 57.9919 | 105.0119 | -4.9445 | 48.9881 | -1.0305 | 36.9771 | 63.6183 | 48.5132 | 0 | 66.8051 | 671.205 | 665.9904 | 642.4475 | 642.1786 | 627.0293 | 622.9556 | 392.184 | 396.7179 | 641.4765 | 644.6808 | 699.3209 | 712.3184 | 708.9938 | 711.4759 | 715.2903 | 714.9367 | 716.7979 | 715.8151 | 710.0499 | 708.1272 | 706.0989 | 701.9255 | 703.9297 | 701.4244 | 699.7649 | 699.2694 | 704.8997 | 705.2366 | 703.7051 | 707.1436 | 714.512 | 710.5107 | 711.5237
2025-04-09 23:39 | 9 | 23 | 39 | 6.2817e-272 | 1 | 29.379 | 474.3333 | 0.27307 | 0.007395 | 117.426 | 117.426 | 117.426 | 117.426 | 9.3475 | 11.9235 | 564.7788 | 564.7788 | 564.7788 | 564.7788 | 58.1297 | 50.0714 | 15.7527 | 49.0839 | 15.6013 | 10.3011 | 36.9342 | 0 | 50.0715 | 13.9149 | 22.1 | 221 | 154840 | 237681 | 3547550.9787 | 100.1428 | -5.959e-05 | -0.0017883 | -0.0017883 | -0.0017883 | 7.9917 | 1105.5602 | 1076.8306 | 1076.8319 | 1075.5602 | 1141.8511 | 1141.8511 | 1141.8511 | 1141.8511 | 699.3701 | 699.3701 | 699.3701 | 2.037 | 0 | 2.0301 | 57.7092 | 168.0904 | 168.25 | 195.1248 | 1.4539 | 2.5877 | 0 | 62.7708 | 55.8052 | 58.1297 | 105.0181 | -5.0878 | 49.0839 | -0.99507 | 37.01 | 63.6088 | 48.5141 | 0 | 66.8047 | 671.3115 | 666.036 | 642.2463 | 641.9228 | 626.8132 | 622.7279 | 391.8836 | 396.5394 | 641.2588 | 644.3756 | 698.7706 | 711.9906 | 708.695 | 711.3098 | 714.9483 | 714.5446 | 716.5554 | 715.3694 | 709.4647 | 707.4767 | 705.4222 | 701.374 | 703.1921 | 700.8587 | 699.1736 | 698.7076 | 704.6013 | 704.5705 | 702.978 | 706.6649 | 714.0789 | 710.1056 | 711.2389
2025-04-09 23:40 | 9 | 23 | 40 | 6.2817e-272 | 1 | 29.3785 | 475.0643 | 0.27843 | 0.0073984 | 117.7638 | 117.7638 | 117.7638 | 117.7638 | 9.3716 | 11.9514 | 565.2918 | 565.2918 | 565.2918 | 565.2918 | 58.2557 | 50.0867 | 15.7488 | 49.7019 | 15.5992 | 10.3751 | 37.2225 | 0 | 50.0874 | 14.9787 | 22.1 | 221 | 154840 | 237681 | 3547559.1702 | 100.1731 | -0.0053693 | -0.16108 | -0.16108 | -0.16108 | 7.9917 | 1105.1319 | 1076.3902 | 1076.3955 | 1075.1319 | 1141.0468 | 1141.0468 | 1141.0468 | 1141.0468 | 701.122 | 701.122 | 701.122 | 2.0335 | 0 | 2.0568 | 57.9016 | 168.5485 | 168.7099 | 195.2122 | 1.4401 | 2.5855 | 0 | 62.9522 | 55.8318 | 58.2557 | 104.9918 | -5.4682 | 49.7019 | -0.98987 | 37.2758 | 63.6212 | 48.5266 | 0 | 66.8043 | 671.4011 | 666.0528 | 642.0323 | 641.7464 | 626.6935 | 622.6305 | 391.7423 | 396.3757 | 641.0131 | 644.1195 | 700.4493 | 713.6487 | 710.3581 | 712.9398 | 716.6796 | 716.311 | 718.2435 | 717.0241 | 711.3457 | 709.353 | 707.294 | 703.0722 | 705.0906 | 702.7243 | 701.094 | 700.3251 | 706.3027 | 706.5427 | 704.8651 | 708.4565 | 715.8506 | 711.7364 | 712.8776
2025-04-09 23:41 | 9 | 23 | 41 | 6.2817e-272 | 1 | 29.3805 | 474.8696 | 0.27322 | 0.0073976 | 117.4872 | 117.4872 | 117.4872 | 117.4872 | 9.3514 | 11.9271 | 565.2583 | 565.2583 | 565.2583 | 565.2583 | 58.5274 | 50.0692 | 15.7517 | 49.1429 | 15.5999 | 10.3081 | 36.9638 | 0 | 50.0696 | 14.1277 | 22.1 | 221 | 154840 | 237681 | 3547567.4043 | 100.1382 | -0.0012483 | -0.037451 | -0.037451 | -0.037451 | 7.9917 | 1105.4896 | 1076.7587 | 1076.7572 | 1075.4896 | 1141.7751 | 1141.7751 | 1141.7751 | 1141.7751 | 699.839 | 699.839 | 699.839 | 2.0414 | 0 | 2.0324 | 57.7217 | 168.1661 | 168.3143 | 195.4253 | 1.4417 | 2.5826 | 0 | 62.8334 | 55.901 | 58.5274 | 105.011 | -5.2551 | 49.1429 | -0.97169 | 37.0349 | 63.6197 | 48.5246 | 0 | 66.8043 | 671.529 | 666.1972 | 641.902 | 641.6676 | 626.4946 | 622.4923 | 391.5923 | 396.2547 | 640.9178 | 643.8578 | 699.1342 | 712.3246 | 709.0873 | 711.5654 | 715.5501 | 715.2089 | 717.1733 | 716.0536 | 710.1566 | 707.8977 | 705.9703 | 701.8186 | 703.8403 | 701.3402 | 699.6975 | 698.9386 | 704.9512 | 705.0533 | 703.601 | 707.0479 | 714.4894 | 710.5504 | 711.6591
2025-04-09 23:42 | 9 | 23 | 42 | 6.2817e-272 | 1 | 29.3834 | 476.2386 | 0.26912 | 0.0073935 | 117.7692 | 117.7692 | 117.7692 | 117.7692 | 9.3705 | 11.954 | 566.2589 | 566.2589 | 566.2589 | 566.2589 | 58.8229 | 50.061 | 15.7499 | 49.4572 | 15.6001 | 10.3405 | 37.1027 | 0 | 50.0614 | 14.1739 | 22.1 | 221 | 154840 | 237681 | 3547575.5652 | 100.1219 | -0.0024837 | -0.07451 | -0.07451 | -0.07451 | 7.9917 | 1105.1474 | 1076.4061 | 1076.4052 | 1075.1474 | 1141.3654 | 1141.3654 | 1141.3654 | 1141.3654 | 700.0041 | 700.0041 | 700.0041 | 2.0651 | 0 | 2.0497 | 57.8454 | 168.5634 | 168.71 | 195.5245 | 1.481 | 2.5967 | 0 | 63.0761 | 56.0241 | 58.8229 | 104.999 | -5.1011 | 49.4572 | -1.0071 | 37.1515 | 63.6087 | 48.5124 | 0 | 66.804 | 671.6203 | 666.2672 | 641.7058 | 641.5123 | 626.329 | 622.3433 | 391.388 | 396.0548 | 640.63 | 643.5605 | 699.2952 | 712.5037 | 709.4155 | 711.7665 | 715.7043 | 715.4321 | 717.3474 | 716.2072 | 710.3588 | 708.0648 | 706.1857 | 701.9205 | 703.9858 | 701.4112 | 699.823 | 698.8739 | 705.0299 | 705.1816 | 703.8925 | 707.1754 | 714.6679 | 710.7526 | 711.803
2025-04-09 23:43 | 9 | 23 | 43 | 6.2817e-272 | 1 | 29.3855 | 475.0314 | 0.27467 | 0.0073974 | 117.3922 | 117.3922 | 117.3922 | 117.3922 | 9.3432 | 11.9275 | 566.3998 | 566.3998 | 566.3998 | 566.3998 | 59.0582 | 50.0715 | 15.7503 | 49.0066 | 15.5988 | 10.28 | 36.9037 | 0 | 50.0719 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3547583.6809 | 100.1427 | -0.001115 | -0.033452 | -0.033452 | -0.033452 | 7.9917 | 1105.6377 | 1076.9121 | 1076.9115 | 1075.6377 | 1141.9526 | 1141.9526 | 1141.9526 | 1141.9526 | 699.6858 | 699.6858 | 699.6858 | 2.0326 | 0 | 2.0272 | 57.6866 | 168.0496 | 168.2121 | 195.7033 | 1.506 | 2.604 | 0 | 62.8823 | 56.3135 | 59.0582 | 105.0018 | -5.224 | 49.0066 | -1.0171 | 36.9339 | 63.6156 | 48.5297 | 0 | 66.8038 | 671.7695 | 666.3744 | 641.5584 | 641.3408 | 626.1562 | 622.1856 | 391.0566 | 395.7266 | 640.4972 | 643.2658 | 699.0033 | 712.1746 | 708.8804 | 711.2197 | 715.2317 | 715.0103 | 716.9438 | 715.781 | 709.9256 | 707.6901 | 705.8405 | 701.6308 | 703.7722 | 701.385 | 699.4926 | 698.5559 | 704.8723 | 704.9149 | 703.508 | 706.8736 | 714.4155 | 710.4164 | 711.5523
2025-04-09 23:44 | 9 | 23 | 44 | 6.2817e-272 | 1 | 29.3861 | 475.8788 | 0.27351 | 0.0074009 | 117.5083 | 117.5083 | 117.5083 | 117.5083 | 9.3513 | 11.9338 | 566.4283 | 566.4283 | 566.4283 | 566.4283 | 59.2696 | 50.0688 | 15.7516 | 49.1561 | 15.601 | 10.3013 | 36.9679 | 0 | 50.0692 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3547591.8936 | 100.1373 | -0.0044493 | -0.13348 | -0.13348 | -0.13348 | 7.9917 | 1105.4923 | 1076.7632 | 1076.7638 | 1075.4923 | 1141.7579 | 1141.7579 | 1141.7579 | 1141.7579 | 700.2119 | 700.2119 | 700.2119 | 2.0671 | 0 | 2.0453 | 57.7378 | 168.197 | 168.3573 | 195.7774 | 1.4861 | 2.6015 | 0 | 62.9521 | 56.4278 | 59.2696 | 105.0106 | -5.2614 | 49.1561 | -1.0058 | 37.0107 | 63.6104 | 48.545 | 0 | 66.8039 | 671.7839 | 666.362 | 641.4169 | 641.079 | 625.9746 | 621.9214 | 390.6871 | 395.5661 | 640.2166 | 642.9417 | 699.5138 | 712.9696 | 709.7037 | 711.924 | 716.0383 | 715.5817 | 717.5774 | 716.2757 | 710.3547 | 708.0546 | 706.3696 | 701.9792 | 704.1452 | 701.77 | 700.0074 | 699.0418 | 705.1787 | 705.3338 | 703.9309 | 707.382 | 715.0486 | 711.0177 | 712.2659
2025-04-09 23:45 | 9 | 23 | 45 | 6.2817e-272 | 1 | 29.3842 | 474.7086 | 0.27351 | 0.0074037 | 117.0761 | 117.0761 | 117.0761 | 117.0761 | 9.3212 | 11.8968 | 565.8341 | 565.8341 | 565.8341 | 565.8341 | 59.2789 | 50.0916 | 15.7521 | 48.7867 | 15.6007 | 10.266 | 36.8319 | 0 | 50.0921 | 13.7447 | 22.1 | 221 | 154840 | 237681 | 3547600 | 100.183 | -0.00011389 | -0.0034167 | -0.0034167 | -0.0034167 | 7.9917 | 1106.0353 | 1077.3217 | 1077.324 | 1076.0353 | 1142.2385 | 1142.2385 | 1142.2385 | 1142.2385 | 700.0209 | 700.0209 | 700.0209 | 2.0036 | 0 | 2.0283 | 57.6117 | 167.6384 | 167.7956 | 195.7605 | 1.4268 | 2.5768 | 0 | 62.6419 | 56.4274 | 59.2789 | 105.014 | -5.5087 | 48.7867 | -1.0337 | 36.8837 | 63.6028 | 48.5539 | 0 | 66.8034 | 671.6444 | 666.2883 | 641.2115 | 640.815 | 625.8267 | 621.7193 | 390.2978 | 395.166 | 639.7419 | 642.6621 | 699.4538 | 712.8114 | 709.3353 | 711.5949 | 715.7711 | 715.3322 | 717.294 | 716.1557 | 710.2969 | 708.0433 | 706.3096 | 701.9204 | 704.0166 | 701.5231 | 699.6217 | 698.9778 | 704.9542 | 705.2421 | 703.6971 | 707.053 | 714.8702 | 710.7728 | 711.9903
2025-04-09 23:46 | 9 | 23 | 46 | 6.2817e-272 | 1 | 29.3843 | 475.0732 | 0.2756 | 0.0074023 | 117.115 | 117.115 | 117.115 | 117.115 | 9.3239 | 11.9028 | 566.017 | 566.017 | 566.017 | 566.017 | 59.1325 | 50.0956 | 15.7528 | 48.6598 | 15.6016 | 10.2486 | 36.7439 | 0 | 50.0962 | 14.2979 | 22.1 | 221 | 154840 | 237681 | 3547608.1702 | 100.191 | 0.0017476 | 0.05243 | 0.05243 | 0.05243 | 7.9917 | 1105.9817 | 1077.266 | 1077.2679 | 1075.9817 | 1142.4045 | 1142.4045 | 1142.4045 | 1142.4045 | 699.3923 | 699.3923 | 699.3923 | 2.0272 | 0 | 2.0452 | 57.5852 | 167.6769 | 167.8386 | 195.7135 | 1.4337 | 2.5827 | 0 | 62.6596 | 56.4818 | 59.1325 | 105.0182 | -5.4935 | 48.6598 | -0.98176 | 36.8214 | 63.606 | 48.5472 | 0 | 66.8035 | 671.6032 | 666.2191 | 640.9768 | 640.594 | 625.6151 | 621.4553 | 389.9457 | 394.9065 | 639.3905 | 642.3117 | 698.8347 | 712.1273 | 708.8137 | 711.0192 | 715.1844 | 714.7033 | 716.5936 | 715.4599 | 709.4236 | 707.167 | 705.6691 | 701.3802 | 703.3917 | 700.877 | 698.971 | 698.2196 | 704.4386 | 704.618 | 703.1944 | 706.4029 | 714.2582 | 710.2049 | 711.2916
2025-04-09 23:47 | 9 | 23 | 47 | 6.2817e-272 | 1 | 29.3859 | 473.369 | 0.27603 | 0.0074048 | 116.854 | 116.854 | 116.854 | 116.854 | 9.3049 | 11.8772 | 565.0809 | 565.0809 | 565.0809 | 565.0809 | 58.9678 | 50.1055 | 15.7523 | 48.6629 | 15.6009 | 10.2502 | 36.7715 | 0 | 50.106 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3547616.234 | 100.2107 | -0.0036873 | -0.11062 | -0.11062 | -0.11062 | 7.9917 | 1106.3277 | 1077.6226 | 1077.6251 | 1076.3277 | 1142.3998 | 1142.3998 | 1142.3998 | 1142.3998 | 700.3449 | 700.3449 | 700.3449 | 2.0042 | 0 | 2.022 | 57.5448 | 167.392 | 167.5591 | 195.4463 | 1.421 | 2.5597 | 0 | 62.4392 | 56.3231 | 58.9678 | 105.0153 | -5.5894 | 48.6629 | -0.96974 | 36.8268 | 63.6251 | 48.5604 | 0 | 66.8034 | 671.2696 | 665.8564 | 640.575 | 640.2519 | 625.2956 | 621.2221 | 389.5289 | 394.5439 | 639.0911 | 641.9426 | 699.968 | 712.8969 | 709.5506 | 711.8047 | 715.9802 | 715.6257 | 717.4181 | 716.2013 | 710.5759 | 708.4042 | 706.7455 | 702.4807 | 704.5472 | 702.0386 | 700.1281 | 699.4576 | 705.2819 | 705.5756 | 704.1234 | 707.3374 | 715.0523 | 711.0241 | 712.1764
2025-04-09 23:48 | 9 | 23 | 48 | 6.2817e-272 | 1 | 29.3849 | 476.0647 | 0.27439 | 0.0074032 | 117.7036 | 117.7036 | 117.7036 | 117.7036 | 9.3655 | 11.9487 | 566.1874 | 566.1874 | 566.1874 | 566.1874 | 58.839 | 50.085 | 15.7513 | 49.3744 | 15.5988 | 10.3481 | 37.0807 | 0 | 50.0851 | 14.3404 | 22.1 | 221 | 154840 | 237681 | 3547624.4043 | 100.1698 | 0.0069714 | 0.20914 | 0.20914 | 0.20914 | 7.9917 | 1105.2383 | 1076.5009 | 1076.5002 | 1075.2383 | 1141.473 | 1141.473 | 1141.473 | 1141.473 | 700.4277 | 700.4277 | 700.4277 | 2.0554 | 0 | 2.0495 | 57.8838 | 168.5577 | 168.7181 | 195.368 | 1.4507 | 2.5955 | 0 | 62.9899 | 56.2203 | 58.839 | 105.0088 | -5.5396 | 49.3744 | -0.98695 | 37.1788 | 63.6267 | 48.5521 | 0 | 66.8025 | 671.1921 | 665.6698 | 640.2711 | 640.0944 | 624.9318 | 620.9909 | 389.2259 | 394.3372 | 638.9541 | 641.4536 | 699.7433 | 713.0064 | 710.0761 | 712.3669 | 716.3013 | 715.9598 | 717.8119 | 716.4252 | 710.6922 | 708.4188 | 706.4167 | 702.3186 | 704.299 | 701.7727 | 700.2328 | 699.3831 | 705.3322 | 705.5238 | 704.3069 | 707.5969 | 715.1752 | 711.3246 | 712.367
2025-04-09 23:49 | 9 | 23 | 49 | 6.2817e-272 | 1 | 29.3851 | 473.0399 | 0.27412 | 0.0073994 | 116.5402 | 116.5402 | 116.5402 | 116.5402 | 9.2829 | 11.8544 | 564.743 | 564.743 | 564.743 | 564.743 | 58.8606 | 50.1266 | 15.7511 | 48.2267 | 15.6018 | 10.2105 | 36.5921 | 0 | 50.127 | 13.2766 | 22.1 | 221 | 154840 | 237681 | 3547632.5532 | 100.2533 | -0.00023837 | -0.0071513 | -0.0071513 | -0.0071513 | 7.9917 | 1106.7257 | 1078.033 | 1078.0313 | 1076.7257 | 1142.9683 | 1142.9683 | 1142.9683 | 1142.9683 | 699.4593 | 699.4593 | 699.4593 | 2.006 | 0 | 2.0225 | 57.3824 | 166.9381 | 167.0846 | 195.3243 | 1.4173 | 2.5564 | 0 | 62.2262 | 56.1252 | 58.8606 | 105.0074 | -5.8809 | 48.2267 | -1.0308 | 36.6842 | 63.6235 | 48.5375 | 0 | 66.8022 | 671.0699 | 665.445 | 639.9246 | 639.983 | 624.6005 | 620.8538 | 388.9626 | 394.0504 | 638.3736 | 641.1273 | 698.7156 | 711.95 | 708.8471 | 711.0287 | 714.859 | 714.913 | 716.6829 | 715.2625 | 709.7781 | 707.6243 | 705.5851 | 701.5789 | 703.7487 | 701.1313 | 699.4272 | 698.6113 | 704.3809 | 704.4124 | 703.312 | 706.5357 | 714.0457 | 710.3305 | 711.3423
2025-04-09 23:50 | 9 | 23 | 50 | 6.2817e-272 | 1 | 29.3848 | 476.9444 | 0.2788 | 0.007395 | 117.7371 | 117.7371 | 117.7371 | 117.7371 | 9.3679 | 11.9537 | 566.6784 | 566.6784 | 566.6784 | 566.6784 | 58.9487 | 50.1484 | 15.7536 | 49.1039 | 15.6006 | 10.3213 | 36.9435 | 0 | 50.1489 | 14.5652 | 22.1 | 221 | 154840 | 237681 | 3547640.5652 | 100.297 | 0.006693 | 0.20079 | 0.20079 | 0.20079 | 7.9917 | 1105.1902 | 1076.4513 | 1076.452 | 1075.1902 | 1141.8252 | 1141.8252 | 1141.8252 | 1141.8252 | 700.164 | 700.164 | 700.164 | 2.0796 | 0 | 2.05 | 57.9784 | 168.6862 | 168.8451 | 195.1192 | 1.4295 | 2.5992 | 0 | 62.9123 | 56.1838 | 58.9487 | 105.0241 | -6.4987 | 49.1039 | -1.0024 | 37.0823 | 63.6202 | 48.5189 | 0 | 66.8023 | 670.9602 | 665.2705 | 639.7072 | 640.0004 | 624.2854 | 620.7954 | 388.7345 | 393.9022 | 637.9374 | 640.7209 | 699.3359 | 712.5332 | 709.9427 | 711.9697 | 715.5183 | 715.7713 | 717.4545 | 716.0261 | 710.7349 | 708.1499 | 706.046 | 702.6828 | 704.322 | 701.4629 | 700.0861 | 699.1634 | 705.1816 | 705.06 | 704.2871 | 707.2922 | 714.6385 | 711.2758 | 712.0523
2025-04-09 23:51 | 9 | 23 | 51 | 6.2817e-272 | 1 | 29.3853 | 473.7013 | 0.27425 | 0.0073929 | 116.8001 | 116.8001 | 116.8001 | 116.8001 | 9.3013 | 11.8726 | 565.2189 | 565.2189 | 565.2189 | 565.2189 | 58.9543 | 50.168 | 15.7523 | 48.4902 | 15.6005 | 10.2452 | 36.6888 | 0 | 50.1682 | 13.7447 | 22.1 | 221 | 154840 | 237681 | 3547648.617 | 100.336 | 0.0026706 | 0.080119 | 0.080119 | 0.080119 | 7.9917 | 1106.3962 | 1077.6949 | 1077.6902 | 1076.3962 | 1142.6255 | 1142.6255 | 1142.6255 | 1142.6255 | 699.6486 | 699.6486 | 699.6486 | 1.9935 | 0 | 2.022 | 57.6272 | 167.4067 | 167.5579 | 195.0057 | 1.4257 | 2.5687 | 0 | 62.2922 | 56.1919 | 58.9543 | 105.0151 | -6.796 | 48.4902 | -1.0438 | 36.809 | 63.6317 | 48.5119 | 0 | 66.8021 | 670.7904 | 665.0682 | 639.4356 | 639.935 | 624.0132 | 620.7368 | 388.579 | 393.5252 | 637.6115 | 640.4186 | 698.766 | 711.9412 | 709.458 | 711.2649 | 714.8433 | 715.3877 | 716.6538 | 715.0813 | 710.182 | 707.7306 | 705.5185 | 702.1803 | 704.1839 | 701.1734 | 699.8696 | 698.8467 | 704.5504 | 704.3901 | 703.771 | 706.7421 | 713.8808 | 710.6847 | 711.4034
2025-04-09 23:52 | 9 | 23 | 52 | 6.2817e-272 | 1 | 29.3858 | 476.1717 | 0.27558 | 0.0073903 | 117.4431 | 117.4431 | 117.4431 | 117.4431 | 9.3467 | 11.9299 | 566.4265 | 566.4265 | 566.4265 | 566.4265 | 58.8593 | 50.1629 | 15.7518 | 49.0022 | 15.6011 | 10.305 | 36.9106 | 0 | 50.163 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3547656.7872 | 100.3257 | 0.0044991 | 0.13497 | 0.13497 | 0.13497 | 7.9917 | 1105.5745 | 1076.8477 | 1076.8477 | 1075.5745 | 1141.9579 | 1141.9579 | 1141.9579 | 1141.9579 | 700.0797 | 700.0797 | 700.0797 | 1.9999 | 0 | 2.0371 | 57.9185 | 168.2861 | 168.4272 | 194.9151 | 1.4247 | 2.5839 | 0 | 62.7073 | 56.3147 | 58.8593 | 105.0117 | -6.8649 | 49.0022 | -1.0269 | 37.0237 | 63.6094 | 48.5007 | 0 | 66.8016 | 670.7485 | 664.9807 | 639.245 | 639.877 | 623.7633 | 620.6073 | 388.3183 | 393.2261 | 637.3257 | 640.0753 | 698.9595 | 712.2409 | 710.0358 | 711.8887 | 715.3624 | 715.9428 | 717.172 | 715.5662 | 710.8117 | 708.1186 | 705.8729 | 702.508 | 704.5886 | 701.4483 | 700.2791 | 699.1102 | 704.9654 | 704.9303 | 704.4002 | 707.1994 | 714.2961 | 711.2112 | 711.7648
2025-04-09 23:53 | 9 | 23 | 53 | 6.2817e-272 | 1 | 29.386 | 472.9755 | 0.277 | 0.0073924 | 116.6415 | 116.6415 | 116.6415 | 116.6415 | 9.2899 | 11.8613 | 565.1337 | 565.1337 | 565.1337 | 565.1337 | 58.7558 | 50.191 | 15.7524 | 48.2039 | 15.599 | 10.2173 | 36.5793 | 0 | 50.1916 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3547664.8723 | 100.3819 | -0.001168 | -0.035041 | -0.035041 | -0.035041 | 7.9917 | 1106.6009 | 1077.9036 | 1077.9049 | 1076.6009 | 1142.9979 | 1142.9979 | 1142.9979 | 1142.9979 | 699.8203 | 699.8203 | 699.8203 | 2.007 | 0 | 2.022 | 57.5853 | 167.217 | 167.3611 | 194.857 | 1.4028 | 2.5492 | 0 | 62.1502 | 56.3767 | 58.7558 | 105.0159 | -7.146 | 48.2039 | -0.96974 | 36.7086 | 63.6215 | 48.5087 | 0 | 66.8015 | 670.5347 | 664.711 | 638.9674 | 639.6606 | 623.4711 | 620.4577 | 388.0348 | 392.8509 | 637.0362 | 639.7759 | 698.6525 | 711.9948 | 709.7905 | 711.4636 | 714.981 | 715.7425 | 716.796 | 715.1046 | 710.4633 | 707.9218 | 705.5916 | 702.4807 | 704.5801 | 701.3794 | 700.0926 | 699.0203 | 704.5971 | 704.4678 | 704.0969 | 706.8401 | 713.8635 | 710.9298 | 711.4826
2025-04-09 23:54 | 9 | 23 | 54 | 6.2817e-272 | 1 | 29.3863 | 475.1118 | 0.28023 | 0.0073925 | 117.3602 | 117.3602 | 117.3602 | 117.3602 | 9.3407 | 11.9159 | 565.7174 | 565.7174 | 565.7174 | 565.7174 | 58.6399 | 50.1939 | 15.7536 | 49.0499 | 15.5994 | 10.3235 | 36.9372 | 0 | 50.1938 | 14 | 22.1 | 221 | 154840 | 237681 | 3547672.9362 | 100.3878 | -0.0016047 | -0.048141 | -0.048141 | -0.048141 | 7.9917 | 1105.6849 | 1076.9604 | 1076.9617 | 1075.6849 | 1141.8955 | 1141.8955 | 1141.8955 | 1141.8955 | 700.7016 | 700.7016 | 700.7016 | 2.0338 | 0 | 2.0365 | 57.9694 | 168.2476 | 168.4018 | 194.6596 | 1.4033 | 2.5579 | 0 | 62.5331 | 56.3363 | 58.6399 | 105.0241 | -7.2839 | 49.0499 | -0.95449 | 37.0904 | 63.6357 | 48.5104 | 0 | 66.8013 | 670.3032 | 664.4074 | 638.6982 | 639.5169 | 623.2027 | 620.3146 | 387.7499 | 392.5843 | 636.7445 | 639.4311 | 699.6477 | 712.796 | 710.8401 | 712.6904 | 715.9467 | 716.8167 | 717.6214 | 715.9298 | 711.4189 | 708.7114 | 706.1423 | 703.6143 | 705.3415 | 702.0134 | 701.0731 | 699.8811 | 705.493 | 705.4218 | 705.0454 | 707.6778 | 714.6873 | 711.9004 | 712.366
2025-04-09 23:55 | 9 | 23 | 55 | 6.2817e-272 | 1 | 29.3899 | 476.29 | 0.27992 | 0.007388 | 117.7367 | 117.7367 | 117.7367 | 117.7367 | 9.3664 | 11.9473 | 566.3722 | 566.3722 | 566.3722 | 566.3722 | 58.516 | 50.1917 | 15.7539 | 49.2146 | 15.601 | 10.3314 | 36.9766 | 0 | 50.1919 | 14 | 22.1 | 221 | 154840 | 237681 | 3547681.1277 | 100.3833 | 0.00025514 | 0.0076542 | 0.0076542 | 0.0076542 | 7.9917 | 1105.2223 | 1076.484 | 1076.4838 | 1075.2223 | 1141.6811 | 1141.6811 | 1141.6811 | 1141.6811 | 699.7626 | 699.7626 | 699.7626 | 2.0221 | 0 | 2.0349 | 58.1226 | 168.7722 | 168.9186 | 194.6357 | 1.4425 | 2.5809 | 0 | 62.7451 | 56.3445 | 58.516 | 105.0256 | -7.1525 | 49.2146 | -1.0029 | 37.1189 | 63.6213 | 48.4956 | 0 | 66.8013 | 670.2931 | 664.4272 | 638.5214 | 639.5082 | 622.9249 | 620.1412 | 387.5013 | 392.2983 | 636.4651 | 639.0961 | 698.3831 | 711.7467 | 709.9541 | 711.7033 | 714.9141 | 715.7861 | 716.8011 | 715.1772 | 710.5287 | 707.7731 | 705.1453 | 702.4887 | 704.3612 | 701.0557 | 700.1804 | 698.8149 | 704.6897 | 704.3469 | 704.1374 | 706.9078 | 713.7616 | 711.0827 | 711.4406
2025-04-09 23:56 | 9 | 23 | 56 | 6.2817e-272 | 1 | 29.3879 | 474.3195 | 0.28302 | 0.0073881 | 117.307 | 117.307 | 117.307 | 117.307 | 9.3365 | 11.9104 | 565.7497 | 565.7497 | 565.7497 | 565.7497 | 58.6886 | 50.1982 | 15.7517 | 48.8234 | 15.5992 | 10.2894 | 36.8089 | 0 | 50.1988 | 14 | 22.1 | 221 | 154840 | 237681 | 3547689.3404 | 100.3964 | -0.0022476 | -0.067428 | -0.067428 | -0.067428 | 7.9917 | 1105.7585 | 1077.037 | 1077.036 | 1075.7585 | 1142.1906 | 1142.1906 | 1142.1906 | 1142.1906 | 699.6063 | 699.6063 | 699.6063 | 2.0063 | 0 | 2.0245 | 57.8865 | 168.1711 | 168.3155 | 194.6342 | 1.4152 | 2.5754 | 0 | 62.4836 | 56.3017 | 58.6886 | 105.011 | -7.3171 | 48.8234 | -1.3717 | 36.968 | 63.6335 | 48.4949 | 0 | 66.8011 | 670.2852 | 664.3849 | 638.381 | 639.4034 | 622.7452 | 619.9852 | 387.2353 | 392.0935 | 636.3188 | 638.9476 | 698.1869 | 711.7506 | 709.8287 | 711.6481 | 714.7265 | 715.8166 | 716.6717 | 714.9308 | 710.3439 | 707.7201 | 704.9174 | 702.3334 | 704.222 | 700.9207 | 699.9377 | 698.7573 | 704.5164 | 704.2184 | 703.8617 | 706.6333 | 713.3537 | 710.8465 | 711.2823
2025-04-09 23:57 | 9 | 23 | 57 | 6.2817e-272 | 1 | 29.3891 | 471.211 | 0.28393 | 0.0073949 | 116.8507 | 116.8507 | 116.8507 | 116.8507 | 9.3038 | 11.8703 | 564.7459 | 564.7459 | 564.7459 | 564.7459 | 58.8799 | 50.2171 | 15.7526 | 48.5295 | 15.6001 | 10.2595 | 36.7189 | 0 | 50.2175 | 13.7447 | 22.1 | 221 | 154840 | 237681 | 3547697.4043 | 100.4343 | -0.00047653 | -0.014296 | -0.014296 | -0.014296 | 7.9917 | 1106.3504 | 1077.6464 | 1077.6472 | 1076.3504 | 1142.5743 | 1142.5743 | 1142.5743 | 1142.5743 | 700.3507 | 700.3507 | 700.3507 | 2.015 | 0 | 2.0254 | 57.7319 | 167.5449 | 167.6853 | 194.4533 | 1.4293 | 2.5546 | 0 | 62.1786 | 56.2718 | 58.8799 | 105.0173 | -7.3879 | 48.5295 | -3.9455 | 36.8604 | 63.6293 | 48.5225 | 0 | 66.8015 | 670.1617 | 664.1924 | 638.1359 | 639.1849 | 622.5667 | 619.8776 | 386.9598 | 391.9558 | 636.2256 | 638.885 | 698.9108 | 712.5069 | 710.4547 | 712.3417 | 715.3237 | 716.2947 | 717.3264 | 715.5765 | 711.0551 | 708.4755 | 705.6302 | 703.1509 | 704.8935 | 701.7876 | 700.6148 | 699.5967 | 705.4514 | 705.2164 | 704.8349 | 707.4898 | 714.0649 | 711.5057 | 712.1032
2025-04-09 23:58 | 9 | 23 | 58 | 6.2817e-272 | 1 | 29.3865 | 474.6041 | 0.28044 | 0.0074101 | 117.7875 | 117.7875 | 117.7875 | 117.7875 | 9.3709 | 11.9493 | 566.5137 | 566.5137 | 566.5137 | 566.5137 | 59.0405 | 50.2071 | 15.7515 | 49.2697 | 15.5997 | 10.3404 | 37.0068 | 0 | 50.2073 | 14.2609 | 22.1 | 221 | 154840 | 237681 | 3547705.5 | 100.4144 | -0.00049826 | -0.014948 | -0.014948 | -0.014948 | 7.9917 | 1105.1402 | 1076.3993 | 1076.3983 | 1075.1402 | 1141.61 | 1141.61 | 1141.61 | 1141.61 | 699.9488 | 699.9488 | 699.9488 | 2.0679 | 0 | 2.0495 | 58.1854 | 168.9147 | 169.0392 | 194.5338 | 1.4258 | 2.5925 | 0 | 62.7765 | 56.2397 | 59.0405 | 105.0099 | -6.998 | 49.2697 | -3.9109 | 37.1509 | 63.6229 | 48.5813 | 0 | 66.8006 | 670.4052 | 664.3974 | 638.2211 | 639.2275 | 622.4707 | 619.7915 | 386.7222 | 391.9682 | 636.2339 | 638.7923 | 698.2509 | 712.2543 | 710.2605 | 712.2786 | 715.1331 | 716.0179 | 717.2486 | 715.4524 | 710.5448 | 707.9675 | 705.0615 | 702.3719 | 704.3469 | 701.2542 | 700.0227 | 698.8559 | 705.07 | 704.6709 | 704.3593 | 707.2995 | 713.8027 | 711.1503 | 711.8723
2025-04-09 23:59 | 9 | 23 | 59 | 6.2817e-272 | 1 | 29.3888 | 473.5681 | 0.27831 | 0.0074208 | 117.4507 | 117.4507 | 117.4507 | 117.4507 | 9.3464 | 11.9246 | 566.5237 | 566.5237 | 566.5237 | 566.5237 | 59.291 | 50.2072 | 15.7536 | 48.8437 | 15.5985 | 10.2918 | 36.8388 | 0 | 50.2074 | 14.1702 | 22.1 | 221 | 154840 | 237681 | 3547713.617 | 100.4146 | 0.0018541 | 0.055622 | 0.055622 | 0.055622 | 7.9917 | 1105.5806 | 1076.8538 | 1076.8536 | 1075.5806 | 1142.1643 | 1142.1643 | 1142.1643 | 1142.1643 | 699.7755 | 699.7755 | 699.7755 | 2.0462 | 0 | 2.0321 | 57.9951 | 168.373 | 168.5043 | 194.756 | 1.4407 | 2.5916 | 0 | 62.6188 | 56.4196 | 59.291 | 105.0236 | -6.8672 | 48.8437 | -3.9144 | 36.9764 | 63.6381 | 48.6276 | 0 | 66.8009 | 670.6563 | 664.6507 | 638.3143 | 639.227 | 622.5171 | 619.6984 | 386.4649 | 391.7878 | 636.2729 | 638.8038 | 698.2657 | 712.1421 | 709.978 | 711.977 | 714.8606 | 715.59 | 716.9981 | 715.2129 | 710.3458 | 707.8661 | 704.9569 | 702.1841 | 704.0782 | 701.2143 | 699.7254 | 698.8621 | 704.914 | 704.5461 | 704.0985 | 707.1443 | 713.7174 | 711.0287 | 711.786
2025-04-10 | 10 | 0 | 0 | 6.2817e-272 | 1 | 29.3892 | 471.467 | 0.28059 | 0.0074244 | 116.8136 | 116.8136 | 116.8136 | 116.8136 | 9.3011 | 11.8744 | 566.0103 | 566.0103 | 566.0103 | 566.0103 | 59.7132 | 50.2299 | 15.7517 | 48.1509 | 15.5999 | 10.2124 | 36.5389 | 0 | 50.2301 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3547721.7021 | 100.4599 | 0.001067 | 0.03201 | 0.03201 | 0.03201 | 7.9917 | 1106.3972 | 1077.6951 | 1077.6915 | 1076.3972 | 1143.0668 | 1143.0668 | 1143.0668 | 1143.0668 | 699.604 | 699.604 | 699.604 | 2.0174 | 0 | 2.022 | 57.7332 | 167.512 | 167.6519 | 194.86 | 1.4471 | 2.5873 | 0 | 62.2538 | 56.449 | 59.7132 | 105.0108 | -5.4393 | 48.1509 | -3.8563 | 36.6912 | 63.6393 | 48.6423 | 0 | 66.8006 | 670.8551 | 664.7823 | 638.3485 | 639.1615 | 622.5517 | 619.6247 | 386.2204 | 391.5988 | 636.2954 | 638.8553 | 698.3193 | 712.0955 | 709.6516 | 711.5785 | 714.5369 | 715.3842 | 716.8896 | 715.0196 | 709.9597 | 707.6658 | 704.9404 | 702.1707 | 703.9613 | 701.1794 | 699.5507 | 698.887 | 704.8421 | 704.422 | 703.7843 | 706.8869 | 713.5078 | 710.6784 | 711.6525
2025-04-10 00:01 | 10 | 0 | 1 | 6.2817e-272 | 1 | 29.3894 | 473.6501 | 0.28121 | 0.0074255 | 117.4559 | 117.4559 | 117.4559 | 117.4559 | 9.3466 | 11.9252 | 566.7718 | 566.7718 | 566.7718 | 566.7718 | 59.9772 | 50.2742 | 15.7528 | 48.8825 | 15.6003 | 10.3144 | 36.8768 | 0 | 50.2747 | 13.5319 | 22.1 | 221 | 154840 | 237681 | 3547729.7234 | 100.5484 | -0.00039692 | -0.011908 | -0.011908 | -0.011908 | 7.9917 | 1105.5789 | 1076.8502 | 1076.8519 | 1075.5789 | 1142.1145 | 1142.1145 | 1142.1145 | 1142.1145 | 700.5934 | 700.5934 | 700.5934 | 2.0383 | 0 | 2.0618 | 58.1471 | 168.5119 | 168.6415 | 194.8946 | 1.4518 | 2.591 | 0 | 62.568 | 56.3993 | 59.9772 | 105.0187 | -5.318 | 48.8825 | -3.8884 | 37.0578 | 63.6375 | 48.6475 | 0 | 66.7997 | 671.0283 | 664.9223 | 638.5271 | 639.1282 | 622.6318 | 619.5977 | 385.9078 | 391.5172 | 636.3138 | 639.0829 | 699.0644 | 713.2633 | 710.5759 | 712.7488 | 715.6886 | 716.2552 | 717.907 | 716.0627 | 710.8997 | 708.7641 | 706.02 | 702.7179 | 704.823 | 702.2158 | 700.3677 | 699.6529 | 705.5788 | 705.5571 | 704.7581 | 708.1323 | 714.6898 | 711.6505 | 712.8801
2025-04-10 00:02 | 10 | 0 | 2 | 6.2817e-272 | 1 | 29.3889 | 477.2048 | 0.28026 | 0.0074251 | 118.5716 | 118.5716 | 118.5716 | 118.5716 | 9.4258 | 12.0112 | 567.938 | 567.938 | 567.938 | 567.938 | 59.8483 | 50.2283 | 15.7535 | 49.9052 | 15.5981 | 10.4307 | 37.2873 | 0 | 50.2289 | 15.9574 | 22.1 | 221 | 154840 | 237681 | 3547737.9787 | 100.4567 | -0.0050552 | -0.15166 | -0.15166 | -0.15166 | 7.9917 | 1104.1515 | 1075.3802 | 1075.38 | 1074.1515 | 1140.7817 | 1140.7817 | 1140.7817 | 1140.7817 | 700.5072 | 700.5072 | 700.5072 | 2.1015 | 0 | 2.1094 | 58.5766 | 170.0291 | 170.1395 | 195.2244 | 1.4596 | 2.6141 | 0 | 63.2598 | 56.1052 | 59.8483 | 105.0232 | -5.2463 | 49.9052 | -3.8352 | 37.4755 | 63.6353 | 48.6443 | 0 | 66.7998 | 671.5159 | 665.381 | 638.7964 | 639.2181 | 622.7322 | 619.4971 | 385.7035 | 391.4967 | 636.3463 | 638.9495 | 698.8343 | 713.2975 | 710.6022 | 713.0247 | 715.8138 | 716.0924 | 718.0416 | 716.3277 | 710.7279 | 708.625 | 705.7372 | 702.3923 | 704.3253 | 701.8548 | 699.988 | 699.2589 | 705.7198 | 705.624 | 704.6437 | 708.2445 | 714.8406 | 711.6581 | 712.9857
2025-04-10 00:03 | 10 | 0 | 3 | 6.2817e-272 | 1 | 29.3895 | 475.0402 | 0.27784 | 0.0074246 | 117.975 | 117.975 | 117.975 | 117.975 | 9.3834 | 11.9582 | 566.4196 | 566.4196 | 566.4196 | 566.4196 | 59.6669 | 50.1764 | 15.7538 | 49.4231 | 15.5998 | 10.3597 | 37.0882 | 0 | 50.1768 | 14.5957 | 22.1 | 221 | 154840 | 237681 | 3547746.234 | 100.3528 | -0.0024596 | -0.073789 | -0.073789 | -0.073789 | 7.9917 | 1104.9134 | 1076.1647 | 1076.1668 | 1074.9134 | 1141.4106 | 1141.4106 | 1141.4106 | 1141.4106 | 699.8804 | 699.8804 | 699.8804 | 2.0661 | 0 | 2.0603 | 58.1675 | 169.0644 | 169.191 | 195.4453 | 1.4637 | 2.5971 | 0 | 62.9618 | 55.8961 | 59.6669 | 105.0251 | -4.6939 | 49.4231 | -3.9001 | 37.2204 | 63.641 | 48.6425 | 0 | 66.7996 | 671.6827 | 665.4606 | 638.7231 | 639.0909 | 622.6558 | 619.3022 | 385.3859 | 391.3884 | 636.3389 | 638.8264 | 698.3421 | 712.6721 | 709.7429 | 712.3614 | 715.3917 | 715.6241 | 717.6315 | 715.9762 | 710.2262 | 708.2274 | 705.2166 | 701.6093 | 703.5234 | 701.1018 | 699.2842 | 698.7453 | 705.1599 | 704.9609 | 703.7859 | 707.5181 | 714.1414 | 710.8807 | 712.3293
2025-04-10 00:04 | 10 | 0 | 4 | 6.2817e-272 | 1 | 29.3897 | 472.0162 | 0.27899 | 0.007425 | 117.3466 | 117.3466 | 117.3466 | 117.3466 | 9.3388 | 11.9071 | 564.9639 | 564.9639 | 564.9639 | 564.9639 | 59.4571 | 50.189 | 15.7522 | 48.8658 | 15.6001 | 10.3089 | 36.8924 | 0 | 50.1894 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3547754.4043 | 100.3779 | 0.0043162 | 0.12948 | 0.12948 | 0.12948 | 7.9917 | 1105.7202 | 1076.9966 | 1076.9962 | 1075.7202 | 1142.1364 | 1142.1364 | 1142.1364 | 1142.1364 | 700.2259 | 700.2259 | 700.2259 | 2.0479 | 0 | 2.0626 | 57.9373 | 168.1999 | 168.3385 | 195.4052 | 1.4643 | 2.5802 | 0 | 62.5434 | 55.9173 | 59.4571 | 105.0147 | -4.623 | 48.8658 | -3.9066 | 37.038 | 63.6473 | 48.6445 | 0 | 66.7993 | 671.5095 | 665.2808 | 638.4928 | 638.7759 | 622.5557 | 619.0927 | 385.0468 | 391.2331 | 636.341 | 638.7876 | 698.6195 | 713.103 | 709.8982 | 712.6047 | 715.5941 | 715.8074 | 717.9847 | 716.2428 | 710.4052 | 708.5896 | 705.7298 | 701.8983 | 704.0453 | 701.9301 | 699.59 | 699.103 | 705.4173 | 705.339 | 704.0359 | 707.8871 | 714.444 | 711.0951 | 712.7322
2025-04-10 00:05 | 10 | 0 | 5 | 6.2817e-272 | 1 | 29.3891 | 476.0257 | 0.2795 | 0.0074218 | 118.233 | 118.233 | 118.233 | 118.233 | 9.4018 | 11.9782 | 566.339 | 566.339 | 566.339 | 566.339 | 59.3266 | 50.1257 | 15.753 | 49.5871 | 15.6004 | 10.3681 | 37.1349 | 0 | 50.1259 | 15.5319 | 22.1 | 221 | 154840 | 237681 | 3547762.7021 | 100.2514 | 0.0014359 | 0.043075 | 0.043075 | 0.043075 | 7.9917 | 1104.5823 | 1075.8236 | 1075.8223 | 1074.5823 | 1141.196 | 1141.196 | 1141.196 | 1141.196 | 699.0639 | 699.0639 | 699.0639 | 2.1055 | 0 | 2.0873 | 58.2099 | 169.3373 | 169.4694 | 195.4652 | 1.4775 | 2.6076 | 0 | 63.1684 | 56.0103 | 59.3266 | 105.0197 | -4.7181 | 49.5871 | -3.8663 | 37.2506 | 63.6155 | 48.6311 | 0 | 66.799 | 671.5854 | 665.2893 | 638.4583 | 638.6653 | 622.3989 | 618.825 | 384.789 | 391.0855 | 636.4147 | 638.6074 | 697.3353 | 712.0363 | 708.971 | 711.6762 | 714.5359 | 714.6354 | 717.1497 | 715.4506 | 709.315 | 707.3986 | 704.3988 | 700.5854 | 702.4728 | 700.3749 | 698.2686 | 697.7855 | 704.5768 | 704.1214 | 702.8535 | 706.8237 | 713.2798 | 710.0211 | 711.6635
2025-04-10 00:06 | 10 | 0 | 6 | 6.2817e-272 | 1 | 29.3865 | 470.9587 | 0.27815 | 0.0074224 | 117.0561 | 117.0561 | 117.0561 | 117.0561 | 9.3191 | 11.8789 | 564.0937 | 564.0937 | 564.0937 | 564.0937 | 59.3798 | 50.1532 | 15.7529 | 48.8035 | 15.603 | 10.2989 | 36.8821 | 0 | 50.1536 | 14.2174 | 22.1 | 221 | 154840 | 237681 | 3547770.7174 | 100.3065 | -0.00045951 | -0.013786 | -0.013786 | -0.013786 | 7.9917 | 1106.0752 | 1077.363 | 1077.3646 | 1076.0752 | 1142.217 | 1142.217 | 1142.217 | 1142.217 | 700.8224 | 700.8224 | 700.8224 | 2.0623 | 0 | 2.0788 | 57.7593 | 167.7205 | 167.8689 | 195.3132 | 1.4262 | 2.5591 | 0 | 62.4043 | 56.0659 | 59.3798 | 105.0188 | -4.3174 | 48.8035 | -3.9255 | 37.0019 | 63.6337 | 48.6306 | 0 | 66.7987 | 671.3216 | 665.0183 | 638.2377 | 638.3464 | 622.3156 | 618.6701 | 384.4865 | 390.7961 | 636.2032 | 638.5645 | 699.2314 | 713.8244 | 710.4535 | 713.2075 | 716.2118 | 716.2755 | 718.5721 | 716.8411 | 711.0388 | 709.3094 | 706.4361 | 702.4855 | 704.5346 | 702.5453 | 700.0279 | 699.699 | 705.9751 | 706.1297 | 704.6638 | 708.5278 | 715.1668 | 711.4629 | 713.3683
2025-04-10 00:07 | 10 | 0 | 7 | 6.2817e-272 | 1 | 29.3858 | 472.0024 | 0.27686 | 0.0074244 | 117.1557 | 117.1557 | 117.1557 | 117.1557 | 9.3264 | 11.8896 | 564.4069 | 564.4069 | 564.4069 | 564.4069 | 59.3093 | 50.1598 | 15.7528 | 48.8083 | 15.6002 | 10.2962 | 36.8837 | 0 | 50.1599 | 14.1702 | 22.1 | 221 | 154840 | 237681 | 3547778.766 | 100.3196 | 0.0040353 | 0.12106 | 0.12106 | 0.12106 | 7.9917 | 1105.9417 | 1077.2262 | 1077.226 | 1075.9417 | 1142.2109 | 1142.2109 | 1142.2109 | 1142.2109 | 699.8492 | 699.8492 | 699.8492 | 2.0609 | 0 | 2.0677 | 57.7859 | 167.8817 | 168.0315 | 195.2201 | 1.4236 | 2.567 | 0 | 62.4656 | 55.9542 | 59.3093 | 105.0188 | -3.6965 | 48.8083 | -3.8955 | 36.9922 | 63.6219 | 48.6384 | 0 | 66.7989 | 671.2712 | 664.9185 | 638.1726 | 638.2056 | 622.2146 | 618.4833 | 384.2934 | 390.6421 | 636.0725 | 638.458 | 698.4089 | 712.8651 | 709.4367 | 712.1217 | 715.2288 | 715.2127 | 717.7728 | 715.9143 | 709.9686 | 708.2454 | 705.4492 | 701.4987 | 703.4398 | 701.5436 | 699.0649 | 698.7975 | 705.268 | 705.1148 | 703.5837 | 707.4675 | 714.116 | 710.5969 | 712.5717
2025-04-10 00:08 | 10 | 0 | 8 | 6.2817e-272 | 1 | 29.386 | 477.4951 | 0.28091 | 0.0074186 | 118.5717 | 118.5717 | 118.5717 | 118.5717 | 9.4267 | 12.0046 | 566.2983 | 566.2983 | 566.2983 | 566.2983 | 58.8443 | 50.1039 | 15.7526 | 50.0483 | 15.6018 | 10.428 | 37.3787 | 0 | 50.1042 | 15.7021 | 22.1 | 221 | 154840 | 237681 | 3547787.0638 | 100.2078 | -0.0044084 | -0.13225 | -0.13225 | -0.13225 | 7.9917 | 1104.1343 | 1075.3615 | 1075.3615 | 1074.1343 | 1140.5955 | 1140.5955 | 1140.5955 | 1140.5955 | 699.9887 | 699.9887 | 699.9887 | 2.1397 | 0 | 2.1124 | 58.3652 | 169.8033 | 169.9429 | 195.2051 | 1.4477 | 2.5896 | 0 | 63.3555 | 55.9359 | 58.8443 | 105.0171 | -3.1487 | 50.0483 | -3.88 | 37.466 | 63.6302 | 48.6144 | 0 | 66.7984 | 671.2668 | 664.8698 | 638.1769 | 638.1591 | 622.0685 | 618.3299 | 384.0864 | 390.4105 | 636.1848 | 638.147 | 698.3755 | 712.9211 | 709.9439 | 712.7339 | 715.5239 | 715.3251 | 718.0762 | 716.2019 | 710.1662 | 708.2218 | 705.3074 | 701.4991 | 703.2628 | 701.5416 | 699.2696 | 698.7792 | 705.4671 | 705.194 | 703.812 | 707.746 | 714.3885 | 710.776 | 712.7217
2025-04-10 00:09 | 10 | 0 | 9 | 6.2817e-272 | 1 | 29.3859 | 476.1015 | 0.27991 | 0.007412 | 118.1217 | 118.1217 | 118.1217 | 118.1217 | 9.3948 | 11.9679 | 565.3537 | 565.3537 | 565.3537 | 565.3537 | 58.4158 | 50.0327 | 15.753 | 49.9303 | 15.6005 | 10.3964 | 37.3392 | 0 | 50.033 | 15.617 | 22.1 | 221 | 154840 | 237681 | 3547795.3617 | 100.0654 | -0.0099191 | -0.29758 | -0.29758 | -0.29758 | 7.9917 | 1104.7096 | 1075.9551 | 1075.9547 | 1074.7096 | 1140.7491 | 1140.7491 | 1140.7491 | 1140.7491 | 700.149 | 700.149 | 700.149 | 2.031 | 0 | 2.0581 | 58.0209 | 169.0413 | 169.1824 | 195.2213 | 1.4362 | 2.5844 | 0 | 63.1958 | 56.047 | 58.4158 | 105.0195 | -2.1331 | 49.9303 | -3.9134 | 37.3522 | 63.6334 | 48.5886 | 0 | 66.7979 | 671.0156 | 664.6947 | 637.9348 | 637.9602 | 621.8631 | 618.0778 | 383.8854 | 390.1366 | 635.9771 | 637.8537 | 698.8014 | 712.9349 | 709.9548 | 712.763 | 715.7078 | 715.5726 | 718.2175 | 716.2924 | 710.4017 | 708.41 | 705.6655 | 701.6812 | 703.6193 | 701.7619 | 699.7836 | 699.2192 | 705.548 | 705.1855 | 703.898 | 707.7899 | 714.407 | 710.7354 | 712.6899
2025-04-10 00:10 | 10 | 0 | 10 | 6.2817e-272 | 1 | 29.3854 | 474.7603 | 0.26888 | 0.0074066 | 117.7322 | 117.7322 | 117.7322 | 117.7322 | 9.3674 | 11.934 | 564.5479 | 564.5479 | 564.5479 | 564.5479 | 58.1799 | 49.974 | 15.7521 | 49.6328 | 15.6035 | 10.3819 | 37.2725 | 0 | 49.9756 | 15.1064 | 22.1 | 221 | 154840 | 237681 | 3547803.7021 | 99.9481 | -0.013581 | -0.40744 | -0.40744 | -0.40744 | 7.9917 | 1105.2011 | 1076.4617 | 1076.4645 | 1075.2011 | 1141.137 | 1141.137 | 1141.137 | 1141.137 | 699.9249 | 699.9249 | 699.9249 | 2.066 | 0 | 2.0459 | 57.6316 | 168.4124 | 168.5223 | 195.1302 | 1.4295 | 2.5852 | 0 | 63.0376 | 56.2356 | 58.1799 | 105.0137 | -1.7478 | 49.6328 | -3.9358 | 37.3003 | 63.6221 | 48.5651 | 0 | 66.7982 | 670.4797 | 664.3851 | 637.554 | 637.6258 | 621.5856 | 617.805 | 383.6338 | 389.8954 | 635.1769 | 637.5402 | 698.7812 | 712.548 | 709.6265 | 712.3376 | 715.6128 | 715.4788 | 717.7887 | 715.9867 | 710.1665 | 708.1796 | 705.4696 | 701.6534 | 703.3904 | 701.3634 | 699.5718 | 699.0074 | 705.3349 | 705.1097 | 703.7938 | 707.5914 | 714.3523 | 710.6001 | 712.1903
2025-04-10 00:11 | 10 | 0 | 11 | 6.2817e-272 | 1 | 29.3869 | 470.7741 | 0.2766 | 0.0074028 | 116.7971 | 116.7971 | 116.7971 | 116.7971 | 9.3007 | 11.8603 | 562.9796 | 562.9796 | 562.9796 | 562.9796 | 58.1304 | 50.0108 | 15.7533 | 48.6946 | 15.6012 | 10.2568 | 36.882 | 0 | 50.0109 | 14.0426 | 22.1 | 221 | 154840 | 237681 | 3547811.8298 | 100.0215 | 0.011258 | 0.33773 | 0.33773 | 0.33773 | 7.9917 | 1106.407 | 1077.7051 | 1077.7055 | 1076.407 | 1142.3585 | 1142.3585 | 1142.3585 | 1142.3585 | 700.1664 | 700.1664 | 700.1664 | 2.0447 | 0 | 2.0437 | 57.3193 | 167.1459 | 167.2753 | 194.8053 | 1.4382 | 2.534 | 0 | 62.4209 | 56.3013 | 58.1304 | 105.0221 | -2.1184 | 48.6946 | -3.9199 | 36.8507 | 63.6065 | 48.5519 | 0 | 66.7983 | 669.8001 | 663.8139 | 637.1584 | 637.1928 | 621.343 | 617.5713 | 383.3352 | 389.5884 | 634.9346 | 637.3307 | 699.2273 | 712.8044 | 709.9492 | 712.3898 | 715.7703 | 715.6725 | 717.7439 | 716.0923 | 710.4795 | 708.3359 | 705.8247 | 702.1937 | 703.853 | 701.7153 | 699.9665 | 699.4414 | 705.3424 | 705.2518 | 703.996 | 707.5901 | 714.4667 | 710.7877 | 712.2843
2025-04-10 00:12 | 10 | 0 | 12 | 6.2817e-272 | 1 | 29.3893 | 473.3304 | 0.27416 | 0.007397 | 117.4163 | 117.4163 | 117.4163 | 117.4163 | 9.3438 | 11.9123 | 564.2792 | 564.2792 | 564.2792 | 564.2792 | 58.0218 | 49.9929 | 15.7537 | 49.3051 | 15.5989 | 10.3354 | 37.1321 | 0 | 49.9945 | 14 | 22.1 | 221 | 154840 | 237681 | 3547820.0213 | 99.9859 | -0.013245 | -0.39734 | -0.39734 | -0.39734 | 7.9917 | 1105.6283 | 1076.9015 | 1076.9036 | 1075.6283 | 1141.5636 | 1141.5636 | 1141.5636 | 1141.5636 | 699.8784 | 699.8784 | 699.8784 | 2.0184 | 0 | 2.0337 | 57.5446 | 167.967 | 168.0939 | 194.6316 | 1.4712 | 2.5678 | 0 | 62.8242 | 56.3793 | 58.0218 | 105.0245 | -1.9991 | 49.3051 | -3.9387 | 37.133 | 63.6154 | 48.5311 | 0 | 66.798 | 669.4481 | 663.5853 | 636.9823 | 637.0588 | 621.0933 | 617.3501 | 383.2115 | 389.3432 | 634.4294 | 636.9567 | 698.8477 | 712.3861 | 709.5988 | 712.1575 | 715.6049 | 715.5386 | 717.4624 | 715.9347 | 710.3819 | 708.1218 | 705.518 | 701.7573 | 703.5704 | 701.1257 | 699.837 | 699.0208 | 705.0197 | 704.9641 | 703.8488 | 707.2644 | 714.1876 | 710.5256 | 711.8859
2025-04-10 00:13 | 10 | 0 | 13 | 6.2817e-272 | 1 | 29.3867 | 469.217 | 0.28306 | 0.0073943 | 116.2738 | 116.2738 | 116.2738 | 116.2738 | 9.2636 | 11.8208 | 562.8115 | 562.8115 | 562.8115 | 562.8115 | 57.9737 | 50.0496 | 15.7543 | 48.1746 | 15.6007 | 10.219 | 36.7166 | 0 | 50.0502 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3547828.1064 | 100.0991 | -0.012958 | -0.38875 | -0.38875 | -0.38875 | 7.9917 | 1107.0755 | 1078.3945 | 1078.3951 | 1077.0755 | 1143.0364 | 1143.0364 | 1143.0364 | 1143.0364 | 699.9502 | 699.9502 | 699.9502 | 2.0548 | 0 | 2.0487 | 57.1786 | 166.4938 | 166.6108 | 194.476 | 1.4224 | 2.5147 | 0 | 62.0468 | 56.4864 | 57.9737 | 105.0286 | -2.3439 | 48.1746 | -3.8209 | 36.7148 | 63.596 | 48.5178 | 0 | 66.7977 | 668.9164 | 663.3216 | 636.752 | 636.9215 | 620.941 | 617.2307 | 382.9656 | 388.8795 | 634.4147 | 636.7696 | 699.203 | 712.2789 | 709.4939 | 711.6717 | 715.4416 | 715.5917 | 717.1598 | 715.6798 | 710.4331 | 708.215 | 705.9656 | 702.3009 | 704.1686 | 701.4522 | 699.9446 | 699.2753 | 704.9023 | 705.0559 | 704.0444 | 707.1739 | 714.2247 | 710.506 | 711.6261
2025-04-10 00:14 | 10 | 0 | 14 | 6.2817e-272 | 1 | 29.3846 | 475.1643 | 0.27958 | 0.0073954 | 117.8388 | 117.8388 | 117.8388 | 117.8388 | 9.3751 | 11.9498 | 565.0609 | 565.0609 | 565.0609 | 565.0609 | 57.995 | 50.0344 | 15.7553 | 49.5013 | 15.6024 | 10.3733 | 37.2349 | 0 | 50.0357 | 15.234 | 22.1 | 221 | 154840 | 237681 | 3547836.2766 | 100.0688 | -0.030203 | -0.90608 | -0.90608 | -0.90608 | 7.9917 | 1105.0632 | 1076.3202 | 1076.3172 | 1075.0632 | 1141.3081 | 1141.3081 | 1141.3081 | 1141.3081 | 700.2458 | 700.2458 | 700.2458 | 2.1135 | 0 | 2.1126 | 57.9542 | 168.7188 | 168.8408 | 194.3015 | 1.4227 | 2.5782 | 0 | 63.0226 | 56.4463 | 57.995 | 105.0349 | -2.1112 | 49.5013 | -3.8848 | 37.2693 | 63.6036 | 48.5194 | 0 | 66.7977 | 668.6476 | 663.1609 | 636.7499 | 637.0143 | 620.7896 | 617.2116 | 382.9452 | 388.7194 | 633.8513 | 636.4668 | 699.1838 | 712.8814 | 710.5606 | 712.5952 | 716.2342 | 716.2765 | 717.6038 | 716.2979 | 711.0389 | 708.2659 | 705.8698 | 702.2302 | 703.9146 | 701.0151 | 700.2254 | 698.9591 | 704.8158 | 704.9187 | 704.3934 | 707.511 | 714.6518 | 711.3168 | 712.0854
2025-04-10 00:15 | 10 | 0 | 15 | 6.2817e-272 | 1 | 29.3852 | 474.802 | 0.27167 | 0.0073977 | 117.371 | 117.371 | 117.371 | 117.371 | 9.3418 | 11.9069 | 564.7235 | 564.7235 | 564.7235 | 564.7235 | 58.1059 | 49.9817 | 15.7552 | 48.9047 | 15.602 | 10.2904 | 36.9903 | 0 | 49.9828 | 14.7391 | 22.1 | 221 | 154840 | 237681 | 3547844.5 | 99.9635 | -0.019131 | -0.57394 | -0.57394 | -0.57394 | 7.9917 | 1105.663 | 1076.9376 | 1076.9333 | 1075.663 | 1142.0841 | 1142.0841 | 1142.0841 | 1142.0841 | 698.4847 | 698.4847 | 698.4847 | 2.0833 | 0 | 2.0642 | 57.5039 | 167.9188 | 168.0321 | 194.4125 | 1.442 | 2.5609 | 0 | 62.815 | 56.4913 | 58.1059 | 105.0341 | -1.4331 | 48.9047 | -3.8117 | 36.9714 | 63.6158 | 48.5301 | 0 | 66.7976 | 668.6942 | 663.2335 | 636.7143 | 637.0666 | 620.6359 | 617.1172 | 382.9035 | 388.4731 | 633.3022 | 636.1897 | 697.3666 | 710.976 | 708.7856 | 710.6747 | 714.4379 | 714.6211 | 715.8738 | 714.5764 | 709.2724 | 706.365 | 704.2083 | 700.4405 | 702.5156 | 699.3205 | 698.6941 | 697.2554 | 703.2217 | 703.1803 | 702.5628 | 705.4336 | 712.636 | 709.4501 | 710.0748
2025-04-10 00:16 | 10 | 0 | 16 | 6.2817e-272 | 1 | 29.3855 | 472.6087 | 0.27175 | 0.0073975 | 117.2526 | 117.2526 | 117.2526 | 117.2526 | 9.3333 | 11.8984 | 564.2687 | 564.2687 | 564.2687 | 564.2687 | 58.2464 | 49.9851 | 15.752 | 49.1376 | 15.598 | 10.342 | 37.1423 | 0 | 49.9867 | 14.5106 | 22.1 | 221 | 154840 | 237681 | 3547852.5319 | 99.9703 | -0.012412 | -0.37237 | -0.37237 | -0.37237 | 7.9917 | 1105.8181 | 1077.0977 | 1077.1 | 1075.8181 | 1141.7819 | 1141.7819 | 1141.7819 | 1141.7819 | 700.6401 | 700.6401 | 700.6401 | 2.0468 | 0 | 2.0661 | 57.5726 | 167.804 | 167.9174 | 194.2783 | 1.465 | 2.5567 | 0 | 62.7633 | 56.5144 | 58.2464 | 105.0135 | -1.0173 | 49.1376 | -3.8881 | 37.1569 | 63.5943 | 48.5303 | 0 | 66.7973 | 668.4068 | 662.9667 | 636.4884 | 636.9036 | 620.5607 | 617.1418 | 382.8021 | 388.251 | 633.1749 | 636.0845 | 699.7494 | 712.9761 | 710.8156 | 712.7034 | 716.5044 | 716.8306 | 717.7368 | 716.3701 | 711.5281 | 708.5521 | 706.3768 | 703.0741 | 704.7502 | 701.4157 | 700.7956 | 699.3707 | 705.1157 | 705.3595 | 704.913 | 707.761 | 715.0968 | 711.7364 | 712.2019
2025-04-10 00:17 | 10 | 0 | 17 | 6.2817e-272 | 1 | 29.3833 | 471.6995 | 0.27563 | 0.007398 | 116.8116 | 116.8116 | 116.8116 | 116.8116 | 9.3027 | 11.862 | 563.715 | 563.715 | 563.715 | 563.715 | 58.4337 | 49.9931 | 15.7534 | 48.7507 | 15.5996 | 10.2864 | 36.9892 | 0 | 49.9935 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3547860.6809 | 99.9861 | -0.012399 | -0.37198 | -0.37198 | -0.37198 | 7.9917 | 1106.3728 | 1077.6694 | 1077.6698 | 1076.3728 | 1142.2864 | 1142.2864 | 1142.2864 | 1142.2864 | 700.3388 | 700.3388 | 700.3388 | 2.0646 | 0 | 2.047 | 57.3633 | 167.1756 | 167.3156 | 194.2666 | 1.4262 | 2.542 | 0 | 62.4948 | 56.3062 | 58.4337 | 105.0226 | -0.97821 | 48.7507 | -3.9514 | 36.957 | 63.607 | 48.5284 | 0 | 66.7972 | 668.2482 | 662.8091 | 636.3777 | 636.8744 | 620.4302 | 617.0695 | 382.6503 | 388.092 | 633.0805 | 635.8462 | 699.4346 | 712.5901 | 710.5008 | 712.1791 | 716.1515 | 716.4766 | 717.2822 | 716.0022 | 711.321 | 708.3017 | 706.1273 | 702.9621 | 704.6084 | 701.0511 | 700.5203 | 698.9946 | 704.9647 | 705.2531 | 704.7468 | 707.3645 | 714.6635 | 711.455 | 711.7436
2025-04-10 00:18 | 10 | 0 | 18 | 6.2817e-272 | 1 | 29.3821 | 459.6424 | 0.27443 | 0.0073985 | 114.0165 | 114.0165 | 114.0165 | 114.0165 | 9.1049 | 11.6428 | 559.7453 | 559.7453 | 559.7453 | 559.7453 | 58.6502 | 49.9818 | 15.7537 | 45.688 | 15.603 | 9.8807 | 35.557 | 0 | 49.9814 | 18 | 22.1 | 221 | 154840 | 237681 | 3547868.6596 | 99.9636 | -0.00012092 | -0.0036277 | -0.0036277 | -0.0036277 | 7.9917 | 1109.9264 | 1081.3306 | 1081.3247 | 1079.9264 | 1146.2745 | 1146.2745 | 1146.2745 | 1146.2745 | 697.5867 | 697.5867 | 697.5867 | 2.0245 | 0 | 2.0373 | 55.9084 | 163.1671 | 163.2693 | 194.1138 | 1.3506 | 2.471 | 0 | 60.9185 | 56.2122 | 58.6502 | 105.0247 | -1.0949 | 45.688 | -3.8816 | 35.4994 | 63.5857 | 48.5308 | 0 | 66.7973 | 667.8685 | 662.3471 | 636.0202 | 636.4751 | 620.2485 | 616.9017 | 382.433 | 387.8841 | 632.9402 | 635.7802 | 697.2271 | 710.167 | 708.0016 | 709.1461 | 713.222 | 713.7593 | 714.3567 | 713.0806 | 708.1309 | 705.0478 | 703.3981 | 700.3617 | 701.8607 | 698.6604 | 697.7685 | 696.7909 | 702.2663 | 701.708 | 701.5274 | 704.3247 | 711.8622 | 708.8814 | 709.1183
2025-04-10 00:19 | 10 | 0 | 19 | 6.2817e-272 | 1 | 29.384 | 401.4691 | 0.28105 | 0.0073958 | 105.8558 | 105.8558 | 105.8558 | 105.8558 | 8.526 | 11.0752 | 545.2097 | 545.2097 | 545.2097 | 545.2097 | 58.6133 | 49.9794 | 15.7539 | 36.3685 | 15.601 | 8.7975 | 31.633 | 0 | 49.9786 | 18 | 22.1 | 221 | 154840 | 237681 | 3547875.5319 | 99.9589 | 0.022377 | 0.6713 | 0.6713 | 0.6713 | 7.9917 | 1120.3664 | 1092.0889 | 1092.0804 | 1090.3664 | 1158.4145 | 1158.4145 | 1158.4145 | 1158.4145 | 687.0131 | 687.0131 | 687.0131 | 1.2033 | 0 | 2.022 | 52.0026 | 151.3974 | 151.4877 | 192.6453 | 1.2647 | 2.2376 | 0 | 57.1312 | 56.0419 | 58.6133 | 105.0258 | -1.3686 | 36.3685 | -3.8033 | 31.6077 | 63.5978 | 48.5213 | 0 | 66.7977 | 665.3572 | 659.8357 | 634.2296 | 634.7418 | 619.6047 | 616.2881 | 381.7675 | 386.989 | 632.9045 | 635.8212 | 688.2736 | 701.7633 | 698.7152 | 698.6466 | 701.9199 | 703.098 | 703.3579 | 701.3705 | 694.8498 | 690.6723 | 690.1342 | 687.5519 | 689.029 | 689.7268 | 691.5128 | 688.6423 | 690.6202 | 687.826 | 688.861 | 692.848 | 701.2338 | 699.3594 | 699.9405
2025-04-10 00:20 | 10 | 0 | 20 | 6.2817e-272 | 1 | 29.384 | 396.3549 | 0.28867 | 0.0073898 | 103.039 | 103.039 | 103.039 | 103.039 | 8.3263 | 11.0533 | 537.6694 | 537.6694 | 537.6694 | 537.6694 | 58.4984 | 49.9632 | 15.7552 | 30.0387 | 15.6032 | 7.9857 | 28.7093 | 0 | 49.9624 | 15.2766 | 22.1 | 221 | 154840 | 237681 | 3547880.9362 | 99.9263 | 0.017771 | 0.53312 | 0.53312 | 0.53312 | 7.9917 | 1123.9687 | 1095.8 | 1095.7953 | 1093.9687 | 1166.6602 | 1166.6602 | 1166.6602 | 1166.6602 | 657.1664 | 657.1664 | 657.1664 | -0.0063554 | 0 | 1.5457 | 50.2422 | 146.8822 | 146.9855 | 190.5114 | 1.2799 | 2.229 | 0 | 57 | 55.9208 | 58.4984 | 105.0342 | -1.4066 | 30.0387 | -3.8592 | 28.6911 | 63.6169 | 48.4991 | 0 | 66.7973 | 660.3674 | 655.0447 | 631.9559 | 632.4497 | 618.4586 | 615.1393 | 381.0176 | 385.1669 | 632.5001 | 635.4525 | 662.2092 | 673.7501 | 669.0306 | 670.0014 | 672.2793 | 673.0474 | 672.4525 | 669.318 | 661.0609 | 656.7215 | 657.1484 | 656.3646 | 657.3974 | 661.8321 | 666.7989 | 664.7715 | 660.8158 | 655.0263 | 656.1611 | 659.8663 | 668.6133 | 667.3981 | 669.0881
2025-04-10 00:21 | 10 | 0 | 21 | 6.2817e-272 | 1 | 29.3813 | 396.8179 | 0.28877 | 0.0073906 | 102.8503 | 102.8503 | 102.8503 | 102.8503 | 8.3136 | 11.0555 | 536.7264 | 536.7264 | 536.7264 | 536.7264 | 58.4842 | 49.988 | 15.7544 | 29.5665 | 15.5984 | 7.9498 | 28.5958 | 0 | 49.9877 | 13.9149 | 22.1 | 221 | 154840 | 237681 | 3547885.8936 | 99.9761 | 0.0022369 | 0.067106 | 0.067106 | 0.067106 | 7.9917 | 1124.2019 | 1096.0398 | 1096.04 | 1094.2019 | 1167.2753 | 1167.2753 | 1167.2753 | 1167.2753 | 649.6227 | 649.6227 | 649.6227 | -0.0063864 | 0 | 1.4358 | 50.3314 | 146.7248 | 146.8388 | 189.1053 | 1.2505 | 2.2419 | 0 | 57 | 55.9034 | 58.4842 | 105.0292 | -1.8237 | 29.5665 | -3.9082 | 28.562 | 63.6684 | 48.4982 | 0 | 66.7972 | 655.4728 | 650.3133 | 630.2257 | 630.6247 | 617.0995 | 613.7256 | 380.2166 | 383.87 | 631.499 | 634.487 | 654.9547 | 663.9355 | 660.1282 | 660.4348 | 663.1313 | 663.8976 | 663.6256 | 661.2957 | 654.3591 | 650.7512 | 651.6087 | 650.6951 | 652.0376 | 654.5775 | 659.0885 | 657.5855 | 653.9816 | 648.8186 | 648.603 | 652.2254 | 660.7846 | 658.7357 | 659.8244
2025-04-10 00:22 | 10 | 0 | 22 | 6.2817e-272 | 1 | 29.3782 | 397.7201 | 0.2859 | 0.0073924 | 102.9398 | 102.9398 | 102.9398 | 102.9398 | 8.3208 | 11.0564 | 537.1297 | 537.1297 | 537.1297 | 537.1297 | 58.4194 | 49.9917 | 15.7545 | 29.5743 | 15.6003 | 7.968 | 28.5966 | 0 | 49.9925 | 14.2979 | 22.1 | 221 | 154840 | 237681 | 3547890.8511 | 99.9834 | -0.010244 | -0.30732 | -0.30732 | -0.30732 | 7.9917 | 1124.07 | 1095.9028 | 1095.9032 | 1094.07 | 1167.2655 | 1167.2655 | 1167.2655 | 1167.2655 | 650.0141 | 650.0141 | 650.0141 | -0.0063535 | 0 | 1.4358 | 50.4893 | 146.975 | 147.0818 | 188.3264 | 1.1909 | 2.2362 | 0 | 57 | 55.8884 | 58.4194 | 105.0299 | -1.9734 | 29.5743 | -3.9059 | 28.6274 | 63.7862 | 48.5014 | 0 | 66.797 | 651.9501 | 646.9173 | 628.9398 | 629.2597 | 615.5544 | 612.2666 | 379.3769 | 382.8769 | 630.2012 | 633.214 | 655.0336 | 663.4195 | 660.1718 | 660.0434 | 662.653 | 663.1118 | 663.2182 | 661.542 | 655.0434 | 651.764 | 652.8591 | 651.5613 | 653.4123 | 655.8377 | 659.387 | 657.6384 | 653.9732 | 649.7889 | 649.4595 | 652.9801 | 661.3823 | 659.1294 | 660.0898
2025-04-10 00:23 | 10 | 0 | 23 | 6.2817e-272 | 1 | 29.3796 | 398.3998 | 0.28365 | 0.0073928 | 103.491 | 103.491 | 103.491 | 103.491 | 8.3595 | 11.0551 | 538.424 | 538.424 | 538.424 | 538.424 | 58.4487 | 49.9778 | 15.7514 | 31.0629 | 15.6028 | 8.1495 | 29.2967 | 0 | 49.9791 | 14.9565 | 22.1 | 221 | 154840 | 237681 | 3547895.8261 | 99.9557 | -0.014056 | -0.42168 | -0.42168 | -0.42168 | 7.9917 | 1123.3728 | 1095.1865 | 1095.1861 | 1093.3728 | 1165.3259 | 1165.3259 | 1165.3259 | 1165.3259 | 655.802 | 655.802 | 655.802 | -0.0063994 | 0 | 2.022 | 50.799 | 147.8132 | 147.9247 | 187.9147 | 1.1905 | 2.2271 | 0 | 57 | 55.9758 | 58.4487 | 105.0094 | -2.1546 | 31.0629 | -3.8545 | 29.2797 | 63.9143 | 48.5055 | 0 | 66.7967 | 649.3265 | 644.4303 | 627.8762 | 628.1277 | 613.9917 | 610.7697 | 378.7191 | 382.1479 | 628.7528 | 631.7602 | 659.1003 | 667.7769 | 664.8134 | 664.0847 | 666.9538 | 667.7748 | 668.581 | 667.8661 | 661.9167 | 659.1905 | 660.4004 | 658.155 | 660.325 | 661.1824 | 664.3657 | 662.5065 | 660.2302 | 657.3833 | 656.1816 | 659.9945 | 668.5197 | 665.6166 | 665.9452
2025-04-10 00:24 | 10 | 0 | 24 | 6.2817e-272 | 1 | 29.3833 | 397.0695 | 0.28381 | 0.007394 | 103.1749 | 103.1749 | 103.1749 | 103.1749 | 8.3361 | 11.0544 | 537.3253 | 537.3253 | 537.3253 | 537.3253 | 58.3401 | 49.9671 | 15.7544 | 30.249 | 15.5975 | 8.0518 | 28.9159 | 0 | 49.9673 | 14.383 | 22.1 | 221 | 154840 | 237681 | 3547900.9149 | 99.9342 | -0.0080671 | -0.24201 | -0.24201 | -0.24201 | 7.9917 | 1123.7915 | 1095.617 | 1095.6168 | 1093.7915 | 1166.3855 | 1166.3855 | 1166.3855 | 1166.3855 | 651.4968 | 651.4968 | 651.4968 | -0.0064304 | 0 | 1.7289 | 50.6222 | 147.3318 | 147.4576 | 187.5732 | 1.2349 | 2.2361 | 0 | 57 | 56.0192 | 58.3401 | 105.029 | -1.9568 | 30.249 | -3.9514 | 28.9284 | 63.9948 | 48.5137 | 0 | 66.7968 | 647.3416 | 642.5303 | 626.7455 | 626.884 | 612.5316 | 609.2567 | 378.0853 | 381.6401 | 627.3362 | 630.3186 | 655.3287 | 664.0411 | 660.7179 | 660.4579 | 662.91 | 663.4794 | 664.3351 | 663.3437 | 656.9446 | 654.3663 | 655.5957 | 653.4553 | 655.602 | 657.2381 | 660.0206 | 658.6079 | 656.0171 | 652.5822 | 651.3018 | 655.3247 | 663.7181 | 660.9734 | 661.7864
2025-04-10 00:25 | 10 | 0 | 25 | 6.2817e-272 | 1 | 29.3865 | 396.5981 | 0.28243 | 0.0073967 | 103.087 | 103.087 | 103.087 | 103.087 | 8.3291 | 11.0548 | 536.984 | 536.984 | 536.984 | 536.984 | 58.1669 | 49.9637 | 15.754 | 30.143 | 15.598 | 8.0287 | 28.867 | 0 | 49.9642 | 14 | 22.1 | 221 | 154840 | 237681 | 3547905.8936 | 99.9274 | -0.014123 | -0.4237 | -0.4237 | -0.4237 | 7.9917 | 1123.9194 | 1095.7489 | 1095.747 | 1093.9194 | 1166.5238 | 1166.5238 | 1166.5238 | 1166.5238 | 649.922 | 649.922 | 649.922 | -0.0063947 | 0 | 1.7289 | 50.628 | 147.281 | 147.4094 | 187.2822 | 1.2479 | 2.2309 | 0 | 57 | 56.1033 | 58.1669 | 105.0264 | -2.0196 | 30.143 | -3.914 | 28.8454 | 64.048 | 48.5272 | 0 | 66.797 | 645.3187 | 640.5943 | 625.5933 | 625.6348 | 611.0876 | 607.8479 | 377.444 | 381.0588 | 625.8552 | 628.8283 | 653.742 | 662.286 | 658.869 | 658.6188 | 661.1335 | 661.6743 | 662.5967 | 661.8293 | 655.245 | 652.8663 | 654.195 | 651.9311 | 654.1244 | 655.6703 | 658.2655 | 657.0993 | 654.5789 | 651.3152 | 649.6722 | 653.8479 | 662.331 | 659.335 | 660.2485
2025-04-10 00:26 | 10 | 0 | 26 | 6.2817e-272 | 1 | 29.3865 | 395.9836 | 0.28331 | 0.0074092 | 103.1166 | 103.1166 | 103.1166 | 103.1166 | 8.3312 | 11.0545 | 537.1547 | 537.1547 | 537.1547 | 537.1547 | 58.1122 | 49.9565 | 15.7537 | 30.1825 | 15.6004 | 8.0146 | 28.8669 | 0 | 49.9566 | 14.4255 | 22.1 | 221 | 154840 | 237681 | 3547911 | 99.913 | 0.0059465 | 0.1784 | 0.1784 | 0.1784 | 7.9917 | 1123.8794 | 1095.7085 | 1095.7062 | 1093.8794 | 1166.4732 | 1166.4732 | 1166.4732 | 1166.4732 | 650.4586 | 650.4586 | 650.4586 | -0.0064531 | 0 | 1.8388 | 50.688 | 147.3187 | 147.4444 | 187.067 | 1.2697 | 2.2255 | 0 | 57 | 56.1899 | 58.1122 | 105.0245 | -1.9143 | 30.1825 | -3.8053 | 28.7949 | 64.0632 | 48.5768 | 0 | 66.7968 | 643.8461 | 639.1594 | 624.5676 | 624.5635 | 609.6913 | 606.5423 | 376.8205 | 380.6339 | 624.4309 | 627.3751 | 654.0446 | 662.7889 | 659.315 | 659.1669 | 661.5224 | 661.991 | 663.2443 | 662.2943 | 655.5368 | 653.3421 | 654.6826 | 652.3618 | 654.7018 | 656.504 | 658.86 | 657.6249 | 655.0184 | 651.9312 | 650.228 | 654.4498 | 662.7972 | 659.9151 | 661.0641
2025-04-10 00:27 | 10 | 0 | 27 | 6.2817e-272 | 1 | 29.3859 | 394.9249 | 0.28083 | 0.0074151 | 103.2841 | 103.2841 | 103.2841 | 103.2841 | 8.3432 | 11.0524 | 537.0714 | 537.0714 | 537.0714 | 537.0714 | 58.0979 | 49.9365 | 15.7524 | 30.6923 | 15.6013 | 8.1326 | 29.1463 | 0 | 49.9371 | 15.0638 | 22.1 | 221 | 154840 | 237681 | 3547916.0213 | 99.873 | -0.0021654 | -0.064963 | -0.064963 | -0.064963 | 7.9917 | 1123.664 | 1095.4857 | 1095.4872 | 1093.664 | 1165.8087 | 1165.8087 | 1165.8087 | 1165.8087 | 651.2067 | 651.2067 | 651.2067 | -0.0063812 | 0 | 1.9487 | 50.7231 | 147.5472 | 147.6716 | 186.858 | 1.2424 | 2.2094 | 0 | 57 | 56.1305 | 58.0979 | 105.0158 | -1.5817 | 30.6923 | -3.8566 | 29.2188 | 64.1006 | 48.6 | 0 | 66.7971 | 642.5044 | 637.7486 | 623.5687 | 623.471 | 608.3407 | 605.2455 | 376.1649 | 380.1853 | 623.0923 | 625.9505 | 653.9787 | 662.8912 | 659.6734 | 659.3526 | 661.8526 | 662.4217 | 664.0231 | 663.3296 | 656.8211 | 654.8007 | 656.0582 | 653.4316 | 655.8699 | 656.9136 | 659.2333 | 657.8722 | 656.3307 | 653.5558 | 651.4922 | 655.7731 | 663.8708 | 660.7318 | 661.5887
2025-04-10 00:28 | 10 | 0 | 28 | 6.2817e-272 | 1 | 29.3843 | 392.3599 | 0.28389 | 0.0074159 | 102.8362 | 102.8362 | 102.8362 | 102.8362 | 8.3118 | 11.0537 | 535.7541 | 535.7541 | 535.7541 | 535.7541 | 58.0164 | 49.9471 | 15.7529 | 29.5188 | 15.5987 | 7.941 | 28.597 | 0 | 49.9477 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3547921.0426 | 99.8943 | -0.0015094 | -0.045284 | -0.045284 | -0.045284 | 7.9917 | 1124.2313 | 1096.0696 | 1096.0696 | 1094.2313 | 1167.3372 | 1167.3372 | 1167.3372 | 1167.3372 | 645.5311 | 645.5311 | 645.5311 | -0.0064409 | 0 | 1.5457 | 50.5199 | 146.8874 | 147.0261 | 186.5682 | 1.2425 | 2.221 | 0 | 57 | 56.0381 | 58.0164 | 105.0193 | -1.281 | 29.5188 | -3.8235 | 28.5306 | 64.0973 | 48.6004 | 0 | 66.7973 | 641.2619 | 636.3697 | 622.4932 | 622.4471 | 607.0495 | 604.0404 | 375.6001 | 379.5271 | 621.8079 | 624.519 | 649.2124 | 658.0001 | 654.4235 | 654.6509 | 656.7211 | 657.0329 | 658.4987 | 657.248 | 650.3382 | 648.3241 | 649.4954 | 647.2683 | 649.614 | 651.8165 | 653.7829 | 652.9815 | 650.4863 | 646.7432 | 644.9932 | 649.3421 | 657.3286 | 654.5187 | 656.0016
2025-04-10 00:29 | 10 | 0 | 29 | 6.2817e-272 | 1 | 29.3847 | 392.2759 | 0.28384 | 0.0074102 | 102.9553 | 102.9553 | 102.9553 | 102.9553 | 8.3202 | 11.055 | 535.828 | 535.828 | 535.828 | 535.828 | 57.859 | 49.9528 | 15.7517 | 29.7111 | 15.6008 | 7.9812 | 28.6528 | 0 | 49.9531 | 14.1702 | 22.1 | 221 | 154840 | 237681 | 3547926.0213 | 99.9055 | -0.0026733 | -0.0802 | -0.0802 | -0.0802 | 7.9917 | 1124.0804 | 1095.9145 | 1095.9134 | 1094.0804 | 1167.0864 | 1167.0864 | 1167.0864 | 1167.0864 | 646.4309 | 646.4309 | 646.4309 | -0.0063967 | 0 | 1.9487 | 50.5663 | 147.0484 | 147.173 | 186.3387 | 1.2335 | 2.2221 | 0 | 57 | 55.8955 | 57.859 | 105.011 | -1.4017 | 29.7111 | -3.9296 | 28.675 | 64.1123 | 48.5792 | 0 | 66.7976 | 640.0615 | 635.0761 | 621.4809 | 621.4262 | 605.8132 | 602.8857 | 374.9375 | 379.0838 | 620.5446 | 623.1003 | 649.8921 | 658.4395 | 655.1508 | 655.261 | 657.1133 | 657.577 | 659.2979 | 658.0569 | 651.4802 | 649.6081 | 650.5716 | 648.3137 | 650.5607 | 652.7575 | 654.6862 | 653.9612 | 651.3503 | 647.8954 | 646.1963 | 650.4188 | 658.4063 | 655.5879 | 657.1961
2025-04-10 00:30 | 10 | 0 | 30 | 6.2817e-272 | 1 | 29.3828 | 392.3258 | 0.2821 | 0.0074038 | 102.8835 | 102.8835 | 102.8835 | 102.8835 | 8.3156 | 11.0559 | 535.6941 | 535.6941 | 535.6941 | 535.6941 | 57.7622 | 49.9577 | 15.7546 | 29.6061 | 15.6015 | 7.9575 | 28.6749 | 0 | 49.9582 | 13.6596 | 22.1 | 221 | 154840 | 237681 | 3547930.9574 | 99.9155 | -0.011606 | -0.34817 | -0.34817 | -0.34817 | 7.9917 | 1124.1602 | 1095.9981 | 1095.9977 | 1094.1602 | 1167.2236 | 1167.2236 | 1167.2236 | 1167.2236 | 645.5384 | 645.5384 | 645.5384 | -0.0064189 | 0 | 1.7655 | 50.5871 | 147.0574 | 147.1654 | 186.1174 | 1.213 | 2.2239 | 0 | 57 | 55.785 | 57.7622 | 105.0304 | -1.6019 | 29.6061 | -3.8959 | 28.5898 | 64.1169 | 48.551 | 0 | 66.7975 | 639.054 | 633.9077 | 620.5191 | 620.4955 | 604.7011 | 601.829 | 374.2532 | 378.4901 | 619.4079 | 621.7391 | 648.6297 | 657.2724 | 654.0477 | 654.136 | 656.0584 | 656.5145 | 658.4569 | 657.143 | 650.6885 | 648.9391 | 649.8433 | 647.4665 | 649.7651 | 651.7702 | 653.5328 | 652.9093 | 650.8342 | 647.2337 | 645.3762 | 649.9725 | 657.8606 | 654.9576 | 656.3227
2025-04-10 00:31 | 10 | 0 | 31 | 6.2817e-272 | 1 | 29.3846 | 390.6684 | 0.28622 | 0.0073966 | 103.0735 | 103.0735 | 103.0735 | 103.0735 | 8.3286 | 11.0557 | 536.0402 | 536.0402 | 536.0402 | 536.0402 | 57.7932 | 49.9556 | 15.7531 | 30.0676 | 15.6 | 8.0065 | 28.8839 | 0 | 49.9552 | 14.2609 | 22.1 | 221 | 154840 | 237681 | 3547935.913 | 99.9113 | 0.0095991 | 0.28797 | 0.28797 | 0.28797 | 7.9917 | 1123.9272 | 1095.7565 | 1095.7589 | 1093.9272 | 1166.6217 | 1166.6217 | 1166.6217 | 1166.6217 | 647.5604 | 647.5604 | 647.5604 | -0.006471 | 0 | 1.7974 | 50.7433 | 147.3308 | 147.4389 | 185.978 | 1.2356 | 2.2331 | 0 | 57 | 55.7647 | 57.7932 | 105.0207 | -1.6258 | 30.0676 | -3.8694 | 28.7657 | 64.1274 | 48.5251 | 0 | 66.7978 | 638.3861 | 633.1273 | 619.7872 | 619.7173 | 603.834 | 600.8951 | 373.665 | 378.0717 | 618.3613 | 620.467 | 650.3063 | 658.8539 | 656.0288 | 656.0791 | 658.0799 | 658.4763 | 660.5264 | 659.167 | 653.0157 | 651.3145 | 652.1426 | 649.5023 | 651.9568 | 653.9431 | 655.5362 | 654.6964 | 652.7818 | 649.3539 | 647.5479 | 652.2681 | 660.0146 | 656.9273 | 658.4316
2025-04-10 00:32 | 10 | 0 | 32 | 6.2817e-272 | 1 | 29.3886 | 388.915 | 0.28569 | 0.0073905 | 103.0237 | 103.0237 | 103.0237 | 103.0237 | 8.3241 | 11.0579 | 536.3168 | 536.3168 | 536.3168 | 536.3168 | 57.8416 | 49.9829 | 15.7525 | 29.8283 | 15.5989 | 8.0125 | 28.7663 | 0 | 49.9832 | 13.9149 | 22.1 | 221 | 154840 | 237681 | 3547940.8298 | 99.9658 | 0.010699 | 0.32098 | 0.32098 | 0.32098 | 7.9917 | 1124.0109 | 1095.8445 | 1095.8417 | 1094.0109 | 1166.9338 | 1166.9338 | 1166.9338 | 1166.9338 | 646.7918 | 646.7918 | 646.7918 | -0.0063602 | 0 | 1.8388 | 50.7492 | 147.254 | 147.3655 | 185.8798 | 1.2833 | 2.2356 | 0 | 57 | 55.8516 | 57.8416 | 105.0169 | -1.7252 | 29.8283 | -3.8514 | 28.7874 | 64.1365 | 48.505 | 0 | 66.7979 | 637.8455 | 632.5026 | 619.1964 | 618.9949 | 603.0676 | 600.0404 | 373.1629 | 377.6163 | 617.3713 | 619.3691 | 649.6039 | 658.1395 | 655.3737 | 655.4744 | 657.482 | 657.7117 | 659.7787 | 658.2291 | 651.9635 | 650.3937 | 651.3846 | 648.533 | 651.1091 | 653.1101 | 654.8071 | 654.0768 | 651.9655 | 648.3449 | 646.7074 | 651.5056 | 659.4476 | 656.2236 | 657.7573
2025-04-10 00:33 | 10 | 0 | 33 | 6.2817e-272 | 1 | 29.3883 | 388.5498 | 0.28768 | 0.0073874 | 103.0714 | 103.0714 | 103.0714 | 103.0714 | 8.3275 | 11.0601 | 536.7307 | 536.7307 | 536.7307 | 536.7307 | 57.9266 | 50.0099 | 15.7535 | 29.8694 | 15.5992 | 8.032 | 28.8304 | 0 | 50.0089 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3547945.766 | 100.0199 | 0.035238 | 1.0572 | 1.0572 | 1.0572 | 7.9917 | 1123.9462 | 1095.7777 | 1095.7785 | 1093.9462 | 1166.8806 | 1166.8806 | 1166.8806 | 1166.8806 | 646.843 | 646.843 | 646.843 | -0.0063777 | 0 | 1.8388 | 50.8142 | 147.4029 | 147.514 | 185.7598 | 1.2728 | 2.2445 | 0 | 57 | 55.9299 | 57.9266 | 105.023 | -1.854 | 29.8694 | -3.902 | 28.8573 | 64.147 | 48.4911 | 0 | 66.798 | 637.2988 | 631.925 | 618.644 | 618.4095 | 602.3514 | 599.3327 | 372.7103 | 377.1199 | 616.4944 | 618.357 | 649.6093 | 657.9945 | 655.4244 | 655.2987 | 657.5066 | 657.7432 | 659.8142 | 658.268 | 652.1174 | 650.5713 | 651.7079 | 648.8159 | 651.3685 | 653.0475 | 654.7076 | 654.0221 | 652.2354 | 648.6964 | 646.8448 | 651.4642 | 659.5579 | 656.2466 | 657.6454
2025-04-10 00:34 | 10 | 0 | 34 | 6.2817e-272 | 1 | 29.3847 | 388.786 | 0.28254 | 0.0073844 | 103.0188 | 103.0188 | 103.0188 | 103.0188 | 8.3247 | 11.0621 | 536.6251 | 536.6251 | 536.6251 | 536.6251 | 57.8934 | 50.031 | 15.7545 | 29.5289 | 15.598 | 7.9802 | 28.6485 | 0 | 50.0311 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3547950.766 | 100.0621 | 0.0061885 | 0.18565 | 0.18565 | 0.18565 | 7.9917 | 1124.0004 | 1095.8317 | 1095.8311 | 1094.0004 | 1167.3238 | 1167.3238 | 1167.3238 | 1167.3238 | 645.75 | 645.75 | 645.75 | -0.0063481 | 0 | 1.7655 | 50.8082 | 147.3415 | 147.4569 | 185.736 | 1.2583 | 2.2362 | 0 | 57 | 55.97 | 57.8934 | 105.0296 | -2.0208 | 29.5289 | -3.8274 | 28.6712 | 64.1417 | 48.4753 | 0 | 66.7982 | 636.8929 | 631.5066 | 618.1645 | 617.8784 | 601.7698 | 598.7159 | 372.2476 | 376.6798 | 615.623 | 617.4279 | 648.8317 | 657.1814 | 654.6785 | 654.5516 | 656.7003 | 656.7821 | 658.6694 | 656.9718 | 650.8467 | 649.0696 | 650.2813 | 647.5031 | 649.9591 | 652.1116 | 653.8983 | 653.0256 | 650.8571 | 647.1601 | 645.7783 | 650.0981 | 658.252 | 655.1433 | 656.6724
2025-04-10 00:35 | 10 | 0 | 35 | 6.2817e-272 | 1 | 29.3818 | 390.1681 | 0.28579 | 0.0073837 | 103.0669 | 103.0669 | 103.0669 | 103.0669 | 8.3288 | 11.0639 | 536.9283 | 536.9283 | 536.9283 | 536.9283 | 57.8913 | 50.052 | 15.7545 | 29.6909 | 15.5971 | 7.9899 | 28.6858 | 0 | 50.0526 | 13.7447 | 22.1 | 221 | 154840 | 237681 | 3547955.6809 | 100.104 | -0.010325 | -0.30976 | -0.30976 | -0.30976 | 7.9917 | 1123.9228 | 1095.7523 | 1095.7526 | 1093.9228 | 1167.1128 | 1167.1128 | 1167.1128 | 1167.1128 | 645.7216 | 645.7216 | 645.7216 | -0.0063343 | 0 | 1.8754 | 50.8278 | 147.414 | 147.5216 | 185.673 | 1.2104 | 2.23 | 0 | 57 | 56.0093 | 57.8913 | 105.0296 | -2.0653 | 29.6909 | -3.8975 | 28.7062 | 64.1446 | 48.47 | 0 | 66.7989 | 636.4246 | 631.0321 | 617.7437 | 617.4486 | 601.2517 | 598.1906 | 371.8679 | 376.2917 | 614.8343 | 616.5904 | 648.9133 | 656.8442 | 654.6077 | 654.2495 | 656.5988 | 656.7397 | 658.4843 | 656.912 | 651.1892 | 649.1713 | 650.5032 | 647.6708 | 650.116 | 651.9507 | 654.0681 | 653.0559 | 650.7458 | 647.1682 | 645.9043 | 650.0472 | 658.3049 | 654.9903 | 656.3108
2025-04-10 00:36 | 10 | 0 | 36 | 6.2817e-272 | 1 | 29.3823 | 390.7516 | 0.28636 | 0.0073796 | 102.9748 | 102.9748 | 102.9748 | 102.9748 | 8.3222 | 11.0665 | 536.8899 | 536.8899 | 536.8899 | 536.8899 | 57.9602 | 50.0822 | 15.7536 | 29.2087 | 15.5998 | 7.9441 | 28.5068 | 0 | 50.0829 | 13.3191 | 22.1 | 221 | 154840 | 237681 | 3547960.617 | 100.1644 | -0.0044741 | -0.13422 | -0.13422 | -0.13422 | 7.9917 | 1124.0423 | 1095.8751 | 1095.8753 | 1094.0423 | 1167.7406 | 1167.7406 | 1167.7406 | 1167.7406 | 643.9298 | 643.9298 | 643.9298 | -0.0062809 | 0 | 1.5823 | 50.8977 | 147.3409 | 147.4554 | 185.7 | 1.2188 | 2.2208 | 0 | 57 | 56.081 | 57.9602 | 105.0241 | -2.3782 | 29.2087 | -3.8874 | 28.5415 | 64.162 | 48.4546 | 0 | 66.799 | 636.0392 | 630.6288 | 617.2802 | 617.115 | 600.7573 | 597.7819 | 371.5735 | 375.8376 | 614.1157 | 615.8024 | 647.3356 | 655.2415 | 653.2621 | 652.8079 | 655.2083 | 655.2863 | 656.711 | 654.9385 | 649.1954 | 646.9697 | 648.4496 | 645.8527 | 648.1889 | 650.0696 | 652.4719 | 651.2042 | 648.7772 | 645.0042 | 644.0015 | 647.9281 | 656.3181 | 653.1608 | 654.5035
2025-04-10 00:37 | 10 | 0 | 37 | 6.2817e-272 | 1 | 29.3815 | 390.4036 | 0.28308 | 0.0073752 | 103.386 | 103.386 | 103.386 | 103.386 | 8.3515 | 11.0675 | 538.0056 | 538.0056 | 538.0056 | 538.0056 | 57.9665 | 50.0936 | 15.7538 | 30.2176 | 15.6002 | 8.0785 | 28.96 | 0 | 50.0938 | 14.766 | 22.1 | 221 | 154840 | 237681 | 3547965.5319 | 100.1869 | -0.0066342 | -0.19902 | -0.19902 | -0.19902 | 7.9917 | 1123.513 | 1095.3315 | 1095.333 | 1093.513 | 1166.4274 | 1166.4274 | 1166.4274 | 1166.4274 | 648.4349 | 648.4349 | 648.4349 | -0.0063974 | 0 | 2.022 | 51.1588 | 147.9888 | 148.0991 | 185.6204 | 1.2212 | 2.2331 | 0 | 57 | 56.082 | 57.9665 | 105.025 | -2.5718 | 30.2176 | -3.8864 | 29.0247 | 64.1547 | 48.4363 | 0 | 66.7997 | 635.7023 | 630.2783 | 616.918 | 616.8688 | 600.3124 | 597.4582 | 371.1894 | 375.4528 | 613.4403 | 615.071 | 651.0966 | 658.7611 | 657.4236 | 656.3142 | 659.073 | 659.4054 | 660.966 | 659.7775 | 654.6179 | 652.2772 | 653.7591 | 650.8368 | 653.4607 | 654.2848 | 656.7993 | 655.1563 | 653.2511 | 650.2645 | 649.2864 | 653.2683 | 661.6944 | 658.2534 | 658.8333
2025-04-10 00:38 | 10 | 0 | 38 | 6.2817e-272 | 1 | 29.3802 | 390.5786 | 0.28553 | 0.0073787 | 103.2195 | 103.2195 | 103.2195 | 103.2195 | 8.3401 | 11.0669 | 537.643 | 537.643 | 537.643 | 537.643 | 57.9936 | 50.0864 | 15.7531 | 29.8254 | 15.6003 | 8.0232 | 28.7804 | 0 | 50.0867 | 14.0426 | 22.1 | 221 | 154840 | 237681 | 3547970.5532 | 100.1726 | -0.00046484 | -0.013945 | -0.013945 | -0.013945 | 7.9917 | 1123.7234 | 1095.5468 | 1095.547 | 1093.7234 | 1166.9381 | 1166.9381 | 1166.9381 | 1166.9381 | 647.2315 | 647.2315 | 647.2315 | -0.0063428 | 0 | 1.9487 | 51.0074 | 147.7152 | 147.8155 | 185.6971 | 1.2131 | 2.2459 | 0 | 57 | 56.0496 | 57.9936 | 105.0208 | -2.234 | 29.8254 | -3.8621 | 28.8257 | 64.1662 | 48.4494 | 0 | 66.7995 | 635.5997 | 630.2303 | 616.583 | 616.596 | 599.8199 | 597.1248 | 370.9024 | 375.1138 | 612.8097 | 614.4623 | 650.2822 | 657.9385 | 656.4654 | 655.516 | 658.0584 | 658.5087 | 659.7539 | 658.3607 | 653.1566 | 650.6971 | 652.2089 | 649.459 | 651.9972 | 653.2218 | 655.9225 | 654.296 | 651.8659 | 648.5499 | 647.9197 | 651.4154 | 659.8843 | 657.0114 | 657.6072
2025-04-10 00:39 | 10 | 0 | 39 | 6.2817e-272 | 1 | 29.3797 | 390.4961 | 0.28797 | 0.0073812 | 103.3497 | 103.3497 | 103.3497 | 103.3497 | 8.3494 | 11.0675 | 538.1465 | 538.1465 | 538.1465 | 538.1465 | 58.0603 | 50.095 | 15.7512 | 30.2437 | 15.599 | 8.0743 | 28.9847 | 0 | 50.0957 | 14.5652 | 22.1 | 221 | 154840 | 237681 | 3547975.4565 | 100.1898 | -0.0062699 | -0.1881 | -0.1881 | -0.1881 | 7.9917 | 1123.5526 | 1095.3711 | 1095.3735 | 1093.5526 | 1166.393 | 1166.393 | 1166.393 | 1166.393 | 648.3443 | 648.3443 | 648.3443 | -0.0063763 | 0 | 1.6851 | 51.1397 | 147.953 | 148.0564 | 185.734 | 1.23 | 2.2422 | 0 | 57 | 55.987 | 58.0603 | 105.0079 | -2.1762 | 30.2437 | -3.8844 | 29.0095 | 64.1521 | 48.4581 | 0 | 66.7999 | 635.4182 | 630.113 | 616.3078 | 616.3278 | 599.5332 | 596.7732 | 370.5306 | 374.7423 | 612.2204 | 613.9634 | 650.9142 | 658.7562 | 657.5302 | 656.3533 | 659.3382 | 659.8457 | 660.9281 | 659.7011 | 654.6208 | 652.1063 | 653.6915 | 650.799 | 653.4062 | 653.8244 | 656.7847 | 654.8301 | 653.1749 | 650.1575 | 649.3135 | 652.9629 | 661.4783 | 658.2231 | 658.4773
2025-04-10 00:40 | 10 | 0 | 40 | 6.2817e-272 | 1 | 29.3777 | 391.1336 | 0.28994 | 0.0073838 | 103.1306 | 103.1306 | 103.1306 | 103.1306 | 8.3344 | 11.0672 | 537.7223 | 537.7223 | 537.7223 | 537.7223 | 58.0683 | 50.0927 | 15.7525 | 29.5714 | 15.6006 | 7.9827 | 28.657 | 0 | 50.0929 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3547980.4468 | 100.1851 | 0.0034375 | 0.10313 | 0.10313 | 0.10313 | 7.9917 | 1123.8251 | 1095.6526 | 1095.6504 | 1093.8251 | 1167.2689 | 1167.2689 | 1167.2689 | 1167.2689 | 646.5987 | 646.5987 | 646.5987 | -0.0064038 | 0 | 1.8388 | 50.9599 | 147.5935 | 147.7003 | 185.795 | 1.2073 | 2.2316 | 0 | 57 | 55.9822 | 58.0683 | 105.0166 | -2.0292 | 29.5714 | -3.8653 | 28.6803 | 64.1449 | 48.4663 | 0 | 66.8 | 635.2467 | 630.1621 | 616.0457 | 616.0268 | 599.3052 | 596.4332 | 370.1308 | 374.4051 | 611.6858 | 613.5961 | 650.0126 | 657.8423 | 656.0834 | 655.1993 | 657.9472 | 658.2146 | 659.0687 | 657.7828 | 652.2296 | 649.4754 | 651.2547 | 648.6901 | 651.0636 | 652.408 | 655.3746 | 653.6139 | 650.8845 | 647.6731 | 646.9726 | 650.4501 | 659.2788 | 656.3914 | 657.0167
2025-04-10 00:41 | 10 | 0 | 41 | 6.2817e-272 | 1 | 29.3771 | 390.4544 | 0.2861 | 0.0073852 | 103.4086 | 103.4086 | 103.4086 | 103.4086 | 8.3543 | 11.0658 | 538.1507 | 538.1507 | 538.1507 | 538.1507 | 58.0088 | 50.0787 | 15.7499 | 30.3833 | 15.6035 | 8.0987 | 29.0559 | 0 | 50.0793 | 14.4255 | 22.1 | 221 | 154840 | 237681 | 3547985.4468 | 100.1571 | 0.0017961 | 0.053883 | 0.053883 | 0.053883 | 7.9917 | 1123.4672 | 1095.2828 | 1095.28 | 1093.4672 | 1166.2115 | 1166.2115 | 1166.2115 | 1166.2115 | 649.4574 | 649.4574 | 649.4574 | -0.0063215 | 0 | 2.022 | 51.0682 | 147.9663 | 148.0781 | 185.8692 | 1.2454 | 2.2446 | 0 | 57 | 55.8865 | 58.0088 | 104.9993 | -1.8523 | 30.3833 | -3.9033 | 29.0972 | 64.1482 | 48.4723 | 0 | 66.8005 | 635.0405 | 630.1906 | 615.8102 | 615.7204 | 599.0361 | 596.1366 | 369.6683 | 374.1171 | 611.1579 | 613.2881 | 652.0928 | 660.09 | 658.3783 | 657.2893 | 660.5082 | 660.9767 | 662.0306 | 661.1964 | 655.5876 | 653.1025 | 655.0475 | 651.9697 | 654.652 | 654.8119 | 657.7463 | 655.8809 | 654.0833 | 651.453 | 650.0597 | 653.8682 | 662.882 | 659.4165 | 659.4267
2025-04-10 00:42 | 10 | 0 | 42 | 6.2817e-272 | 1 | 29.3755 | 390.7394 | 0.28544 | 0.0073901 | 103.1179 | 103.1179 | 103.1179 | 103.1179 | 8.3341 | 11.0677 | 537.4413 | 537.4413 | 537.4413 | 537.4413 | 57.9915 | 50.0977 | 15.755 | 29.5067 | 15.602 | 7.9936 | 28.6558 | 0 | 50.0981 | 13.9574 | 22.1 | 221 | 154840 | 237681 | 3547990.4468 | 100.1952 | 0.0003867 | 0.0116 | 0.0116 | 0.0116 | 7.9917 | 1123.8309 | 1095.6579 | 1095.6583 | 1093.8309 | 1167.3532 | 1167.3532 | 1167.3532 | 1167.3532 | 646.2026 | 646.2026 | 646.2026 | -0.0063328 | 0 | 1.7289 | 50.9853 | 147.5826 | 147.6986 | 185.9551 | 1.214 | 2.2353 | 0 | 57 | 55.7498 | 57.9915 | 105.033 | -2.1429 | 29.5067 | -3.8988 | 28.7195 | 64.148 | 48.4898 | 0 | 66.8004 | 634.8074 | 630.1644 | 615.5587 | 615.4354 | 598.7957 | 595.8336 | 369.2252 | 373.7496 | 610.6922 | 613.0187 | 649.5249 | 657.7948 | 655.4591 | 654.7607 | 657.7591 | 658.0216 | 658.5383 | 657.6144 | 651.4969 | 648.919 | 651.018 | 648.3222 | 650.8702 | 651.8704 | 654.7183 | 653.0023 | 650.4265 | 647.6385 | 646.2745 | 649.9236 | 658.9701 | 655.9654 | 656.3298
2025-04-10 00:43 | 10 | 0 | 43 | 6.2817e-272 | 1 | 29.3751 | 391.1169 | 0.28614 | 0.0073896 | 103.2764 | 103.2764 | 103.2764 | 103.2764 | 8.3454 | 11.0687 | 537.6308 | 537.6308 | 537.6308 | 537.6308 | 57.9806 | 50.1053 | 15.7526 | 29.9022 | 15.5996 | 8.0371 | 28.8342 | 0 | 50.1055 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3547995.4043 | 100.2106 | -0.0023477 | -0.070432 | -0.070432 | -0.070432 | 7.9917 | 1123.6249 | 1095.4443 | 1095.4443 | 1093.6249 | 1166.8383 | 1166.8383 | 1166.8383 | 1166.8383 | 647.5525 | 647.5525 | 647.5525 | -0.0063406 | 0 | 1.9121 | 51.1083 | 147.846 | 147.9549 | 186.0194 | 1.2075 | 2.2294 | 0 | 57 | 55.6568 | 57.9806 | 105.0171 | -2.3703 | 29.9022 | -3.89 | 28.8758 | 64.1462 | 48.489 | 0 | 66.8001 | 634.6261 | 630.1194 | 615.3554 | 615.1623 | 598.5859 | 595.5706 | 368.7646 | 373.3535 | 610.2874 | 612.761 | 650.6507 | 658.8098 | 656.3839 | 655.5856 | 658.7753 | 659.1656 | 659.8376 | 659.4052 | 653.2097 | 650.7769 | 652.8981 | 649.88 | 652.5123 | 652.9541 | 655.8467 | 654.1734 | 651.9649 | 649.5824 | 647.889 | 651.6095 | 660.6575 | 657.3207 | 657.4277
2025-04-10 00:44 | 10 | 0 | 44 | 6.2817e-272 | 1 | 29.3753 | 391.5636 | 0.28887 | 0.0073857 | 103.3935 | 103.3935 | 103.3935 | 103.3935 | 8.3537 | 11.069 | 537.8309 | 537.8309 | 537.8309 | 537.8309 | 57.9551 | 50.1104 | 15.7531 | 30.1089 | 15.5983 | 8.0708 | 28.9317 | 0 | 50.1106 | 14.5106 | 22.1 | 221 | 154840 | 237681 | 3548000.4043 | 100.2208 | 0.0052377 | 0.15713 | 0.15713 | 0.15713 | 7.9917 | 1123.4726 | 1095.2896 | 1095.2889 | 1093.4726 | 1166.5683 | 1166.5683 | 1166.5683 | 1166.5683 | 649.2969 | 649.2969 | 649.2969 | -0.0063015 | 0 | 1.9121 | 51.1925 | 148.0515 | 148.1732 | 186.079 | 1.1932 | 2.2329 | 0 | 57 | 55.6129 | 57.9551 | 105.0202 | -2.4765 | 30.1089 | -3.8913 | 28.9967 | 64.1455 | 48.4728 | 0 | 66.8006 | 634.517 | 630.1461 | 615.0939 | 614.9767 | 598.3269 | 595.3259 | 368.3984 | 372.9844 | 609.8945 | 612.4641 | 652.2081 | 660.2486 | 658.0938 | 657.0889 | 660.5163 | 660.9188 | 661.4692 | 661.2104 | 654.988 | 652.6065 | 654.8442 | 651.9299 | 654.5044 | 654.6582 | 657.498 | 655.7771 | 653.5658 | 651.4301 | 649.6396 | 653.5224 | 662.7599 | 659.3811 | 659.2436
2025-04-10 00:45 | 10 | 0 | 45 | 6.2817e-272 | 1 | 29.3745 | 392.518 | 0.29203 | 0.0073794 | 103.1605 | 103.1605 | 103.1605 | 103.1605 | 8.3374 | 11.0724 | 537.5364 | 537.5364 | 537.5364 | 537.5364 | 57.9636 | 50.1463 | 15.7523 | 29.6161 | 15.6002 | 8.0081 | 28.7057 | 0 | 50.1467 | 14 | 22.1 | 221 | 154840 | 237681 | 3548005.3404 | 100.2927 | -0.0037068 | -0.1112 | -0.1112 | -0.1112 | 7.9917 | 1123.7704 | 1095.5966 | 1095.5983 | 1093.7704 | 1167.2104 | 1167.2104 | 1167.2104 | 1167.2104 | 645.187 | 645.187 | 645.187 | -0.0062865 | 0 | 1.5091 | 51.1224 | 147.7151 | 147.8433 | 186.0603 | 1.1624 | 2.24 | 0 | 57 | 55.6994 | 57.9636 | 105.015 | -2.981 | 29.6161 | -3.9027 | 28.7715 | 64.1478 | 48.4448 | 0 | 66.801 | 634.306 | 630.0067 | 614.806 | 614.7858 | 598.0644 | 595.1367 | 367.985 | 372.6081 | 609.5518 | 612.2219 | 648.4682 | 656.5994 | 654.0287 | 653.448 | 656.7468 | 657.0891 | 657.3936 | 656.9354 | 650.5587 | 648.242 | 650.395 | 647.6718 | 650.2249 | 650.4778 | 653.34 | 651.8895 | 649.5229 | 647.1257 | 645.136 | 649.1983 | 658.122 | 654.9557 | 654.7496
2025-04-10 00:46 | 10 | 0 | 46 | 6.2817e-272 | 1 | 29.3756 | 391.3371 | 0.28701 | 0.0073791 | 103.4439 | 103.4439 | 103.4439 | 103.4439 | 8.3572 | 11.0705 | 538.6625 | 538.6625 | 538.6625 | 538.6625 | 58.0908 | 50.1294 | 15.753 | 30.2641 | 15.5996 | 8.0914 | 29 | 0 | 50.1295 | 14.7234 | 22.1 | 221 | 154840 | 237681 | 3548010.3404 | 100.259 | -0.0029694 | -0.089083 | -0.089083 | -0.089083 | 7.9917 | 1123.4128 | 1095.2279 | 1095.2281 | 1093.4128 | 1166.3668 | 1166.3668 | 1166.3668 | 1166.3668 | 649.7471 | 649.7471 | 649.7471 | -0.0062965 | 0 | 1.9121 | 51.2447 | 148.1688 | 148.2917 | 186.0803 | 1.1723 | 2.2355 | 0 | 57 | 55.9059 | 58.0908 | 105.02 | -2.4472 | 30.2641 | -3.8712 | 29.071 | 64.1484 | 48.4443 | 0 | 66.8014 | 634.4358 | 630.1274 | 614.6451 | 614.7334 | 597.7778 | 594.9857 | 367.6773 | 372.3958 | 609.2819 | 611.914 | 652.3818 | 660.7027 | 658.4197 | 657.4827 | 660.7115 | 661.2878 | 661.8886 | 661.7414 | 655.5666 | 653.2347 | 655.3181 | 652.4565 | 655.1522 | 655.0703 | 657.805 | 656.1649 | 653.9575 | 652.0607 | 650.2399 | 654.163 | 662.965 | 659.9557 | 659.5781
2025-04-10 00:47 | 10 | 0 | 47 | 6.2817e-272 | 1 | 29.3816 | 389.9551 | 0.28364 | 0.0073771 | 103.4087 | 103.4087 | 103.4087 | 103.4087 | 8.3531 | 11.0667 | 538.7247 | 538.7247 | 538.7247 | 538.7247 | 58.1835 | 50.0974 | 15.7536 | 30.3525 | 15.5987 | 8.1002 | 29.044 | 0 | 50.0975 | 15 | 22.1 | 221 | 154840 | 237681 | 3548015.3478 | 100.1948 | 0.002269 | 0.068069 | 0.068069 | 0.068069 | 7.9917 | 1123.4859 | 1095.3033 | 1095.3004 | 1093.4859 | 1166.2515 | 1166.2515 | 1166.2515 | 1166.2515 | 650.463 | 650.463 | 650.463 | -0.0062948 | 0 | 1.9471 | 51.1716 | 148.0567 | 148.1703 | 186.1298 | 1.2382 | 2.2451 | 0 | 57 | 56.079 | 58.1835 | 105.0239 | -2.3217 | 30.3525 | -3.8767 | 29.1025 | 64.1677 | 48.4436 | 0 | 66.8016 | 634.6695 | 630.246 | 614.4124 | 614.6063 | 597.5268 | 594.8218 | 367.4014 | 372.2081 | 609.0861 | 611.6181 | 652.9894 | 661.5066 | 659.2956 | 658.4679 | 661.595 | 662.2508 | 662.7959 | 662.3966 | 656.189 | 653.8234 | 655.7313 | 653.1491 | 655.754 | 655.8763 | 658.6459 | 656.783 | 654.745 | 652.6051 | 650.8535 | 654.7159 | 663.5583 | 660.693 | 660.3975
2025-04-10 00:48 | 10 | 0 | 48 | 6.2817e-272 | 1 | 29.3808 | 388.7239 | 0.28571 | 0.0073749 | 103.2811 | 103.2811 | 103.2811 | 103.2811 | 8.3443 | 11.0665 | 538.4837 | 538.4837 | 538.4837 | 538.4837 | 58.233 | 50.0956 | 15.7538 | 29.9855 | 15.6002 | 8.0561 | 28.8923 | 0 | 50.0959 | 14.2553 | 22.1 | 221 | 154840 | 237681 | 3548020.3191 | 100.1911 | 0.001188 | 0.035642 | 0.035642 | 0.035642 | 7.9917 | 1123.6434 | 1095.4645 | 1095.4636 | 1093.6434 | 1166.7289 | 1166.7289 | 1166.7289 | 1166.7289 | 648.8444 | 648.8444 | 648.8444 | -0.0062835 | 0 | 1.7289 | 51.0961 | 147.8526 | 147.9686 | 186.0779 | 1.252 | 2.2456 | 0 | 57 | 56.2196 | 58.233 | 105.0251 | -2.4943 | 29.9855 | -3.8618 | 28.9439 | 64.1819 | 48.4336 | 0 | 66.8019 | 634.7884 | 630.2337 | 614.126 | 614.3452 | 597.2629 | 594.6791 | 367.1447 | 372.0563 | 608.9551 | 611.3945 | 651.3987 | 660.2241 | 657.877 | 657.2172 | 660.0547 | 660.874 | 661.2904 | 660.6436 | 654.3117 | 652.0109 | 653.733 | 651.2115 | 653.9739 | 654.4245 | 657.0367 | 655.3302 | 652.9794 | 650.5634 | 648.962 | 653.0929 | 661.5912 | 659.0032 | 659.0202
2025-04-10 00:49 | 10 | 0 | 49 | 6.2817e-272 | 1 | 29.3813 | 388.1314 | 0.28612 | 0.0073706 | 103.5002 | 103.5002 | 103.5002 | 103.5002 | 8.3597 | 11.0652 | 538.7279 | 538.7279 | 538.7279 | 538.7279 | 58.2578 | 50.0791 | 15.7523 | 30.5351 | 15.6008 | 8.1146 | 29.1439 | 0 | 50.0796 | 14.6383 | 22.1 | 221 | 154840 | 237681 | 3548025.3617 | 100.1579 | 0.0055251 | 0.16575 | 0.16575 | 0.16575 | 7.9917 | 1123.3677 | 1095.1796 | 1095.1802 | 1093.3677 | 1166.0138 | 1166.0138 | 1166.0138 | 1166.0138 | 651.2226 | 651.2226 | 651.2226 | -0.0062982 | 0 | 1.9487 | 51.1413 | 148.1132 | 148.2342 | 186.04 | 1.2496 | 2.237 | 0 | 57 | 56.2345 | 58.2578 | 105.0151 | -2.2193 | 30.5351 | -3.952 | 29.1541 | 64.1489 | 48.4172 | 0 | 66.8017 | 634.884 | 630.257 | 613.9086 | 614.2234 | 597.0112 | 594.5061 | 366.8588 | 371.9651 | 608.8104 | 611.1586 | 653.3566 | 661.9041 | 659.8746 | 659.0335 | 662.0864 | 663.0165 | 663.7622 | 663.2119 | 657.1203 | 654.9089 | 656.5368 | 654.0037 | 656.7367 | 656.7342 | 659.3062 | 657.4681 | 655.7628 | 653.5359 | 651.7646 | 655.8124 | 664.2076 | 661.4463 | 661.2234
2025-04-10 00:50 | 10 | 0 | 50 | 6.2817e-272 | 1 | 29.3806 | 388.7828 | 0.28583 | 0.0073706 | 103.2317 | 103.2317 | 103.2317 | 103.2317 | 8.3408 | 11.0627 | 538.2276 | 538.2276 | 538.2276 | 538.2276 | 58.2735 | 50.0561 | 15.7539 | 30.0045 | 15.5982 | 8.0322 | 28.8409 | 0 | 50.0568 | 14.6809 | 22.1 | 221 | 154840 | 237681 | 3548030.4468 | 100.1122 | -0.005665 | -0.16995 | -0.16995 | -0.16995 | 7.9917 | 1123.706 | 1095.5298 | 1095.5277 | 1093.706 | 1166.7049 | 1166.7049 | 1166.7049 | 1166.7049 | 649.5929 | 649.5929 | 649.5929 | -0.0063743 | 0 | 1.9121 | 50.9651 | 147.6858 | 147.7898 | 186.1024 | 1.2189 | 2.231 | 0 | 57 | 56.1472 | 58.2735 | 105.026 | -2.0266 | 30.0045 | -3.8777 | 28.8582 | 64.1479 | 48.4171 | 0 | 66.8022 | 635.0219 | 630.3552 | 613.6942 | 614.0263 | 596.8268 | 594.3304 | 366.6594 | 371.7627 | 608.6928 | 611.0032 | 652.2273 | 661.2291 | 658.7518 | 658.2566 | 660.7375 | 661.6332 | 662.2739 | 661.3672 | 654.9415 | 652.5016 | 654.0146 | 651.7971 | 654.3663 | 655.5179 | 658.05 | 656.2915 | 653.7766 | 651.0664 | 649.7059 | 653.5828 | 661.9541 | 659.6827 | 660.0141
2025-04-10 00:51 | 10 | 0 | 51 | 6.2817e-272 | 1 | 29.3816 | 388.0721 | 0.28658 | 0.0073705 | 103.2164 | 103.2164 | 103.2164 | 103.2164 | 8.3395 | 11.0613 | 537.8538 | 537.8538 | 537.8538 | 537.8538 | 58.3613 | 50.0436 | 15.7537 | 30.0178 | 15.6007 | 8.0478 | 28.8701 | 0 | 50.0444 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3548035.4681 | 100.0872 | -0.00383 | -0.1149 | -0.1149 | -0.1149 | 7.9917 | 1123.7296 | 1095.5532 | 1095.554 | 1093.7296 | 1166.6868 | 1166.6868 | 1166.6868 | 1166.6868 | 648.4951 | 648.4951 | 648.4951 | -0.0063129 | 0 | 1.9487 | 50.902 | 147.621 | 147.7292 | 186.0942 | 1.2355 | 2.2348 | 0 | 57 | 56.1704 | 58.3613 | 105.0245 | -1.929 | 30.0178 | -3.855 | 28.9143 | 64.1495 | 48.4173 | 0 | 66.8024 | 634.8916 | 630.1696 | 613.4336 | 613.7516 | 596.6696 | 594.125 | 366.423 | 371.6121 | 608.6176 | 610.851 | 650.8718 | 659.8656 | 657.3747 | 656.7768 | 659.3067 | 660.3578 | 661.1283 | 660.346 | 654.1128 | 651.7605 | 653.1552 | 650.8583 | 653.4326 | 654.0873 | 656.764 | 655.1823 | 653.1263 | 650.4067 | 648.7571 | 652.7061 | 661.0599 | 658.4466 | 658.7268
2025-04-10 00:52 | 10 | 0 | 52 | 6.2817e-272 | 1 | 29.3832 | 387.3021 | 0.28588 | 0.0073697 | 102.8369 | 102.8369 | 102.8369 | 102.8369 | 8.3122 | 11.0631 | 537.02 | 537.02 | 537.02 | 537.02 | 58.3406 | 50.0645 | 15.753 | 28.8232 | 15.5976 | 7.912 | 28.3818 | 0 | 50.0652 | 13.4468 | 22.1 | 221 | 154840 | 237681 | 3548040.3617 | 100.1288 | 0.00034161 | 0.010248 | 0.010248 | 0.010248 | 7.9917 | 1124.2245 | 1096.0636 | 1096.0617 | 1094.2245 | 1168.2436 | 1168.2436 | 1168.2436 | 1168.2436 | 643.4166 | 643.4166 | 643.4166 | -0.0062897 | 0 | 1.6923 | 50.7067 | 147.0486 | 147.1577 | 185.9964 | 1.2387 | 2.2268 | 0 | 57 | 56.1456 | 58.3406 | 105.0199 | -2.2314 | 28.8232 | -3.8871 | 28.4262 | 64.1449 | 48.4166 | 0 | 66.8028 | 634.6607 | 629.9123 | 613.1571 | 613.5461 | 596.4636 | 593.9602 | 366.1784 | 371.3828 | 608.5036 | 610.6723 | 646.562 | 655.4554 | 652.6174 | 652.3751 | 654.5742 | 655.4307 | 656.0881 | 654.9517 | 648.4292 | 645.9407 | 647.2022 | 645.4163 | 647.7834 | 649.4527 | 651.9439 | 650.6942 | 647.9281 | 644.619 | 643.078 | 646.9883 | 655.271 | 652.9798 | 653.7357
2025-04-10 00:53 | 10 | 0 | 53 | 6.2817e-272 | 1 | 29.3807 | 387.5067 | 0.28456 | 0.0073691 | 103.2859 | 103.2859 | 103.2859 | 103.2859 | 8.3447 | 11.0641 | 538.0649 | 538.0649 | 538.0649 | 538.0649 | 58.3112 | 50.0726 | 15.7538 | 30.1124 | 15.5992 | 8.0691 | 28.9666 | 0 | 50.0723 | 14.5532 | 22.1 | 221 | 154840 | 237681 | 3548045.2979 | 100.145 | -0.00016342 | -0.0049034 | -0.0049034 | -0.0049034 | 7.9917 | 1123.6379 | 1095.4602 | 1095.4628 | 1093.6379 | 1166.5636 | 1166.5636 | 1166.5636 | 1166.5636 | 648.3446 | 648.3446 | 648.3446 | -0.0062736 | 0 | 1.9121 | 51.008 | 147.7589 | 147.8643 | 185.9936 | 1.2219 | 2.2361 | 0 | 57 | 56.0812 | 58.3112 | 105.0253 | -2.3457 | 30.1124 | -3.8614 | 28.9906 | 64.1391 | 48.4121 | 0 | 66.8032 | 634.6047 | 629.7131 | 613.0566 | 613.4457 | 596.2603 | 593.7991 | 365.7912 | 371.2152 | 608.3901 | 610.4295 | 650.4747 | 659.3592 | 657.1394 | 656.3193 | 658.7698 | 659.8463 | 660.9197 | 660.1443 | 654.0607 | 651.9941 | 653.2487 | 650.8846 | 653.3941 | 653.9715 | 656.439 | 654.9138 | 653.1108 | 650.4692 | 648.7421 | 652.9395 | 661.1265 | 658.4211 | 658.6624
2025-04-10 00:54 | 10 | 0 | 54 | 6.2817e-272 | 1 | 29.3794 | 388.0887 | 0.28734 | 0.0073672 | 103.2583 | 103.2583 | 103.2583 | 103.2583 | 8.343 | 11.0639 | 538.2213 | 538.2213 | 538.2213 | 538.2213 | 58.3198 | 50.0724 | 15.7534 | 30.0747 | 15.5968 | 8.0626 | 28.9421 | 0 | 50.0729 | 14.1702 | 22.1 | 221 | 154840 | 237681 | 3548050.2766 | 100.1446 | -0.00027535 | -0.0082609 | -0.0082609 | -0.0082609 | 7.9917 | 1123.6666 | 1095.4898 | 1095.4928 | 1093.6666 | 1166.6119 | 1166.6119 | 1166.6119 | 1166.6119 | 648.6312 | 648.6312 | 648.6312 | -0.0062477 | 0 | 1.9121 | 51.0136 | 147.7447 | 147.8465 | 186.0342 | 1.2135 | 2.2488 | 0 | 57 | 56.095 | 58.3198 | 105.0227 | -2.4511 | 30.0747 | -3.904 | 28.9674 | 64.1455 | 48.403 | 0 | 66.8035 | 634.7753 | 629.7919 | 613.0682 | 613.2914 | 596.1945 | 593.5619 | 365.521 | 371.0377 | 608.301 | 610.244 | 650.9704 | 659.5482 | 657.2277 | 656.6768 | 659.2151 | 660.0941 | 661.3898 | 660.4523 | 654.3348 | 652.3519 | 653.6406 | 651.1584 | 653.6738 | 654.5081 | 656.8903 | 655.3404 | 653.5131 | 650.815 | 648.9586 | 652.9994 | 661.0812 | 658.3061 | 658.8047
2025-04-10 00:55 | 10 | 0 | 55 | 6.2817e-272 | 1 | 29.3782 | 388.5406 | 0.28948 | 0.0073682 | 103.2367 | 103.2367 | 103.2367 | 103.2367 | 8.3418 | 11.0632 | 538.8886 | 538.8886 | 538.8886 | 538.8886 | 58.6228 | 50.0792 | 15.7534 | 29.9039 | 15.5996 | 8.0502 | 28.8702 | 0 | 50.0794 | 13.7391 | 22.1 | 221 | 154840 | 237681 | 3548055.2391 | 100.1582 | 0.003968 | 0.11904 | 0.11904 | 0.11904 | 7.9917 | 1123.6904 | 1095.5139 | 1095.5104 | 1093.6904 | 1166.8354 | 1166.8354 | 1166.8354 | 1166.8354 | 649.5474 | 649.5474 | 649.5474 | -0.0062336 | 0 | 1.9471 | 51.0414 | 147.7328 | 147.8425 | 186.1333 | 1.2123 | 2.2447 | 0 | 57 | 56.2119 | 58.6228 | 105.0228 | -2.2437 | 29.9039 | -3.888 | 28.9228 | 64.1432 | 48.4049 | 0 | 66.8031 | 635.0634 | 629.94 | 613.1317 | 613.238 | 596.1694 | 593.4432 | 365.323 | 370.841 | 608.2025 | 610.1004 | 651.843 | 660.5942 | 658.2612 | 657.7056 | 660.2672 | 660.9885 | 662.4156 | 661.5009 | 655.3522 | 653.1795 | 654.4607 | 651.8437 | 654.3725 | 655.5493 | 657.694 | 656.2088 | 654.3229 | 651.5671 | 649.8317 | 653.8351 | 662.1548 | 659.3247 | 659.9787
2025-04-10 00:56 | 10 | 0 | 56 | 6.2817e-272 | 1 | 29.3778 | 388.442 | 0.2851 | 0.0073681 | 103.4271 | 103.4271 | 103.4271 | 103.4271 | 8.3554 | 11.0609 | 539.6648 | 539.6648 | 539.6648 | 539.6648 | 59.0232 | 50.0719 | 15.7528 | 30.603 | 15.6012 | 8.1256 | 29.1672 | 0 | 50.0721 | 14.766 | 22.1 | 221 | 154840 | 237681 | 3548060.234 | 100.1437 | -0.0045914 | -0.13774 | -0.13774 | -0.13774 | 7.9917 | 1123.4462 | 1095.2621 | 1095.2619 | 1093.4462 | 1165.9249 | 1165.9249 | 1165.9249 | 1165.9249 | 652.0857 | 652.0857 | 652.0857 | -0.0062685 | 0 | 2.022 | 51.0733 | 148.0132 | 148.1251 | 186.2496 | 1.206 | 2.2492 | 0 | 57 | 56.2487 | 59.0232 | 105.0186 | -2.1347 | 30.603 | -3.8465 | 29.1937 | 64.165 | 48.4048 | 0 | 66.8038 | 635.4426 | 630.2106 | 613.2347 | 613.2146 | 596.2025 | 593.369 | 365.1431 | 370.9393 | 608.1919 | 609.9649 | 654.1043 | 662.8445 | 660.7017 | 660.155 | 662.7937 | 663.5002 | 665.2076 | 664.2034 | 658.1668 | 656.0087 | 657.3003 | 654.3777 | 657.004 | 657.9221 | 660.0636 | 658.4344 | 657.0028 | 654.2375 | 652.4206 | 656.7239 | 665.0857 | 661.9656 | 662.7304
2025-04-10 00:57 | 10 | 0 | 57 | 6.2817e-272 | 1 | 29.3777 | 389.3159 | 0.28663 | 0.0073642 | 102.9783 | 102.9783 | 102.9783 | 102.9783 | 8.3236 | 11.0625 | 539.0774 | 539.0774 | 539.0774 | 539.0774 | 59.1763 | 50.0961 | 15.7535 | 29.0501 | 15.6012 | 7.9421 | 28.4646 | 0 | 50.0965 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3548065.234 | 100.192 | 0.0068577 | 0.20573 | 0.20573 | 0.20573 | 7.9917 | 1124.0166 | 1095.8485 | 1095.8477 | 1094.0166 | 1167.9477 | 1167.9477 | 1167.9477 | 1167.9477 | 647.2659 | 647.2659 | 647.2659 | -0.0062457 | 0 | 1.5823 | 50.8986 | 147.3667 | 147.4812 | 186.2812 | 1.1859 | 2.2374 | 0 | 57 | 56.3049 | 59.1763 | 105.0231 | -2.1013 | 29.0501 | -3.8342 | 28.5346 | 64.1464 | 48.388 | 0 | 66.8036 | 635.6583 | 630.2579 | 613.1997 | 613.0449 | 596.1881 | 593.2172 | 364.9119 | 370.8063 | 608.1547 | 609.8141 | 650.3569 | 659.1618 | 656.6574 | 656.5109 | 658.9033 | 659.2085 | 660.5426 | 658.9002 | 652.3034 | 649.9339 | 651.3367 | 648.7349 | 651.2559 | 653.7543 | 655.7634 | 654.4619 | 651.5513 | 648.0128 | 646.7224 | 651.0044 | 659.4692 | 656.7089 | 658.2172
2025-04-10 00:58 | 10 | 0 | 58 | 6.2817e-272 | 1 | 29.3772 | 389.335 | 0.29136 | 0.007362 | 103.092 | 103.092 | 103.092 | 103.092 | 8.3318 | 11.0671 | 539.2471 | 539.2471 | 539.2471 | 539.2471 | 59.1929 | 50.1504 | 15.7545 | 29.2901 | 15.5997 | 7.9956 | 28.647 | 0 | 50.1508 | 13.4043 | 22.1 | 221 | 154840 | 237681 | 3548070.0213 | 100.301 | 0.0043106 | 0.12932 | 0.12932 | 0.12932 | 7.9917 | 1123.8728 | 1095.7015 | 1095.7006 | 1093.8728 | 1167.6355 | 1167.6355 | 1167.6355 | 1167.6355 | 645.5982 | 645.5982 | 645.5982 | -0.0062848 | 0 | 1.6923 | 51.0441 | 147.5643 | 147.6789 | 186.1929 | 1.2076 | 2.2541 | 0 | 57 | 56.3305 | 59.1929 | 105.0297 | -2.8747 | 29.2901 | -3.8624 | 28.7265 | 64.1402 | 48.3788 | 0 | 66.8038 | 635.4172 | 629.9274 | 613.1718 | 612.9287 | 596.1884 | 593.127 | 364.6134 | 370.4823 | 608.108 | 609.6778 | 648.1758 | 656.9056 | 654.5505 | 654.1446 | 656.8748 | 657.1718 | 658.8453 | 657.3718 | 651.1284 | 649.11 | 650.4141 | 647.2995 | 649.9583 | 651.4244 | 653.6015 | 652.4335 | 650.511 | 647.1771 | 645.4173 | 649.9077 | 658.3376 | 655.0059 | 656.1371
2025-04-10 00:59 | 10 | 0 | 59 | 6.2817e-272 | 1 | 29.3777 | 389.3093 | 0.28671 | 0.0073548 | 103.5051 | 103.5051 | 103.5051 | 103.5051 | 8.361 | 11.0628 | 540.6449 | 540.6449 | 540.6449 | 540.6449 | 59.4223 | 50.1134 | 15.7525 | 30.6201 | 15.6025 | 8.1345 | 29.1682 | 0 | 50.1142 | 15.4043 | 22.1 | 221 | 154840 | 237681 | 3548075.1064 | 100.2267 | -0.0061985 | -0.18596 | -0.18596 | -0.18596 | 7.9917 | 1123.3434 | 1095.1547 | 1095.1566 | 1093.3434 | 1165.903 | 1165.903 | 1165.903 | 1165.903 | 652.6726 | 652.6726 | 652.6726 | -0.0061919 | 0 | 1.9487 | 51.2541 | 148.2168 | 148.3291 | 186.2451 | 1.194 | 2.2474 | 0 | 57 | 56.4019 | 59.4223 | 105.0165 | -2.7617 | 30.6201 | -3.8978 | 29.2255 | 64.1433 | 48.3514 | 0 | 66.8044 | 635.808 | 630.1919 | 613.3235 | 613.0442 | 596.0826 | 593.039 | 364.3036 | 370.2399 | 607.9686 | 609.4871 | 654.6981 | 663.2453 | 661.4604 | 660.7436 | 663.5831 | 663.9552 | 665.8571 | 664.673 | 658.8007 | 656.724 | 658.0764 | 654.8144 | 657.6129 | 658.7419 | 660.5869 | 658.8734 | 657.4153 | 654.7887 | 653.11 | 657.3828 | 665.8742 | 662.5363 | 663.4399
2025-04-10 01:00 | 10 | 1 | 0 | 6.2817e-272 | 1 | 29.3777 | 388.7561 | 0.28526 | 0.0073499 | 103.472 | 103.472 | 103.472 | 103.472 | 8.3586 | 11.0582 | 540.1357 | 540.1357 | 540.1357 | 540.1357 | 59.3076 | 50.0575 | 15.752 | 30.7643 | 15.5996 | 8.1536 | 29.2663 | 0 | 50.0572 | 15.1064 | 22.1 | 221 | 154840 | 237681 | 3548080.234 | 100.1149 | 0.0099932 | 0.2998 | 0.2998 | 0.2998 | 7.9917 | 1123.3877 | 1095.2019 | 1095.2013 | 1093.3877 | 1165.7153 | 1165.7153 | 1165.7153 | 1165.7153 | 653.3777 | 653.3777 | 653.3777 | -0.0062317 | 0 | 2.022 | 51.1208 | 148.0543 | 148.1718 | 186.2532 | 1.2124 | 2.2385 | 0 | 57 | 56.421 | 59.3076 | 105.0131 | -2.9235 | 30.7643 | -3.8679 | 29.2942 | 64.1622 | 48.3299 | 0 | 66.8043 | 635.9605 | 630.3413 | 613.1232 | 612.8521 | 595.8756 | 592.8438 | 364.1128 | 370.0214 | 607.6689 | 609.1937 | 655.0792 | 663.9181 | 662.1775 | 661.4782 | 664.3198 | 664.886 | 666.7314 | 665.4254 | 659.5145 | 657.3827 | 658.6463 | 655.3826 | 658.1734 | 659.1606 | 661.2945 | 659.4312 | 658.3217 | 655.4159 | 653.8959 | 658.3869 | 666.8143 | 663.5003 | 664.2656
2025-04-10 01:01 | 10 | 1 | 1 | 6.2817e-272 | 1 | 29.3776 | 388.0736 | 0.28214 | 0.0073471 | 103.0363 | 103.0363 | 103.0363 | 103.0363 | 8.3278 | 11.0551 | 539.2962 | 539.2962 | 539.2962 | 539.2962 | 59.4153 | 50.0254 | 15.7518 | 29.8173 | 15.6015 | 8.0135 | 28.7731 | 0 | 50.0256 | 14.5106 | 22.1 | 221 | 154840 | 237681 | 3548085.3404 | 100.0509 | 0.0053215 | 0.15964 | 0.15964 | 0.15964 | 7.9917 | 1123.9419 | 1095.7728 | 1095.7672 | 1093.9419 | 1166.9483 | 1166.9483 | 1166.9483 | 1166.9483 | 649.7825 | 649.7825 | 649.7825 | -0.0061893 | 0 | 1.7655 | 50.7808 | 147.3146 | 147.4317 | 186.1231 | 1.2228 | 2.2525 | 0 | 57 | 56.4367 | 59.4153 | 105.0121 | -2.9784 | 29.8173 | -3.8663 | 28.7908 | 64.1482 | 48.3195 | 0 | 66.8048 | 635.8636 | 630.2737 | 612.7568 | 612.576 | 595.5537 | 592.67 | 363.8753 | 369.8555 | 607.325 | 608.8925 | 652.2873 | 661.3094 | 659.1956 | 658.8616 | 661.2459 | 661.7035 | 663.0652 | 661.5378 | 655.3887 | 652.8204 | 654.1253 | 651.2991 | 653.9971 | 655.9426 | 658.1171 | 656.3458 | 654.3256 | 650.806 | 649.8143 | 653.993 | 662.4616 | 659.5411 | 660.7235
2025-04-10 01:02 | 10 | 1 | 2 | 6.2817e-272 | 1 | 29.3777 | 388.0929 | 0.28569 | 0.0073472 | 103.055 | 103.055 | 103.055 | 103.055 | 8.3291 | 11.0554 | 539.0133 | 539.0133 | 539.0133 | 539.0133 | 59.37 | 50.0265 | 15.7518 | 29.8718 | 15.5984 | 8.02 | 28.7799 | 0 | 50.0259 | 14.5106 | 22.1 | 221 | 154840 | 237681 | 3548090.2766 | 100.0529 | 0.017828 | 0.53483 | 0.53483 | 0.53483 | 7.9917 | 1123.9172 | 1095.7462 | 1095.7496 | 1093.9172 | 1166.8772 | 1166.8772 | 1166.8772 | 1166.8772 | 648.7761 | 648.7761 | 648.7761 | -0.0062346 | 0 | 2.022 | 50.8129 | 147.3606 | 147.4783 | 185.8373 | 1.2315 | 2.2386 | 0 | 57 | 56.4937 | 59.37 | 105.012 | -2.989 | 29.8718 | -3.8572 | 28.8143 | 64.146 | 48.3193 | 0 | 66.8045 | 635.319 | 629.8291 | 612.4089 | 612.3272 | 595.3043 | 592.4565 | 363.5331 | 369.2301 | 606.9278 | 608.5894 | 651.0717 | 660.0306 | 658.0526 | 657.3937 | 660.0198 | 660.5657 | 661.9166 | 660.494 | 654.5377 | 652.0014 | 653.3537 | 650.5736 | 653.1757 | 654.803 | 657.2267 | 655.4642 | 653.3917 | 650.029 | 648.9078 | 653.0121 | 661.4737 | 658.6039 | 659.4446
2025-04-10 01:03 | 10 | 1 | 3 | 6.2817e-272 | 1 | 29.3776 | 387.6085 | 0.28519 | 0.0073431 | 103.0694 | 103.0694 | 103.0694 | 103.0694 | 8.3301 | 11.057 | 539.2938 | 539.2938 | 539.2938 | 539.2938 | 59.3653 | 50.0465 | 15.7515 | 29.894 | 15.5982 | 8.0297 | 28.8247 | 0 | 50.0475 | 13.6087 | 22.1 | 221 | 154840 | 237681 | 3548095.1739 | 100.093 | -0.0048042 | -0.14413 | -0.14413 | -0.14413 | 7.9917 | 1123.9011 | 1095.7298 | 1095.7315 | 1093.9011 | 1166.848 | 1166.848 | 1166.848 | 1166.848 | 648.1176 | 648.1176 | 648.1176 | -0.0061551 | 0 | 1.7225 | 50.869 | 147.4211 | 147.552 | 185.6189 | 1.234 | 2.2559 | 0 | 57 | 56.52 | 59.3653 | 105.0097 | -3.1747 | 29.894 | -3.8844 | 28.8493 | 64.1354 | 48.303 | 0 | 66.805 | 634.808 | 629.4592 | 612.146 | 612.1235 | 595.0792 | 592.259 | 363.2078 | 368.827 | 606.5508 | 608.3466 | 650.1738 | 659.2062 | 657.2806 | 656.393 | 659.1273 | 659.7591 | 661.0722 | 659.9946 | 654.332 | 651.769 | 652.901 | 650.0541 | 652.7148 | 653.784 | 656.3819 | 654.6682 | 652.7246 | 649.6025 | 648.4366 | 652.6099 | 661.1571 | 658.0159 | 658.6419
2025-04-10 01:04 | 10 | 1 | 4 | 6.2817e-272 | 1 | 29.3771 | 387.4134 | 0.28493 | 0.0073377 | 103.4528 | 103.4528 | 103.4528 | 103.4528 | 8.3574 | 11.0541 | 540.0443 | 540.0443 | 540.0443 | 540.0443 | 59.395 | 50.0145 | 15.7495 | 31.0332 | 15.6009 | 8.175 | 29.3691 | 0 | 50.0156 | 15.7021 | 22.1 | 221 | 154840 | 237681 | 3548100.1702 | 100.029 | -0.010436 | -0.31308 | -0.31308 | -0.31308 | 7.9917 | 1123.4104 | 1095.2249 | 1095.2253 | 1093.4104 | 1165.3643 | 1165.3643 | 1165.3643 | 1165.3643 | 653.3469 | 653.3469 | 653.3469 | -0.0062684 | 0 | 2.022 | 51.0593 | 147.9778 | 148.0988 | 185.6444 | 1.2284 | 2.2446 | 0 | 57 | 56.5345 | 59.395 | 104.9963 | -3.1216 | 31.0332 | -3.7965 | 29.3712 | 64.145 | 48.2809 | 0 | 66.8052 | 634.8301 | 629.5615 | 612.1124 | 612.0875 | 594.91 | 592.0895 | 362.8902 | 368.5474 | 606.2822 | 608.153 | 654.6751 | 663.7609 | 662.2083 | 661.1683 | 664.1317 | 664.8133 | 666.3231 | 665.5521 | 660.0572 | 657.6865 | 658.9163 | 655.6647 | 658.44 | 658.6475 | 661.2611 | 659.0389 | 657.9426 | 655.6197 | 654.3117 | 658.5487 | 666.9108 | 663.5939 | 663.8086
2025-04-10 01:05 | 10 | 1 | 5 | 6.2817e-272 | 1 | 29.3764 | 387.5684 | 0.28345 | 0.0073351 | 102.6906 | 102.6906 | 102.6906 | 102.6906 | 8.3036 | 11.0516 | 538.0096 | 538.0096 | 538.0096 | 538.0096 | 59.2338 | 49.979 | 15.7525 | 29.2186 | 15.6022 | 7.9197 | 28.4522 | 0 | 49.9798 | 14.1277 | 22.1 | 221 | 154840 | 237681 | 3548105.2766 | 99.9581 | -0.00026176 | -0.0078533 | -0.0078533 | -0.0078533 | 7.9917 | 1124.3762 | 1096.2194 | 1096.2191 | 1094.3762 | 1167.7274 | 1167.7274 | 1167.7274 | 1167.7274 | 646.2881 | 646.2881 | 646.2881 | -0.0062891 | 0 | 1.6556 | 50.521 | 146.7761 | 146.9046 | 185.6563 | 1.2182 | 2.2492 | 0 | 57 | 56.5763 | 59.2338 | 105.0162 | -2.7361 | 29.2186 | -3.8403 | 28.4539 | 64.1432 | 48.2686 | 0 | 66.8055 | 634.787 | 629.6519 | 611.9224 | 611.7607 | 594.8036 | 591.813 | 362.636 | 368.4937 | 606.0328 | 608.0374 | 649.4441 | 658.5167 | 655.8143 | 655.7883 | 658.045 | 658.3462 | 659.1454 | 657.8136 | 651.3951 | 648.7778 | 650.1694 | 647.7495 | 650.2016 | 652.6452 | 654.9994 | 653.4081 | 650.3612 | 646.8371 | 645.8046 | 649.8488 | 658.3272 | 655.82 | 657.0011
2025-04-10 01:06 | 10 | 1 | 6 | 6.2817e-272 | 1 | 29.3785 | 387.24 | 0.28411 | 0.0073313 | 102.8841 | 102.8841 | 102.8841 | 102.8841 | 8.3167 | 11.0519 | 538.1279 | 538.1279 | 538.1279 | 538.1279 | 59.2627 | 49.9828 | 15.7547 | 29.6802 | 15.6031 | 7.9848 | 28.76 | 0 | 49.9837 | 14.2553 | 22.1 | 221 | 154840 | 237681 | 3548110.1915 | 99.9656 | -0.010246 | -0.30738 | -0.30738 | -0.30738 | 7.9917 | 1124.143 | 1095.9783 | 1095.9774 | 1094.143 | 1167.1272 | 1167.1272 | 1167.1272 | 1167.1272 | 646.6934 | 646.6934 | 646.6934 | -0.0062944 | 0 | 1.4724 | 50.6775 | 147.0818 | 147.1967 | 185.655 | 1.2399 | 2.2391 | 0 | 57 | 56.6684 | 59.2627 | 105.0313 | -2.7843 | 29.6802 | -3.8209 | 28.688 | 64.1526 | 48.2561 | 0 | 66.8058 | 634.3036 | 629.2716 | 611.7316 | 611.4866 | 594.6827 | 591.6336 | 362.3169 | 368.0774 | 605.7728 | 607.9123 | 649.3652 | 658.0149 | 655.7362 | 655.3267 | 658.0682 | 658.4189 | 659.5686 | 658.6358 | 652.4092 | 650.0161 | 651.3156 | 648.6881 | 651.0923 | 652.1946 | 654.9124 | 653.4992 | 651.1483 | 648.1982 | 646.7814 | 651.1911 | 659.6432 | 656.3826 | 656.9696
2025-04-10 01:07 | 10 | 1 | 7 | 6.2817e-272 | 1 | 29.3836 | 386.9298 | 0.28391 | 0.0073368 | 102.9828 | 102.9828 | 102.9828 | 102.9828 | 8.3224 | 11.0538 | 538.4241 | 538.4241 | 538.4241 | 538.4241 | 59.1487 | 50.001 | 15.7515 | 29.8049 | 15.6013 | 8.0126 | 28.7636 | 0 | 49.9994 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3548115.1277 | 100.0021 | 0.033688 | 1.0106 | 1.0106 | 1.0106 | 7.9917 | 1124.0398 | 1095.8723 | 1095.8726 | 1094.0398 | 1166.9645 | 1166.9645 | 1166.9645 | 1166.9645 | 647.5552 | 647.5552 | 647.5552 | -0.0061821 | 0 | 1.8754 | 50.7403 | 147.2379 | 147.3472 | 185.6836 | 1.2711 | 2.246 | 0 | 57 | 56.7477 | 59.1487 | 105.0098 | -2.8664 | 29.8049 | -3.8741 | 28.7877 | 64.1385 | 48.2834 | 0 | 66.8057 | 634.0793 | 629.119 | 611.6699 | 611.4205 | 594.5873 | 591.5039 | 362.0058 | 367.9334 | 605.6339 | 607.788 | 649.958 | 658.7611 | 656.4732 | 655.9809 | 658.7703 | 659.043 | 660.1802 | 659.3824 | 653.2853 | 651.1216 | 652.4757 | 649.5504 | 652.077 | 653.1871 | 655.6734 | 654.3426 | 652.0164 | 649.3307 | 647.8248 | 652.1523 | 660.5705 | 657.2409 | 657.9028
2025-04-10 01:08 | 10 | 1 | 8 | 6.2817e-272 | 1 | 29.3847 | 385.5396 | 0.28298 | 0.0073438 | 103.1268 | 103.1268 | 103.1268 | 103.1268 | 8.3324 | 11.0554 | 538.1101 | 538.1101 | 538.1101 | 538.1101 | 59.0319 | 50.0056 | 15.7512 | 30.0961 | 15.5975 | 8.0558 | 28.9166 | 0 | 50.007 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3548120.0638 | 100.0112 | -0.02374 | -0.71219 | -0.71219 | -0.71219 | 7.9917 | 1123.8604 | 1095.6883 | 1095.6898 | 1093.8604 | 1166.5851 | 1166.5851 | 1166.5851 | 1166.5851 | 648.2031 | 648.2031 | 648.2031 | -0.0062294 | 0 | 1.7289 | 50.8406 | 147.4493 | 147.5506 | 185.7303 | 1.2718 | 2.2214 | 0 | 57 | 56.7643 | 59.0319 | 105.0081 | -3.0028 | 30.0961 | -3.8783 | 28.9427 | 64.1405 | 48.3122 | 0 | 66.806 | 634.1111 | 629.0079 | 611.6612 | 611.4329 | 594.4729 | 591.4518 | 361.8247 | 367.7774 | 605.6316 | 607.6529 | 650.4946 | 659.1152 | 656.9425 | 656.4777 | 659.1769 | 659.5438 | 660.9059 | 660.0389 | 654.0873 | 652.0826 | 653.4197 | 650.463 | 652.9729 | 653.8304 | 656.213 | 654.869 | 652.905 | 650.247 | 648.5642 | 653.0129 | 661.1882 | 657.7544 | 658.4404
2025-04-10 01:09 | 10 | 1 | 9 | 6.2817e-272 | 1 | 29.3805 | 385.9981 | 0.28459 | 0.0073529 | 102.853 | 102.853 | 102.853 | 102.853 | 8.314 | 11.0564 | 537.1993 | 537.1993 | 537.1993 | 537.1993 | 58.9798 | 50.0211 | 15.7555 | 29.3019 | 15.6008 | 7.9468 | 28.5606 | 0 | 50.0204 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3548125.0638 | 100.0422 | 0.014302 | 0.42907 | 0.42907 | 0.42907 | 7.9917 | 1124.1919 | 1096.0296 | 1096.033 | 1094.1919 | 1167.6196 | 1167.6196 | 1167.6196 | 1167.6196 | 645.1413 | 645.1413 | 645.1413 | -0.006184 | 0 | 1.4724 | 50.6665 | 147.0627 | 147.1727 | 185.8078 | 1.2271 | 2.2198 | 0 | 57 | 56.6322 | 58.9798 | 105.0366 | -2.9864 | 29.3019 | -3.9446 | 28.5511 | 64.1589 | 48.3446 | 0 | 66.8066 | 634.1092 | 628.9508 | 611.6033 | 611.4652 | 594.3903 | 591.4416 | 361.7739 | 367.7315 | 605.6107 | 607.5355 | 648.1644 | 656.7946 | 654.3345 | 654.2334 | 656.577 | 656.9707 | 657.8687 | 656.6189 | 650.4204 | 648.1754 | 649.383 | 646.8931 | 649.2918 | 651.0524 | 653.5649 | 652.3293 | 649.4752 | 646.2129 | 644.9578 | 649.2163 | 657.5472 | 654.628 | 655.6618
2025-04-10 01:10 | 10 | 1 | 10 | 6.2817e-272 | 1 | 29.381 | 387.084 | 0.28317 | 0.007365 | 103.266 | 103.266 | 103.266 | 103.266 | 8.3432 | 11.0566 | 537.9449 | 537.9449 | 537.9449 | 537.9449 | 58.8416 | 50.012 | 15.747 | 30.3997 | 15.6002 | 8.0835 | 29.0965 | 0 | 50.0117 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3548130.0638 | 100.024 | 0.01783 | 0.5349 | 0.5349 | 0.5349 | 7.9917 | 1123.6636 | 1095.4862 | 1095.4862 | 1093.6636 | 1166.19 | 1166.19 | 1166.19 | 1166.19 | 649.7212 | 649.7212 | 649.7212 | -0.0061139 | 0 | 2.022 | 50.9441 | 147.7088 | 147.8046 | 185.7736 | 1.2154 | 2.2349 | 0 | 57 | 56.5751 | 58.8416 | 104.9803 | -3.1787 | 30.3997 | -3.855 | 29.0426 | 64.147 | 48.3935 | 0 | 66.8066 | 634.1078 | 628.8766 | 611.5801 | 611.546 | 594.2673 | 591.4763 | 361.6632 | 367.5949 | 605.539 | 607.3599 | 651.6915 | 660.206 | 658.3849 | 657.7026 | 660.4163 | 661.116 | 662.339 | 661.5679 | 655.8997 | 653.742 | 655.0317 | 652.1641 | 654.816 | 655.3879 | 657.9088 | 656.1046 | 654.4193 | 651.7874 | 650.4785 | 654.637 | 662.7329 | 659.5476 | 659.8241
2025-04-10 01:11 | 10 | 1 | 11 | 6.2817e-272 | 1 | 29.3813 | 386.6176 | 0.28449 | 0.0073789 | 102.9634 | 102.9634 | 102.9634 | 102.9634 | 8.3216 | 11.0571 | 536.946 | 536.946 | 536.946 | 536.946 | 58.7659 | 50.0186 | 15.7504 | 29.5828 | 15.6019 | 7.9916 | 28.7027 | 0 | 50.018 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3548135.0851 | 100.0371 | 0.017613 | 0.52839 | 0.52839 | 0.52839 | 7.9917 | 1124.0498 | 1095.884 | 1095.887 | 1094.0498 | 1167.254 | 1167.254 | 1167.254 | 1167.254 | 645.9065 | 645.9065 | 645.9065 | -0.0061343 | 0 | 1.4724 | 50.7605 | 147.2571 | 147.3551 | 185.7294 | 1.2245 | 2.2258 | 0 | 57 | 56.4999 | 58.7659 | 105.0027 | -2.9643 | 29.5828 | -3.8452 | 28.7122 | 64.1422 | 48.4505 | 0 | 66.807 | 634.1398 | 628.757 | 611.3576 | 611.4953 | 594.0268 | 591.4187 | 361.5895 | 367.5556 | 605.5782 | 607.1663 | 648.6637 | 657.2619 | 655.0028 | 654.7316 | 656.8202 | 657.6202 | 658.6477 | 657.2245 | 651.4133 | 649.0372 | 650.2508 | 647.9637 | 650.3737 | 651.9621 | 654.5617 | 653.0215 | 650.5191 | 647.093 | 646.0297 | 650.2184 | 658.2481 | 655.5464 | 656.3523
2025-04-10 01:12 | 10 | 1 | 12 | 6.2817e-272 | 1 | 29.3789 | 387.5994 | 0.28237 | 0.0073987 | 103.0033 | 103.0033 | 103.0033 | 103.0033 | 8.3251 | 11.0583 | 537.1408 | 537.1408 | 537.1408 | 537.1408 | 58.7565 | 50.0302 | 15.7512 | 29.4477 | 15.601 | 7.9664 | 28.6073 | 0 | 50.0303 | 14.3913 | 22.1 | 221 | 154840 | 237681 | 3548140.0217 | 100.0604 | 0.0085195 | 0.25558 | 0.25558 | 0.25558 | 7.9917 | 1123.9898 | 1095.8217 | 1095.8204 | 1093.9898 | 1167.4293 | 1167.4293 | 1167.4293 | 1167.4293 | 646.8243 | 646.8243 | 646.8243 | -0.0061764 | 0 | 1.6102 | 50.7941 | 147.3332 | 147.4509 | 185.6225 | 1.1939 | 2.2266 | 0 | 57 | 56.4314 | 58.7565 | 105.0075 | -3.1515 | 29.4477 | -3.8436 | 28.6218 | 64.1592 | 48.5282 | 0 | 66.8072 | 634.0667 | 628.5858 | 611.214 | 611.4938 | 593.8182 | 591.3287 | 361.4045 | 367.3048 | 605.5244 | 607.0373 | 649.6279 | 657.9933 | 656.2031 | 655.6512 | 657.8052 | 658.5765 | 659.5687 | 658.1118 | 652.4433 | 649.9047 | 650.9291 | 649.0427 | 651.387 | 653.1125 | 655.6145 | 653.9147 | 651.2337 | 647.9587 | 647.2087 | 650.9559 | 658.8968 | 656.4061 | 657.3321
2025-04-10 01:13 | 10 | 1 | 13 | 6.2817e-272 | 1 | 29.3775 | 388.2009 | 0.28823 | 0.0074227 | 102.9065 | 102.9065 | 102.9065 | 102.9065 | 8.3186 | 11.0621 | 537.0539 | 537.0539 | 537.0539 | 537.0539 | 58.918 | 50.0766 | 15.7511 | 29.4639 | 15.599 | 7.9842 | 28.6805 | 0 | 50.0775 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3548144.7447 | 100.153 | -0.012159 | -0.36476 | -0.36476 | -0.36476 | 7.9917 | 1124.1094 | 1095.9445 | 1095.9466 | 1094.1094 | 1167.4089 | 1167.4089 | 1167.4089 | 1167.4089 | 643.3611 | 643.3611 | 643.3611 | -0.006149 | 0 | 1.7655 | 50.8623 | 147.2557 | 147.3741 | 185.5181 | 1.2074 | 2.2588 | 0 | 57 | 56.421 | 58.918 | 105.007 | -3.9446 | 29.4639 | -3.8939 | 28.6856 | 64.143 | 48.6227 | 0 | 66.8069 | 633.7054 | 628.223 | 611.1291 | 611.4315 | 593.7879 | 591.3358 | 361.1723 | 367.0331 | 605.5076 | 606.9823 | 645.6324 | 654.2354 | 652.4034 | 651.68 | 654.1559 | 655.0093 | 656.2229 | 654.7556 | 649.1548 | 646.9865 | 648.0556 | 645.552 | 648.0979 | 648.9006 | 651.704 | 650.4027 | 648.4562 | 645.0587 | 643.6326 | 647.7503 | 655.8591 | 652.9753 | 653.4915
2025-04-10 01:14 | 10 | 1 | 14 | 6.2817e-272 | 1 | 29.3794 | 388.7338 | 0.281 | 0.007452 | 103.164 | 103.164 | 103.164 | 103.164 | 8.3363 | 11.0567 | 537.9172 | 537.9172 | 537.9172 | 537.9172 | 59.197 | 50.0331 | 15.7541 | 29.9961 | 15.599 | 8.0416 | 28.8787 | 0 | 50.0331 | 14.766 | 22.1 | 221 | 154840 | 237681 | 3548149.7872 | 100.0661 | 0.0085923 | 0.25777 | 0.25777 | 0.25777 | 7.9917 | 1123.7879 | 1095.614 | 1095.6123 | 1093.7879 | 1166.7157 | 1166.7157 | 1166.7157 | 1166.7157 | 649.2812 | 649.2812 | 649.2812 | -0.0060611 | 0 | 1.8754 | 50.9109 | 147.6046 | 147.711 | 185.5825 | 1.1915 | 2.2324 | 0 | 57 | 56.5897 | 59.197 | 105.0273 | -3.2139 | 29.9961 | -3.8585 | 28.8918 | 64.1475 | 48.7413 | 0 | 66.8075 | 633.9377 | 628.508 | 611.2486 | 611.5416 | 593.6882 | 591.2588 | 361.0562 | 366.8497 | 605.2431 | 606.8743 | 651.4013 | 660.2637 | 658.681 | 657.7257 | 659.9972 | 660.8344 | 661.9986 | 660.7955 | 655.2676 | 652.6801 | 653.8135 | 651.4661 | 653.9385 | 655.2294 | 657.7851 | 655.8764 | 653.5578 | 650.8328 | 650.0198 | 653.9803 | 662.0635 | 659.4211 | 659.9517
2025-04-10 01:15 | 10 | 1 | 15 | 6.2817e-272 | 1 | 29.3789 | 389.0517 | 0.28167 | 0.0074836 | 102.998 | 102.998 | 102.998 | 102.998 | 8.3247 | 11.0578 | 537.1897 | 537.1897 | 537.1897 | 537.1897 | 58.8567 | 50.0265 | 15.7505 | 29.6913 | 15.5996 | 8.011 | 28.7621 | 0 | 50.026 | 14.0426 | 22.1 | 221 | 154840 | 237681 | 3548154.766 | 100.053 | 0.013416 | 0.40247 | 0.40247 | 0.40247 | 7.9917 | 1123.9996 | 1095.8306 | 1095.8309 | 1093.9996 | 1167.1123 | 1167.1123 | 1167.1123 | 1167.1123 | 646.6312 | 646.6312 | 646.6312 | -0.0062648 | 0 | 1.9854 | 50.8164 | 147.346 | 147.4543 | 185.5464 | 1.2058 | 2.2384 | 0 | 57 | 56.6717 | 58.8567 | 105.0035 | -3.1282 | 29.6913 | -3.9033 | 28.782 | 64.1515 | 48.8697 | 0 | 66.8078 | 633.7551 | 628.4399 | 611.1629 | 611.3914 | 593.6157 | 591.0922 | 360.7844 | 366.4959 | 605.0334 | 606.7573 | 649.166 | 657.7727 | 655.868 | 655.0497 | 657.4645 | 658.1769 | 659.2226 | 658.0532 | 652.3221 | 649.8226 | 651.1414 | 648.8467 | 651.1721 | 652.3918 | 655.2426 | 653.615 | 651.2421 | 648.1679 | 647.1266 | 650.9319 | 659.2276 | 656.5079 | 657.1044
2025-04-10 01:16 | 10 | 1 | 16 | 6.2817e-272 | 1 | 29.3806 | 389.9972 | 0.28159 | 0.0075148 | 103.0851 | 103.0851 | 103.0851 | 103.0851 | 8.3305 | 11.0597 | 537.4645 | 537.4645 | 537.4645 | 537.4645 | 58.762 | 50.0443 | 15.7503 | 29.9516 | 15.5992 | 8.0474 | 28.8976 | 0 | 50.0444 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3548159.6809 | 100.0886 | 0.002157 | 0.06471 | 0.06471 | 0.06471 | 7.9917 | 1123.8949 | 1095.7245 | 1095.7249 | 1093.8949 | 1166.7736 | 1166.7736 | 1166.7736 | 1166.7736 | 647.2659 | 647.2659 | 647.2659 | -0.0062234 | 0 | 2.022 | 50.9098 | 147.5584 | 147.6692 | 185.4745 | 1.2407 | 2.2522 | 0 | 57 | 56.3923 | 58.762 | 105.0019 | -3.2203 | 29.9516 | -3.905 | 28.9127 | 64.1396 | 48.9966 | 0 | 66.8079 | 633.5417 | 628.3256 | 611.1284 | 611.2912 | 593.53 | 590.9947 | 360.4726 | 366.2575 | 604.8328 | 606.6359 | 649.5136 | 658.0677 | 656.1189 | 655.1686 | 657.9454 | 658.7316 | 659.9896 | 659.0776 | 653.2689 | 650.8747 | 652.3112 | 649.7413 | 652.2042 | 652.9439 | 655.5792 | 653.8553 | 652.1549 | 649.4396 | 647.8035 | 651.6771 | 659.8949 | 657.0271 | 657.3651
2025-04-10 01:17 | 10 | 1 | 17 | 6.2817e-272 | 1 | 29.379 | 389.3984 | 0.28044 | 0.0075345 | 103.1733 | 103.1733 | 103.1733 | 103.1733 | 8.3371 | 11.0588 | 537.5657 | 537.5657 | 537.5657 | 537.5657 | 58.8423 | 50.0404 | 15.7509 | 30.0948 | 15.5996 | 8.0611 | 28.9155 | 0 | 50.0401 | 14.6809 | 22.1 | 221 | 154840 | 237681 | 3548164.7021 | 100.0808 | 0.00011575 | 0.003472 | 0.003472 | 0.003472 | 7.9917 | 1123.7732 | 1095.5985 | 1095.5987 | 1093.7732 | 1166.5864 | 1166.5864 | 1166.5864 | 1166.5864 | 648.5761 | 648.5761 | 648.5761 | -0.0061743 | 0 | 1.8022 | 50.9378 | 147.6006 | 147.7087 | 185.4824 | 1.1952 | 2.238 | 0 | 57 | 56.1744 | 58.8423 | 105.0056 | -3.2058 | 30.0948 | -3.8709 | 28.9621 | 64.1329 | 49.0757 | 0 | 66.8079 | 633.6208 | 628.4567 | 611.1429 | 611.2586 | 593.5141 | 590.899 | 360.144 | 365.9109 | 604.6601 | 606.5739 | 650.8323 | 659.6084 | 657.5504 | 656.7089 | 659.5794 | 660.1998 | 661.3432 | 660.4445 | 654.4854 | 651.9599 | 653.4934 | 650.8186 | 653.2857 | 654.2556 | 656.7878 | 655.0313 | 653.1237 | 650.5783 | 649.0133 | 652.9987 | 661.4941 | 658.573 | 659.0496
2025-04-10 01:18 | 10 | 1 | 18 | 6.2817e-272 | 1 | 29.3779 | 389.371 | 0.28035 | 0.0075374 | 103.0811 | 103.0811 | 103.0811 | 103.0811 | 8.3309 | 11.0591 | 537.336 | 537.336 | 537.336 | 537.336 | 58.9218 | 50.0467 | 15.7517 | 29.8146 | 15.5984 | 8.0174 | 28.7891 | 0 | 50.0473 | 13.8298 | 22.1 | 221 | 154840 | 237681 | 3548169.7021 | 100.0933 | 0.0043262 | 0.12979 | 0.12979 | 0.12979 | 7.9917 | 1123.8881 | 1095.7162 | 1095.7172 | 1093.8881 | 1166.9521 | 1166.9521 | 1166.9521 | 1166.9521 | 647.7202 | 647.7202 | 647.7202 | -0.0060813 | 0 | 1.8754 | 50.8749 | 147.4817 | 147.5657 | 185.4952 | 1.1954 | 2.2289 | 0 | 57 | 56.0366 | 58.9218 | 105.011 | -3.2477 | 29.8146 | -3.8595 | 28.8048 | 64.1404 | 49.0854 | 0 | 66.808 | 633.5819 | 628.5377 | 611.2043 | 611.1945 | 593.5411 | 590.7771 | 359.8398 | 365.7196 | 604.5434 | 606.52 | 650.445 | 659.1463 | 656.6806 | 656.0412 | 658.9608 | 659.4536 | 660.5044 | 659.6252 | 653.1893 | 650.6541 | 652.4229 | 649.7704 | 652.2264 | 653.5617 | 655.9812 | 654.4062 | 652.1039 | 649.3554 | 647.8023 | 651.8207 | 660.6278 | 657.6289 | 658.1975
2025-04-10 01:19 | 10 | 1 | 19 | 6.2817e-272 | 1 | 29.3776 | 389.7648 | 0.28407 | 0.0075386 | 103.0763 | 103.0763 | 103.0763 | 103.0763 | 8.3306 | 11.0586 | 536.9436 | 536.9436 | 536.9436 | 536.9436 | 58.9058 | 50.0404 | 15.7517 | 29.877 | 15.5999 | 8.0292 | 28.8249 | 0 | 50.041 | 14.383 | 22.1 | 221 | 154840 | 237681 | 3548174.6809 | 100.0807 | -0.0031399 | -0.094198 | -0.094198 | -0.094198 | 7.9917 | 1123.8934 | 1095.7217 | 1095.7247 | 1093.8934 | 1166.8698 | 1166.8698 | 1166.8698 | 1166.8698 | 647.0948 | 647.0948 | 647.0948 | -0.0061887 | 0 | 1.8754 | 50.8439 | 147.399 | 147.5211 | 185.5366 | 1.1775 | 2.2242 | 0 | 57 | 55.8765 | 58.9058 | 105.0111 | -3.056 | 29.877 | -3.8933 | 28.8475 | 64.1306 | 49.0884 | 0 | 66.8084 | 633.5177 | 628.3966 | 611.1141 | 611.1014 | 593.4429 | 590.6593 | 359.5694 | 365.4658 | 604.4043 | 606.3061 | 649.7387 | 658.4956 | 656.0262 | 655.4262 | 658.4113 | 658.8736 | 659.8696 | 658.8973 | 652.546 | 650.0955 | 651.9521 | 649.2365 | 651.7632 | 652.8596 | 655.2713 | 653.636 | 651.6193 | 648.871 | 647.0746 | 651.1091 | 659.9033 | 656.8921 | 657.5462
2025-04-10 01:20 | 10 | 1 | 20 | 6.2817e-272 | 1 | 29.378 | 388.596 | 0.28239 | 0.0075474 | 103.2189 | 103.2189 | 103.2189 | 103.2189 | 8.3406 | 11.0631 | 537.2077 | 537.2077 | 537.2077 | 537.2077 | 58.3428 | 50.0637 | 15.7509 | 30.1111 | 15.599 | 8.0627 | 28.9554 | 0 | 50.0643 | 14.0435 | 22.1 | 221 | 154840 | 237681 | 3548179.6087 | 100.1272 | -0.0032994 | -0.098981 | -0.098981 | -0.098981 | 7.9917 | 1123.7107 | 1095.5341 | 1095.5354 | 1093.7107 | 1166.5659 | 1166.5659 | 1166.5659 | 1166.5659 | 647.8889 | 647.8889 | 647.8889 | -0.0061131 | 0 | 1.7974 | 50.9683 | 147.6717 | 147.7901 | 185.3624 | 1.2082 | 2.2231 | 0 | 57 | 55.8689 | 58.3428 | 105.0055 | -2.8021 | 30.1111 | -3.8691 | 28.9677 | 64.1261 | 49.125 | 0 | 66.8089 | 633.2867 | 628.1527 | 610.9709 | 611.0141 | 593.251 | 590.5447 | 359.2952 | 365.0943 | 604.2062 | 606.099 | 650.3503 | 658.7612 | 656.3619 | 655.6898 | 658.8516 | 659.4913 | 660.6638 | 659.8018 | 653.5434 | 651.3655 | 653.1456 | 650.4539 | 652.8908 | 653.4998 | 655.8812 | 654.4353 | 652.7764 | 650.1215 | 648.1497 | 652.238 | 660.8695 | 657.7453 | 657.9733
2025-04-10 01:21 | 10 | 1 | 21 | 6.2817e-272 | 1 | 29.3784 | 388.152 | 0.28269 | 0.0075726 | 103.0876 | 103.0876 | 103.0876 | 103.0876 | 8.3312 | 11.0626 | 536.7125 | 536.7125 | 536.7125 | 536.7125 | 58.2287 | 50.0517 | 15.7525 | 29.6094 | 15.5994 | 8.0091 | 28.7198 | 0 | 50.0522 | 14.1702 | 22.1 | 221 | 154840 | 237681 | 3548184.5745 | 100.1032 | 0.0024975 | 0.074926 | 0.074926 | 0.074926 | 7.9917 | 1123.8832 | 1095.7119 | 1095.7104 | 1093.8832 | 1167.2191 | 1167.2191 | 1167.2191 | 1167.2191 | 647.4099 | 647.4099 | 647.4099 | -0.0060866 | 0 | 1.9121 | 50.8761 | 147.467 | 147.5893 | 185.2977 | 1.2225 | 2.2252 | 0 | 57 | 55.9227 | 58.2287 | 105.0162 | -2.6219 | 29.6094 | -3.827 | 28.775 | 64.1242 | 49.2292 | 0 | 66.8087 | 633.3227 | 628.1343 | 610.7749 | 610.8819 | 593.0418 | 590.3845 | 359.0567 | 365.0355 | 604.1072 | 605.8569 | 650.177 | 658.8097 | 656.2556 | 655.8859 | 658.5894 | 659.2047 | 660.1603 | 659.0794 | 652.621 | 650.334 | 652.0381 | 649.5489 | 652.0281 | 653.4372 | 655.7116 | 654.3579 | 651.8278 | 648.8744 | 647.3378 | 651.4448 | 660.0532 | 657.2799 | 657.9447
2025-04-10 01:22 | 10 | 1 | 22 | 6.2817e-272 | 1 | 29.3756 | 389.2171 | 0.28389 | 0.0076017 | 102.9176 | 102.9176 | 102.9176 | 102.9176 | 8.3199 | 11.0695 | 536.3777 | 536.3777 | 536.3777 | 536.3777 | 58.1424 | 50.1238 | 15.7514 | 28.9559 | 15.601 | 7.9384 | 28.4609 | 0 | 50.1239 | 13.1915 | 22.1 | 221 | 154840 | 237681 | 3548189.4255 | 100.2477 | 0.0070686 | 0.21206 | 0.21206 | 0.21206 | 7.9917 | 1124.0849 | 1095.9202 | 1095.9194 | 1094.0849 | 1168.0713 | 1168.0713 | 1168.0713 | 1168.0713 | 642.9605 | 642.9605 | 642.9605 | -0.0060814 | 0 | 1.4724 | 50.9444 | 147.3326 | 147.4651 | 185.1733 | 1.1807 | 2.2267 | 0 | 57 | 55.6755 | 58.1424 | 105.0091 | -3.5932 | 28.9559 | -3.9059 | 28.521 | 64.1209 | 49.3415 | 0 | 66.8092 | 632.9842 | 627.707 | 610.5992 | 610.716 | 592.8998 | 590.2631 | 358.783 | 364.7458 | 604.0406 | 605.6927 | 645.9248 | 654.4196 | 651.8441 | 651.5854 | 654.3108 | 654.799 | 655.7923 | 654.3868 | 647.9799 | 645.82 | 647.3818 | 645.0028 | 647.4143 | 649.0366 | 651.2599 | 650.1566 | 647.5883 | 644.2585 | 642.7534 | 646.9355 | 655.3209 | 652.5831 | 653.3412
2025-04-10 01:23 | 10 | 1 | 23 | 6.2817e-272 | 1 | 29.3739 | 390.2231 | 0.27967 | 0.0076176 | 103.7166 | 103.7166 | 103.7166 | 103.7166 | 8.3769 | 11.0642 | 538.0961 | 538.0961 | 538.0961 | 538.0961 | 58.022 | 50.0586 | 15.7496 | 31.4886 | 15.5962 | 8.238 | 29.5619 | 0 | 50.059 | 16.1277 | 22.1 | 221 | 154840 | 237681 | 3548194.5319 | 100.117 | -0.013261 | -0.39782 | -0.39782 | -0.39782 | 7.9917 | 1123.0553 | 1094.8581 | 1094.8585 | 1093.0553 | 1164.7713 | 1164.7713 | 1164.7713 | 1164.7713 | 654.1777 | 654.1777 | 654.1777 | -0.0061059 | 0 | 2.022 | 51.3287 | 148.5028 | 148.6086 | 185.1425 | 1.1382 | 2.2271 | 0 | 57 | 55.629 | 58.022 | 104.9974 | -3.0455 | 31.4886 | -3.8634 | 29.5975 | 64.1259 | 49.4023 | 0 | 66.8093 | 633.3154 | 627.86 | 610.6019 | 610.7776 | 592.6718 | 590.1607 | 358.5974 | 364.6567 | 603.8873 | 605.4529 | 655.4207 | 663.8248 | 662.5585 | 661.6015 | 664.6448 | 665.5471 | 667.1009 | 666.3014 | 660.746 | 658.7072 | 660.1208 | 657.1181 | 659.8396 | 659.7502 | 661.9423 | 659.7379 | 659.0743 | 656.9206 | 655.2322 | 659.6097 | 667.7569 | 664.4501 | 664.376
2025-04-10 01:24 | 10 | 1 | 24 | 6.2817e-272 | 1 | 29.3721 | 390.7578 | 0.28174 | 0.0076309 | 103.0338 | 103.0338 | 103.0338 | 103.0338 | 8.329 | 11.0641 | 536.5797 | 536.5797 | 536.5797 | 536.5797 | 58.1192 | 50.0586 | 15.7518 | 29.7143 | 15.6017 | 7.9999 | 28.7226 | 0 | 50.0588 | 14 | 22.1 | 221 | 154840 | 237681 | 3548199.5745 | 100.1171 | 0.00185 | 0.055498 | 0.055498 | 0.055498 | 7.9917 | 1123.9223 | 1095.7519 | 1095.75 | 1093.9223 | 1167.0821 | 1167.0821 | 1167.0821 | 1167.0821 | 646.8884 | 646.8884 | 646.8884 | -0.0061044 | 0 | 1.6556 | 50.886 | 147.43 | 147.5485 | 185.071 | 1.1314 | 2.2285 | 0 | 57 | 55.4983 | 58.1192 | 105.0118 | -2.6945 | 29.7143 | -3.8897 | 28.742 | 64.1211 | 49.4542 | 0 | 66.8091 | 633.3936 | 627.8282 | 610.3278 | 610.6395 | 592.4296 | 590.0251 | 358.543 | 364.5835 | 603.8333 | 605.2165 | 649.3561 | 658.1952 | 656.0861 | 655.9565 | 658.0696 | 658.9301 | 659.9736 | 658.2913 | 652.318 | 649.9977 | 651.07 | 648.9693 | 651.3322 | 653.0769 | 655.4078 | 653.8484 | 651.441 | 647.8881 | 646.8155 | 651.0075 | 659.0503 | 656.6554 | 657.6097
2025-04-10 01:25 | 10 | 1 | 25 | 6.2817e-272 | 1 | 29.3757 | 390.5427 | 0.27826 | 0.0076399 | 103.2539 | 103.2539 | 103.2539 | 103.2539 | 8.3437 | 11.0652 | 536.5623 | 536.5623 | 536.5623 | 536.5623 | 57.8555 | 50.0594 | 15.7511 | 30.1875 | 15.5987 | 8.0648 | 28.973 | 0 | 50.0599 | 14 | 22.1 | 221 | 154840 | 237681 | 3548204.5745 | 100.1187 | -0.0044169 | -0.13251 | -0.13251 | -0.13251 | 7.9917 | 1123.6545 | 1095.4768 | 1095.4772 | 1093.6545 | 1166.4664 | 1166.4664 | 1166.4664 | 1166.4664 | 648.248 | 648.248 | 648.248 | -0.0061003 | 0 | 2.022 | 51.0544 | 147.7823 | 147.9062 | 184.9026 | 1.1538 | 2.2114 | 0 | 57 | 55.4457 | 57.8555 | 105.007 | -2.4429 | 30.1875 | -3.8537 | 28.9752 | 64.1227 | 49.4946 | 0 | 66.8094 | 633.2362 | 627.5945 | 610.1073 | 610.562 | 592.2318 | 589.9818 | 358.4017 | 364.4791 | 603.748 | 605.0855 | 650.4279 | 658.8272 | 657.1176 | 656.5868 | 658.8917 | 660.0605 | 661.2897 | 659.7093 | 654.1947 | 652.0224 | 652.9383 | 650.7304 | 653.2353 | 654.1739 | 656.6941 | 655.3084 | 653.1635 | 649.7757 | 648.5525 | 652.7726 | 660.5932 | 658.0089 | 658.6246
2025-04-10 01:26 | 10 | 1 | 26 | 6.2817e-272 | 1 | 29.3767 | 389.6645 | 0.28037 | 0.00765 | 103.1663 | 103.1663 | 103.1663 | 103.1663 | 8.3372 | 11.0646 | 536.2796 | 536.2796 | 536.2796 | 536.2796 | 57.8679 | 50.0548 | 15.7508 | 29.9199 | 15.5992 | 8.0644 | 28.8805 | 0 | 50.0548 | 14.1277 | 22.1 | 221 | 154840 | 237681 | 3548209.5957 | 100.1096 | 0.0072843 | 0.21853 | 0.21853 | 0.21853 | 7.9917 | 1123.7715 | 1095.597 | 1095.5974 | 1093.7715 | 1166.8147 | 1166.8147 | 1166.8147 | 1166.8147 | 647.5835 | 647.5835 | 647.5835 | -0.0060892 | 0 | 1.9487 | 50.9191 | 147.5943 | 147.7097 | 184.8786 | 1.1925 | 2.2208 | 0 | 57 | 55.3761 | 57.8679 | 105.0051 | -2.4413 | 29.9199 | -3.8524 | 28.9737 | 64.1246 | 49.5352 | 0 | 66.8095 | 633.1977 | 627.5713 | 609.9916 | 610.5207 | 592.1572 | 589.9168 | 358.2811 | 364.2799 | 603.7256 | 605.0406 | 649.6919 | 658.4483 | 656.7091 | 656.3086 | 658.3685 | 659.4214 | 660.5808 | 659.0033 | 653.3387 | 651.0146 | 651.9013 | 649.82 | 652.2963 | 653.776 | 656.1677 | 654.6096 | 652.3194 | 648.8661 | 647.8387 | 652.0414 | 659.7923 | 657.3878 | 658.1424
2025-04-10 01:27 | 10 | 1 | 27 | 6.2817e-272 | 1 | 29.3744 | 390.2851 | 0.28012 | 0.0076605 | 103.3863 | 103.3863 | 103.3863 | 103.3863 | 8.3534 | 11.0645 | 536.8464 | 536.8464 | 536.8464 | 536.8464 | 58.0803 | 50.0624 | 15.7505 | 30.4883 | 15.6054 | 8.1178 | 29.1293 | 0 | 50.0631 | 14.5957 | 22.1 | 221 | 154840 | 237681 | 3548214.5957 | 100.1246 | -0.0033767 | -0.1013 | -0.1013 | -0.1013 | 7.9917 | 1123.4774 | 1095.2936 | 1095.2964 | 1093.4774 | 1166.0745 | 1166.0745 | 1166.0745 | 1166.0745 | 650.0165 | 650.0165 | 650.0165 | -0.0060824 | 0 | 2.022 | 51.1223 | 147.962 | 148.0836 | 184.8464 | 1.1618 | 2.239 | 0 | 57 | 55.3688 | 58.0803 | 105.0035 | -2.6254 | 30.4883 | -3.8556 | 29.1657 | 64.1151 | 49.5763 | 0 | 66.8095 | 633.158 | 627.5654 | 610.0354 | 610.5226 | 592.1871 | 589.8728 | 358.1538 | 364.2415 | 603.6713 | 605.0298 | 651.6678 | 660.3194 | 658.9429 | 658.0853 | 660.4875 | 661.6579 | 663.0065 | 661.5949 | 656.1934 | 654.0683 | 654.9786 | 652.6056 | 655.0449 | 655.7513 | 658.3164 | 656.7683 | 654.877 | 651.7936 | 650.6628 | 654.9711 | 662.8378 | 660.1545 | 660.4922
2025-04-10 01:28 | 10 | 1 | 28 | 6.2817e-272 | 1 | 29.3712 | 391.2786 | 0.27761 | 0.0076711 | 103.0721 | 103.0721 | 103.0721 | 103.0721 | 8.3319 | 11.0643 | 536.3768 | 536.3768 | 536.3768 | 536.3768 | 58.1006 | 50.0643 | 15.7495 | 29.6975 | 15.6003 | 8.015 | 28.7719 | 0 | 50.0642 | 13.7826 | 22.1 | 221 | 154840 | 237681 | 3548219.6087 | 100.1285 | 0.0044357 | 0.13307 | 0.13307 | 0.13307 | 7.9917 | 1123.8691 | 1095.6967 | 1095.6957 | 1093.8691 | 1167.1048 | 1167.1048 | 1167.1048 | 1167.1048 | 647.4871 | 647.4871 | 647.4871 | -0.0060458 | 0 | 1.76 | 50.9243 | 147.501 | 147.6376 | 184.8666 | 1.1333 | 2.2521 | 0 | 57 | 55.3036 | 58.1006 | 104.9964 | -2.3842 | 29.6975 | -3.8565 | 28.7965 | 64.1048 | 49.6152 | 0 | 66.8096 | 633.1797 | 627.6897 | 610.0371 | 610.4495 | 592.1474 | 589.8053 | 358.0907 | 364.1493 | 603.577 | 605.0521 | 650.0419 | 658.6926 | 656.8563 | 656.2927 | 658.3486 | 659.3247 | 660.2945 | 658.7917 | 653.0202 | 650.6446 | 651.7458 | 649.55 | 652.1093 | 653.6419 | 656.2746 | 654.7087 | 651.8926 | 648.4597 | 647.6943 | 651.807 | 659.7462 | 657.31 | 658.0458
2025-04-10 01:29 | 10 | 1 | 29 | 6.2817e-272 | 1 | 29.3703 | 391.903 | 0.27962 | 0.0076822 | 103.0984 | 103.0984 | 103.0984 | 103.0984 | 8.334 | 11.0669 | 536.4725 | 536.4725 | 536.4725 | 536.4725 | 57.9983 | 50.0852 | 15.7508 | 29.6957 | 15.5978 | 8.0347 | 28.7921 | 0 | 50.0855 | 14 | 22.1 | 221 | 154840 | 237681 | 3548224.4468 | 100.1702 | 0.0017764 | 0.053293 | 0.053293 | 0.053293 | 7.9917 | 1123.8302 | 1095.6577 | 1095.656 | 1093.8302 | 1167.1064 | 1167.1064 | 1167.1064 | 1167.1064 | 646.3542 | 646.3542 | 646.3542 | -0.0059864 | 0 | 1.8754 | 51.048 | 147.6048 | 147.7504 | 184.8489 | 1.1203 | 2.2172 | 0 | 57 | 55.5646 | 57.9983 | 105.0049 | -2.6408 | 29.6957 | -3.8991 | 28.8671 | 64.1026 | 49.6581 | 0 | 66.81 | 632.9457 | 627.6214 | 610.0757 | 610.3936 | 592.206 | 589.7744 | 357.9303 | 363.8784 | 603.4889 | 605.0487 | 648.8463 | 657.361 | 655.4586 | 654.8133 | 657.063 | 657.9682 | 659.0454 | 657.8657 | 652.2058 | 649.8294 | 650.9724 | 648.5375 | 651.0488 | 652.221 | 654.9103 | 653.5417 | 651.0943 | 647.9103 | 646.8607 | 650.6934 | 658.6927 | 655.8973 | 656.5352
2025-04-10 01:30 | 10 | 1 | 30 | 6.2817e-272 | 1 | 29.3703 | 391.9074 | 0.27778 | 0.0077032 | 103.3177 | 103.3177 | 103.3177 | 103.3177 | 8.3496 | 11.0654 | 536.7469 | 536.7469 | 536.7469 | 536.7469 | 57.7578 | 50.0604 | 15.7538 | 30.2872 | 15.5989 | 8.0918 | 29.0207 | 0 | 50.0605 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3548229.4894 | 100.1207 | -0.0025108 | -0.075323 | -0.075323 | -0.075323 | 7.9917 | 1123.5481 | 1095.3674 | 1095.3664 | 1093.5481 | 1166.336 | 1166.336 | 1166.336 | 1166.336 | 649.5549 | 649.5549 | 649.5549 | -0.0060471 | 0 | 2.022 | 51.1716 | 147.9405 | 148.0623 | 184.8951 | 1.1249 | 2.2204 | 0 | 57 | 55.4811 | 57.7578 | 105.0253 | -2.9852 | 30.2872 | -3.8537 | 29.0724 | 64.0931 | 49.743 | 0 | 66.8102 | 632.8997 | 627.6803 | 610.1239 | 610.3116 | 592.173 | 589.6251 | 357.7484 | 363.7407 | 603.3458 | 605.0474 | 651.7169 | 660.3374 | 658.6924 | 657.7605 | 660.224 | 660.9566 | 662.1809 | 661.2422 | 655.623 | 653.1943 | 654.4089 | 651.7939 | 654.2931 | 655.2973 | 658.089 | 656.3941 | 654.1269 | 651.4546 | 650.3498 | 654.3906 | 662.2907 | 659.4281 | 659.8807
2025-04-10 01:31 | 10 | 1 | 31 | 6.2817e-272 | 1 | 29.3703 | 391.7584 | 0.27749 | 0.0077227 | 103.2581 | 103.2581 | 103.2581 | 103.2581 | 8.3454 | 11.063 | 536.1529 | 536.1529 | 536.1529 | 536.1529 | 57.7181 | 50.0337 | 15.7497 | 30.3578 | 15.6003 | 8.0986 | 29.089 | 0 | 50.0349 | 14.5106 | 22.1 | 221 | 154840 | 237681 | 3548234.5532 | 100.0675 | -0.0087866 | -0.2636 | -0.2636 | -0.2636 | 7.9917 | 1123.6264 | 1095.4468 | 1095.4481 | 1093.6264 | 1166.2438 | 1166.2438 | 1166.2438 | 1166.2438 | 648.917 | 648.917 | 648.917 | -0.0059873 | 0 | 2.022 | 51.0085 | 147.7844 | 147.9129 | 184.9457 | 1.1318 | 2.2406 | 0 | 57 | 55.3842 | 57.7181 | 104.9979 | -2.8811 | 30.3578 | -3.9215 | 29.0968 | 64.1098 | 49.8215 | 0 | 66.8097 | 632.8211 | 627.7215 | 610.1075 | 610.0544 | 592.1131 | 589.3512 | 357.4547 | 363.596 | 603.2009 | 604.994 | 651.0689 | 659.6967 | 657.8614 | 657.0716 | 659.5982 | 660.2889 | 661.5927 | 660.7491 | 655.0118 | 652.6771 | 653.934 | 651.0221 | 653.5783 | 654.5767 | 657.5003 | 655.7631 | 653.6194 | 651.0085 | 649.7099 | 653.6322 | 661.7165 | 658.528 | 659.0826
2025-04-10 01:32 | 10 | 1 | 32 | 6.2817e-272 | 1 | 29.3703 | 392.6549 | 0.27896 | 0.0077375 | 102.6741 | 102.6741 | 102.6741 | 102.6741 | 8.3039 | 11.0608 | 534.9589 | 534.9589 | 534.9589 | 534.9589 | 57.7646 | 50.0077 | 15.7507 | 28.9642 | 15.6007 | 7.9149 | 28.3842 | 0 | 50.0093 | 16.2553 | 22.1 | 221 | 154840 | 237681 | 3548239.5319 | 100.0154 | -0.01284 | -0.38521 | -0.38521 | -0.38521 | 7.9917 | 1124.373 | 1096.2162 | 1096.2155 | 1094.373 | 1168.0596 | 1168.0596 | 1168.0596 | 1168.0596 | 643.3465 | 643.3465 | 643.3465 | -0.00604 | 0 | 1.216 | 50.6433 | 146.8649 | 146.9922 | 184.8487 | 1.1101 | 2.2232 | 0 | 57 | 55.5068 | 57.7646 | 105.0046 | -2.8625 | 28.9642 | -3.8244 | 28.4366 | 64.115 | 49.8801 | 0 | 66.8102 | 632.5444 | 627.5866 | 609.9297 | 609.752 | 592.0001 | 589.1187 | 357.2482 | 363.4335 | 603.0193 | 604.9728 | 646.7472 | 655.4749 | 653.0174 | 652.7694 | 655.0687 | 655.1801 | 655.9855 | 654.61 | 648.2583 | 645.7166 | 647.1032 | 644.6949 | 647.0256 | 649.5618 | 652.3493 | 650.985 | 647.4816 | 644.1058 | 643.1245 | 647.1333 | 655.3504 | 652.544 | 653.6787
2025-04-10 01:33 | 10 | 1 | 33 | 6.2817e-272 | 1 | 29.3703 | 392.7186 | 0.27936 | 0.0077514 | 101.4727 | 101.4727 | 101.4727 | 101.4727 | 8.2187 | 11.0559 | 531.7353 | 531.7353 | 531.7353 | 531.7353 | 57.4791 | 49.9431 | 15.7518 | 26.2208 | 15.5999 | 7.536 | 27.1123 | 0 | 49.9438 | 15.9574 | 22.1 | 221 | 154840 | 237681 | 3548244.1277 | 99.8862 | 0.0010378 | 0.031135 | 0.031135 | 0.031135 | 7.9917 | 1125.9085 | 1097.7977 | 1097.7962 | 1095.9085 | 1171.6332 | 1171.6332 | 1171.6332 | 1171.6332 | 628.3034 | 628.3034 | 628.3034 | -0.0060028 | 0 | 0.44655 | 49.9229 | 144.9873 | 145.1351 | 184.5456 | 1.1009 | 2.2299 | 0 | 57 | 55.618 | 57.4791 | 105.012 | -2.523 | 26.2208 | -3.9585 | 27.0754 | 64.0939 | 49.9366 | 0 | 66.8102 | 631.2458 | 626.3606 | 609.4011 | 609.1852 | 591.7364 | 588.8312 | 356.8878 | 362.8005 | 602.7558 | 604.7964 | 633.4519 | 641.8734 | 639.0002 | 639.3171 | 641.5593 | 640.9794 | 640.9166 | 638.508 | 631.6614 | 628.8971 | 630.3926 | 629.0247 | 630.8271 | 634.8154 | 637.7584 | 637.0166 | 632.2592 | 627.7064 | 627.1123 | 630.7578 | 638.882 | 636.3739 | 638.4368
2025-04-10 01:34 | 10 | 1 | 34 | 6.2817e-272 | 1 | 29.3702 | 393.0802 | 0.28461 | 0.0077675 | 101.1115 | 101.1115 | 101.1115 | 101.1115 | 8.1931 | 11.051 | 530.3335 | 530.3335 | 530.3335 | 530.3335 | 57.4682 | 49.889 | 15.7511 | 25.4981 | 15.5991 | 7.4602 | 26.8569 | 0 | 49.8894 | 15.0638 | 22.1 | 221 | 154840 | 237681 | 3548248.4681 | 99.778 | 0.00054744 | 0.016423 | 0.016423 | 0.016423 | 7.9917 | 1126.3698 | 1098.274 | 1098.2728 | 1096.3698 | 1172.5747 | 1172.5747 | 1172.5747 | 1172.5747 | 622.5609 | 622.5609 | 622.5609 | -0.0060362 | 0 | 0.3 | 49.6655 | 144.4283 | 144.5618 | 184.0766 | 1.1018 | 2.2361 | 0 | 57 | 55.5632 | 57.4682 | 105.007 | -2.1038 | 25.4981 | -3.8608 | 26.8031 | 64.0935 | 49.9983 | 0 | 66.8108 | 629.4884 | 624.5651 | 608.7049 | 608.5459 | 591.2033 | 588.3758 | 356.4406 | 362.1129 | 602.2834 | 604.3444 | 627.6533 | 635.7312 | 632.877 | 633.007 | 635.4464 | 634.8809 | 634.7673 | 632.6889 | 626.2314 | 623.564 | 625.0396 | 623.5986 | 625.1229 | 628.5953 | 631.6279 | 631.1709 | 626.7334 | 622.4295 | 621.5309 | 625.1855 | 633.3262 | 630.6418 | 632.3909
2025-04-10 01:35 | 10 | 1 | 35 | 6.2817e-272 | 1 | 29.3696 | 393.5144 | 0.28563 | 0.0077888 | 100.4607 | 100.4607 | 100.4607 | 100.4607 | 8.1472 | 11.0579 | 529.2449 | 529.2449 | 529.2449 | 529.2449 | 57.6377 | 49.9709 | 15.7505 | 23.6379 | 15.5969 | 7.231 | 26.0683 | 0 | 49.9711 | 13.1489 | 22.1 | 221 | 154840 | 237681 | 3548252.4255 | 99.9417 | 0.0084507 | 0.25352 | 0.25352 | 0.25352 | 7.9917 | 1127.197 | 1098.9085 | 1098.9104 | 1097.197 | 1174.9977 | 1174.9977 | 1174.9977 | 1174.9977 | 611.419 | 611.419 | 611.419 | -0.0060301 | 0 | 0.3 | 49.5314 | 143.6099 | 143.7791 | 183.6599 | 1.1213 | 2.2529 | 0 | 57 | 55.4964 | 57.6377 | 105.003 | -3.0429 | 23.6379 | -3.8851 | 25.9795 | 64.1089 | 50.0637 | 0 | 66.8106 | 627.516 | 622.6923 | 608.2057 | 607.9833 | 590.6826 | 587.9464 | 355.8036 | 361.1237 | 601.7133 | 603.8927 | 617.1717 | 624.8887 | 622.3202 | 622.3649 | 625.2447 | 624.1095 | 622.8807 | 620.7077 | 614.5743 | 611.995 | 613.6575 | 612.4168 | 613.8467 | 617.2148 | 620.3526 | 620.2767 | 615.4974 | 611.052 | 610.0026 | 613.5649 | 621.689 | 618.8295 | 620.8467
2025-04-10 01:36 | 10 | 1 | 36 | 6.2817e-272 | 1 | 29.3703 | 394.1904 | 0.28459 | 0.0078111 | 101.194 | 101.194 | 101.194 | 101.194 | 8.199 | 11.0554 | 531.0312 | 531.0312 | 531.0312 | 531.0312 | 57.738 | 49.9493 | 15.7511 | 25.5107 | 15.5989 | 7.4872 | 26.9331 | 0 | 49.9491 | 14.8696 | 22.1 | 221 | 154840 | 237681 | 3548256.587 | 99.8987 | 0.0071694 | 0.21508 | 0.21508 | 0.21508 | 7.9917 | 1126.2663 | 1098.1672 | 1098.1661 | 1096.2663 | 1172.5587 | 1172.5587 | 1172.5587 | 1172.5587 | 620.072 | 620.072 | 620.072 | -0.0060123 | 0 | 0.3 | 49.8762 | 144.6549 | 144.805 | 183.5901 | 1.1386 | 2.2371 | 0 | 57 | 55.5317 | 57.738 | 105.0074 | -3.0529 | 25.5107 | -3.8455 | 26.9002 | 64.1609 | 50.1269 | 0 | 66.8106 | 626.5689 | 621.8794 | 608.1668 | 607.881 | 590.2416 | 587.4964 | 355.294 | 360.395 | 600.9423 | 603.3276 | 624.19 | 632.2673 | 629.6756 | 629.0814 | 631.807 | 631.366 | 631.4744 | 630.59 | 624.6002 | 622.3474 | 623.9759 | 621.6588 | 623.5068 | 625.3453 | 628.2823 | 628.0237 | 624.1121 | 621.4848 | 619.7082 | 623.5776 | 632.0332 | 628.6643 | 629.6877
2025-04-10 01:37 | 10 | 1 | 37 | 6.2817e-272 | 1 | 29.3703 | 395.5001 | 0.28652 | 0.0078227 | 100.9907 | 100.9907 | 100.9907 | 100.9907 | 8.1846 | 11.0566 | 530.4926 | 530.4926 | 530.4926 | 530.4926 | 57.6664 | 49.9604 | 15.7527 | 24.8129 | 15.6026 | 7.4025 | 26.5884 | 0 | 49.9605 | 13.5319 | 22.1 | 221 | 154840 | 237681 | 3548260.7447 | 99.9208 | 0.0077344 | 0.23203 | 0.23203 | 0.23203 | 7.9917 | 1126.5245 | 1098.4328 | 1098.4309 | 1096.5245 | 1173.467 | 1173.467 | 1173.467 | 1173.467 | 617.4181 | 617.4181 | 617.4181 | -0.0060492 | 0 | 0.3 | 49.82 | 144.3961 | 144.549 | 183.5609 | 1.0997 | 2.214 | 0 | 57 | 55.4609 | 57.6664 | 105.0177 | -3.0361 | 24.8129 | -3.8829 | 26.5957 | 64.1804 | 50.1602 | 0 | 66.8102 | 625.8003 | 621.2496 | 607.9675 | 607.5741 | 589.7296 | 586.9095 | 354.7527 | 359.8625 | 600.1673 | 602.6944 | 622.2931 | 630.21 | 627.2904 | 627.0222 | 629.6579 | 628.8826 | 628.7383 | 627.687 | 621.3491 | 618.8831 | 620.6903 | 618.7148 | 620.4483 | 623.026 | 625.8411 | 625.6551 | 620.9091 | 618.0739 | 616.5963 | 620.5809 | 629.0893 | 625.9977 | 627.244
2025-04-10 01:38 | 10 | 1 | 38 | 6.2817e-272 | 1 | 29.3702 | 393.8905 | 0.28639 | 0.0078276 | 101.0062 | 101.0062 | 101.0062 | 101.0062 | 8.1857 | 11.0562 | 530.4644 | 530.4644 | 530.4644 | 530.4644 | 57.496 | 49.9461 | 15.7515 | 25.1325 | 15.6002 | 7.4392 | 26.7424 | 0 | 49.9459 | 15.1064 | 22.1 | 221 | 154840 | 237681 | 3548264.9362 | 99.8921 | 0.008848 | 0.26544 | 0.26544 | 0.26544 | 7.9917 | 1126.5026 | 1098.4106 | 1098.4123 | 1096.5026 | 1173.0515 | 1173.0515 | 1173.0515 | 1173.0515 | 618.0412 | 618.0412 | 618.0412 | -0.0060456 | 0 | 0.3 | 49.8087 | 144.4367 | 144.5879 | 183.4895 | 1.1051 | 2.2384 | 0 | 57 | 55.4249 | 57.496 | 105.0097 | -2.9896 | 25.1325 | -4.0209 | 26.7276 | 64.2297 | 50.1741 | 0 | 66.8106 | 625.1487 | 620.5957 | 607.7004 | 607.1295 | 589.2027 | 586.2654 | 354.2646 | 359.3421 | 599.4552 | 601.9879 | 622.5683 | 630.6086 | 627.7268 | 627.3942 | 630.1188 | 629.279 | 629.4093 | 628.5261 | 622.2232 | 619.8361 | 621.705 | 619.364 | 620.9927 | 623.4632 | 626.1559 | 626.05 | 621.8456 | 619.3704 | 617.4666 | 621.4519 | 630.1024 | 626.6285 | 627.9295
2025-04-10 01:39 | 10 | 1 | 39 | 6.2817e-272 | 1 | 29.3711 | 392.6649 | 0.28511 | 0.007835 | 100.7976 | 100.7976 | 100.7976 | 100.7976 | 8.1707 | 11.0554 | 530.3216 | 530.3216 | 530.3216 | 530.3216 | 57.8597 | 49.9542 | 15.7508 | 24.497 | 15.5992 | 7.3692 | 26.4894 | 0 | 49.9546 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3548269.0638 | 99.9084 | -0.00061945 | -0.018584 | -0.018584 | -0.018584 | 7.9917 | 1126.776 | 1098.693 | 1098.6909 | 1096.776 | 1173.8785 | 1173.8785 | 1173.8785 | 1173.8785 | 614.9211 | 614.9211 | 614.9211 | -0.0059541 | 0 | 0.3 | 49.6562 | 144.0832 | 144.2226 | 183.3223 | 1.1441 | 2.2503 | 0 | 57 | 55.4138 | 57.8597 | 105.005 | -3.0214 | 24.497 | -3.8683 | 26.4762 | 64.2399 | 50.1949 | 0 | 66.8108 | 624.4589 | 619.872 | 607.3381 | 606.6843 | 588.6586 | 585.5747 | 353.7318 | 358.8988 | 598.7769 | 601.3106 | 619.4665 | 627.492 | 624.6951 | 624.4384 | 627.2791 | 626.2524 | 626.4305 | 625.3486 | 619.059 | 616.7571 | 618.5806 | 616.0747 | 617.5352 | 620.0826 | 622.8654 | 622.9137 | 618.7848 | 616.0799 | 614.0477 | 618.0718 | 626.8502 | 623.2664 | 624.7169
2025-04-10 01:40 | 10 | 1 | 40 | 6.2817e-272 | 1 | 29.3717 | 393.5606 | 0.28761 | 0.0078451 | 100.9756 | 100.9756 | 100.9756 | 100.9756 | 8.1831 | 11.0551 | 530.9057 | 530.9057 | 530.9057 | 530.9057 | 58.0217 | 49.9585 | 15.7526 | 25.0041 | 15.6013 | 7.4346 | 26.7102 | 0 | 49.9586 | 14 | 22.1 | 221 | 154840 | 237681 | 3548273.1702 | 99.917 | 0.0048589 | 0.14577 | 0.14577 | 0.14577 | 7.9917 | 1126.5517 | 1098.4609 | 1098.4609 | 1096.5517 | 1173.2177 | 1173.2177 | 1173.2177 | 1173.2177 | 617.1375 | 617.1375 | 617.1375 | -0.0059825 | 0 | 0.3 | 49.8263 | 144.3874 | 144.5421 | 183.1592 | 1.1476 | 2.2561 | 0 | 57 | 55.3802 | 58.0217 | 105.0172 | -3.3034 | 25.0041 | -3.8446 | 26.7112 | 64.2496 | 50.227 | 0 | 66.8111 | 624.0103 | 619.2817 | 607.0949 | 606.4143 | 588.1142 | 585.0904 | 353.2985 | 358.3577 | 598.1419 | 600.5475 | 621.3072 | 629.4276 | 626.6142 | 626.1274 | 628.9444 | 627.98 | 628.5176 | 627.7588 | 621.4649 | 619.4248 | 621.2235 | 618.3954 | 620.0873 | 622.3994 | 625.1399 | 625.2696 | 620.967 | 618.5691 | 616.4852 | 620.623 | 629.3211 | 625.6493 | 627.0171
2025-04-10 01:41 | 10 | 1 | 41 | 6.2817e-272 | 1 | 29.3723 | 392.6486 | 0.28195 | 0.007863 | 101.0756 | 101.0756 | 101.0756 | 101.0756 | 8.1901 | 11.0512 | 531.1463 | 531.1463 | 531.1463 | 531.1463 | 58.012 | 49.914 | 15.7504 | 25.4475 | 15.5988 | 7.4722 | 26.8717 | 0 | 49.9146 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3548277.4255 | 99.828 | -0.00092313 | -0.027694 | -0.027694 | -0.027694 | 7.9917 | 1126.4253 | 1098.33 | 1098.3319 | 1096.4253 | 1172.6402 | 1172.6402 | 1172.6402 | 1172.6402 | 620.413 | 620.413 | 620.413 | -0.0059983 | 0 | 0.3 | 49.7974 | 144.4869 | 144.6386 | 183.0406 | 1.1883 | 2.2344 | 0 | 57 | 55.7018 | 58.012 | 105.0024 | -3.0954 | 25.4475 | -3.7689 | 26.846 | 64.2517 | 50.278 | 0 | 66.8113 | 623.9275 | 619.059 | 606.7936 | 606.1853 | 587.5885 | 584.6241 | 353.0043 | 358.0114 | 597.6205 | 599.8441 | 624.3634 | 632.5573 | 629.8148 | 629.3065 | 631.8663 | 630.9713 | 631.7144 | 631.0138 | 624.8151 | 622.7543 | 624.5454 | 621.8677 | 623.5741 | 625.9219 | 628.4241 | 628.556 | 624.2887 | 622.018 | 620.1373 | 624.2812 | 632.8608 | 629.1766 | 630.5438
2025-04-10 01:42 | 10 | 1 | 42 | 6.2817e-272 | 1 | 29.3731 | 392.5137 | 0.2814 | 0.0079002 | 101.0206 | 101.0206 | 101.0206 | 101.0206 | 8.186 | 11.0537 | 530.9169 | 530.9169 | 530.9169 | 530.9169 | 57.8936 | 49.9344 | 15.7528 | 25.2937 | 15.5989 | 7.4902 | 26.8513 | 0 | 49.9346 | 14.2553 | 22.1 | 221 | 154840 | 237681 | 3548281.6596 | 99.8689 | -0.0021804 | -0.065413 | -0.065413 | -0.065413 | 7.9917 | 1126.5004 | 1098.4081 | 1098.4081 | 1096.5004 | 1172.8417 | 1172.8417 | 1172.8417 | 1172.8417 | 618.2736 | 618.2736 | 618.2736 | -0.0060278 | 0 | 0.3 | 49.8208 | 144.4562 | 144.5892 | 182.8639 | 1.1775 | 2.238 | 0 | 57 | 55.8793 | 57.8936 | 105.0188 | -3.2334 | 25.2937 | -3.8131 | 26.9107 | 64.2712 | 50.3879 | 0 | 66.8111 | 623.683 | 618.6821 | 606.476 | 605.8512 | 587.0907 | 584.1727 | 352.5957 | 357.7658 | 597.224 | 599.2089 | 622.279 | 630.0439 | 627.4586 | 627.0671 | 629.717 | 628.8946 | 629.8347 | 628.8287 | 622.7978 | 620.8023 | 622.3792 | 619.7215 | 621.3731 | 623.6408 | 626.1903 | 626.3863 | 622.6961 | 620.0091 | 617.9295 | 622.1546 | 630.559 | 626.7363 | 628.2736
2025-04-10 01:43 | 10 | 1 | 43 | 6.2817e-272 | 1 | 29.3737 | 392.2189 | 0.28154 | 0.0079567 | 100.6577 | 100.6577 | 100.6577 | 100.6577 | 8.1601 | 11.0557 | 530.5767 | 530.5767 | 530.5767 | 530.5767 | 58.0444 | 49.9634 | 15.7517 | 24.2533 | 15.5981 | 7.3174 | 26.3354 | 0 | 49.9642 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3548285.766 | 99.9269 | -0.0043858 | -0.13157 | -0.13157 | -0.13157 | 7.9917 | 1126.9643 | 1098.886 | 1098.8877 | 1096.9643 | 1174.1957 | 1174.1957 | 1174.1957 | 1174.1957 | 614.0344 | 614.0344 | 614.0344 | -0.0060181 | 0 | 0.3 | 49.6426 | 143.9403 | 144.0729 | 182.7923 | 1.2032 | 2.2585 | 0 | 57 | 55.6267 | 58.0444 | 105.0113 | -3.4612 | 24.2533 | -3.8916 | 26.29 | 64.259 | 50.5513 | 0 | 66.8112 | 623.4397 | 618.2764 | 606.1715 | 605.6151 | 586.6717 | 583.842 | 352.2635 | 357.4825 | 596.8835 | 598.6931 | 618.7839 | 626.5076 | 623.8433 | 623.8068 | 626.1641 | 625.1425 | 625.6385 | 624.0616 | 617.9447 | 615.8095 | 617.3843 | 615.0881 | 616.6159 | 619.9273 | 622.2513 | 622.4745 | 618.1032 | 614.699 | 613.1736 | 617.1793 | 625.2952 | 621.9666 | 624.0788
2025-04-10 01:44 | 10 | 1 | 44 | 6.2817e-272 | 1 | 29.3762 | 391.4442 | 0.2788 | 0.0080038 | 101.0411 | 101.0411 | 101.0411 | 101.0411 | 8.1867 | 11.0508 | 531.6336 | 531.6336 | 531.6336 | 531.6336 | 58.3168 | 49.9229 | 15.7508 | 25.4444 | 15.6014 | 7.5102 | 26.9208 | 0 | 49.9229 | 14.8261 | 22.1 | 221 | 154840 | 237681 | 3548289.913 | 99.8458 | 0.0044667 | 0.134 | 0.134 | 0.134 | 7.9917 | 1126.4865 | 1098.3946 | 1098.3948 | 1096.4865 | 1172.6443 | 1172.6443 | 1172.6443 | 1172.6443 | 619.4766 | 619.4766 | 619.4766 | -0.0060504 | 0 | 0.3 | 49.7712 | 144.4306 | 144.5689 | 182.7216 | 1.2196 | 2.2319 | 0 | 57 | 55.9645 | 58.3168 | 105.005 | -3.3202 | 25.4444 | -3.831 | 26.9826 | 64.265 | 50.6899 | 0 | 66.8115 | 623.4199 | 618.0572 | 605.988 | 605.5284 | 586.2951 | 583.5862 | 351.9978 | 357.1697 | 596.5574 | 598.1544 | 622.9563 | 630.9221 | 628.7565 | 628.1914 | 630.5651 | 629.9443 | 631.185 | 630.0766 | 624.377 | 622.3387 | 623.6087 | 620.9993 | 622.7138 | 624.9704 | 627.2501 | 627.2503 | 624.0195 | 621.2697 | 619.3927 | 623.6712 | 632.007 | 628.3733 | 629.808
2025-04-10 01:45 | 10 | 1 | 45 | 6.2817e-272 | 1 | 29.3789 | 390.0166 | 0.28274 | 0.0080434 | 101.0211 | 101.0211 | 101.0211 | 101.0211 | 8.1846 | 11.0483 | 531.7187 | 531.7187 | 531.7187 | 531.7187 | 58.5329 | 49.9117 | 15.7521 | 25.4405 | 15.5978 | 7.4721 | 26.8746 | 0 | 49.9122 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3548294.0851 | 99.8234 | 0.0027013 | 0.081038 | 0.081038 | 0.081038 | 7.9917 | 1126.5272 | 1098.437 | 1098.4349 | 1096.5272 | 1172.6498 | 1172.6498 | 1172.6498 | 1172.6498 | 620.1094 | 620.1094 | 620.1094 | -0.0060431 | 0 | 0.3 | 49.786 | 144.3961 | 144.548 | 182.7125 | 1.2404 | 2.2328 | 0 | 57 | 56.3092 | 58.5329 | 105.014 | -3.3839 | 25.4405 | -3.8589 | 26.8458 | 64.2509 | 50.8058 | 0 | 66.8117 | 623.6168 | 617.9968 | 605.7633 | 605.5099 | 585.9084 | 583.4613 | 351.7439 | 357.1704 | 596.2837 | 597.6484 | 623.6486 | 631.79 | 629.511 | 629.112 | 631.1602 | 630.6747 | 631.8686 | 630.4456 | 624.6913 | 622.615 | 623.8499 | 621.5302 | 623.2818 | 625.916 | 628.0669 | 628.0507 | 624.3911 | 621.4665 | 619.9375 | 624.4112 | 632.4392 | 629.0648 | 630.6691
2025-04-10 01:46 | 10 | 1 | 46 | 6.2817e-272 | 1 | 29.3792 | 389.5909 | 0.28014 | 0.0080899 | 100.7836 | 100.7836 | 100.7836 | 100.7836 | 8.1676 | 11.05 | 531.1887 | 531.1887 | 531.1887 | 531.1887 | 58.5524 | 49.9297 | 15.7535 | 24.8044 | 15.6005 | 7.3798 | 26.6501 | 0 | 49.9301 | 14.0851 | 22.1 | 221 | 154840 | 237681 | 3548298.2128 | 99.8594 | -0.00070698 | -0.02121 | -0.02121 | -0.02121 | 7.9917 | 1126.8285 | 1098.747 | 1098.7457 | 1096.8285 | 1173.4779 | 1173.4779 | 1173.4779 | 1173.4779 | 616.6616 | 616.6616 | 616.6616 | -0.0059937 | 0 | 0.3 | 49.7047 | 144.0659 | 144.2206 | 182.5725 | 1.2433 | 2.2405 | 0 | 57 | 56.3759 | 58.5524 | 105.023 | -3.4731 | 24.8044 | -3.9244 | 26.5142 | 64.2621 | 50.9425 | 0 | 66.8123 | 623.4086 | 617.6527 | 605.421 | 605.3637 | 585.5882 | 583.2687 | 351.3849 | 356.8851 | 596.0504 | 597.2474 | 620.322 | 628.2368 | 626.0142 | 625.9225 | 627.902 | 627.5579 | 628.4606 | 626.7282 | 621.1934 | 619.2073 | 620.3124 | 618.2591 | 619.7514 | 622.3246 | 624.5235 | 624.6938 | 621.2939 | 617.8165 | 616.1618 | 620.6622 | 628.5362 | 625.3196 | 627.0236
2025-04-10 01:47 | 10 | 1 | 47 | 6.2817e-272 | 1 | 29.3813 | 388.6319 | 0.2828 | 0.0081387 | 100.6734 | 100.6734 | 100.6734 | 100.6734 | 8.1593 | 11.0501 | 531.2843 | 531.2843 | 531.2843 | 531.2843 | 58.8412 | 49.941 | 15.7536 | 24.4356 | 15.6007 | 7.329 | 26.4694 | 0 | 49.9411 | 13.617 | 22.1 | 221 | 154840 | 237681 | 3548302.3617 | 99.8821 | 0.0024016 | 0.072047 | 0.072047 | 0.072047 | 7.9917 | 1126.9791 | 1098.9023 | 1098.9019 | 1096.9791 | 1173.9589 | 1173.9589 | 1173.9589 | 1173.9589 | 615.7075 | 615.7075 | 615.7075 | -0.0060037 | 0 | 0.3 | 49.6188 | 143.926 | 144.08 | 182.5322 | 1.2649 | 2.2587 | 0 | 57 | 56.5447 | 58.8412 | 105.0241 | -3.5979 | 24.4356 | -3.8959 | 26.3316 | 64.2512 | 51.0826 | 0 | 66.8121 | 623.3234 | 617.4694 | 605.2596 | 605.3054 | 585.304 | 583.1054 | 351.06 | 356.663 | 595.7363 | 596.8174 | 619.5947 | 627.5786 | 625.397 | 625.5168 | 627.2307 | 626.8716 | 627.5235 | 625.4911 | 619.859 | 617.8966 | 618.8074 | 617.0772 | 618.6265 | 621.4802 | 623.8429 | 623.9901 | 620.0668 | 616.3847 | 615.0109 | 619.4238 | 627.1321 | 624.257 | 626.1121
2025-04-10 01:48 | 10 | 1 | 48 | 6.2817e-272 | 1 | 29.3812 | 387.7727 | 0.2782 | 0.0081919 | 100.8489 | 100.8489 | 100.8489 | 100.8489 | 8.1718 | 11.0478 | 531.6708 | 531.6708 | 531.6708 | 531.6708 | 59.0551 | 49.93 | 15.753 | 24.8979 | 15.5966 | 7.4242 | 26.6561 | 0 | 49.9304 | 14.5532 | 22.1 | 221 | 154840 | 237681 | 3548306.5106 | 99.86 | 0.0043383 | 0.13015 | 0.13015 | 0.13015 | 7.9917 | 1126.7553 | 1098.6698 | 1098.6717 | 1096.7553 | 1173.3568 | 1173.3568 | 1173.3568 | 1173.3568 | 617.8497 | 617.8497 | 617.8497 | -0.0060191 | 0 | 0.3 | 49.7238 | 144.1567 | 144.2887 | 182.4281 | 1.2687 | 2.2658 | 0 | 57 | 56.5718 | 59.0551 | 105.0198 | -3.5938 | 24.8979 | -3.9666 | 26.6736 | 64.2365 | 51.2395 | 0 | 66.8122 | 623.2562 | 617.3387 | 605.0639 | 605.3241 | 585.0182 | 583.0021 | 350.8593 | 356.4034 | 595.3601 | 596.4248 | 621.3809 | 629.357 | 627.4865 | 627.2757 | 628.9003 | 628.8326 | 629.6042 | 627.9165 | 622.4905 | 620.3871 | 621.1914 | 619.4352 | 621.0871 | 623.5987 | 625.9213 | 625.9663 | 622.0778 | 618.798 | 617.5761 | 621.9441 | 629.5924 | 626.8471 | 628.3114
2025-04-10 01:49 | 10 | 1 | 49 | 6.2817e-272 | 1 | 29.3801 | 387.32 | 0.27812 | 0.0082299 | 100.8203 | 100.8203 | 100.8203 | 100.8203 | 8.17 | 11.05 | 531.11 | 531.11 | 531.11 | 531.11 | 59.0212 | 49.947 | 15.7509 | 24.8331 | 15.6014 | 7.4071 | 26.6647 | 0 | 49.9472 | 14.3404 | 22.1 | 221 | 154840 | 237681 | 3548310.617 | 99.8939 | 0.002303 | 0.069089 | 0.069089 | 0.069089 | 7.9917 | 1126.7874 | 1098.7049 | 1098.7045 | 1096.7874 | 1173.4404 | 1173.4404 | 1173.4404 | 1173.4404 | 615.7373 | 615.7373 | 615.7373 | -0.0060657 | 0 | 0.3 | 49.7275 | 144.1787 | 144.3101 | 182.2903 | 1.2693 | 2.2721 | 0 | 57 | 56.6069 | 59.0212 | 105.0061 | -3.7499 | 24.8331 | -3.8494 | 26.6122 | 64.259 | 51.3482 | 0 | 66.8124 | 622.9241 | 616.9463 | 604.7778 | 605.2779 | 584.7125 | 582.9588 | 350.6245 | 356.1476 | 595.0569 | 596.0284 | 618.9221 | 626.9873 | 625.3549 | 624.9646 | 626.7605 | 626.9024 | 627.4705 | 625.8074 | 620.7295 | 618.5787 | 619.2919 | 617.4366 | 619.1406 | 620.8784 | 623.7305 | 623.7434 | 620.1353 | 616.8043 | 615.6352 | 619.9476 | 627.6082 | 624.7939 | 625.9055
2025-04-10 01:50 | 10 | 1 | 50 | 6.2817e-272 | 1 | 29.3803 | 387.3683 | 0.279 | 0.0082317 | 100.7739 | 100.7739 | 100.7739 | 100.7739 | 8.1667 | 11.0504 | 530.6642 | 530.6642 | 530.6642 | 530.6642 | 58.8269 | 49.946 | 15.7521 | 24.48 | 15.5979 | 7.3313 | 26.4651 | 0 | 49.9466 | 13.9149 | 22.1 | 221 | 154840 | 237681 | 3548314.766 | 99.8919 | -0.006056 | -0.18168 | -0.18168 | -0.18168 | 7.9917 | 1126.8432 | 1098.7619 | 1098.7621 | 1096.8432 | 1173.9009 | 1173.9009 | 1173.9009 | 1173.9009 | 615.8421 | 615.8421 | 615.8421 | -0.0059873 | 0 | 0.3 | 49.6802 | 144.1191 | 144.2625 | 182.256 | 1.2691 | 2.2716 | 0 | 57 | 56.2375 | 58.8269 | 105.0137 | -3.8104 | 24.48 | -3.8449 | 26.34 | 64.2408 | 51.3524 | 0 | 66.8121 | 622.7441 | 616.7719 | 604.61 | 605.2611 | 584.4373 | 582.8451 | 350.4199 | 355.8105 | 594.7054 | 595.6594 | 619.5937 | 627.5566 | 625.9035 | 625.6227 | 627.0324 | 627.1926 | 627.3054 | 625.4328 | 620.4175 | 617.9944 | 618.7766 | 617.4992 | 619.106 | 621.6078 | 624.3906 | 624.2187 | 619.7141 | 616.2089 | 615.6236 | 619.5054 | 627.0248 | 624.8273 | 626.1559
2025-04-10 01:51 | 10 | 1 | 51 | 6.2817e-272 | 1 | 29.3803 | 387.3469 | 0.27886 | 0.0081954 | 101.1343 | 101.1343 | 101.1343 | 101.1343 | 8.1922 | 11.051 | 531.1064 | 531.1064 | 531.1064 | 531.1064 | 58.3894 | 49.9333 | 15.7527 | 25.4711 | 15.5989 | 7.5267 | 26.9565 | 0 | 49.9336 | 14.6809 | 22.1 | 221 | 154840 | 237681 | 3548318.9362 | 99.8665 | 0.0022812 | 0.068437 | 0.068437 | 0.068437 | 7.9917 | 1126.3866 | 1098.2906 | 1098.2928 | 1096.3866 | 1172.6098 | 1172.6098 | 1172.6098 | 1172.6098 | 619.1724 | 619.1724 | 619.1724 | -0.0059802 | 0 | 0.3 | 49.8743 | 144.6115 | 144.7578 | 182.2093 | 1.2675 | 2.2758 | 0 | 57 | 56.0032 | 58.3894 | 105.018 | -3.7361 | 25.4711 | -3.8394 | 27.0421 | 64.2433 | 51.2465 | 0 | 66.8124 | 622.4171 | 616.6341 | 604.5017 | 605.2047 | 584.2441 | 582.7756 | 350.1883 | 355.4355 | 594.3472 | 595.4413 | 622.1548 | 630.0292 | 628.7981 | 627.8841 | 629.5086 | 630.1631 | 630.5683 | 629.2456 | 624.6005 | 622.1589 | 622.8837 | 621.2884 | 623.1672 | 624.5006 | 627.6467 | 627.1807 | 623.3464 | 620.4958 | 619.6227 | 623.4455 | 631.0436 | 628.5399 | 629.1826
2025-04-10 01:52 | 10 | 1 | 52 | 6.2817e-272 | 1 | 29.3793 | 388.1092 | 0.27691 | 0.0081384 | 101.1738 | 101.1738 | 101.1738 | 101.1738 | 8.1953 | 11.0489 | 530.8628 | 530.8628 | 530.8628 | 530.8628 | 58.2223 | 49.8997 | 15.7508 | 25.7547 | 15.5989 | 7.533 | 27.0771 | 0 | 49.8997 | 14.9565 | 22.1 | 221 | 154840 | 237681 | 3548323.1304 | 99.7994 | 0.0036718 | 0.11015 | 0.11015 | 0.11015 | 7.9917 | 1126.3309 | 1098.2333 | 1098.2352 | 1096.3309 | 1172.2398 | 1172.2398 | 1172.2398 | 1172.2398 | 620.0748 | 620.0748 | 620.0748 | -0.0059575 | 0 | 0.3 | 49.8724 | 144.6651 | 144.8232 | 182.2348 | 1.2284 | 2.2659 | 0 | 57 | 55.7625 | 58.2223 | 105.0053 | -3.1525 | 25.7547 | -3.8591 | 27.0646 | 64.2325 | 51.0815 | 0 | 66.8121 | 622.1714 | 616.6314 | 604.3922 | 605.0918 | 584.1019 | 582.6298 | 349.9647 | 355.0496 | 593.9466 | 595.2716 | 623.1316 | 630.901 | 629.6881 | 628.564 | 630.4093 | 631.0375 | 631.2744 | 630.2555 | 625.649 | 623.0576 | 623.9477 | 622.3734 | 624.1188 | 625.1192 | 628.5528 | 627.9222 | 624.2385 | 621.5152 | 620.6331 | 624.4846 | 632.1978 | 629.5445 | 629.9272
2025-04-10 01:53 | 10 | 1 | 53 | 6.2817e-272 | 1 | 29.3779 | 389.8573 | 0.27957 | 0.008087 | 100.6976 | 100.6976 | 100.6976 | 100.6976 | 8.1619 | 11.0509 | 529.8623 | 529.8623 | 529.8623 | 529.8623 | 58.1461 | 49.9189 | 15.7522 | 24.4046 | 15.6017 | 7.3614 | 26.4377 | 0 | 49.9191 | 13.4894 | 22.1 | 221 | 154840 | 237681 | 3548327.2766 | 99.8379 | -0.00039975 | -0.011992 | -0.011992 | -0.011992 | 7.9917 | 1126.9298 | 1098.8517 | 1098.8517 | 1096.9298 | 1173.9991 | 1173.9991 | 1173.9991 | 1173.9991 | 614.3209 | 614.3209 | 614.3209 | -0.0060324 | 0 | 0.3 | 49.6568 | 143.9677 | 144.1336 | 182.2161 | 1.1686 | 2.2366 | 0 | 57 | 55.78 | 58.1461 | 105.0144 | -2.9748 | 24.4046 | -3.853 | 26.4481 | 64.2281 | 50.9313 | 0 | 66.8116 | 621.862 | 616.593 | 604.2971 | 604.8905 | 584.049 | 582.4596 | 349.7742 | 354.7818 | 593.6684 | 595.202 | 618.55 | 626.2127 | 624.6433 | 623.9126 | 625.8214 | 626.0363 | 625.5584 | 624.0297 | 618.9745 | 615.96 | 617.2365 | 616.1121 | 617.7238 | 619.7373 | 623.2215 | 622.4984 | 618.192 | 614.7758 | 614.209 | 617.4344 | 625.3837 | 623.1114 | 624.0417
2025-04-10 01:54 | 10 | 1 | 54 | 6.2817e-272 | 1 | 29.381 | 389.5704 | 0.27576 | 0.0080499 | 100.9077 | 100.9077 | 100.9077 | 100.9077 | 8.176 | 11.0505 | 530.4343 | 530.4343 | 530.4343 | 530.4343 | 58.1508 | 49.9157 | 15.7513 | 24.9745 | 15.5995 | 7.4029 | 26.7204 | 0 | 49.9163 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3548331.4043 | 99.8314 | -0.0044386 | -0.13316 | -0.13316 | -0.13316 | 7.9917 | 1126.6783 | 1098.5919 | 1098.5913 | 1096.6783 | 1173.2572 | 1173.2572 | 1173.2572 | 1173.2572 | 616.7607 | 616.7607 | 616.7607 | -0.0059529 | 0 | 0.3 | 49.7475 | 144.2447 | 144.4279 | 182.1409 | 1.2379 | 2.2704 | 0 | 57 | 55.8385 | 58.1508 | 105.0084 | -3.3149 | 24.9745 | -3.8975 | 26.5972 | 64.2066 | 50.8268 | 0 | 66.8122 | 621.5685 | 616.4531 | 604.2404 | 604.7894 | 583.9598 | 582.3626 | 349.4837 | 354.3512 | 593.4119 | 595.109 | 620.4687 | 628.202 | 626.8353 | 625.5936 | 627.7893 | 628.0828 | 627.8079 | 626.7323 | 621.919 | 619.0161 | 620.3243 | 618.8729 | 620.5148 | 621.9251 | 625.5048 | 624.6883 | 620.604 | 617.8915 | 617.1234 | 620.2555 | 628.4014 | 625.9948 | 626.4267
2025-04-10 01:55 | 10 | 1 | 55 | 6.2817e-272 | 1 | 29.3781 | 390.4846 | 0.27759 | 0.0080236 | 101.1904 | 101.1904 | 101.1904 | 101.1904 | 8.1968 | 11.0498 | 530.6016 | 530.6016 | 530.6016 | 530.6016 | 58.0097 | 49.9013 | 15.7521 | 25.6048 | 15.599 | 7.5117 | 27.0544 | 0 | 49.9016 | 14.9362 | 22.1 | 221 | 154840 | 237681 | 3548335.6383 | 99.8026 | -8.7847e-05 | -0.0026353 | -0.0026353 | -0.0026353 | 7.9917 | 1126.3057 | 1098.2081 | 1098.2085 | 1096.3057 | 1172.4364 | 1172.4364 | 1172.4364 | 1172.4364 | 619.8683 | 619.8683 | 619.8683 | -0.0059864 | 0 | 0.40991 | 49.8591 | 144.6178 | 144.796 | 182.1271 | 1.186 | 2.2699 | 0 | 57 | 55.6641 | 58.0097 | 105.0138 | -3.3958 | 25.6048 | -3.827 | 26.9879 | 64.2148 | 50.7489 | 0 | 66.8129 | 621.4252 | 616.3977 | 604.1821 | 604.6568 | 583.8562 | 582.1713 | 349.1422 | 354.0219 | 593.2248 | 594.9886 | 623.1425 | 630.8984 | 629.4994 | 628.0381 | 630.4513 | 630.8647 | 630.8212 | 630.3621 | 625.4902 | 622.4915 | 623.9179 | 622.2533 | 623.9378 | 624.7629 | 628.4233 | 627.4858 | 623.9009 | 621.6742 | 620.4464 | 623.8306 | 632.191 | 629.3026 | 629.4722
2025-04-10 01:56 | 10 | 1 | 56 | 6.2817e-272 | 1 | 29.3764 | 391.6962 | 0.27846 | 0.0080091 | 100.7357 | 100.7357 | 100.7357 | 100.7357 | 8.1649 | 11.0533 | 529.8188 | 529.8188 | 529.8188 | 529.8188 | 58.05 | 49.9403 | 15.7523 | 24.4594 | 15.6001 | 7.3717 | 26.5087 | 0 | 49.9408 | 13.3191 | 22.1 | 221 | 154840 | 237681 | 3548339.766 | 99.8806 | -0.0020251 | -0.060753 | -0.060753 | -0.060753 | 7.9917 | 1126.8785 | 1098.7951 | 1098.7957 | 1096.8785 | 1173.9274 | 1173.9274 | 1173.9274 | 1173.9274 | 614.5025 | 614.5025 | 614.5025 | -0.0059715 | 0 | 0.3 | 49.7594 | 144.0573 | 144.2313 | 182.0578 | 1.14 | 2.2688 | 0 | 57 | 55.6636 | 58.05 | 105.0152 | -3.2838 | 24.4594 | -3.9452 | 26.485 | 64.2047 | 50.7036 | 0 | 66.8119 | 621.244 | 616.2774 | 604.1248 | 604.4676 | 583.8111 | 581.9887 | 348.8112 | 353.7521 | 593.0246 | 594.9023 | 618.6638 | 626.497 | 624.5492 | 623.5884 | 626.1352 | 626.04 | 625.5785 | 624.576 | 619.3263 | 616.2171 | 617.9876 | 616.3019 | 618.062 | 619.6586 | 622.9966 | 622.3887 | 618.2585 | 615.4607 | 614.3554 | 617.6464 | 626.2203 | 623.5786 | 624.1851
2025-04-10 01:57 | 10 | 1 | 57 | 6.2817e-272 | 1 | 29.3796 | 391.4058 | 0.28022 | 0.0080275 | 100.9557 | 100.9557 | 100.9557 | 100.9557 | 8.1798 | 11.0546 | 530.4282 | 530.4282 | 530.4282 | 530.4282 | 58.0492 | 49.953 | 15.7537 | 24.8568 | 15.6028 | 7.4321 | 26.7232 | 0 | 49.9542 | 14.383 | 22.1 | 221 | 154840 | 237681 | 3548343.9362 | 99.9059 | -0.0071094 | -0.21328 | -0.21328 | -0.21328 | 7.9917 | 1126.6102 | 1098.5221 | 1098.5238 | 1096.6102 | 1173.4096 | 1173.4096 | 1173.4096 | 1173.4096 | 617.4169 | 617.4169 | 617.4169 | -0.0060553 | 0 | 0.3 | 49.8596 | 144.3967 | 144.573 | 181.9998 | 1.1878 | 2.2701 | 0 | 57 | 55.6892 | 58.0492 | 105.0246 | -3.627 | 24.8568 | -3.8796 | 26.7022 | 64.2034 | 50.7612 | 0 | 66.8123 | 621.3187 | 616.4029 | 604.2024 | 604.4157 | 583.8041 | 581.8558 | 348.4781 | 353.4708 | 592.9267 | 594.8231 | 621.2053 | 629.1556 | 627.1856 | 626.1329 | 628.6188 | 628.6004 | 628.442 | 627.746 | 622.3439 | 619.6045 | 621.3027 | 619.2989 | 621.1952 | 622.4997 | 625.696 | 625.1589 | 621.2252 | 618.8494 | 617.4989 | 621.0045 | 629.5442 | 626.6859 | 627.1669
2025-04-10 01:58 | 10 | 1 | 58 | 6.2817e-272 | 1 | 29.3782 | 392.4598 | 0.27762 | 0.0080631 | 100.9724 | 100.9724 | 100.9724 | 100.9724 | 8.1813 | 11.0552 | 530.0888 | 530.0888 | 530.0888 | 530.0888 | 57.9289 | 49.9558 | 15.7519 | 25.0745 | 15.6009 | 7.4427 | 26.7807 | 0 | 49.9556 | 14.5532 | 22.1 | 221 | 154840 | 237681 | 3548348.0426 | 99.9117 | 0.0058409 | 0.17523 | 0.17523 | 0.17523 | 7.9917 | 1126.5834 | 1098.494 | 1098.4962 | 1096.5834 | 1173.1264 | 1173.1264 | 1173.1264 | 1173.1264 | 616.9231 | 616.9231 | 616.9231 | -0.0058949 | 0 | 0.3 | 49.8899 | 144.4154 | 144.5909 | 181.9859 | 1.1475 | 2.2735 | 0 | 57 | 55.4917 | 57.9289 | 105.0125 | -3.7425 | 25.0745 | -3.9329 | 26.74 | 64.1993 | 50.8626 | 0 | 66.8119 | 621.2833 | 616.3586 | 604.2077 | 604.2643 | 583.7679 | 581.6498 | 348.148 | 353.3144 | 592.8432 | 594.7439 | 620.7397 | 628.7317 | 626.6256 | 625.7116 | 628.3216 | 628.1756 | 628.0643 | 627.2923 | 621.6888 | 619.1663 | 620.8347 | 618.5489 | 620.5432 | 621.9943 | 625.1749 | 624.6721 | 620.7362 | 618.3211 | 616.8126 | 620.6262 | 629.2435 | 626.1215 | 626.7861
2025-04-10 01:59 | 10 | 1 | 59 | 6.2817e-272 | 1 | 29.3775 | 392.8596 | 0.27985 | 0.0080934 | 100.9168 | 100.9168 | 100.9168 | 100.9168 | 8.1775 | 11.0514 | 529.8045 | 529.8045 | 529.8045 | 529.8045 | 57.7947 | 49.9077 | 15.7528 | 25.0247 | 15.6015 | 7.4319 | 26.7104 | 0 | 49.9081 | 14.4681 | 22.1 | 221 | 154840 | 237681 | 3548352.2979 | 99.8155 | -0.0021016 | -0.063046 | -0.063046 | -0.063046 | 7.9917 | 1126.6532 | 1098.5657 | 1098.5643 | 1096.6532 | 1173.1915 | 1173.1915 | 1173.1915 | 1173.1915 | 618.0213 | 618.0213 | 618.0213 | -0.0059708 | 0 | 0.3 | 49.8012 | 144.2993 | 144.4739 | 181.9874 | 1.1342 | 2.2664 | 0 | 57 | 55.4621 | 57.7947 | 105.0186 | -3.4783 | 25.0247 | -3.8238 | 26.7015 | 64.1849 | 50.9501 | 0 | 66.8123 | 621.4278 | 616.4752 | 604.1002 | 603.9969 | 583.6692 | 581.3719 | 347.8511 | 353.1682 | 592.741 | 594.6516 | 622.1534 | 629.9839 | 627.7178 | 627.1086 | 629.4671 | 629.1604 | 629.2677 | 628.3207 | 622.5125 | 620.0735 | 621.6261 | 619.4739 | 621.3074 | 623.5201 | 626.4359 | 625.8752 | 621.6316 | 619.1212 | 617.7309 | 621.6066 | 630.1117 | 627.1323 | 628.1305
2025-04-10 02:00 | 10 | 2 | 0 | 6.2817e-272 | 1 | 29.379 | 393.3674 | 0.27819 | 0.0081209 | 100.8798 | 100.8798 | 100.8798 | 100.8798 | 8.1745 | 11.0527 | 529.3948 | 529.3948 | 529.3948 | 529.3948 | 57.8052 | 49.9235 | 15.7521 | 24.8529 | 15.604 | 7.4075 | 26.6641 | 0 | 49.9236 | 13.7826 | 22.1 | 221 | 154840 | 237681 | 3548356.3913 | 99.8469 | 0.0085627 | 0.25688 | 0.25688 | 0.25688 | 7.9917 | 1126.7039 | 1098.6178 | 1098.6193 | 1096.7039 | 1173.4148 | 1173.4148 | 1173.4148 | 1173.4148 | 616.5814 | 616.5814 | 616.5814 | -0.0059462 | 0 | 0.3 | 49.766 | 144.2412 | 144.4049 | 181.8669 | 1.1499 | 2.2516 | 0 | 57 | 55.3408 | 57.8052 | 105.0139 | -3.8827 | 24.8529 | -4.0124 | 26.6137 | 64.1899 | 51.0327 | 0 | 66.8123 | 621.3196 | 616.3392 | 604.003 | 603.7521 | 583.5985 | 581.1685 | 347.4438 | 353.09 | 592.7582 | 594.5603 | 620.492 | 628.5712 | 626.131 | 625.6879 | 628.1912 | 627.774 | 627.9799 | 627.0541 | 620.8494 | 618.9139 | 620.353 | 617.8793 | 619.8625 | 622.2204 | 624.7221 | 624.3423 | 620.5766 | 617.8639 | 616.1725 | 620.0894 | 628.4988 | 625.2034 | 626.5365
2025-04-10 02:01 | 10 | 2 | 1 | 6.2817e-272 | 1 | 29.3783 | 394.2378 | 0.27719 | 0.0081565 | 101.0641 | 101.0641 | 101.0641 | 101.0641 | 8.1878 | 11.0552 | 529.5367 | 529.5367 | 529.5367 | 529.5367 | 57.5414 | 49.9404 | 15.7513 | 25.1406 | 15.6005 | 7.4855 | 26.8453 | 0 | 49.9408 | 13.9574 | 22.1 | 221 | 154840 | 237681 | 3548360.4894 | 99.8809 | -0.00066816 | -0.020045 | -0.020045 | -0.020045 | 7.9917 | 1126.4681 | 1098.376 | 1098.3749 | 1096.4681 | 1173.04 | 1173.04 | 1173.04 | 1173.04 | 617.2759 | 617.2759 | 617.2759 | -0.0059091 | 0 | 0.3 | 49.9607 | 144.5805 | 144.7351 | 181.7624 | 1.1503 | 2.2384 | 0 | 57 | 55.223 | 57.5414 | 105.0083 | -4.3914 | 25.1406 | -3.928 | 26.894 | 64.1742 | 51.1326 | 0 | 66.8127 | 621.2891 | 616.2151 | 603.964 | 603.594 | 583.6116 | 580.98 | 347.0835 | 352.876 | 592.7691 | 594.4809 | 621.0583 | 628.8439 | 626.2756 | 625.8551 | 628.5103 | 628.0768 | 628.6764 | 628.2277 | 621.7864 | 620.256 | 621.4268 | 618.7029 | 620.5846 | 622.5543 | 625.0858 | 624.8689 | 621.6388 | 619.1013 | 616.9753 | 621.2171 | 629.6899 | 625.9925 | 627.2404
2025-04-10 02:02 | 10 | 2 | 2 | 6.2817e-272 | 1 | 29.3811 | 395.8728 | 0.27877 | 0.0081708 | 100.6125 | 100.6125 | 100.6125 | 100.6125 | 8.1551 | 11.0629 | 528.4638 | 528.4638 | 528.4638 | 528.4638 | 57.0871 | 49.9964 | 15.7545 | 23.7332 | 15.6024 | 7.2971 | 26.1545 | 0 | 49.9966 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3548364.5532 | 99.9929 | 0.001156 | 0.034681 | 0.034681 | 0.034681 | 7.9917 | 1127.054 | 1098.8417 | 1098.8413 | 1097.054 | 1174.8732 | 1174.8732 | 1174.8732 | 1174.8732 | 610.6837 | 610.6837 | 610.6837 | -0.0059817 | 0 | 0.3 | 49.7857 | 144.006 | 144.1616 | 181.7208 | 1.1734 | 2.2589 | 0 | 57 | 54.9527 | 57.0871 | 105.0297 | -5.0958 | 23.7332 | -3.8861 | 26.2169 | 64.1623 | 51.1757 | 0 | 66.8123 | 621.0121 | 616.0094 | 603.9528 | 603.3944 | 583.5679 | 580.8217 | 346.7335 | 352.7739 | 592.7796 | 594.4565 | 615.7301 | 623.0132 | 620.4123 | 620.4848 | 623.1816 | 621.9279 | 621.9799 | 620.8223 | 614.3574 | 612.6096 | 613.9683 | 611.7587 | 613.4306 | 616.6759 | 618.9128 | 618.8717 | 614.8324 | 611.4527 | 609.6749 | 613.8362 | 622.0629 | 618.6554 | 620.5144
2025-04-10 02:03 | 10 | 2 | 3 | 6.2817e-272 | 1 | 29.3776 | 395.9088 | 0.27863 | 0.0081617 | 101.5307 | 101.5307 | 101.5307 | 101.5307 | 8.221 | 11.0573 | 530.236 | 530.236 | 530.236 | 530.236 | 57.0001 | 49.9327 | 15.7503 | 26.5897 | 15.5988 | 7.6153 | 27.4679 | 0 | 49.9325 | 15.6596 | 22.1 | 221 | 154840 | 237681 | 3548368.8298 | 99.8655 | 0.010232 | 0.30697 | 0.30697 | 0.30697 | 7.9917 | 1125.8647 | 1097.754 | 1097.7579 | 1095.8647 | 1171.1526 | 1171.1526 | 1171.1526 | 1171.1526 | 623.1299 | 623.1299 | 623.1299 | -0.0059371 | 0 | 0.7763 | 50.1793 | 145.3387 | 145.4929 | 181.7115 | 1.1406 | 2.2513 | 0 | 57 | 55.0216 | 57.0001 | 105.002 | -4.3963 | 26.5897 | -3.8825 | 27.3602 | 64.1504 | 51.1471 | 0 | 66.8125 | 621.3046 | 616.1614 | 603.9836 | 603.3515 | 583.4728 | 580.6347 | 346.4204 | 352.5822 | 592.7251 | 594.2931 | 626.5023 | 633.7473 | 631.6009 | 631.0269 | 633.839 | 633.0653 | 634.5402 | 634.3347 | 628.2823 | 627.0232 | 628.3314 | 625.0638 | 627.0913 | 628.5679 | 630.5554 | 630.265 | 627.6666 | 625.8042 | 623.2721 | 627.8852 | 636.1877 | 632.0323 | 633.1854
2025-04-10 02:04 | 10 | 2 | 4 | 6.2817e-272 | 1 | 29.3794 | 396.1433 | 0.27581 | 0.0081389 | 100.7477 | 100.7477 | 100.7477 | 100.7477 | 8.1651 | 11.0587 | 528.3498 | 528.3498 | 528.3498 | 528.3498 | 56.9064 | 49.9417 | 15.7536 | 24.3543 | 15.6007 | 7.3465 | 26.4203 | 0 | 49.9422 | 13.7021 | 22.1 | 221 | 154840 | 237681 | 3548373.0851 | 99.8834 | 0.00058449 | 0.017535 | 0.017535 | 0.017535 | 7.9917 | 1126.877 | 1098.7977 | 1098.7966 | 1096.877 | 1174.0649 | 1174.0649 | 1174.0649 | 1174.0649 | 614.2017 | 614.2017 | 614.2017 | -0.0059651 | 0 | 0.3 | 49.7712 | 144.1268 | 144.2567 | 181.6879 | 1.1495 | 2.2469 | 0 | 57 | 55.0406 | 56.9064 | 105.0239 | -4.3088 | 24.3543 | -3.8527 | 26.3947 | 64.1554 | 51.0826 | 0 | 66.8124 | 621.4095 | 616.3368 | 603.8733 | 603.1041 | 583.3561 | 580.3906 | 346.1652 | 352.6971 | 592.7198 | 594.2523 | 619.1968 | 626.6516 | 623.4617 | 624.057 | 626.3722 | 625.1612 | 625.9433 | 624.4406 | 617.5561 | 615.9351 | 617.5043 | 615.1344 | 616.6489 | 620.2633 | 622.3019 | 622.5242 | 618.4779 | 615.0355 | 612.9611 | 617.4544 | 625.7101 | 622.167 | 624.4502
2025-04-10 02:05 | 10 | 2 | 5 | 6.2817e-272 | 1 | 29.3822 | 394.9467 | 0.27813 | 0.008118 | 100.9033 | 100.9033 | 100.9033 | 100.9033 | 8.1754 | 11.0592 | 529.0021 | 529.0021 | 529.0021 | 529.0021 | 56.9645 | 49.9521 | 15.7522 | 24.8732 | 15.6025 | 7.4448 | 26.7114 | 0 | 49.9526 | 13.8723 | 22.1 | 221 | 154840 | 237681 | 3548377.1277 | 99.9041 | -0.0034211 | -0.10263 | -0.10263 | -0.10263 | 7.9917 | 1126.69 | 1098.604 | 1098.607 | 1096.69 | 1173.3881 | 1173.3881 | 1173.3881 | 1173.3881 | 615.4884 | 615.4884 | 615.4884 | -0.0060056 | 0 | 0.3 | 49.8933 | 144.3807 | 144.5107 | 181.4803 | 1.204 | 2.2666 | 0 | 57 | 55.1345 | 56.9645 | 105.0144 | -4.6854 | 24.8732 | -3.9634 | 26.7478 | 64.1584 | 51.0251 | 0 | 66.8123 | 621.1098 | 615.8571 | 603.7005 | 602.8886 | 583.2139 | 580.2349 | 345.8088 | 352.3409 | 592.6718 | 593.9884 | 619.8567 | 627.2798 | 624.2215 | 624.3999 | 626.9298 | 625.885 | 627.212 | 626.0528 | 619.4781 | 617.9956 | 619.6767 | 616.7505 | 618.3512 | 621.1282 | 623.1731 | 623.5167 | 620.2849 | 617.0831 | 614.6527 | 619.4879 | 627.7753 | 623.779 | 625.6731
2025-04-10 02:06 | 10 | 2 | 6 | 6.2817e-272 | 1 | 29.3804 | 394.7201 | 0.27814 | 0.008121 | 101.0505 | 101.0505 | 101.0505 | 101.0505 | 8.1863 | 11.059 | 529.306 | 529.306 | 529.306 | 529.306 | 56.8115 | 49.9459 | 15.753 | 25.0946 | 15.6018 | 7.4343 | 26.7611 | 0 | 49.9468 | 14.8511 | 22.1 | 221 | 154840 | 237681 | 3548381.3404 | 99.8919 | -0.00092432 | -0.027729 | -0.027729 | -0.027729 | 7.9917 | 1126.4911 | 1098.3996 | 1098.3981 | 1096.4911 | 1173.1 | 1173.1 | 1173.1 | 1173.1 | 617.8849 | 617.8849 | 617.8849 | -0.0059899 | 0 | 0.3 | 49.9539 | 144.6033 | 144.7511 | 181.3571 | 1.2135 | 2.274 | 0 | 57 | 55.0711 | 56.8115 | 105.0199 | -4.0279 | 25.0946 | -3.9066 | 26.7099 | 64.1561 | 51.033 | 0 | 66.8125 | 621.2378 | 615.761 | 603.5625 | 602.8379 | 582.9512 | 580.1136 | 345.608 | 352.117 | 592.5463 | 593.7101 | 622.5041 | 629.6643 | 626.7986 | 627.0278 | 629.0987 | 627.9554 | 629.5551 | 628.3126 | 621.9336 | 620.1482 | 621.8877 | 619.1461 | 620.8264 | 623.9023 | 625.9081 | 626.328 | 622.3198 | 619.0935 | 617.0862 | 621.7684 | 629.8988 | 626.2945 | 628.414
2025-04-10 02:07 | 10 | 2 | 7 | 6.2817e-272 | 1 | 29.3785 | 395.404 | 0.27773 | 0.0081407 | 100.8707 | 100.8707 | 100.8707 | 100.8707 | 8.174 | 11.0611 | 529.1227 | 529.1227 | 529.1227 | 529.1227 | 56.9123 | 49.9701 | 15.7513 | 24.7788 | 15.6022 | 7.4219 | 26.6745 | 0 | 49.9706 | 13.7872 | 22.1 | 221 | 154840 | 237681 | 3548385.4894 | 99.9402 | -0.007895 | -0.23685 | -0.23685 | -0.23685 | 7.9917 | 1126.7138 | 1098.6294 | 1098.6317 | 1096.7138 | 1173.5113 | 1173.5113 | 1173.5113 | 1173.5113 | 614.8771 | 614.8771 | 614.8771 | -0.0058933 | 0 | 0.3 | 49.9665 | 144.398 | 144.5339 | 181.1773 | 1.1657 | 2.2537 | 0 | 57 | 55.3307 | 56.9123 | 105.0087 | -0.6351 | 24.7788 | -3.879 | 26.6655 | 64.1507 | 51.0873 | 0 | 66.8123 | 620.9827 | 615.3853 | 603.2864 | 602.7086 | 582.757 | 579.9933 | 345.3427 | 352.0234 | 592.467 | 593.4239 | 619.1955 | 626.5696 | 623.7565 | 624.0376 | 626.1742 | 625.2932 | 626.6272 | 625.3697 | 618.9425 | 617.1689 | 618.8272 | 616.0936 | 617.7514 | 620.5592 | 622.7097 | 623.2339 | 619.6806 | 616.3185 | 614.0094 | 618.8657 | 626.879 | 623.0836 | 625.1341
2025-04-10 02:08 | 10 | 2 | 8 | 6.2817e-272 | 1 | 29.3778 | 396.0621 | 0.27891 | 0.008176 | 101.1666 | 101.1666 | 101.1666 | 101.1666 | 8.1951 | 11.0588 | 529.6042 | 529.6042 | 529.6042 | 529.6042 | 56.9891 | 49.9499 | 15.7524 | 25.507 | 15.5999 | 7.5109 | 26.9903 | 0 | 49.9501 | 14.8085 | 22.1 | 221 | 154840 | 237681 | 3548389.7021 | 99.8998 | 0.00052455 | 0.015737 | 0.015737 | 0.015737 | 7.9917 | 1126.3336 | 1098.2385 | 1098.2379 | 1096.3336 | 1172.5638 | 1172.5638 | 1172.5638 | 1172.5638 | 618.5701 | 618.5701 | 618.5701 | -0.0059374 | 0 | 0.3 | 50.0424 | 144.8126 | 144.9461 | 181.145 | 1.1361 | 2.2484 | 0 | 57 | 55.4714 | 56.9891 | 105.0156 | 0.3865 | 25.507 | -3.9299 | 26.9852 | 64.1471 | 51.1897 | 0 | 66.8123 | 621.0597 | 615.3354 | 603.2286 | 602.7409 | 582.5619 | 579.9434 | 345.1913 | 351.7905 | 592.3297 | 593.1913 | 622.4418 | 629.763 | 627.3997 | 627.4033 | 629.4382 | 628.8208 | 630.2735 | 629.1619 | 623.0323 | 621.2071 | 622.8477 | 620.0274 | 621.8573 | 624.2763 | 626.5552 | 626.7517 | 623.3437 | 620.3556 | 618.1989 | 622.9017 | 630.9256 | 627.1033 | 628.9744
2025-04-10 02:09 | 10 | 2 | 9 | 6.2817e-272 | 1 | 29.3789 | 395.1416 | 0.27673 | 0.0082173 | 100.6954 | 100.6954 | 100.6954 | 100.6954 | 8.1615 | 11.0599 | 528.9723 | 528.9723 | 528.9723 | 528.9723 | 57.0783 | 49.9693 | 15.7525 | 24.131 | 15.5997 | 7.3438 | 26.3362 | 0 | 49.9702 | 13.6522 | 22.1 | 221 | 154840 | 237681 | 3548393.8261 | 99.9386 | -0.010883 | -0.32648 | -0.32648 | -0.32648 | 7.9917 | 1126.9365 | 1098.858 | 1098.8574 | 1096.9365 | 1174.3557 | 1174.3557 | 1174.3557 | 1174.3557 | 614.3825 | 614.3825 | 614.3825 | -0.0058855 | 0 | 0.3 | 49.8084 | 144.1251 | 144.2631 | 181.0559 | 1.1857 | 2.2606 | 0 | 57 | 55.5728 | 57.0783 | 105.0169 | 0.50036 | 24.1308 | -3.8983 | 26.3848 | 64.1482 | 51.3088 | 0 | 66.813 | 621.0617 | 615.2687 | 603.057 | 602.6775 | 582.4237 | 579.9055 | 345.0853 | 351.6528 | 592.1974 | 593.0002 | 619.4114 | 626.5252 | 624.0374 | 624.4111 | 626.2198 | 625.2353 | 625.9127 | 624.1323 | 617.964 | 615.7904 | 617.4613 | 615.3725 | 617.1388 | 620.757 | 622.9162 | 623.2111 | 618.4705 | 614.7311 | 613.6143 | 617.8688 | 625.6279 | 622.6038 | 624.9347
2025-04-10 02:10 | 10 | 2 | 10 | 6.2817e-272 | 1 | 29.3776 | 397.2782 | 0.27569 | 0.0082674 | 101.0577 | 101.0577 | 101.0577 | 101.0577 | 8.1875 | 11.059 | 529.6384 | 529.6384 | 529.6384 | 529.6384 | 57.203 | 49.9642 | 15.7511 | 25.0813 | 15.6011 | 7.4692 | 26.8256 | 0 | 49.9648 | 14.9362 | 22.1 | 221 | 154840 | 237681 | 3548397.9149 | 99.9285 | 0.010232 | 0.30695 | 0.30695 | 0.30695 | 7.9917 | 1126.4711 | 1098.3783 | 1098.3779 | 1096.4711 | 1173.117 | 1173.117 | 1173.117 | 1173.117 | 617.2404 | 617.2404 | 617.2404 | -0.0058957 | 0 | 0.3 | 49.987 | 144.6397 | 144.7802 | 180.925 | 1.1003 | 2.2436 | 0 | 57 | 55.3971 | 57.203 | 105.0076 | 0.48526 | 25.0813 | -3.9527 | 26.8354 | 64.1792 | 51.4534 | 0 | 66.8124 | 620.9174 | 615.0612 | 602.9416 | 602.7979 | 582.3013 | 580.0105 | 344.9989 | 351.3415 | 592.0994 | 592.8053 | 621.4362 | 628.1679 | 626.2868 | 626.1459 | 628.115 | 627.7436 | 628.844 | 627.456 | 621.8846 | 620.0334 | 621.3321 | 618.7662 | 620.6989 | 622.9952 | 625.5808 | 625.7651 | 621.655 | 618.4866 | 616.9933 | 621.3899 | 629.1825 | 625.7965 | 627.4766
2025-04-10 02:11 | 10 | 2 | 11 | 6.2817e-272 | 1 | 29.3761 | 398.6441 | 0.28314 | 0.0083214 | 99.6863 | 99.6863 | 99.6863 | 99.6863 | 8.0906 | 11.064 | 526.9934 | 526.9934 | 526.9934 | 526.9934 | 57.299 | 50.0251 | 15.751 | 21.4606 | 15.6035 | 6.965 | 25.0155 | 0 | 50.026 | 16.0426 | 22.1 | 221 | 154840 | 237681 | 3548401.8298 | 100.0501 | -0.0039317 | -0.11795 | -0.11795 | -0.11795 | 7.9917 | 1128.2162 | 1099.5415 | 1099.54 | 1098.2162 | 1177.834 | 1177.834 | 1177.834 | 1177.834 | 600.3276 | 600.3276 | 600.3276 | -0.0058749 | 0 | 0.3 | 49.4584 | 142.8189 | 142.9411 | 180.8281 | 1.0656 | 2.2319 | 0 | 57 | 55.2388 | 57.299 | 105.0064 | -0.10272 | 21.4606 | -3.8293 | 25.024 | 64.1772 | 51.6088 | 0 | 66.8123 | 620.3683 | 614.602 | 602.7061 | 602.7278 | 582.1676 | 580.0399 | 344.8047 | 351.1476 | 592.0015 | 592.7353 | 607.1521 | 613.6619 | 611.6161 | 612.2794 | 614.3907 | 612.7001 | 611.3529 | 608.349 | 602.7459 | 600.2679 | 601.7661 | 600.7991 | 602.3553 | 607.1003 | 609.7987 | 609.9525 | 604.1619 | 598.8406 | 598.7178 | 602.2097 | 609.6587 | 607.4179 | 610.3364
2025-04-10 02:12 | 10 | 2 | 12 | 6.2817e-272 | 1 | 29.3763 | 397.4325 | 0.28633 | 0.0083711 | 97.9059 | 97.9059 | 97.9059 | 97.9059 | 7.9643 | 11.0571 | 522.5793 | 522.5793 | 522.5793 | 522.5793 | 57.5147 | 49.954 | 15.7517 | 17.6463 | 15.6018 | 6.4699 | 23.3107 | 0 | 49.9545 | 16.5106 | 22.1 | 221 | 154840 | 237681 | 3548405.1277 | 99.908 | -0.0051767 | -0.1553 | -0.1553 | -0.1553 | 7.9917 | 1129.65 | 1100 | 1100 | 1100.4909 | 1182.8017 | 1182.8017 | 1182.8017 | 1182.8017 | 577.8761 | 577.8761 | 577.8761 | -0.0059395 | 0 | 0.3 | 48.6129 | 140.3843 | 140.5193 | 180.3403 | 1.0793 | 2.2423 | 0 | 57 | 55.1693 | 57.5147 | 105.0113 | 0.12817 | 17.6463 | -3.8485 | 23.2452 | 64.1766 | 51.7523 | 0 | 66.8125 | 618.1531 | 612.5556 | 601.9329 | 602.0928 | 581.6971 | 579.7159 | 344.3859 | 350.3312 | 591.5835 | 592.5346 | 586.8229 | 592.6441 | 590.9322 | 591.6124 | 594.7044 | 591.274 | 587.6386 | 584.0733 | 578.8217 | 575.9558 | 577.7869 | 577.9546 | 579.0028 | 584.689 | 588.0349 | 588.3609 | 581.5888 | 574.9623 | 575.356 | 578.1396 | 585.4794 | 583.641 | 586.8659
2025-04-10 02:13 | 10 | 2 | 13 | 6.2817e-272 | 1 | 29.3764 | 396.5015 | 0.28428 | 0.0084161 | 96.4095 | 96.4095 | 96.4095 | 96.4095 | 7.8582 | 11.0584 | 518.8107 | 518.8107 | 518.8107 | 518.8107 | 57.5096 | 49.9705 | 15.7538 | 13.7908 | 15.6009 | 6.0236 | 21.6423 | 0 | 49.9707 | 16.4681 | 22.1 | 221 | 154840 | 237681 | 3548407.766 | 99.9409 | -0.0034329 | -0.10299 | -0.10299 | -0.10299 | 7.9917 | 1130 | 1100 | 1100 | 1102.4051 | 1187.8245 | 1187.8245 | 1187.8245 | 1187.8245 | 554.5181 | 554.5181 | 554.5181 | -0.0059166 | 0 | 0.3 | 48.0717 | 138.3486 | 138.4605 | 179.5945 | 1.0968 | 2.2347 | 0 | 57 | 55.0683 | 57.5096 | 105.0254 | -0.055492 | 13.7908 | -3.804 | 21.6416 | 64.1791 | 51.8815 | 0 | 66.8122 | 614.6521 | 609.3785 | 600.9161 | 601.2335 | 580.9551 | 579.1539 | 343.6544 | 348.8056 | 591.0014 | 592.0663 | 564.6694 | 569.7387 | 568.8392 | 569.0083 | 573.0777 | 568.0847 | 563.1268 | 559.307 | 554.5304 | 551.8304 | 553.7494 | 554.4237 | 555.2526 | 561.1529 | 565.236 | 565.5481 | 558.2112 | 550.9395 | 551.5875 | 553.7156 | 560.7994 | 559.1789 | 562.1993
2025-04-10 02:14 | 10 | 2 | 14 | 6.2817e-272 | 1 | 29.3794 | 396.2939 | 0.2848 | 0.0084513 | 93.2962 | 93.2962 | 93.2962 | 93.2962 | 7.6368 | 11.0585 | 511.7254 | 511.7254 | 511.7254 | 511.7254 | 57.6664 | 49.9802 | 15.7477 | 6.2956 | 15.5996 | 5.1047 | 18.332 | 0 | 49.9819 | 17.1489 | 22.1 | 221 | 154840 | 237681 | 3548409.4894 | 99.9605 | -0.027943 | -0.83829 | -0.83829 | -0.83829 | 7.9917 | 1130 | 1100 | 1100 | 1106.3938 | 1197.5874 | 1197.5874 | 1197.5874 | 1197.5874 | 514.471 | 514.471 | 514.471 | -0.0059994 | 0 | 0.3 | 47.2259 | 134.6302 | 134.7372 | 178.5383 | 1.1489 | 2.267 | 0 | 57 | 55.1305 | 57.6664 | 104.9847 | -0.063708 | 6.2956 | -3.8861 | 18.3402 | 64.213 | 51.9869 | 0 | 66.8124 | 609.832 | 604.9794 | 599.5561 | 599.9804 | 579.7349 | 578.1587 | 342.6028 | 346.7323 | 590.0797 | 591.2883 | 527.3521 | 530.0839 | 532.2264 | 532.3796 | 537.6676 | 529.0146 | 521.4841 | 516.4951 | 511.6441 | 509.2767 | 511.3401 | 513.1685 | 514.1493 | 522.3387 | 526.9494 | 527.3729 | 517.5704 | 507.7283 | 509.7541 | 510.8336 | 517.2579 | 516.5223 | 520.2664
2025-04-10 02:15 | 10 | 2 | 15 | 6.2817e-272 | 1 | 29.3844 | 325.0722 | 0.24754 | 0.008479 | 76.4954 | 76.4954 | 76.4954 | 76.4954 | 6.4449 | 10.2167 | 465.2114 | 465.2114 | 465.2114 | 465.2114 | 57.9158 | 47.3644 | 14.4623 | 0.32253 | 14.3244 | 3.7595 | 14.1635 | 0 | 49.9679 | 19.7447 | 22.1 | 221 | 154840 | 237681 | 3548410 | 94.7288 | -0.23836 | -7.1508 | -7.1508 | -7.1508 | 7.9917 | 1121.7328 | 1100 | 1100 | 1127.8577 | 1205.3691 | 1205.3691 | 1205.3691 | 1205.3691 | 480.8308 | 480.8308 | 480.8308 | -0.0058918 | 0 | 0.038298 | 37.3556 | 109.6155 | 109.708 | 175.8972 | 1.1347 | 2.096 | 0 | 56.9934 | 55.2982 | 57.9158 | 96.415 | -0.38565 | 0.32253 | -3.8657 | 13.5073 | 64.268 | 52.0703 | 0 | 66.8116 | 600.6095 | 596.0741 | 594.8596 | 595.3429 | 576.2577 | 574.8219 | 341.4481 | 343.9531 | 588.1783 | 590.1579 | 490.8406 | 498.0702 | 500.995 | 499.9861 | 506.3264 | 495.7903 | 488.9611 | 483.7434 | 478.5073 | 476.3389 | 478.5436 | 480.4206 | 481.0383 | 486.9623 | 483.828 | 484.9858 | 485.7152 | 475.5317 | 477.0731 | 478.6484 | 484.7514 | 484.6429 | 489.0162
2025-04-10 02:16 | 10 | 2 | 16 | 6.2817e-272 | 1 | 29.39 | 119.0761 | 0.15816 | 0.008504 | 34.1506 | 34.1506 | 34.1506 | 34.1506 | 3.4431 | 8.7097 | 326.9165 | 326.9165 | 326.9165 | 326.9165 | 58.0827 | 37.5793 | 1.2323 | -0.030037 | 1.2248 | 1.9727 | 9.3903 | 0 | 49.9806 | 20 | 22.1 | 221 | 154840 | 237681 | 3548410 | 75.1587 | -0.3324 | -9.9719 | -9.9719 | -9.9719 | 7.9917 | 1100 | 1100 | 1100 | 1181.9566 | 1205.8277 | 1205.8277 | 1205.8277 | 1205.8277 | 499.5214 | 499.5214 | 499.5214 | -0.006034 | 0 | 0 | 13.0887 | 45.0778 | 45.1491 | 167.1426 | 0.4149 | 0.74541 | 0 | 35.8455 | 55.4214 | 58.0827 | 8.2153 | -0.45687 | -0.030037 | -3.9027 | 7.0877 | 64.3413 | 52.1481 | 0 | 66.8109 | 584.5384 | 579.9768 | 580.2349 | 581.0301 | 566.106 | 564.5109 | 343.8344 | 345.5487 | 587.3617 | 589.6386 | 503.7454 | 510.3424 | 510.6936 | 510.7314 | 514.478 | 511.3838 | 509.8605 | 509.4722 | 506.6708 | 506.2081 | 506.1443 | 503.969 | 500.1108 | 492.8344 | 490.8068 | 498.2593 | 507.8477 | 504.748 | 503.8703 | 503.5162 | 508.8787 | 505.5823 | 505.5856
2025-04-10 02:17 | 10 | 2 | 17 | 6.2817e-272 | 1 | 29.3843 | 119.1155 | 0.084571 | 0.0085277 | 14.1858 | 14.1858 | 14.1858 | 14.1858 | 2.0285 | 8.7 | 220.4114 | 220.4114 | 220.4114 | 220.4114 | 57.9439 | 27.8721 | 0.13098 | -0.03025 | 0.091797 | 1.2964 | 8.357 | 0 | 49.9775 | 20 | 22.1 | 221 | 154840 | 237681 | 3548410 | 55.7442 | -0.29591 | -8.8773 | -8.8773 | -8.8773 | 7.9917 | 1100 | 1100 | 1100 | 1207.4804 | 1205.8287 | 1205.8287 | 1205.8287 | 1205.8287 | 543.2673 | 543.2673 | 543.2673 | -0.0060004 | 0 | 0 | 4.5522 | 17.8797 | 17.9641 | 157.4465 | 0.078994 | 0.28343 | 0 | 34 | 55.4259 | 57.9439 | 0.87319 | -0.46106 | -0.03025 | -3.9796 | 4.6577 | 64.4267 | 52.2116 | 0 | 66.8107 | 576.4139 | 571.6595 | 571.1277 | 572.1557 | 558.0865 | 556.5918 | 344.6153 | 345.1339 | 586.3592 | 588.4689 | 553.9627 | 551.9816 | 551.6339 | 550.6364 | 552.6491 | 551.1575 | 552.727 | 555.0566 | 555.665 | 556.2713 | 554.1951 | 551.4121 | 542.1946 | 532.629 | 538.2143 | 550.5021 | 547.322 | 553.2128 | 550.1806 | 546.3014 | 548.8053 | 546.0928 | 548.1005
2025-04-10 02:18 | 10 | 2 | 18 | 6.2817e-272 | 1 | 29.38 | 119.0425 | 0.05885 | 0.0085582 | 5.6982 | 5.6982 | 5.6982 | 5.6982 | 1.427 | 8.7 | 152.8061 | 152.8061 | 152.8061 | 152.8061 | 57.9493 | 19.9661 | 0.049976 | -0.029473 | 0.027201 | 0.50982 | 4.1833 | 0 | 49.977 | 20.4681 | 22.1 | 221 | 154840 | 237681 | 3548410 | 39.9323 | -0.26566 | -7.9699 | -7.9699 | -7.9699 | 7.9917 | 1100 | 1100 | 1100 | 1218.3294 | 1205.8274 | 1205.8274 | 1205.8274 | 1205.8274 | 496.4712 | 496.4712 | 496.4712 | -0.0060963 | 0 | 0 | 1.7123 | 8.4794 | 8.549 | 151.1236 | -0.056275 | 0.14568 | 0 | 34 | 55.4888 | 57.9493 | 0.33317 | -0.45946 | -0.029473 | 7.7294 | 1.8317 | 64.5054 | 52.2954 | 0 | 59.9035 | 574.0217 | 569.0953 | 568.4199 | 569.1673 | 554.2623 | 553.2504 | 344.487 | 344.4037 | 584.9986 | 586.3941 | 496.5114 | 503.8551 | 512.6373 | 507.3941 | 504.9425 | 510.25 | 499.2707 | 499.4576 | 503.522 | 506.6366 | 501.65 | 499.7555 | 506.0178 | 509.2317 | 492.4106 | 495.8263 | 512.784 | 496.1068 | 498.0027 | 504.3741 | 500.3316 | 500.1327 | 500.9062
2025-04-10 02:19 | 10 | 2 | 19 | 6.2817e-272 | 1 | 29.3816 | 118.9067 | 0.029775 | 0.0085698 | 2.5833 | 2.5833 | 2.5833 | 2.5833 | 1.2061 | 8.7 | 118.6357 | 118.6357 | 118.6357 | 118.6357 | 58.0675 | 14.9185 | 0.022038 | -0.025735 | 0.014491 | 0 | 0 | 0 | 49.9964 | 21 | 22.1 | 221 | 154840 | 237681 | 3548410 | 29.8371 | -0.20512 | -6.1535 | -6.1535 | -6.1535 | 7.9917 | 1100 | 1100 | 1100 | 1222.3153 | 1205.8213 | 1205.8213 | 1205.8213 | 1205.8213 | 376.0195 | 376.0195 | 376.0195 | -0.0060152 | 0 | 0 | 0.76988 | 5.3617 | 5.4211 | 148.0185 | -0.070923 | 0.098619 | 0 | 34 | 55.4928 | 58.0675 | 0.14692 | -0.4594 | -0.025735 | 21.0795 | 0 | 64.5429 | 52.3323 | 0 | 50.8067 | 574.5994 | 570.3263 | 569.2059 | 569.5563 | 555.051 | 554.4201 | 344.2517 | 344.1366 | 582.6629 | 584.0671 | 372.8795 | 388.4277 | 399.8713 | 389.8477 | 389.1991 | 405.8252 | 384.9449 | 381.5881 | 375.2308 | 381.4384 | 366.6644 | 379.706 | 379.0501 | 380.3875 | 371.2877 | 375.4386 | 434.1627 | 366.2537 | 369.3965 | 383.3771 | 371.9417 | 373.8967 | 377.7885
2025-04-10 02:20 | 10 | 2 | 20 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
2025-04-10 02:21 | 10 | 2 | 21 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!

## ION SETUP BRUTO
Date/Time | kW tot |  | MW | kVAR tot | VII avg | I avg | PF sign tot | freq | kWh del int | kVARh del int | kWh rec int | kVARh rec int
10-04-2025 2:09:15.000 | 24435029 |  | 24.435 | -32367451 | 15610654 | 904451050 | 99999916 | 49963585 | 38472488 | 0.636547 | 0.000000 | 578904297
10-04-2025 2:09:10.000 | 25231771 |  | 25.2318 | 167889053 | 15608895 | 934097473 | -99997787 | 49947227 | 38130664 | 0.636547 | 0.000000 | 578683533
10-04-2025 2:09:05.000 | 23661686 |  | 23.6617 | -37372078 | 15610674 | 875877563 | 99999878 | 49975658 | 37789541 | 0.496966 | 0.000000 | 578674927
10-04-2025 2:09:00.000 | 22973361 |  | 22.9734 | 133828827 | 15615435 | 850145874 | -99998306 | 49978409 | 37467847 | 0.489120 | 0.000000 | 578634949
10-04-2025 2:08:55.000 | 23416904 |  | 23.4169 | -3781182 | 15616332 | 866559265 | 100000000 | 49969112 | 37148398 | 0.365768 | 0.000000 | 578634949
10-04-2025 2:08:50.000 | 24818584 |  | 24.8186 | -85843506 | 15615262 | 918430481 | 99999405 | 49935852 | 36815378 | 0.365768 | 0.000000 | 578537048
10-04-2025 2:08:45.000 | 26062557 |  | 26.0626 | -1394507 | 15614271 | 964340820 | 99998566 | 49921719 | 36462615 | 0.318960 | 0.000000 | 578502808
10-04-2025 2:08:40.000 | 26969539 |  | 26.9695 | -1576370 | 15613104 | 998088928 | 100000000 | 49917004 | 36094792 | 0.318960 | 0.000000 | 578328613
10-04-2025 2:08:35.000 | 27235629 |  | 27.2356 | 117850693 | 15610487 | 10079483 | -99999062 | 49910915 | 35715342 | 0.302509 | 0.000000 | 578273804
10-04-2025 2:08:30.000 | 26535084 |  | 26.5351 | -39847290 | 15611104 | 981918152 | 99999886 | 49946865 | 35337981 | 0.189702 | 0.000000 | 578268494
10-04-2025 2:08:25.000 | 26017660 |  | 26.0177 | -1718766 | 15612568 | 962811646 | 99997818 | 49955521 | 34973147 | 0.189702 | 0.000000 | 578102966
10-04-2025 2:08:20.000 | 25562174 |  | 25.5622 | -10796749 | 15611572 | 946109741 | 100000000 | 49954041 | 34612788 | 0.167490 | 0.000000 | 578051331
10-04-2025 2:08:15.000 | 24410619 |  | 24.4106 | 152001511 | 15610139 | 903604797 | -99998062 | 49972546 | 34262329 | 0.081160 | 0.000000 | 578043335
10-04-2025 2:08:10.000 | 23535863 |  | 23.5359 | -35538177 | 15613487 | 871043762 | 99999886 | 49981487 | 33932390 | 0.008428 | 0.000000 | 577967163
10-04-2025 2:08:05.000 | 23147807 |  | 23.1478 | -2747754 | 15616093 | 856569458 | 99992958 | 49974415 | 33608108 | 0.000000 | 0.000000 | 577845642
10-04-2025 2:08:00.000 | 24315133 |  | 24.3151 | -1785743 | 15615026 | 899803955 | 99997307 | 49961273 | 33277947 | 0.000000 | 0.000000 | 577554688
10-04-2025 2:07:55.000 | 25196088 |  | 25.1961 | -3978724 | 15614287 | 932416077 | 99987534 | 49948513 | 32935908 | 0.000000 | 0.000000 | 577267639
10-04-2025 2:07:50.000 | 26714934 |  | 26.7149 | -3484957 | 15612389 | 988749939 | 99991493 | 49919216 | 32574141 | 0.000000 | 0.000000 | 576818848
10-04-2025 2:07:45.000 | 26654752 |  | 26.6548 | -1982577 | 15610722 | 986703247 | 99997231 | 49938400 | 32199429 | 0.000000 | 0.000000 | 576504333
10-04-2025 2:07:40.000 | 25780162 |  | 25.7802 | -4518981 | 15609629 | 954306946 | 99984642 | 49967392 | 31836956 | 0.000000 | 0.000000 | 576207153
10-04-2025 2:07:35.000 | 26037188 |  | 26.0372 | -7167103 | 15614790 | 963708740 | 99962135 | 49958237 | 31476765 | 0.000000 | 0.000000 | 575419006
10-04-2025 2:07:30.000 | 25867148 |  | 25.8671 | -5866053 | 15608762 | 957795654 | 99974297 | 49956104 | 31111829 | 0.000000 | 0.000000 | 574666931
10-04-2025 2:07:25.000 | 25081771 |  | 25.0818 | -3191091 | 15610395 | 928360962 | 99991905 | 49973293 | 30756697 | 0.000000 | 0.000000 | 573874329
10-04-2025 2:07:20.000 | 24293605 |  | 24.2936 | -2940283 | 15612605 | 899224548 | 99992676 | 49992222 | 30412986 | 0.000000 | 0.000000 | 573385315
10-04-2025 2:07:15.000 | 24776432 |  | 24.7764 | -4743630 | 15613306 | 916984253 | 99981674 | 49981155 | 30073989 | 0.000000 | 0.000000 | 572771667
10-04-2025 2:07:10.000 | 24833496 |  | 24.8335 | -6353505 | 15612025 | 919437256 | 99967285 | 49979710 | 29727554 | 0.000000 | 0.000000 | 572145569
10-04-2025 2:07:05.000 | 23465986 |  | 23.466 | -6340839 | 15609644 | 869138611 | 99963509 | 49993862 | 29389883 | 0.000000 | 0.000000 | 571344604
10-04-2025 2:07:00.000 | 23250391 |  | 23.2504 | -1458042 | 15611545 | 862315247 | 99803947 | 49996449 | 29067390 | 0.000000 | 0.000000 | 570010498
10-04-2025 2:06:55.000 | 25183078 |  | 25.1831 | -2526443 | 15612513 | 936677917 | 99500534 | 49956192 | 28734121 | 0.000000 | 0.000000 | 567388184
10-04-2025 2:06:50.000 | 25362396 |  | 25.3624 | -2398764 | 15611197 | 942773560 | 99555717 | 49941711 | 28381921 | 0.000000 | 0.000000 | 564033569
10-04-2025 2:06:45.000 | 24347166 |  | 24.3472 | -2362718 | 15608224 | 905596924 | 99532433 | 49960152 | 28035361 | 0.000000 | 0.000000 | 560679932
10-04-2025 2:06:40.000 | 23449256 |  | 23.4493 | -3117555 | 15608064 | 875871460 | 99127777 | 49967690 | 27706323 | 0.000000 | 0.000000 | 556968994
10-04-2025 2:06:35.000 | 23685391 |  | 23.6854 | -3942496 | 15613632 | 888611877 | 98642815 | 49960495 | 27381743 | 0.000000 | 0.000000 | 551975098
10-04-2025 2:06:30.000 | 23824787 |  | 23.8248 | -3807071 | 15613155 | 892962402 | 98747223 | 49953384 | 27051521 | 0.000000 | 0.000000 | 546552429
10-04-2025 2:06:25.000 | 23967920 |  | 23.9679 | -3931988 | 15614475 | 898854431 | 98680908 | 49960285 | 26722793 | 0.000000 | 0.000000 | 541135925
10-04-2025 2:06:20.000 | 24934871 |  | 24.9349 | -3886090 | 15613685 | 933776367 | 98807228 | 49938835 | 26386514 | 0.000000 | 0.000000 | 535611267
10-04-2025 2:06:15.000 | 26034629 |  | 26.0346 | -3397401 | 15607278 | 971973816 | 99159271 | 49915474 | 26032551 | 0.000000 | 0.000000 | 530453918
10-04-2025 2:06:10.000 | 25686471 |  | 25.6865 | -4613555 | 15609163 | 965977051 | 98425011 | 49923965 | 25673147 | 0.000000 | 0.000000 | 525099670
10-04-2025 2:06:05.000 | 26651672 |  | 26.6517 | -5426453 | 15611344 | 10065584 | 97989517 | 49926949 | 25311274 | 0.000000 | 0.000000 | 518113281
10-04-2025 2:06:00.000 | 27042059 |  | 27.0421 | -5387344 | 15611628 | 10203277 | 98072731 | 49914886 | 24935383 | 0.000000 | 0.000000 | 510578156
10-04-2025 2:05:55.000 | 25696568 |  | 25.6966 | -5171065 | 15609356 | 970190186 | 98034706 | 49947601 | 24562708 | 0.000000 | 0.000000 | 503249847
10-04-2025 2:05:50.000 | 24204344 |  | 24.2043 | -5667262 | 15617101 | 919750854 | 97366661 | 49986870 | 24217769 | 0.000000 | 0.000000 | 495787354
10-04-2025 2:05:45.000 | 25375141 |  | 25.3751 | -5435311 | 15614509 | 960146912 | 97781990 | 49968204 | 23876216 | 0.000000 | 0.000000 | 488103333
10-04-2025 2:05:40.000 | 26190385 |  | 26.1904 | -5418114 | 15612053 | 989694153 | 97926476 | 49955021 | 23519421 | 0.000000 | 0.000000 | 480450409
10-04-2025 2:05:35.000 | 26190115 |  | 26.1901 | -5271597 | 15613473 | 988571045 | 98033829 | 49941902 | 23153633 | 0.000000 | 0.000000 | 472926361
10-04-2025 2:05:30.000 | 25661400 |  | 25.6614 | -5213737 | 15611937 | 969142700 | 97997787 | 49950882 | 22791128 | 0.000000 | 0.000000 | 465785583
10-04-2025 2:05:25.000 | 25291850 |  | 25.2919 | -5455120 | 15611465 | 957482666 | 97752090 | 49956047 | 22434280 | 0.000000 | 0.000000 | 458422119
10-04-2025 2:05:20.000 | 23917650 |  | 23.9176 | -5494063 | 15614355 | 908133362 | 97461746 | 49976387 | 22086995 | 0.000000 | 0.000000 | 450991669
10-04-2025 2:05:15.000 | 22796189 |  | 22.7962 | -5417670 | 15615458 | 866960693 | 97290222 | 49991276 | 21760093 | 0.000000 | 0.000000 | 443531830
10-04-2025 2:05:10.000 | 23381260 |  | 23.3813 | -5321032 | 15616534 | 887367554 | 97506874 | 49976578 | 21439653 | 0.000000 | 0.000000 | 436082214
10-04-2025 2:05:05.000 | 24413193 |  | 24.4132 | -5222071 | 15614224 | 923895630 | 97787888 | 49945446 | 21110234 | 0.000000 | 0.000000 | 428752075
10-04-2025 2:05:00.000 | 25450457 |  | 25.4505 | -5315262 | 15612396 | 962179626 | 97887985 | 49924934 | 20766257 | 0.000000 | 0.000000 | 421450867
10-04-2025 2:04:55.000 | 26838799 |  | 26.8388 | -5267346 | 15610814 | 10121799 | 98128036 | 49911461 | 20402509 | 0.000000 | 0.000000 | 413989532
10-04-2025 2:04:50.000 | 25406773 |  | 25.4068 | -5030248 | 15608833 | 958626526 | 98095833 | 49928104 | 20037590 | 0.000000 | 0.000000 | 406727844
10-04-2025 2:04:45.000 | 24031457 |  | 24.0315 | -5109642 | 15612596 | 909243958 | 97813438 | 49957954 | 19695352 | 0.000000 | 0.000000 | 399637024
10-04-2025 2:04:40.000 | 23799346 |  | 23.7993 | -5154062 | 15612416 | 901246033 | 97734406 | 49972988 | 19363300 | 0.000000 | 0.000000 | 392528229
10-04-2025 2:04:35.000 | 24670445 |  | 24.6704 | -4956320 | 15612500 | 931351685 | 98041039 | 49951473 | 19029492 | 0.000000 | 0.000000 | 385283081
10-04-2025 2:04:30.000 | 23839672 |  | 23.8397 | -5216986 | 15614170 | 903223633 | 97688240 | 49958706 | 18694003 | 0.000000 | 0.000000 | 378327362
10-04-2025 2:04:25.000 | 23562961 |  | 23.563 | -4964526 | 15611800 | 891255493 | 97851707 | 49956039 | 18363611 | 0.000000 | 0.000000 | 371386353
10-04-2025 2:04:20.000 | 23853254 |  | 23.8533 | -5418700 | 15614969 | 905065613 | 97515488 | 49960480 | 18034526 | 0.000000 | 0.000000 | 364197174
10-04-2025 2:04:15.000 | 24901154 |  | 24.9012 | -4791775 | 15611553 | 938469238 | 98198380 | 49934460 | 17696711 | 0.000000 | 0.000000 | 357013397
10-04-2025 2:04:10.000 | 23677418 |  | 23.6774 | -4692012 | 15612938 | 893360291 | 98092552 | 49956726 | 17357750 | 0.000000 | 0.000000 | 350414215
10-04-2025 2:04:05.000 | 24094031 |  | 24.094 | -4981497 | 15615622 | 910366333 | 97928841 | 49934696 | 17029216 | 0.000000 | 0.000000 | 343641113
10-04-2025 2:04:00.000 | 24013279 |  | 24.0133 | -4366292 | 15611668 | 903303955 | 98386818 | 49938625 | 16692152 | 0.000000 | 0.000000 | 337174469
10-04-2025 2:03:55.000 | 23997461 |  | 23.9975 | -4637073 | 15613994 | 904557922 | 98183777 | 49953011 | 16360461 | 0.000000 | 0.000000 | 330838776
10-04-2025 2:03:50.000 | 24756441 |  | 24.7564 | -5073244 | 15616438 | 934946350 | 97964165 | 49933578 | 16024456 | 0.000000 | 0.000000 | 324140198
10-04-2025 2:03:45.000 | 26132863 |  | 26.1329 | -4897910 | 15613960 | 983730591 | 98288582 | 49897655 | 15670094 | 0.000000 | 0.000000 | 317237000
10-04-2025 2:03:40.000 | 25647297 |  | 25.6473 | -4509832 | 15612791 | 963683655 | 98488960 | 49910355 | 15307205 | 0.000000 | 0.000000 | 310701965
10-04-2025 2:03:35.000 | 26010773 |  | 26.0108 | -4765166 | 15612047 | 978499512 | 98362984 | 49915943 | 14952965 | 0.000000 | 0.000000 | 304267731
10-04-2025 2:03:30.000 | 26211916 |  | 26.2119 | -4609125 | 15611623 | 984915833 | 98488953 | 49908787 | 14587833 | 0.000000 | 0.000000 | 297684540
10-04-2025 2:03:25.000 | 25421967 |  | 25.422 | -4424756 | 15611718 | 955030518 | 98518860 | 49920700 | 14228250 | 0.000000 | 0.000000 | 291237030
10-04-2025 2:03:20.000 | 24673467 |  | 24.6735 | -4747205 | 15617374 | 929475525 | 98198944 | 49951763 | 13880576 | 0.000000 | 0.000000 | 284893707
10-04-2025 2:03:15.000 | 26777396 |  | 26.7774 | -4687243 | 15616361 | 10056467 | 98502296 | 49926922 | 13526331 | 0.000000 | 0.000000 | 278316650
10-04-2025 2:03:10.000 | 29175598 |  | 29.1756 | -4859687 | 15613898 | 10942336 | 98640991 | 49890785 | 13141593 | 0.000000 | 0.000000 | 271757538
10-04-2025 2:03:05.000 | 30548373 |  | 30.5484 | -4832097 | 15610122 | 11444436 | 98771973 | 49868374 | 12723275 | 0.000000 | 0.000000 | 265048645
10-04-2025 2:03:00.000 | 29756611 |  | 29.7566 | -5149135 | 15607378 | 11177020 | 98535637 | 49887344 | 12300901 | 0.000000 | 0.000000 | 258178497
10-04-2025 2:02:55.000 | 28396520 |  | 28.3965 | -5046523 | 15605761 | 10676440 | 98457298 | 49922634 | 11892288 | 0.000000 | 0.000000 | 251213547
10-04-2025 2:02:50.000 | 25165727 |  | 25.1657 | -5470632 | 15609454 | 953177185 | 97717781 | 49985603 | 11517344 | 0.000000 | 0.000000 | 243896545
10-04-2025 2:02:45.000 | 22727344 |  | 22.7273 | -5631689 | 15615062 | 866356506 | 97064430 | 50031033 | 11182236 | 0.000000 | 0.000000 | 236275650
10-04-2025 2:02:40.000 | 22915115 |  | 22.9151 | -5678268 | 15615062 | 873727783 | 97064384 | 50022499 | 10866696 | 0.000000 | 0.000000 | 228543564
10-04-2025 2:02:35.000 | 24130402 |  | 24.1304 | -5790746 | 15614002 | 918207947 | 97239235 | 50001431 | 10542986 | 0.000000 | 0.000000 | 220534058
10-04-2025 2:02:30.000 | 26154584 |  | 26.1546 | -5988685 | 15612220 | 992840027 | 97477348 | 49968811 | 10197834 | 0.000000 | 0.000000 | 212367340
10-04-2025 2:02:25.000 | 27497180 |  | 27.4972 | -6000396 | 15608251 | 10416449 | 97700829 | 49943893 | 982442322 | 0.000000 | 0.000000 | 204008789
10-04-2025 2:02:20.000 | 26405406 |  | 26.4054 | -6040174 | 15611311 | 10023528 | 97482117 | 49964264 | 944633728 | 0.000000 | 0.000000 | 195545395
10-04-2025 2:02:15.000 | 23751934 |  | 23.7519 | -5830518 | 15607922 | 905370972 | 97116760 | 50010452 | 909108948 | 0.000000 | 0.000000 | 187494583
10-04-2025 2:02:10.000 | 20852412 |  | 20.8524 | -6020232 | 15612815 | 803364746 | 96076080 | 50057953 | 877801758 | 0.000000 | 0.000000 | 179323242
10-04-2025 2:02:05.000 | 20109785 |  | 20.1098 | -5950271 | 15615816 | 776129883 | 95890434 | 50059605 | 849443726 | 0.000000 | 0.000000 | 171011368
10-04-2025 2:02:00.000 | 20516500 |  | 20.5165 | -5693128 | 15617074 | 787960022 | 96358932 | 50054382 | 821315186 | 0.000000 | 0.000000 | 162965378
10-04-2025 2:01:55.000 | 22377434 |  | 22.3774 | -5782454 | 15619404 | 855032288 | 96819740 | 50010422 | 792038147 | 0.000000 | 0.000000 | 155010162
10-04-2025 2:01:50.000 | 24656393 |  | 24.6564 | -5054034 | 15613345 | 931376587 | 97963150 | 49951977 | 759354919 | 0.000000 | 0.000000 | 147422485
10-04-2025 2:01:45.000 | 24433564 |  | 24.4336 | -4755270 | 15612462 | 921161926 | 98158302 | 49949680 | 725188538 | 0.000000 | 0.000000 | 140487915
10-04-2025 2:01:40.000 | 24293896 |  | 24.2939 | -5210761 | 15614840 | 919303162 | 97776176 | 49961182 | 691590088 | 0.000000 | 0.000000 | 133581619
10-04-2025 2:01:35.000 | 25381018 |  | 25.381 | -5011494 | 15612038 | 957341980 | 98105873 | 49942505 | 657238037 | 0.000000 | 0.000000 | 126429749
10-04-2025 2:01:30.000 | 26024258 |  | 26.0243 | -5040449 | 15613497 | 980814758 | 98175522 | 49934978 | 621675964 | 0.000000 | 0.000000 | 119454735
10-04-2025 2:01:25.000 | 26119139 |  | 26.1191 | -4931827 | 15612386 | 983524292 | 98263634 | 49919796 | 585401794 | 0.000000 | 0.000000 | 112501816
10-04-2025 2:01:20.000 | 25844543 |  | 25.8445 | -4977737 | 15612793 | 973863586 | 98195259 | 49923023 | 549265625 | 0.000000 | 0.000000 | 105538437
10-04-2025 2:01:15.000 | 25303922 |  | 25.3039 | -4915594 | 15610815 | 953956116 | 98164894 | 49938835 | 513433655 | 0.000000 | 0.000000 | 98700729
10-04-2025 2:01:10.000 | 24317576 |  | 24.3176 | -5082705 | 15613272 | 919367371 | 97884727 | 49951180 | 479176086 | 0.000000 | 0.000000 | 91727280
10-04-2025 2:01:05.000 | 24050553 |  | 24.0506 | -4995228 | 15614257 | 908947449 | 97910461 | 49967232 | 445633545 | 0.000000 | 0.000000 | 84732552
10-04-2025 2:01:00.000 | 24769322 |  | 24.7693 | -4952122 | 15614566 | 934598816 | 98059395 | 49958580 | 412009949 | 0.000000 | 0.000000 | 77798309
10-04-2025 2:00:55.000 | 26064707 |  | 26.0647 | -4857197 | 15614655 | 980995300 | 98307610 | 49932728 | 377016846 | 0.000000 | 0.000000 | 70862106
10-04-2025 2:00:50.000 | 26044918 |  | 26.0449 | -4720516 | 15609612 | 979678223 | 98396896 | 49913280 | 340618622 | 0.000000 | 0.000000 | 64209167
10-04-2025 2:00:45.000 | 25207059 |  | 25.2071 | -4719852 | 15609094 | 949250427 | 98291786 | 49935173 | 304828796 | 0.000000 | 0.000000 | 57574356
10-04-2025 2:00:40.000 | 23676273 |  | 23.6763 | -5088830 | 15612497 | 896613342 | 97767242 | 49975403 | 270822266 | 0.000000 | 0.000000 | 50932686
10-04-2025 2:00:35.000 | 23254320 |  | 23.2543 | -4497656 | 15614210 | 876443542 | 98180489 | 49957611 | 238126236 | 0.000000 | 0.000000 | 44089439
10-04-2025 2:00:30.000 | 23014010 |  | 23.014 | -4605878 | 15617034 | 868254395 | 98055550 | 49958950 | 206218002 | 0.000000 | 0.000000 | 37734264
10-04-2025 2:00:25.000 | 25073643 |  | 25.0736 | -4504617 | 15611682 | 942811951 | 98424240 | 49924129 | 172948822 | 0.000000 | 0.000000 | 31433739
10-04-2025 2:00:20.000 | 25532244 |  | 25.5322 | -4454959 | 15612150 | 959132202 | 98511673 | 49905308 | 137660446 | 0.000000 | 0.000000 | 25239822
10-04-2025 2:00:15.000 | 25495887 |  | 25.4959 | -4444315 | 15611141 | 957777283 | 98514481 | 49906624 | 102271355 | 0.000000 | 0.000000 | 19192368
10-04-2025 2:00:10.000 | 24742168 |  | 24.7422 | -4625292 | 15611827 | 931541565 | 98297180 | 49914391 | 67034531 | 0.000000 | 0.000000 | 12940805
10-04-2025 2:00:05.000 | 23943215 |  | 23.9432 | -4744989 | 15618293 | 903010193 | 98092308 | 49940437 | 33382221 | 0.000000 | 0.000000 | 6336285
10-04-2025 2:00:00.000 | 24711178 |  | 24.7112 | -4559898 | 15613239 | 930047241 | 98339760 | 49937565 | 62508892 | 0.000000 | 0.000000 | 10173399
10-04-2025 1:59:55.000 | 26523896 |  | 26.5239 | -4322007 | 15611412 | 994474304 | 98698273 | 49890984 | 62154355 | 0.000000 | 0.000000 | 10108748
10-04-2025 1:59:50.000 | 26165773 |  | 26.1658 | -4092046 | 15610566 | 980086609 | 98799103 | 49897896 | 61787246 | 0.000000 | 0.000000 | 10049365
10-04-2025 1:59:45.000 | 25326727 |  | 25.3267 | -4169181 | 15612918 | 949792053 | 98672012 | 49910877 | 61427241 | 0.000000 | 0.000000 | 999075317
10-04-2025 1:59:40.000 | 24815904 |  | 24.8159 | -4301787 | 15613256 | 932114990 | 98530556 | 49924099 | 61079175 | 0.000000 | 0.000000 | 993348572
10-04-2025 1:59:35.000 | 24036650 |  | 24.0367 | -4039295 | 15611986 | 902024231 | 98617226 | 49933949 | 60735977 | 0.000000 | 0.000000 | 987605652
10-04-2025 1:59:30.000 | 22895566 |  | 22.8956 | -4330719 | 15615512 | 862292297 | 98257713 | 49951931 | 60409106 | 0.000000 | 0.000000 | 981945862
10-04-2025 1:59:25.000 | 24745973 |  | 24.746 | -4476258 | 15613295 | 930560547 | 98403053 | 49914970 | 60082305 | 0.000000 | 0.000000 | 975874878
10-04-2025 1:59:20.000 | 25763057 |  | 25.7631 | -4109884 | 15614535 | 965256042 | 98751350 | 49887203 | 59730908 | 0.000000 | 0.000000 | 969682983
10-04-2025 1:59:15.000 | 25280402 |  | 25.2804 | -3894572 | 15610564 | 946666077 | 98834068 | 49892090 | 59376724 | 0.000000 | 0.000000 | 964229797
10-04-2025 1:59:10.000 | 24868453 |  | 24.8685 | -4089657 | 15612983 | 932755188 | 98674606 | 49905891 | 59027964 | 0.000000 | 0.000000 | 958809326
10-04-2025 1:59:05.000 | 24775207 |  | 24.7752 | -3977538 | 15612414 | 928584900 | 98735657 | 49894287 | 58682427 | 0.000000 | 0.000000 | 953185242
10-04-2025 1:59:00.000 | 24220408 |  | 24.2204 | -3967950 | 15615509 | 908186157 | 98684464 | 49920670 | 58340103 | 0.000000 | 0.000000 | 947650208
10-04-2025 1:58:55.000 | 24247047 |  | 24.247 | -4056214 | 15614654 | 909605286 | 98629456 | 49923992 | 58005552 | 0.000000 | 0.000000 | 942187927
10-04-2025 1:58:50.000 | 26157074 |  | 26.1571 | -3939760 | 15614210 | 978732971 | 98884636 | 49892551 | 57660044 | 0.000000 | 0.000000 | 936590759
10-04-2025 1:58:45.000 | 27368643 |  | 27.3686 | -3709567 | 15609839 | 10222599 | 99093903 | 49875877 | 57290215 | 0.000000 | 0.000000 | 931174805
10-04-2025 1:58:40.000 | 27523580 |  | 27.5236 | -4024505 | 15610143 | 10294305 | 98947823 | 49886269 | 56909321 | 0.000000 | 0.000000 | 925792358
10-04-2025 1:58:35.000 | 27190098 |  | 27.1901 | -4215880 | 15608574 | 10183450 | 98819191 | 49904404 | 56529043 | 0.000000 | 0.000000 | 920158813
10-04-2025 1:58:30.000 | 26652324 |  | 26.6523 | -4226706 | 15609097 | 998700012 | 98765747 | 49928291 | 56155195 | 0.000000 | 0.000000 | 914149475
10-04-2025 1:58:25.000 | 24641459 |  | 24.6415 | -4481006 | 15610666 | 927032593 | 98386467 | 49958385 | 55797192 | 0.000000 | 0.000000 | 908119141
10-04-2025 1:58:20.000 | 24365354 |  | 24.3654 | -4816456 | 15613792 | 919079224 | 98101662 | 49966553 | 55457173 | 0.000000 | 0.000000 | 901708374
10-04-2025 1:58:15.000 | 24036143 |  | 24.0361 | -4633641 | 15614920 | 905691956 | 98192070 | 49976311 | 55117905 | 0.000000 | 0.000000 | 895150574
10-04-2025 1:58:10.000 | 24081057 |  | 24.0811 | -4804668 | 15617951 | 908433838 | 98067101 | 49987617 | 54785942 | 0.000000 | 0.000000 | 888599731
10-04-2025 1:58:05.000 | 25712834 |  | 25.7128 | -4464893 | 15615607 | 965497314 | 98525635 | 49953892 | 54442715 | 0.000000 | 0.000000 | 882303772
10-04-2025 1:58:00.000 | 26563453 |  | 26.5635 | -3973973 | 15609914 | 994050537 | 98899384 | 49931450 | 54074971 | 0.000000 | 0.000000 | 876597900
10-04-2025 1:57:55.000 | 25226473 |  | 25.2265 | -4089573 | 15610748 | 946000610 | 98711296 | 49958054 | 53713247 | 0.000000 | 0.000000 | 871229919
10-04-2025 1:57:50.000 | 24116893 |  | 24.1169 | -4165355 | 15614251 | 905574707 | 98541031 | 49978664 | 53370229 | 0.000000 | 0.000000 | 865537048
10-04-2025 1:57:45.000 | 22867209 |  | 22.8672 | -4237173 | 15616801 | 860710022 | 98326271 | 49990871 | 53043916 | 0.000000 | 0.000000 | 859851318
10-04-2025 1:57:40.000 | 23930674 |  | 23.9307 | -4233458 | 15613398 | 899305969 | 98471024 | 49977921 | 52720049 | 0.000000 | 0.000000 | 854117249
10-04-2025 1:57:35.000 | 26526098 |  | 26.5261 | -4241960 | 15612791 | 994083679 | 98745346 | 49927727 | 52375571 | 0.000000 | 0.000000 | 848036865
10-04-2025 1:57:30.000 | 26086086 |  | 26.0861 | -4110316 | 15609070 | 977367065 | 98781273 | 49934452 | 52004585 | 0.000000 | 0.000000 | 842336304
10-04-2025 1:57:25.000 | 24778191 |  | 24.7782 | -4484815 | 15615166 | 931638672 | 98401154 | 49954311 | 51650391 | 0.000000 | 0.000000 | 836426819
10-04-2025 1:57:20.000 | 24480199 |  | 24.4802 | -4088644 | 15613454 | 918454041 | 98633759 | 49964481 | 51304209 | 0.000000 | 0.000000 | 830446045
10-04-2025 1:57:15.000 | 23134980 |  | 23.135 | -4329331 | 15616032 | 871061462 | 98293739 | 49992046 | 50972993 | 0.000000 | 0.000000 | 824800415
10-04-2025 1:57:10.000 | 25150760 |  | 25.1508 | -4253868 | 15615726 | 943719116 | 98599648 | 49949940 | 50639258 | 0.000000 | 0.000000 | 818856995
10-04-2025 1:57:05.000 | 26206664 |  | 26.2067 | -4154437 | 15613154 | 981739502 | 98766670 | 49924496 | 50282666 | 0.000000 | 0.000000 | 812990845
10-04-2025 1:57:00.000 | 25654893 |  | 25.6549 | -3960421 | 15611147 | 961017395 | 98829330 | 49943039 | 49918281 | 0.000000 | 0.000000 | 807335144
10-04-2025 1:56:55.000 | 24240303 |  | 24.2403 | -3914286 | 15610276 | 908884583 | 98721191 | 49975311 | 49571914 | 0.000000 | 0.000000 | 801671082
10-04-2025 1:56:50.000 | 23512385 |  | 23.5124 | -4167885 | 15615030 | 883803406 | 98464966 | 49983906 | 49243604 | 0.000000 | 0.000000 | 795903687
10-04-2025 1:56:45.000 | 24551709 |  | 24.5517 | -4287251 | 15617038 | 922168701 | 98509377 | 49954323 | 48911357 | 0.000000 | 0.000000 | 790038513
10-04-2025 1:56:40.000 | 25983010 |  | 25.983 | -3756951 | 15610972 | 971589294 | 98970757 | 49933746 | 48560464 | 0.000000 | 0.000000 | 784375427
10-04-2025 1:56:35.000 | 26329418 |  | 26.3294 | -3934186 | 15610866 | 985144470 | 98902008 | 49921703 | 48200313 | 0.000000 | 0.000000 | 778724670
10-04-2025 1:56:30.000 | 25897545 |  | 25.8975 | -4038356 | 15614799 | 969772095 | 98805931 | 49920082 | 47834824 | 0.000000 | 0.000000 | 773147888
10-04-2025 1:56:25.000 | 25237289 |  | 25.2373 | -4060970 | 15613575 | 945872498 | 98729988 | 49937977 | 47476167 | 0.000000 | 0.000000 | 767748230
10-04-2025 1:56:20.000 | 25212920 |  | 25.2129 | -3999354 | 15613629 | 944722107 | 98765190 | 49945179 | 47125483 | 0.000000 | 0.000000 | 762157593
10-04-2025 1:56:15.000 | 25265195 |  | 25.2652 | -3808175 | 15610341 | 945650085 | 98883049 | 49943760 | 46773584 | 0.000000 | 0.000000 | 756706482
10-04-2025 1:56:10.000 | 24655154 |  | 24.6552 | -3960500 | 15612579 | 924097168 | 98734253 | 49946846 | 46428394 | 0.000000 | 0.000000 | 751265991
10-04-2025 1:56:05.000 | 24475234 |  | 24.4752 | -3775827 | 15610059 | 916579163 | 98830849 | 49951649 | 46085103 | 0.000000 | 0.000000 | 745881104
10-04-2025 1:56:00.000 | 23674605 |  | 23.6746 | -3851825 | 15613241 | 887589478 | 98702171 | 49955658 | 45751338 | 0.000000 | 0.000000 | 740494385
10-04-2025 1:55:55.000 | 22712938 |  | 22.7129 | -3706342 | 15612212 | 851787231 | 98694595 | 49953529 | 45425757 | 0.000000 | 0.000000 | 735273254
10-04-2025 1:55:50.000 | 21980229 |  | 21.9802 | -4010144 | 15617496 | 826868958 | 98376152 | 49959328 | 45116030 | 0.000000 | 0.000000 | 730095154
10-04-2025 1:55:45.000 | 23169270 |  | 23.1693 | -3635884 | 15614269 | 867888123 | 98790977 | 49933926 | 44804434 | 0.000000 | 0.000000 | 724814880
10-04-2025 1:55:40.000 | 24689848 |  | 24.6898 | -3681263 | 15615579 | 923638306 | 98906654 | 49903572 | 44475347 | 0.000000 | 0.000000 | 719620972
10-04-2025 1:55:35.000 | 25978414 |  | 25.9784 | -3778558 | 15613186 | 971436523 | 98958710 | 49876774 | 44127808 | 0.000000 | 0.000000 | 714424683
10-04-2025 1:55:30.000 | 25853104 |  | 25.8531 | -3790689 | 15611286 | 967016907 | 98942093 | 49881805 | 43761401 | 0.000000 | 0.000000 | 709319397
10-04-2025 1:55:25.000 | 25320877 |  | 25.3209 | -3975200 | 15612727 | 948458679 | 98789986 | 49891232 | 43403271 | 0.000000 | 0.000000 | 704032166
10-04-2025 1:55:20.000 | 25027350 |  | 25.0273 | -3922044 | 15612952 | 937483826 | 98794258 | 49908920 | 43053047 | 0.000000 | 0.000000 | 698662964
10-04-2025 1:55:15.000 | 25491988 |  | 25.492 | -3951163 | 15613189 | 954540344 | 98820030 | 49901787 | 42705210 | 0.000000 | 0.000000 | 693118774
10-04-2025 1:55:10.000 | 26333541 |  | 26.3335 | -4275419 | 15613930 | 987101135 | 98707520 | 49897465 | 42345864 | 0.000000 | 0.000000 | 687573608
10-04-2025 1:55:05.000 | 28312078 |  | 28.3121 | -4201408 | 15610069 | 10592290 | 98916786 | 49861969 | 41967061 | 0.000000 | 0.000000 | 681652588
10-04-2025 1:55:00.000 | 27068633 |  | 27.0686 | -3743551 | 15607959 | 10114141 | 99057182 | 49888165 | 41577681 | 0.000000 | 0.000000 | 676086853
10-04-2025 1:54:55.000 | 24205221 |  | 24.2052 | -4137297 | 15613168 | 908671509 | 98570465 | 49955631 | 41219087 | 0.000000 | 0.000000 | 670763855
10-04-2025 1:54:50.000 | 24118732 |  | 24.1187 | -4142549 | 15616086 | 905533875 | 98556839 | 49951283 | 40884644 | 0.000000 | 0.000000 | 665014893
10-04-2025 1:54:45.000 | 25169256 |  | 25.1693 | -4214479 | 15614189 | 944503723 | 98626907 | 49914276 | 40545696 | 0.000000 | 0.000000 | 659203918
10-04-2025 1:54:40.000 | 25769879 |  | 25.7699 | -3934640 | 15610476 | 964806152 | 98854378 | 49899822 | 40191558 | 0.000000 | 0.000000 | 653383911
10-04-2025 1:54:35.000 | 24799104 |  | 24.7991 | -3975000 | 15612437 | 929520203 | 98739624 | 49916862 | 39840403 | 0.000000 | 0.000000 | 647760193
10-04-2025 1:54:30.000 | 24143398 |  | 24.1434 | -4102605 | 15612385 | 906525146 | 98586777 | 49932755 | 39499841 | 0.000000 | 0.000000 | 642190186
10-04-2025 1:54:25.000 | 23843941 |  | 23.8439 | -4079272 | 15614573 | 895281982 | 98567909 | 49936741 | 39164985 | 0.000000 | 0.000000 | 636475586
10-04-2025 1:54:20.000 | 23324840 |  | 23.3248 | -3905371 | 15613286 | 875330017 | 98627090 | 49956566 | 38837520 | 0.000000 | 0.000000 | 631099182
10-04-2025 1:54:15.000 | 25059746 |  | 25.0597 | -4068282 | 15614979 | 939378540 | 98707718 | 49906380 | 38508962 | 0.000000 | 0.000000 | 625398621
10-04-2025 1:54:10.000 | 25912422 |  | 25.9124 | -3748413 | 15611918 | 968864380 | 98969856 | 49886467 | 38154280 | 0.000000 | 0.000000 | 619976440
10-04-2025 1:54:05.000 | 25571182 |  | 25.5712 | -3866298 | 15612936 | 956969971 | 98876198 | 49897484 | 37794858 | 0.000000 | 0.000000 | 614818542
10-04-2025 1:54:00.000 | 26182688 |  | 26.1827 | -3789963 | 15610675 | 979055847 | 98968544 | 49888489 | 37435945 | 0.000000 | 0.000000 | 609584106
10-04-2025 1:53:55.000 | 26734971 |  | 26.735 | -3841102 | 15611996 | 999449219 | 98983604 | 49890671 | 37069114 | 0.000000 | 0.000000 | 604086365
10-04-2025 1:53:50.000 | 25770813 |  | 25.7708 | -3654101 | 15610953 | 963367615 | 99009659 | 49904766 | 36701926 | 0.000000 | 0.000000 | 598814453
10-04-2025 1:53:45.000 | 24084641 |  | 24.0846 | -3724168 | 15612214 | 902056458 | 98825523 | 49951248 | 36355454 | 0.000000 | 0.000000 | 593815735
10-04-2025 1:53:40.000 | 24677961 |  | 24.678 | -3892416 | 15613728 | 924599487 | 98778824 | 49945107 | 36019175 | 0.000000 | 0.000000 | 588557678
10-04-2025 1:53:35.000 | 24758984 |  | 24.759 | -3771825 | 15613492 | 926855957 | 98859413 | 49926876 | 35671736 | 0.000000 | 0.000000 | 583351257
10-04-2025 1:53:30.000 | 24596146 |  | 24.5961 | -3792912 | 15612990 | 920933716 | 98831795 | 49930317 | 35325803 | 0.000000 | 0.000000 | 578204407
10-04-2025 1:53:25.000 | 25082324 |  | 25.0823 | -3746943 | 15612578 | 938507629 | 98902527 | 49929493 | 34981519 | 0.000000 | 0.000000 | 572963623
10-04-2025 1:53:20.000 | 24158346 |  | 24.1583 | -3607484 | 15612120 | 903951965 | 98903381 | 49933777 | 34638013 | 0.000000 | 0.000000 | 567757690
10-04-2025 1:53:15.000 | 23192303 |  | 23.1923 | -3670117 | 15613854 | 869007263 | 98770927 | 49946289 | 34309199 | 0.000000 | 0.000000 | 562680725
10-04-2025 1:53:10.000 | 24420275 |  | 24.4203 | -3527941 | 15612265 | 913168030 | 98972511 | 49921280 | 33982190 | 0.000000 | 0.000000 | 557520142
10-04-2025 1:53:05.000 | 24341906 |  | 24.3419 | -3406179 | 15610925 | 909840393 | 99035118 | 49908337 | 33643328 | 0.000000 | 0.000000 | 552568909
10-04-2025 1:53:00.000 | 23353898 |  | 23.3539 | -3430780 | 15615048 | 873489380 | 98938118 | 49921219 | 33311653 | 0.000000 | 0.000000 | 547886292
10-04-2025 1:52:55.000 | 23611605 |  | 23.6116 | -3282257 | 15613000 | 882221985 | 99047585 | 49916924 | 32985120 | 0.000000 | 0.000000 | 543345276
10-04-2025 1:52:50.000 | 24496301 |  | 24.4963 | -3475199 | 15613432 | 915531006 | 99008636 | 49902760 | 32653591 | 0.000000 | 0.000000 | 538654541
10-04-2025 1:52:45.000 | 25152857 |  | 25.1529 | -3488304 | 15613854 | 939703430 | 99051987 | 49889862 | 32309634 | 0.000000 | 0.000000 | 533804016
10-04-2025 1:52:40.000 | 26043314 |  | 26.0433 | -3178544 | 15613611 | 970825439 | 99263428 | 49870480 | 31956973 | 0.000000 | 0.000000 | 529054993
10-04-2025 1:52:35.000 | 25861125 |  | 25.8611 | -3237334 | 15612753 | 964491272 | 99225571 | 49881413 | 31597307 | 0.000000 | 0.000000 | 524600220
10-04-2025 1:52:30.000 | 26365629 |  | 26.3656 | -3367011 | 15614004 | 983462402 | 99194420 | 49876335 | 31234155 | 0.000000 | 0.000000 | 520042358
10-04-2025 1:52:25.000 | 25843250 |  | 25.8433 | -3093739 | 15613579 | 963079285 | 99291069 | 49881550 | 30870054 | 0.000000 | 0.000000 | 515565613
10-04-2025 1:52:20.000 | 25232305 |  | 25.2323 | -3364331 | 15614345 | 941910767 | 99122780 | 49904163 | 30513730 | 0.000000 | 0.000000 | 511153839
10-04-2025 1:52:15.000 | 26772455 |  | 26.7725 | -3468973 | 15611577 | 999166382 | 99170975 | 49876137 | 30156511 | 0.000000 | 0.000000 | 506432129
10-04-2025 1:52:10.000 | 27724297 |  | 27.7243 | -3509631 | 15611000 | 10340923 | 99208244 | 49857090 | 29774675 | 0.000000 | 0.000000 | 501529266
10-04-2025 1:52:05.000 | 26631873 |  | 26.6319 | -3674671 | 15607068 | 995126038 | 99061455 | 49898109 | 29391746 | 0.000000 | 0.000000 | 496679993
10-04-2025 1:52:00.000 | 25335658 |  | 25.3357 | -4286397 | 15611399 | 950914734 | 98598839 | 49921497 | 29032739 | 0.000000 | 0.000000 | 491175659
10-04-2025 1:51:55.000 | 25380750 |  | 25.3807 | -4198687 | 15609835 | 952133118 | 98659134 | 49919815 | 28680359 | 0.000000 | 0.000000 | 485297729
10-04-2025 1:51:50.000 | 24626604 |  | 24.6266 | -4190776 | 15612084 | 924549316 | 98582771 | 49933216 | 28332837 | 0.000000 | 0.000000 | 479414917
10-04-2025 1:51:45.000 | 24370363 |  | 24.3704 | -4281009 | 15614326 | 915569214 | 98491913 | 49938824 | 27993308 | 0.000000 | 0.000000 | 473460815
10-04-2025 1:51:40.000 | 24217314 |  | 24.2173 | -4338253 | 15613761 | 910376160 | 98433083 | 49939404 | 27652654 | 0.000000 | 0.000000 | 467624878
10-04-2025 1:51:35.000 | 24225303 |  | 24.2253 | -4169833 | 15612688 | 909666748 | 98550735 | 49945721 | 27315142 | 0.000000 | 0.000000 | 461744354
10-04-2025 1:51:30.000 | 24630385 |  | 24.6304 | -4442500 | 15613648 | 926070679 | 98412033 | 49937229 | 26978291 | 0.000000 | 0.000000 | 455668915
10-04-2025 1:51:25.000 | 25290506 |  | 25.2905 | -4425477 | 15613658 | 949968201 | 98503288 | 49922321 | 26630984 | 0.000000 | 0.000000 | 449469208
10-04-2025 1:51:20.000 | 25144471 |  | 25.1445 | -4294552 | 15614848 | 943780579 | 98572609 | 49930347 | 26280586 | 0.000000 | 0.000000 | 443506256
10-04-2025 1:51:15.000 | 25583697 |  | 25.5837 | -4290944 | 15616399 | 959680115 | 98622467 | 49925350 | 25933003 | 0.000000 | 0.000000 | 437439026
10-04-2025 1:51:10.000 | 27286156 |  | 27.2862 | -4244407 | 15610270 | 10220697 | 98811707 | 49900597 | 25569014 | 0.000000 | 0.000000 | 431414734
10-04-2025 1:51:05.000 | 27197197 |  | 27.1972 | -4183505 | 15610367 | 10183606 | 98837540 | 49910393 | 25188599 | 0.000000 | 0.000000 | 425579651
10-04-2025 1:51:00.000 | 26378914 |  | 26.3789 | -4203764 | 15611328 | 988491821 | 98753891 | 49932018 | 24814597 | 0.000000 | 0.000000 | 419785889
10-04-2025 1:50:55.000 | 25877213 |  | 25.8772 | -4464291 | 15613505 | 971674438 | 98544289 | 49949421 | 24452083 | 0.000000 | 0.000000 | 413838013
10-04-2025 1:50:50.000 | 25542703 |  | 25.5427 | -4482808 | 15611490 | 959699890 | 98494629 | 49939777 | 24092834 | 0.000000 | 0.000000 | 407742157
10-04-2025 1:50:45.000 | 25050801 |  | 25.0508 | -4214091 | 15610363 | 940187561 | 98614410 | 49951767 | 23738709 | 0.000000 | 0.000000 | 401720551
10-04-2025 1:50:40.000 | 24175033 |  | 24.175 | -4467328 | 15612202 | 909813782 | 98335136 | 49977859 | 23398391 | 0.000000 | 0.000000 | 395687164
10-04-2025 1:50:35.000 | 24328898 |  | 24.3289 | -4418895 | 15612836 | 915109924 | 98390221 | 49971981 | 23063564 | 0.000000 | 0.000000 | 389414368
10-04-2025 1:50:30.000 | 24599926 |  | 24.5999 | -4286133 | 15611710 | 924085632 | 98515839 | 49969120 | 22723665 | 0.000000 | 0.000000 | 383389343
10-04-2025 1:50:25.000 | 24147342 |  | 24.1473 | -4296484 | 15612935 | 907635071 | 98453705 | 49965572 | 22384136 | 0.000000 | 0.000000 | 377414093
10-04-2025 1:50:20.000 | 23551895 |  | 23.5519 | -4260352 | 15612294 | 885979675 | 98402992 | 49960243 | 22053535 | 0.000000 | 0.000000 | 371476349
10-04-2025 1:50:15.000 | 23265391 |  | 23.2654 | -4562012 | 15615719 | 877252686 | 98131241 | 49956318 | 21728835 | 0.000000 | 0.000000 | 365327240
10-04-2025 1:50:10.000 | 23765834 |  | 23.7658 | -4374575 | 15613301 | 894290833 | 98347778 | 49955521 | 21402559 | 0.000000 | 0.000000 | 359052063
10-04-2025 1:50:05.000 | 24863086 |  | 24.8631 | -4323169 | 15613503 | 933847900 | 98521744 | 49933933 | 21068140 | 0.000000 | 0.000000 | 352918884
10-04-2025 1:50:00.000 | 24996598 |  | 24.9966 | -4335860 | 15613589 | 938793152 | 98528732 | 49919456 | 20721594 | 0.000000 | 0.000000 | 346983002
10-04-2025 1:49:55.000 | 25180611 |  | 25.1806 | -4298113 | 15612759 | 945311646 | 98574303 | 49924149 | 20372784 | 0.000000 | 0.000000 | 340968353
10-04-2025 1:49:50.000 | 25187773 |  | 25.1878 | -4281920 | 15614371 | 945397461 | 98585587 | 49924889 | 20023906 | 0.000000 | 0.000000 | 334931732
10-04-2025 1:49:45.000 | 25316676 |  | 25.3167 | -4483088 | 15614699 | 951296692 | 98468063 | 49923904 | 19674047 | 0.000000 | 0.000000 | 328869385
10-04-2025 1:49:40.000 | 26575260 |  | 26.5753 | -4424143 | 15613967 | 996770813 | 98642441 | 49918552 | 19315916 | 0.000000 | 0.000000 | 322546356
10-04-2025 1:49:35.000 | 27525283 |  | 27.5253 | -4229719 | 15611021 | 10304877 | 98839836 | 49899975 | 18941149 | 0.000000 | 0.000000 | 316564270
10-04-2025 1:49:30.000 | 27202709 |  | 27.2027 | -4295117 | 15607975 | 10193331 | 98776321 | 49917900 | 18557526 | 0.000000 | 0.000000 | 310764252
10-04-2025 1:49:25.000 | 25595707 |  | 25.5957 | -4433055 | 15609400 | 961406250 | 98533089 | 49953339 | 18185670 | 0.000000 | 0.000000 | 304685455
10-04-2025 1:49:20.000 | 24062443 |  | 24.0624 | -4603311 | 15612775 | 906620605 | 98218826 | 49976681 | 17838558 | 0.000000 | 0.000000 | 298337585
10-04-2025 1:49:15.000 | 22895971 |  | 22.896 | -4337837 | 15614619 | 862336487 | 98252190 | 49983147 | 17510961 | 0.000000 | 0.000000 | 292105682
10-04-2025 1:49:10.000 | 22585641 |  | 22.5856 | -4339564 | 15613362 | 851158630 | 98203728 | 49977467 | 17192958 | 0.000000 | 0.000000 | 286179535
10-04-2025 1:49:05.000 | 23639857 |  | 23.6399 | -4223640 | 15613676 | 888638367 | 98441147 | 49958389 | 16872623 | 0.000000 | 0.000000 | 280177429
10-04-2025 1:49:00.000 | 24028125 |  | 24.0281 | -4173117 | 15613915 | 902453674 | 98525108 | 49956070 | 16542670 | 0.000000 | 0.000000 | 274295776
10-04-2025 1:48:55.000 | 24403945 |  | 24.4039 | -4339807 | 15614416 | 917138245 | 98455330 | 49947350 | 16206666 | 0.000000 | 0.000000 | 268363556
10-04-2025 1:48:50.000 | 24828865 |  | 24.8289 | -4458701 | 15613225 | 933454102 | 98425575 | 49932831 | 15864586 | 0.000000 | 0.000000 | 262339996
10-04-2025 1:48:45.000 | 24884975 |  | 24.885 | -4417995 | 15613643 | 935198303 | 98460342 | 49936195 | 15519227 | 0.000000 | 0.000000 | 256179993
10-04-2025 1:48:40.000 | 24444066 |  | 24.4441 | -4080233 | 15612235 | 917146057 | 98635315 | 49938946 | 15174248 | 0.000000 | 0.000000 | 250193314
10-04-2025 1:48:35.000 | 23945420 |  | 23.9454 | -4115211 | 15613998 | 899120667 | 98555168 | 49955639 | 14840880 | 0.000000 | 0.000000 | 244561295
10-04-2025 1:48:30.000 | 24573617 |  | 24.5736 | -4130166 | 15612700 | 922081177 | 98616806 | 49943932 | 14508619 | 0.000000 | 0.000000 | 238640121
10-04-2025 1:48:25.000 | 24848447 |  | 24.8484 | -4206728 | 15611521 | 932697693 | 98597038 | 49932087 | 14165345 | 0.000000 | 0.000000 | 232753601
10-04-2025 1:48:20.000 | 23749137 |  | 23.7491 | -4138732 | 15611184 | 892267151 | 98515251 | 49941269 | 13824495 | 0.000000 | 0.000000 | 227030212
10-04-2025 1:48:15.000 | 23562949 |  | 23.5629 | -4071430 | 15613424 | 884858276 | 98539810 | 49943542 | 13497870 | 0.000000 | 0.000000 | 221268280
10-04-2025 1:48:10.000 | 24213145 |  | 24.2131 | -4175791 | 15614528 | 909171692 | 98545258 | 49934368 | 13166382 | 0.000000 | 0.000000 | 215542435
10-04-2025 1:48:05.000 | 25130215 |  | 25.1302 | -4096633 | 15614303 | 942162109 | 98697197 | 49913963 | 12822914 | 0.000000 | 0.000000 | 209878815
10-04-2025 1:48:00.000 | 26178258 |  | 26.1783 | -4172218 | 15612489 | 980862061 | 98753639 | 49902954 | 12468971 | 0.000000 | 0.000000 | 204116455
10-04-2025 1:47:55.000 | 26685668 |  | 26.6857 | -4221231 | 15610600 | 999787659 | 98771896 | 49901737 | 12099519 | 0.000000 | 0.000000 | 198315704
10-04-2025 1:47:50.000 | 26497494 |  | 26.4975 | -4119876 | 15610187 | 992434692 | 98812752 | 49911053 | 11728350 | 0.000000 | 0.000000 | 192494446
10-04-2025 1:47:45.000 | 25453191 |  | 25.4532 | -4132359 | 15611780 | 954267151 | 98707596 | 49940277 | 11364661 | 0.000000 | 0.000000 | 186837784
10-04-2025 1:47:40.000 | 24945809 |  | 24.9458 | -4389999 | 15613856 | 937256531 | 98486588 | 49948330 | 11016152 | 0.000000 | 0.000000 | 180932236
10-04-2025 1:47:35.000 | 25088805 |  | 25.0888 | -4202930 | 15611297 | 941519348 | 98625679 | 49943623 | 10669896 | 0.000000 | 0.000000 | 174981262
10-04-2025 1:47:30.000 | 24823045 |  | 24.823 | -4183406 | 15612547 | 931545166 | 98609451 | 49947590 | 10324032 | 0.000000 | 0.000000 | 169148346
10-04-2025 1:47:25.000 | 24788021 |  | 24.788 | -4239227 | 15613517 | 930516052 | 98568939 | 49957886 | 997993774 | 0.000000 | 0.000000 | 163255920
10-04-2025 1:47:20.000 | 24701443 |  | 24.7014 | -4195668 | 15612520 | 927164612 | 98587944 | 49948574 | 963659668 | 0.000000 | 0.000000 | 157388809
10-04-2025 1:47:15.000 | 24071193 |  | 24.0712 | -4053300 | 15612004 | 903402649 | 98611725 | 49954388 | 929572083 | 0.000000 | 0.000000 | 151624908
10-04-2025 1:47:10.000 | 23346945 |  | 23.3469 | -4025080 | 15612282 | 876784180 | 98546196 | 49957172 | 896572571 | 0.000000 | 0.000000 | 145941193
10-04-2025 1:47:05.000 | 23394301 |  | 23.3943 | -4249219 | 15616301 | 879770813 | 98390167 | 49952805 | 864259888 | 0.000000 | 0.000000 | 140180939
10-04-2025 1:47:00.000 | 24033018 |  | 24.033 | -4138074 | 15614075 | 902382202 | 98549820 | 49935963 | 831305420 | 0.000000 | 0.000000 | 134279297
10-04-2025 1:46:55.000 | 24400377 |  | 24.4004 | -4079814 | 15612244 | 915541626 | 98630806 | 49927273 | 797863647 | 0.000000 | 0.000000 | 128571609
10-04-2025 1:46:50.000 | 24827346 |  | 24.8273 | -4166503 | 15613849 | 931522034 | 98620903 | 49923870 | 763720154 | 0.000000 | 0.000000 | 122886856
10-04-2025 1:46:45.000 | 25080461 |  | 25.0805 | -4144252 | 15614611 | 940530151 | 98662148 | 49920475 | 729198486 | 0.000000 | 0.000000 | 117126572
10-04-2025 1:46:40.000 | 25408420 |  | 25.4084 | -4152675 | 15614742 | 952584229 | 98690590 | 49905643 | 694129333 | 0.000000 | 0.000000 | 111314896
10-04-2025 1:46:35.000 | 25635373 |  | 25.6354 | -4021643 | 15612040 | 960213257 | 98791710 | 49909878 | 658699829 | 0.000000 | 0.000000 | 105553596
10-04-2025 1:46:30.000 | 26344539 |  | 26.3445 | -4132543 | 15612463 | 986752686 | 98791916 | 49912594 | 622794678 | 0.000000 | 0.000000 | 99856964
10-04-2025 1:46:25.000 | 26208553 |  | 26.2086 | -4238756 | 15611378 | 982514954 | 98717255 | 49920822 | 586137695 | 0.000000 | 0.000000 | 94184113
10-04-2025 1:46:20.000 | 25437000 |  | 25.437 | -4056309 | 15611455 | 953380737 | 98752296 | 49933689 | 550064270 | 0.000000 | 0.000000 | 88433868
10-04-2025 1:46:15.000 | 25292441 |  | 25.2924 | -4126109 | 15611486 | 948361328 | 98695313 | 49937153 | 515015320 | 0.000000 | 0.000000 | 82705055
10-04-2025 1:46:10.000 | 24820205 |  | 24.8202 | -4054698 | 15611672 | 930762146 | 98691757 | 49945530 | 480094269 | 0.000000 | 0.000000 | 76964897
10-04-2025 1:46:05.000 | 23551918 |  | 23.5519 | -4000171 | 15614178 | 884040649 | 98588112 | 49955055 | 446449677 | 0.000000 | 0.000000 | 71379272
10-04-2025 1:46:00.000 | 23424492 |  | 23.4245 | -4033291 | 15615887 | 879530762 | 98549820 | 49955315 | 414210754 | 0.000000 | 0.000000 | 65830116
10-04-2025 1:45:55.000 | 24855033 |  | 24.855 | -4096564 | 15613742 | 932191345 | 98668808 | 49927315 | 380782440 | 0.000000 | 0.000000 | 60259892
10-04-2025 1:45:50.000 | 24856109 |  | 24.8561 | -3710183 | 15613011 | 929983765 | 98904251 | 49913269 | 345914459 | 0.000000 | 0.000000 | 54735046
10-04-2025 1:45:45.000 | 23436957 |  | 23.437 | -3996027 | 15613824 | 879787109 | 98577408 | 49935036 | 312162750 | 0.000000 | 0.000000 | 49416855
10-04-2025 1:45:40.000 | 23845006 |  | 23.845 | -4081372 | 15612523 | 895290527 | 98566589 | 49923737 | 279573456 | 0.000000 | 0.000000 | 43753101
10-04-2025 1:45:35.000 | 23906730 |  | 23.9067 | -4274255 | 15615009 | 898672180 | 98439056 | 49914810 | 246254913 | 0.000000 | 0.000000 | 37923019
10-04-2025 1:45:30.000 | 24184158 |  | 24.1842 | -3854475 | 15613904 | 906181458 | 98753593 | 49919971 | 212831848 | 0.000000 | 0.000000 | 32128326
10-04-2025 1:45:25.000 | 24410719 |  | 24.4107 | -3685965 | 15613126 | 913533875 | 98879112 | 49913017 | 179089981 | 0.000000 | 0.000000 | 26837685
10-04-2025 1:45:20.000 | 24891096 |  | 24.8911 | -3915489 | 15615027 | 932292542 | 98785255 | 49908325 | 145014816 | 0.000000 | 0.000000 | 21530796
10-04-2025 1:45:15.000 | 26129986 |  | 26.13 | -3954963 | 15612702 | 977866699 | 98873863 | 49893559 | 109607742 | 0.000000 | 0.000000 | 16148462
10-04-2025 1:45:10.000 | 26944828 |  | 26.9448 | -3865433 | 15612405 | 10071996 | 98986618 | 49891247 | 72928581 | 0.000000 | 0.000000 | 10707066
10-04-2025 1:45:05.000 | 26193695 |  | 26.1937 | -3795485 | 15612682 | 979404419 | 98966438 | 49908268 | 35852139 | 0.000000 | 0.000000 | 5345848
10-04-2025 1:45:00.000 | 25621852 |  | 25.6219 | -3888283 | 15612290 | 958967285 | 98868011 | 49921314 | 64811699 | 0.000000 | 0.000000 | 894899719
10-04-2025 1:44:55.000 | 25829893 |  | 25.8299 | -4030400 | 15613624 | 967283936 | 98804420 | 49923214 | 64454146 | 0.000000 | 0.000000 | 889408264
10-04-2025 1:44:50.000 | 26112369 |  | 26.1124 | -4125986 | 15611375 | 978265991 | 98774559 | 49915878 | 64094360 | 0.000000 | 0.000000 | 883823242
10-04-2025 1:44:45.000 | 26149434 |  | 26.1494 | -4206526 | 15612174 | 980059753 | 98730705 | 49909584 | 63732515 | 0.000000 | 0.000000 | 878016724
10-04-2025 1:44:40.000 | 25222600 |  | 25.2226 | -3885070 | 15612854 | 944451721 | 98834419 | 49927883 | 63373999 | 0.000000 | 0.000000 | 872457458
10-04-2025 1:44:35.000 | 24785711 |  | 24.7857 | -3906881 | 15614308 | 928415222 | 98780380 | 49943008 | 63028809 | 0.000000 | 0.000000 | 867099487
10-04-2025 1:44:30.000 | 25468389 |  | 25.4684 | -4007545 | 15612091 | 954143372 | 98784515 | 49929695 | 62681816 | 0.000000 | 0.000000 | 861646179
10-04-2025 1:44:25.000 | 25721002 |  | 25.721 | -4037116 | 15613266 | 963357056 | 98790512 | 49916031 | 62325249 | 0.000000 | 0.000000 | 856103455
10-04-2025 1:44:20.000 | 25791717 |  | 25.7917 | -4008025 | 15611661 | 965890747 | 98813988 | 49913589 | 61967256 | 0.000000 | 0.000000 | 850503357
10-04-2025 1:44:15.000 | 24255588 |  | 24.2556 | -3744841 | 15611724 | 908300659 | 98829063 | 49938248 | 61617598 | 0.000000 | 0.000000 | 845162842
10-04-2025 1:44:10.000 | 22665377 |  | 22.6654 | -4016706 | 15616981 | 851667053 | 98465736 | 49963203 | 61291279 | 0.000000 | 0.000000 | 839801086
10-04-2025 1:44:05.000 | 23875705 |  | 23.8757 | -4021883 | 15616324 | 895821960 | 98610710 | 49939598 | 60971567 | 0.000000 | 0.000000 | 834309570
10-04-2025 1:44:00.000 | 25909891 |  | 25.9099 | -3784024 | 15613831 | 968947754 | 98950294 | 49901894 | 60627700 | 0.000000 | 0.000000 | 828850586
10-04-2025 1:43:55.000 | 26602057 |  | 26.6021 | -3939741 | 15612498 | 995098206 | 98921051 | 49899086 | 60263882 | 0.000000 | 0.000000 | 823587891
10-04-2025 1:43:50.000 | 27850086 |  | 27.8501 | -4069462 | 15611860 | 10414199 | 98949242 | 49888680 | 59884146 | 0.000000 | 0.000000 | 818080566
10-04-2025 1:43:45.000 | 27158412 |  | 27.1584 | -3800617 | 15607557 | 10150381 | 99034958 | 49901615 | 59501123 | 0.000000 | 0.000000 | 812599487
10-04-2025 1:43:40.000 | 25178588 |  | 25.1786 | -3773043 | 15610559 | 942312195 | 98895790 | 49946941 | 59133062 | 0.000000 | 0.000000 | 807327332
10-04-2025 1:43:35.000 | 23688406 |  | 23.6884 | -4134323 | 15611747 | 889987244 | 98510910 | 49983597 | 58794219 | 0.000000 | 0.000000 | 801968506
10-04-2025 1:43:30.000 | 23694338 |  | 23.6943 | -4244713 | 15613083 | 890950623 | 98432976 | 49985905 | 58466147 | 0.000000 | 0.000000 | 796130737
10-04-2025 1:43:25.000 | 23948732 |  | 23.9487 | -4321628 | 15613943 | 900524719 | 98410545 | 49979229 | 58136079 | 0.000000 | 0.000000 | 790310425
10-04-2025 1:43:20.000 | 24587479 |  | 24.5875 | -4037544 | 15613102 | 922060913 | 98678398 | 49961861 | 57799902 | 0.000000 | 0.000000 | 784600647
10-04-2025 1:43:15.000 | 24592227 |  | 24.5922 | -4107560 | 15611171 | 922763062 | 98633629 | 49965572 | 57459287 | 0.000000 | 0.000000 | 778978699
10-04-2025 1:43:10.000 | 25025813 |  | 25.0258 | -4179030 | 15614183 | 938794250 | 98634232 | 49960625 | 57116499 | 0.000000 | 0.000000 | 773159790
10-04-2025 1:43:05.000 | 24939693 |  | 24.9397 | -4053709 | 15610729 | 935121765 | 98704643 | 49953617 | 56768896 | 0.000000 | 0.000000 | 767474365
10-04-2025 1:43:00.000 | 24456889 |  | 24.4569 | -4164512 | 15613488 | 918034790 | 98581024 | 49961796 | 56422153 | 0.000000 | 0.000000 | 761791382
10-04-2025 1:42:55.000 | 23385270 |  | 23.3853 | -4046752 | 15614235 | 878211121 | 98535545 | 49965054 | 56088418 | 0.000000 | 0.000000 | 756158569
10-04-2025 1:42:50.000 | 23096088 |  | 23.0961 | -4045632 | 15615094 | 867638123 | 98500282 | 49963543 | 55766938 | 0.000000 | 0.000000 | 750571350
10-04-2025 1:42:45.000 | 24113344 |  | 24.1133 | -3884491 | 15614205 | 903732300 | 98727173 | 49945148 | 55440278 | 0.000000 | 0.000000 | 745005127
10-04-2025 1:42:40.000 | 25039668 |  | 25.0397 | -3785187 | 15614433 | 937068176 | 98876633 | 49932442 | 55097705 | 0.000000 | 0.000000 | 739731262
10-04-2025 1:42:35.000 | 25685668 |  | 25.6857 | -4010637 | 15612410 | 961968994 | 98802818 | 49919430 | 54747388 | 0.000000 | 0.000000 | 734352783
10-04-2025 1:42:30.000 | 26624238 |  | 26.6242 | -3853752 | 15611016 | 995602783 | 98968605 | 49913166 | 54383892 | 0.000000 | 0.000000 | 728755798
10-04-2025 1:42:25.000 | 25466166 |  | 25.4662 | -3860392 | 15610871 | 953203308 | 98870468 | 49927536 | 54020737 | 0.000000 | 0.000000 | 723299927
10-04-2025 1:42:20.000 | 24274338 |  | 24.2743 | -3725031 | 15612118 | 908854858 | 98842964 | 49951866 | 53674180 | 0.000000 | 0.000000 | 718028870
10-04-2025 1:42:15.000 | 24425391 |  | 24.4254 | -3683096 | 15614934 | 913955994 | 98882149 | 49961338 | 53340225 | 0.000000 | 0.000000 | 712770752
10-04-2025 1:42:10.000 | 24947781 |  | 24.9478 | -4030883 | 15614558 | 935040039 | 98719727 | 49954617 | 53002075 | 0.000000 | 0.000000 | 707455872
10-04-2025 1:42:05.000 | 25883299 |  | 25.8833 | -3780023 | 15614836 | 967770752 | 98950363 | 49929798 | 52649189 | 0.000000 | 0.000000 | 702046753
10-04-2025 1:42:00.000 | 26211547 |  | 26.2115 | -3749211 | 15612444 | 979796936 | 98992462 | 49923771 | 52287407 | 0.000000 | 0.000000 | 696909729
10-04-2025 1:41:55.000 | 26209455 |  | 26.2095 | -3797936 | 15612265 | 979989624 | 98966347 | 49917992 | 51920576 | 0.000000 | 0.000000 | 691676147
10-04-2025 1:41:50.000 | 25551998 |  | 25.552 | -3826841 | 15609522 | 956336121 | 98897018 | 49923016 | 51558623 | 0.000000 | 0.000000 | 686418030
10-04-2025 1:41:45.000 | 24668424 |  | 24.6684 | -3671510 | 15611568 | 922993591 | 98910484 | 49943020 | 51208716 | 0.000000 | 0.000000 | 681156677
10-04-2025 1:41:40.000 | 23278449 |  | 23.2784 | -3689538 | 15612338 | 872269714 | 98767136 | 49966774 | 50877124 | 0.000000 | 0.000000 | 676023499
10-04-2025 1:41:35.000 | 23337893 |  | 23.3379 | -3837365 | 15615360 | 875263916 | 98675003 | 49955769 | 50555977 | 0.000000 | 0.000000 | 670715637
10-04-2025 1:41:30.000 | 24499324 |  | 24.4993 | -3860606 | 15615333 | 917651550 | 98781082 | 49920998 | 50226343 | 0.000000 | 0.000000 | 665263123
10-04-2025 1:41:25.000 | 25260031 |  | 25.26 | -3507551 | 15613860 | 943641357 | 99049644 | 49915878 | 49881709 | 0.000000 | 0.000000 | 660190308
10-04-2025 1:41:20.000 | 25474963 |  | 25.475 | -3514212 | 15613694 | 951515991 | 99061890 | 49909523 | 49531440 | 0.000000 | 0.000000 | 655237976
10-04-2025 1:41:15.000 | 26209813 |  | 26.2098 | -3472766 | 15610015 | 978470581 | 99133598 | 49892845 | 49175293 | 0.000000 | 0.000000 | 650325439
10-04-2025 1:41:10.000 | 25846711 |  | 25.8467 | -3533127 | 15612129 | 965363403 | 99078613 | 49895309 | 48812065 | 0.000000 | 0.000000 | 645437927
10-04-2025 1:41:05.000 | 25502836 |  | 25.5028 | -3721876 | 15613439 | 953635986 | 98951797 | 49901688 | 48455405 | 0.000000 | 0.000000 | 640436218
10-04-2025 1:41:00.000 | 25066551 |  | 25.0666 | -3799528 | 15613295 | 938195374 | 98870636 | 49908295 | 48101069 | 0.000000 | 0.000000 | 635211182
10-04-2025 1:40:55.000 | 25696291 |  | 25.6963 | -3773881 | 15613749 | 960973877 | 98938675 | 49911919 | 47752417 | 0.000000 | 0.000000 | 630048279
10-04-2025 1:40:50.000 | 26465889 |  | 26.4659 | -3515384 | 15612587 | 987886414 | 99129356 | 49906475 | 47390044 | 0.000000 | 0.000000 | 624879333
10-04-2025 1:40:45.000 | 27021131 |  | 27.0211 | -3760673 | 15612126 | 10097214 | 99045357 | 49910240 | 47021812 | 0.000000 | 0.000000 | 619864563
10-04-2025 1:40:40.000 | 26896738 |  | 26.8967 | -3798461 | 15609518 | 10053535 | 99017464 | 49919781 | 46644023 | 0.000000 | 0.000000 | 614740540
10-04-2025 1:40:35.000 | 25322184 |  | 25.3222 | -3940301 | 15612623 | 948354309 | 98810883 | 49945187 | 46281196 | 0.000000 | 0.000000 | 609328552
10-04-2025 1:40:30.000 | 24548762 |  | 24.5488 | -4103420 | 15613784 | 920990051 | 98631592 | 49967155 | 45934897 | 0.000000 | 0.000000 | 603861938
10-04-2025 1:40:25.000 | 24791695 |  | 24.7917 | -4148265 | 15614540 | 930048157 | 98628845 | 49967190 | 45592939 | 0.000000 | 0.000000 | 598162170
10-04-2025 1:40:20.000 | 25260783 |  | 25.2608 | -4033412 | 15611974 | 946701538 | 98749130 | 49964600 | 45246514 | 0.000000 | 0.000000 | 592548218
10-04-2025 1:40:15.000 | 26157920 |  | 26.1579 | -3971722 | 15613741 | 978938965 | 98866844 | 49941231 | 44891924 | 0.000000 | 0.000000 | 586829651
10-04-2025 1:40:10.000 | 25944766 |  | 25.9448 | -4001209 | 15612660 | 971367676 | 98831604 | 49938095 | 44528896 | 0.000000 | 0.000000 | 581338745
10-04-2025 1:40:05.000 | 25552918 |  | 25.5529 | -3780219 | 15611611 | 955925720 | 98923370 | 49947578 | 44169688 | 0.000000 | 0.000000 | 575977295
10-04-2025 1:40:00.000 | 25050262 |  | 25.0503 | -3621473 | 15611295 | 936704163 | 98971100 | 49961037 | 43819224 | 0.000000 | 0.000000 | 570822571
10-04-2025 1:39:55.000 | 24794998 |  | 24.795 | -3824677 | 15612823 | 928371216 | 98831131 | 49958878 | 43472773 | 0.000000 | 0.000000 | 565689453
10-04-2025 1:39:50.000 | 24028066 |  | 24.0281 | -3646911 | 15613618 | 899416626 | 98867714 | 49971447 | 43132017 | 0.000000 | 0.000000 | 560469971
10-04-2025 1:39:45.000 | 23443586 |  | 23.4436 | -3695853 | 15615068 | 878164185 | 98780037 | 49991390 | 42802485 | 0.000000 | 0.000000 | 555399902
10-04-2025 1:39:40.000 | 24858023 |  | 24.858 | -3809817 | 15612993 | 930625244 | 98845818 | 49964634 | 42470059 | 0.000000 | 0.000000 | 550127136
10-04-2025 1:39:35.000 | 25874543 |  | 25.8745 | -3687238 | 15612180 | 967161316 | 98999832 | 49940025 | 42117900 | 0.000000 | 0.000000 | 544869019
10-04-2025 1:39:30.000 | 25150994 |  | 25.151 | -3547159 | 15610177 | 940129333 | 99020058 | 49955666 | 41761787 | 0.000000 | 0.000000 | 539862061
10-04-2025 1:39:25.000 | 24168893 |  | 24.1689 | -3737991 | 15612531 | 905043762 | 98825035 | 49972034 | 41419897 | 0.000000 | 0.000000 | 534709961
10-04-2025 1:39:20.000 | 24226326 |  | 24.2263 | -3815982 | 15611791 | 907759094 | 98782089 | 49973633 | 41084282 | 0.000000 | 0.000000 | 529415955
10-04-2025 1:39:15.000 | 24425535 |  | 24.4255 | -3748794 | 15612246 | 914491882 | 98842628 | 49961933 | 40745540 | 0.000000 | 0.000000 | 524222107
10-04-2025 1:39:10.000 | 24066201 |  | 24.0662 | -3601798 | 15611754 | 900577698 | 98898529 | 49968525 | 40406528 | 0.000000 | 0.000000 | 519173584
10-04-2025 1:39:05.000 | 23039383 |  | 23.0394 | -3598230 | 15613144 | 862985779 | 98802299 | 49981991 | 40080410 | 0.000000 | 0.000000 | 514208801
10-04-2025 1:39:00.000 | 23186324 |  | 23.1863 | -3643575 | 15618210 | 868332642 | 98787704 | 49966103 | 39761611 | 0.000000 | 0.000000 | 509003265
10-04-2025 1:38:55.000 | 24076314 |  | 24.0763 | -3404456 | 15615249 | 899713867 | 99015007 | 49947926 | 39432664 | 0.000000 | 0.000000 | 504172546
10-04-2025 1:38:50.000 | 24954787 |  | 24.9548 | -3489083 | 15613068 | 932422913 | 99036674 | 49933174 | 39092686 | 0.000000 | 0.000000 | 499532959
10-04-2025 1:38:45.000 | 25835990 |  | 25.836 | -3525108 | 15611114 | 965000732 | 99081978 | 49915932 | 38741785 | 0.000000 | 0.000000 | 494765808
10-04-2025 1:38:40.000 | 25162350 |  | 25.1623 | -3431806 | 15612191 | 939800171 | 99082710 | 49917999 | 38385776 | 0.000000 | 0.000000 | 489902802
10-04-2025 1:38:35.000 | 24073396 |  | 24.0734 | -3716203 | 15612793 | 901421265 | 98829384 | 49941906 | 38041270 | 0.000000 | 0.000000 | 485121674
10-04-2025 1:38:30.000 | 23878734 |  | 23.8787 | -3548652 | 15612187 | 893435181 | 98913696 | 49952835 | 37708591 | 0.000000 | 0.000000 | 480042114
10-04-2025 1:38:25.000 | 24101689 |  | 24.1017 | -3626246 | 15614671 | 901950806 | 98887009 | 49944935 | 37375798 | 0.000000 | 0.000000 | 475053558
10-04-2025 1:38:20.000 | 24177369 |  | 24.1774 | -3543139 | 15614977 | 904252747 | 98943184 | 49945122 | 37040193 | 0.000000 | 0.000000 | 470088348
10-04-2025 1:38:15.000 | 25044621 |  | 25.0446 | -3622788 | 15616830 | 936154785 | 98969910 | 49935783 | 36699973 | 0.000000 | 0.000000 | 465110596
10-04-2025 1:38:10.000 | 26585301 |  | 26.5853 | -3468569 | 15614081 | 991965759 | 99159599 | 49918419 | 36340352 | 0.000000 | 0.000000 | 460157898
10-04-2025 1:38:05.000 | 27029887 |  | 27.0299 | -3332850 | 15613424 | 10076555 | 99248383 | 49920052 | 35968389 | 0.000000 | 0.000000 | 455363434
10-04-2025 1:38:00.000 | 27565814 |  | 27.5658 | -3495293 | 15608841 | 10284075 | 99205681 | 49925243 | 35589060 | 0.000000 | 0.000000 | 450658783
10-04-2025 1:37:55.000 | 26402010 |  | 26.402 | -3662700 | 15609494 | 986508484 | 99051399 | 49946957 | 35210935 | 0.000000 | 0.000000 | 445868683
10-04-2025 1:37:50.000 | 24480799 |  | 24.4808 | -3734742 | 15612209 | 916442200 | 98856232 | 49976006 | 34854607 | 0.000000 | 0.000000 | 440732819
10-04-2025 1:37:45.000 | 23535219 |  | 23.5352 | -3832022 | 15614388 | 882439331 | 98700256 | 49993324 | 34522231 | 0.000000 | 0.000000 | 435572357
10-04-2025 1:37:40.000 | 24326336 |  | 24.3263 | -3731891 | 15613810 | 910725525 | 98843651 | 49974289 | 34192368 | 0.000000 | 0.000000 | 430316925
10-04-2025 1:37:35.000 | 24591939 |  | 24.5919 | -3602538 | 15613740 | 919945190 | 98943962 | 49974384 | 33851956 | 0.000000 | 0.000000 | 425230896
10-04-2025 1:37:30.000 | 25373680 |  | 25.3737 | -3670886 | 15615034 | 948554321 | 98969635 | 49959419 | 33506594 | 0.000000 | 0.000000 | 420189575
10-04-2025 1:37:25.000 | 25782420 |  | 25.7824 | -3595501 | 15613908 | 963209045 | 99041565 | 49948093 | 33148215 | 0.000000 | 0.000000 | 415212799
10-04-2025 1:37:20.000 | 25300010 |  | 25.3 | -3394798 | 15612165 | 944613708 | 99111740 | 49956333 | 32793354 | 0.000000 | 0.000000 | 410401794
10-04-2025 1:37:15.000 | 25208273 |  | 25.2083 | -3632446 | 15612842 | 942476257 | 98977692 | 49959957 | 32442742 | 0.000000 | 0.000000 | 405521240
10-04-2025 1:37:10.000 | 25765088 |  | 25.7651 | -3567184 | 15611021 | 962661255 | 99055138 | 49951298 | 32088403 | 0.000000 | 0.000000 | 400598297
10-04-2025 1:37:05.000 | 26022633 |  | 26.0226 | -3761115 | 15609563 | 973114868 | 98971603 | 49946339 | 31728318 | 0.000000 | 0.000000 | 395611115
10-04-2025 1:37:00.000 | 25144967 |  | 25.145 | -3799712 | 15611734 | 941131287 | 98877441 | 49952904 | 31372178 | 0.000000 | 0.000000 | 390351776
10-04-2025 1:36:55.000 | 23689932 |  | 23.6899 | -3560472 | 15613445 | 886661377 | 98889359 | 49970871 | 31029812 | 0.000000 | 0.000000 | 385223755
10-04-2025 1:36:50.000 | 22562277 |  | 22.5623 | -3602617 | 15615575 | 845484314 | 98749077 | 49982391 | 30708201 | 0.000000 | 0.000000 | 380240753
10-04-2025 1:36:45.000 | 23084082 |  | 23.0841 | -3699633 | 15615938 | 865051575 | 98739937 | 49971825 | 30391077 | 0.000000 | 0.000000 | 375158234
10-04-2025 1:36:40.000 | 25013277 |  | 25.0133 | -3735754 | 15615392 | 935748413 | 98903030 | 49941307 | 30058306 | 0.000000 | 0.000000 | 369989746
10-04-2025 1:36:35.000 | 27103439 |  | 27.1034 | -3637627 | 15612705 | 10118262 | 99111336 | 49902569 | 29697764 | 0.000000 | 0.000000 | 364804932
10-04-2025 1:36:30.000 | 27701363 |  | 27.7014 | -3821098 | 15609995 | 10350002 | 99062004 | 49898445 | 29314207 | 0.000000 | 0.000000 | 359738983
10-04-2025 1:36:25.000 | 26034611 |  | 26.0346 | -3365847 | 15611151 | 971477966 | 99174622 | 49936111 | 28934263 | 0.000000 | 0.000000 | 354734314
10-04-2025 1:36:20.000 | 24147572 |  | 24.1476 | -3371334 | 15613055 | 902272278 | 99039421 | 49974163 | 28584250 | 0.000000 | 0.000000 | 349998596
10-04-2025 1:36:15.000 | 23746840 |  | 23.7468 | -3637422 | 15614224 | 888954773 | 98847122 | 49982922 | 28252546 | 0.000000 | 0.000000 | 345268219
10-04-2025 1:36:10.000 | 24452781 |  | 24.4528 | -3520602 | 15612224 | 914250000 | 98979393 | 49975372 | 27917732 | 0.000000 | 0.000000 | 340278961
10-04-2025 1:36:05.000 | 24963656 |  | 24.9637 | -3787959 | 15613469 | 934289917 | 98868271 | 49967461 | 27575845 | 0.000000 | 0.000000 | 335160950
10-04-2025 1:36:00.000 | 25687002 |  | 25.687 | -3683074 | 15611623 | 960353394 | 98987648 | 49956238 | 27225916 | 0.000000 | 0.000000 | 329988159
10-04-2025 1:35:55.000 | 25416482 |  | 25.4165 | -3732479 | 15612378 | 950606812 | 98938850 | 49954975 | 26870857 | 0.000000 | 0.000000 | 324861481
10-04-2025 1:35:50.000 | 25478922 |  | 25.4789 | -3724081 | 15611857 | 952918091 | 98948631 | 49952396 | 26517529 | 0.000000 | 0.000000 | 319669220
10-04-2025 1:35:45.000 | 25748096 |  | 25.7481 | -3790716 | 15611899 | 963073608 | 98933571 | 49951359 | 26163035 | 0.000000 | 0.000000 | 314407043
10-04-2025 1:35:40.000 | 25470074 |  | 25.4701 | -3726305 | 15612905 | 952519287 | 98946678 | 49952091 | 25807493 | 0.000000 | 0.000000 | 309180054
10-04-2025 1:35:35.000 | 24956824 |  | 24.9568 | -3498054 | 15611991 | 932629822 | 99031937 | 49962120 | 25454480 | 0.000000 | 0.000000 | 304141510
10-04-2025 1:35:30.000 | 24942934 |  | 24.9429 | -3692934 | 15614591 | 932964844 | 98921677 | 49965569 | 25108564 | 0.000000 | 0.000000 | 299122986
10-04-2025 1:35:25.000 | 25741393 |  | 25.7414 | -3890295 | 15614063 | 963249573 | 98877182 | 49948528 | 24758118 | 0.000000 | 0.000000 | 293906860
10-04-2025 1:35:20.000 | 25817016 |  | 25.817 | -3717598 | 15610287 | 965424316 | 98979080 | 49943752 | 24396978 | 0.000000 | 0.000000 | 288723236
10-04-2025 1:35:15.000 | 24980404 |  | 24.9804 | -3728335 | 15610825 | 934730591 | 98904488 | 49963902 | 24041636 | 0.000000 | 0.000000 | 283583344
10-04-2025 1:35:10.000 | 24405367 |  | 24.4054 | -3882225 | 15613668 | 914438477 | 98758308 | 49973423 | 23698032 | 0.000000 | 0.000000 | 278356812
10-04-2025 1:35:05.000 | 24281002 |  | 24.281 | -3687207 | 15612197 | 908857056 | 98866562 | 49964027 | 23357717 | 0.000000 | 0.000000 | 273076538
10-04-2025 1:35:00.000 | 23238816 |  | 23.2388 | -3626529 | 15611335 | 870604797 | 98804146 | 49960392 | 23024875 | 0.000000 | 0.000000 | 267990479
10-04-2025 1:34:55.000 | 21781578 |  | 21.7816 | -3523515 | 15612946 | 816692993 | 98716721 | 49978859 | 22709639 | 0.000000 | 0.000000 | 263021820
10-04-2025 1:34:50.000 | 19675949 |  | 19.6759 | -3294935 | 15615032 | 738478455 | 98626678 | 50011654 | 22419387 | 0.000000 | 0.000000 | 258261475
10-04-2025 1:34:45.000 | 19519061 |  | 19.5191 | -3458909 | 15617533 | 733653381 | 98465927 | 50022373 | 22149673 | 0.000000 | 0.000000 | 253600632
10-04-2025 1:34:40.000 | 22333834 |  | 22.3338 | -3659748 | 15618295 | 837360718 | 98683853 | 49952168 | 21866187 | 0.000000 | 0.000000 | 248685425
10-04-2025 1:34:35.000 | 25922977 |  | 25.923 | -2963223 | 15613109 | 965498596 | 99353012 | 49867493 | 21533164 | 0.000000 | 0.000000 | 243797104
10-04-2025 1:34:30.000 | 24431762 |  | 24.4318 | -2683288 | 15611480 | 909633301 | 99402290 | 49901482 | 21183674 | 0.000000 | 0.000000 | 239914795
10-04-2025 1:34:25.000 | 24297992 |  | 24.298 | -2575621 | 15613128 | 904227417 | 99442879 | 49901859 | 20845869 | 0.000000 | 0.000000 | 236244492
10-04-2025 1:34:20.000 | 24592139 |  | 24.5921 | -2473511 | 15614037 | 914645996 | 99497978 | 49896362 | 20506941 | 0.000000 | 0.000000 | 232636612
10-04-2025 1:34:15.000 | 24725832 |  | 24.7258 | -2443510 | 15614128 | 919447632 | 99515236 | 49900623 | 20163317 | 0.000000 | 0.000000 | 229235214
10-04-2025 1:34:10.000 | 25691281 |  | 25.6913 | -2453798 | 15613358 | 954936279 | 99546982 | 49885178 | 19817740 | 0.000000 | 0.000000 | 225801468
10-04-2025 1:34:05.000 | 26230883 |  | 26.2309 | -2315861 | 15609813 | 974570862 | 99612526 | 49861195 | 19455244 | 0.000000 | 0.000000 | 222454788
10-04-2025 1:34:00.000 | 25761363 |  | 25.7614 | -2610004 | 15613957 | 958105347 | 99490685 | 49884731 | 19095378 | 0.000000 | 0.000000 | 219055267
10-04-2025 1:33:55.000 | 26198986 |  | 26.199 | -2756565 | 15613741 | 974704407 | 99451027 | 49874397 | 18739100 | 0.000000 | 0.000000 | 215330078
10-04-2025 1:33:50.000 | 26704670 |  | 26.7047 | -2468125 | 15611832 | 992522339 | 99575615 | 49879921 | 18369235 | 0.000000 | 0.000000 | 211505157
10-04-2025 1:33:45.000 | 27059518 |  | 27.0595 | -2834538 | 15610572 | 10068414 | 99455826 | 49888359 | 17997164 | 0.000000 | 0.000000 | 207850830
10-04-2025 1:33:40.000 | 26417707 |  | 26.4177 | -2797782 | 15611311 | 983079285 | 99443878 | 49905663 | 17621337 | 0.000000 | 0.000000 | 204081146
10-04-2025 1:33:35.000 | 25365234 |  | 25.3652 | -2830672 | 15611665 | 944524841 | 99383064 | 49929482 | 17260157 | 0.000000 | 0.000000 | 200270676
10-04-2025 1:33:30.000 | 24996355 |  | 24.9964 | -3106137 | 15613096 | 932301025 | 99236755 | 49935791 | 16909552 | 0.000000 | 0.000000 | 196252548
10-04-2025 1:33:25.000 | 25015600 |  | 25.0156 | -3118512 | 15615361 | 932698242 | 99231903 | 49935837 | 16562618 | 0.000000 | 0.000000 | 192070221
10-04-2025 1:33:20.000 | 25364080 |  | 25.3641 | -2992174 | 15614611 | 945120361 | 99311348 | 49932846 | 16212512 | 0.000000 | 0.000000 | 187902267
10-04-2025 1:33:15.000 | 26156473 |  | 26.1565 | -3137295 | 15612696 | 974830750 | 99288353 | 49936863 | 15857454 | 0.000000 | 0.000000 | 183862152
10-04-2025 1:33:10.000 | 27067250 |  | 27.0673 | -3063037 | 15611924 | 10079477 | 99365784 | 49921814 | 15488398 | 0.000000 | 0.000000 | 179437637
10-04-2025 1:33:05.000 | 27363533 |  | 27.3635 | -3060817 | 15609636 | 10190488 | 99380203 | 49926479 | 15109854 | 0.000000 | 0.000000 | 175257233
10-04-2025 1:33:00.000 | 25876623 |  | 25.8766 | -3225950 | 15613838 | 964872803 | 99231857 | 49965790 | 14737634 | 0.000000 | 0.000000 | 170993790
10-04-2025 1:32:55.000 | 25384215 |  | 25.3842 | -3113358 | 15614387 | 946250549 | 99256241 | 49974846 | 14382183 | 0.000000 | 0.000000 | 166476913
10-04-2025 1:32:50.000 | 25980836 |  | 25.9808 | -3316603 | 15615250 | 969042297 | 99195023 | 49983875 | 14026410 | 0.000000 | 0.000000 | 162020813
10-04-2025 1:32:45.000 | 27750889 |  | 27.7509 | -3362010 | 15616396 | 10340867 | 99274117 | 49954784 | 13656720 | 0.000000 | 0.000000 | 157315155
10-04-2025 1:32:40.000 | 28957166 |  | 28.9572 | -3213091 | 15612729 | 10780320 | 99390022 | 49947575 | 13260740 | 0.000000 | 0.000000 | 152879547
10-04-2025 1:32:35.000 | 28671270 |  | 28.6713 | -3276651 | 15610695 | 10678499 | 99353294 | 49965466 | 12856509 | 0.000000 | 0.000000 | 148574310
10-04-2025 1:32:30.000 | 28189668 |  | 28.1897 | -3388594 | 15610831 | 10506522 | 99285248 | 49993427 | 12460947 | 0.000000 | 0.000000 | 144009705
10-04-2025 1:32:25.000 | 28065363 |  | 28.0654 | -3576255 | 15612522 | 10467743 | 99197884 | 50006580 | 12070118 | 0.000000 | 0.000000 | 139167633
10-04-2025 1:32:20.000 | 27801523 |  | 27.8015 | -3601585 | 15612717 | 10373549 | 99171303 | 50023479 | 11683628 | 0.000000 | 0.000000 | 134231903
10-04-2025 1:32:15.000 | 27956525 |  | 27.9565 | -3682711 | 15613105 | 10432784 | 99143494 | 50037663 | 11296691 | 0.000000 | 0.000000 | 129227692
10-04-2025 1:32:10.000 | 28902717 |  | 28.9027 | -3462816 | 15614638 | 10769440 | 99289925 | 50023632 | 10903755 | 0.000000 | 0.000000 | 124192825
10-04-2025 1:32:05.000 | 29160299 |  | 29.1603 | -3293779 | 15611859 | 10858191 | 99368111 | 50011112 | 10501112 | 0.000000 | 0.000000 | 119369728
10-04-2025 1:32:00.000 | 28501184 |  | 28.5012 | -3434558 | 15615665 | 10619974 | 99281731 | 50024773 | 10101153 | 0.000000 | 0.000000 | 114656288
10-04-2025 1:31:55.000 | 29031818 |  | 29.0318 | -3286961 | 15614080 | 10808937 | 99365166 | 50027840 | 970230103 | 0.000000 | 0.000000 | 109977867
10-04-2025 1:31:50.000 | 29883188 |  | 29.8832 | -3260182 | 15615199 | 11120856 | 99410149 | 50016289 | 929521484 | 0.000000 | 0.000000 | 105369247
10-04-2025 1:31:45.000 | 30962732 |  | 30.9627 | -3199235 | 15610879 | 11517723 | 99470428 | 50004730 | 887665466 | 0.000000 | 0.000000 | 100827507
10-04-2025 1:31:40.000 | 31902498 |  | 31.9025 | -3321167 | 15611031 | 11867659 | 99462486 | 49990501 | 844131348 | 0.000000 | 0.000000 | 96185402
10-04-2025 1:31:35.000 | 31517018 |  | 31.517 | -3294644 | 15610188 | 11727179 | 99458054 | 50011776 | 799973694 | 0.000000 | 0.000000 | 91530243
10-04-2025 1:31:30.000 | 30989039 |  | 30.989 | -3202864 | 15610643 | 11528145 | 99470131 | 50018970 | 756565063 | 0.000000 | 0.000000 | 86938866
10-04-2025 1:31:25.000 | 29739551 |  | 29.7396 | -3534762 | 15611983 | 11080621 | 99301041 | 50038391 | 714407410 | 0.000000 | 0.000000 | 82295235
10-04-2025 1:31:20.000 | 29377957 |  | 29.378 | -3442982 | 15611784 | 10944196 | 99320251 | 50050167 | 673355103 | 0.000000 | 0.000000 | 77445473
10-04-2025 1:31:15.000 | 29570563 |  | 29.5706 | -3441774 | 15613705 | 11013676 | 99329453 | 50046062 | 632732483 | 0.000000 | 0.000000 | 72572838
10-04-2025 1:31:10.000 | 30162863 |  | 30.1629 | -3390902 | 15613076 | 11229183 | 99374016 | 50044479 | 591268494 | 0.000000 | 0.000000 | 67805588
10-04-2025 1:31:05.000 | 30272898 |  | 30.2729 | -3310553 | 15612906 | 11267153 | 99407364 | 50033955 | 549219238 | 0.000000 | 0.000000 | 63111855
10-04-2025 1:31:00.000 | 30885109 |  | 30.8851 | -3522581 | 15612751 | 11500414 | 99355858 | 50028202 | 506911804 | 0.000000 | 0.000000 | 58422424
10-04-2025 1:30:55.000 | 31064744 |  | 31.0647 | -3512074 | 15610678 | 11566992 | 99366974 | 50026134 | 463537537 | 0.000000 | 0.000000 | 53577728
10-04-2025 1:30:50.000 | 30372262 |  | 30.3723 | -3515667 | 15613196 | 11311935 | 99336723 | 50036453 | 420676666 | 0.000000 | 0.000000 | 48734871
10-04-2025 1:30:45.000 | 29901072 |  | 29.9011 | -3156719 | 15611435 | 11125013 | 99447342 | 50043514 | 378799347 | 0.000000 | 0.000000 | 43947018
10-04-2025 1:30:40.000 | 29353830 |  | 29.3538 | -3505661 | 15613967 | 10936393 | 99294388 | 50064304 | 337568024 | 0.000000 | 0.000000 | 39403221
10-04-2025 1:30:35.000 | 29695734 |  | 29.6957 | -3379194 | 15614645 | 11055950 | 99358765 | 50055332 | 296719543 | 0.000000 | 0.000000 | 34662930
10-04-2025 1:30:30.000 | 30677414 |  | 30.6774 | -3389748 | 15614297 | 11417224 | 99395058 | 50040417 | 254939850 | 0.000000 | 0.000000 | 29952408
10-04-2025 1:30:25.000 | 31306191 |  | 31.3062 | -3595606 | 15611740 | 11660549 | 99346893 | 50031750 | 212192108 | 0.000000 | 0.000000 | 25208416
10-04-2025 1:30:20.000 | 31619027 |  | 31.619 | -3509954 | 15611141 | 11770731 | 99389503 | 50038887 | 168408752 | 0.000000 | 0.000000 | 20250309
10-04-2025 1:30:15.000 | 30397234 |  | 30.3972 | -3559127 | 15611804 | 11323427 | 99321495 | 50057289 | 125079147 | 0.000000 | 0.000000 | 15334485
10-04-2025 1:30:10.000 | 29895396 |  | 29.8954 | -3685120 | 15612143 | 11145027 | 99248810 | 50064262 | 83030579 | 0.000000 | 0.000000 | 10285390
10-04-2025 1:30:05.000 | 30049795 |  | 30.0498 | -3702181 | 15614083 | 11200869 | 99249603 | 50066914 | 41454323 | 0.000000 | 0.000000 | 5086522
10-04-2025 1:30:00.000 | 29438016 |  | 29.438 | -3610752 | 15614823 | 10972671 | 99256157 | 50075233 | 74772134 | 0.000000 | 0.000000 | 852297058
10-04-2025 1:29:55.000 | 29216611 |  | 29.2166 | -3554000 | 15612912 | 10888988 | 99268257 | 50083252 | 74365254 | 0.000000 | 0.000000 | 847337646
10-04-2025 1:29:50.000 | 30092006 |  | 30.092 | -3553582 | 15615409 | 11208010 | 99309937 | 50071182 | 73955928 | 0.000000 | 0.000000 | 842266418
10-04-2025 1:29:45.000 | 30737174 |  | 30.7372 | -3360149 | 15613082 | 11439053 | 99407776 | 50060131 | 73534458 | 0.000000 | 0.000000 | 837450623
10-04-2025 1:29:40.000 | 30839332 |  | 30.8393 | -3319541 | 15613591 | 11474413 | 99425667 | 50065617 | 73107827 | 0.000000 | 0.000000 | 832765320
10-04-2025 1:29:35.000 | 31510598 |  | 31.5106 | -3355963 | 15611853 | 11724296 | 99437637 | 50071423 | 72675869 | 0.000000 | 0.000000 | 828095032
10-04-2025 1:29:30.000 | 31142316 |  | 31.1423 | -3334083 | 15612050 | 11588463 | 99431793 | 50068699 | 72240737 | 0.000000 | 0.000000 | 823398254
10-04-2025 1:29:25.000 | 30227340 |  | 30.2273 | -3086812 | 15609037 | 11244135 | 99482620 | 50081642 | 71813955 | 0.000000 | 0.000000 | 818893555
10-04-2025 1:29:20.000 | 28311445 |  | 28.3114 | -3343388 | 15614021 | 10546354 | 99309914 | 50109821 | 71403286 | 0.000000 | 0.000000 | 814438477
10-04-2025 1:29:15.000 | 28119895 |  | 28.1199 | -3402293 | 15614903 | 10479344 | 99275986 | 50113960 | 71010854 | 0.000000 | 0.000000 | 809885498
10-04-2025 1:29:10.000 | 29573594 |  | 29.5736 | -3119350 | 15613308 | 11002012 | 99448326 | 50080250 | 70610029 | 0.000000 | 0.000000 | 805216125
10-04-2025 1:29:05.000 | 29272000 |  | 29.272 | -3174768 | 15612244 | 10893533 | 99416985 | 50083199 | 70200854 | 0.000000 | 0.000000 | 800879333
10-04-2025 1:29:00.000 | 29299016 |  | 29.299 | -3066623 | 15614227 | 10897998 | 99456703 | 50089581 | 69793247 | 0.000000 | 0.000000 | 796535706
10-04-2025 1:28:55.000 | 30040873 |  | 30.0409 | -3147974 | 15613726 | 11175197 | 99455437 | 50073479 | 69382720 | 0.000000 | 0.000000 | 792173584
10-04-2025 1:28:50.000 | 30029879 |  | 30.0299 | -2822363 | 15611281 | 11160756 | 99561241 | 50068382 | 68964873 | 0.000000 | 0.000000 | 788006409
10-04-2025 1:28:45.000 | 29203523 |  | 29.2035 | -2885736 | 15612589 | 10857313 | 99515327 | 50092258 | 68554258 | 0.000000 | 0.000000 | 784013733
10-04-2025 1:28:40.000 | 29412492 |  | 29.4125 | -2960819 | 15613910 | 10935851 | 99497139 | 50082035 | 68149995 | 0.000000 | 0.000000 | 779870728
10-04-2025 1:28:35.000 | 29360059 |  | 29.3601 | -2864135 | 15614550 | 10913304 | 99527550 | 50084454 | 67740342 | 0.000000 | 0.000000 | 775888550
10-04-2025 1:28:30.000 | 29341393 |  | 29.3414 | -2930133 | 15614619 | 10909407 | 99505066 | 50092503 | 67333340 | 0.000000 | 0.000000 | 771968201
10-04-2025 1:28:25.000 | 31151266 |  | 31.1513 | -3019735 | 15613062 | 11579352 | 99533440 | 50059616 | 66918066 | 0.000000 | 0.000000 | 767729187
10-04-2025 1:28:20.000 | 30689396 |  | 30.6894 | -2835886 | 15609649 | 11404897 | 99575768 | 50055077 | 66486255 | 0.000000 | 0.000000 | 763733704
10-04-2025 1:28:15.000 | 29385887 |  | 29.3859 | -3083041 | 15611024 | 10933488 | 99454140 | 50075905 | 66067124 | 0.000000 | 0.000000 | 759779785
10-04-2025 1:28:10.000 | 28516590 |  | 28.5166 | -3010359 | 15613529 | 10608724 | 99447411 | 50091888 | 65660571 | 0.000000 | 0.000000 | 755627441
10-04-2025 1:28:05.000 | 28354957 |  | 28.355 | -2909591 | 15614142 | 10546433 | 99477646 | 50076431 | 65267109 | 0.000000 | 0.000000 | 751260071
10-04-2025 1:28:00.000 | 28257453 |  | 28.2575 | -2938587 | 15614341 | 10510939 | 99463615 | 50080589 | 64878096 | 0.000000 | 0.000000 | 747183838
10-04-2025 1:27:55.000 | 29305594 |  | 29.3056 | -2966931 | 15615647 | 10896211 | 99491417 | 50052608 | 64481470 | 0.000000 | 0.000000 | 743002014
10-04-2025 1:27:50.000 | 30672633 |  | 30.6726 | -2944375 | 15614931 | 11398595 | 99542419 | 50027020 | 64064614 | 0.000000 | 0.000000 | 738937317
10-04-2025 1:27:45.000 | 30953006 |  | 30.953 | -2767694 | 15613151 | 11497413 | 99602623 | 50012672 | 63634087 | 0.000000 | 0.000000 | 734885681
10-04-2025 1:27:40.000 | 30812682 |  | 30.8127 | -2987771 | 15612838 | 11452866 | 99533173 | 50033989 | 63205059 | 0.000000 | 0.000000 | 730893494
10-04-2025 1:27:35.000 | 31264201 |  | 31.2642 | -3264828 | 15613423 | 11629475 | 99459167 | 50040894 | 62774800 | 0.000000 | 0.000000 | 726729431
10-04-2025 1:27:30.000 | 31722172 |  | 31.7222 | -2985039 | 15610646 | 11789061 | 99560181 | 50038559 | 62333389 | 0.000000 | 0.000000 | 722427246
10-04-2025 1:27:25.000 | 30684760 |  | 30.6848 | -3056281 | 15611903 | 11408728 | 99507629 | 50068336 | 61901001 | 0.000000 | 0.000000 | 718289185
10-04-2025 1:27:20.000 | 30693627 |  | 30.6936 | -3049552 | 15612608 | 11411921 | 99510056 | 50060314 | 61477598 | 0.000000 | 0.000000 | 713921265
10-04-2025 1:27:15.000 | 31047309 |  | 31.0473 | -3178085 | 15613716 | 11545718 | 99480179 | 50055794 | 61050024 | 0.000000 | 0.000000 | 709616028
10-04-2025 1:27:10.000 | 31029168 |  | 31.0292 | -3169398 | 15610748 | 11540704 | 99482391 | 50048077 | 60615835 | 0.000000 | 0.000000 | 705240112
10-04-2025 1:27:05.000 | 30006316 |  | 30.0063 | -3136384 | 15611653 | 11163173 | 99458168 | 50070801 | 60190620 | 0.000000 | 0.000000 | 700861450
10-04-2025 1:27:00.000 | 29782684 |  | 29.7827 | -3367115 | 15613023 | 11089119 | 99366974 | 50074993 | 59776475 | 0.000000 | 0.000000 | 696386963
10-04-2025 1:26:55.000 | 29278418 |  | 29.2784 | -3193323 | 15612488 | 10896582 | 99410469 | 50086819 | 59364487 | 0.000000 | 0.000000 | 691904175
10-04-2025 1:26:50.000 | 29188564 |  | 29.1886 | -3392679 | 15613811 | 10871315 | 99331261 | 50089951 | 58960640 | 0.000000 | 0.000000 | 687348511
10-04-2025 1:26:45.000 | 30336736 |  | 30.3367 | -3306441 | 15613241 | 11289467 | 99411285 | 50072063 | 58547422 | 0.000000 | 0.000000 | 682748047
10-04-2025 1:26:40.000 | 30621986 |  | 30.622 | -3307244 | 15613581 | 11394414 | 99421829 | 50058929 | 58123330 | 0.000000 | 0.000000 | 678279663
10-04-2025 1:26:35.000 | 30290813 |  | 30.2908 | -3012492 | 15610159 | 11264014 | 99509102 | 50064098 | 57699531 | 0.000000 | 0.000000 | 673955811
10-04-2025 1:26:30.000 | 29712998 |  | 29.713 | -3172728 | 15611077 | 11056381 | 99434738 | 50078217 | 57283179 | 0.000000 | 0.000000 | 669694946
10-04-2025 1:26:25.000 | 28962598 |  | 28.9626 | -3222619 | 15615013 | 10780095 | 99386658 | 50074959 | 56876636 | 0.000000 | 0.000000 | 665198120
10-04-2025 1:26:20.000 | 28598832 |  | 28.5988 | -2981500 | 15610782 | 10641104 | 99460960 | 50074196 | 56478442 | 0.000000 | 0.000000 | 660832825
10-04-2025 1:26:15.000 | 28823029 |  | 28.823 | -3090350 | 15615268 | 10723374 | 99430122 | 50066010 | 56081294 | 0.000000 | 0.000000 | 656527405
10-04-2025 1:26:10.000 | 28938076 |  | 28.9381 | -2901742 | 15613249 | 10760157 | 99501015 | 50059357 | 55678979 | 0.000000 | 0.000000 | 652314575
10-04-2025 1:26:05.000 | 29482090 |  | 29.4821 | -2934943 | 15615729 | 10959574 | 99508141 | 50055500 | 55274111 | 0.000000 | 0.000000 | 648336792
10-04-2025 1:26:00.000 | 30361898 |  | 30.3619 | -2741569 | 15613578 | 11279327 | 99594803 | 50038792 | 54857983 | 0.000000 | 0.000000 | 644356934
10-04-2025 1:25:55.000 | 30323539 |  | 30.3235 | -2892027 | 15613483 | 11269271 | 99548286 | 50044621 | 54436792 | 0.000000 | 0.000000 | 640562866
10-04-2025 1:25:50.000 | 31639004 |  | 31.639 | -2896044 | 15612187 | 11754371 | 99583687 | 50024212 | 54009409 | 0.000000 | 0.000000 | 636481140
10-04-2025 1:25:45.000 | 31629389 |  | 31.6294 | -2881476 | 15610807 | 11751414 | 99587593 | 50025204 | 53567871 | 0.000000 | 0.000000 | 632529114
10-04-2025 1:25:40.000 | 30507537 |  | 30.5075 | -3003917 | 15612497 | 11341456 | 99518730 | 50047165 | 53137334 | 0.000000 | 0.000000 | 628502930
10-04-2025 1:25:35.000 | 30466232 |  | 30.4662 | -3145866 | 15612642 | 11330916 | 99471123 | 50056778 | 52713359 | 0.000000 | 0.000000 | 624301819
10-04-2025 1:25:30.000 | 30323867 |  | 30.3239 | -2957332 | 15612020 | 11272777 | 99527809 | 50052055 | 52290244 | 0.000000 | 0.000000 | 620122131
10-04-2025 1:25:25.000 | 29766014 |  | 29.766 | -3057773 | 15613309 | 11070178 | 99476501 | 50061840 | 51870952 | 0.000000 | 0.000000 | 616113464
10-04-2025 1:25:20.000 | 29666752 |  | 29.6668 | -2914703 | 15610580 | 11030974 | 99520828 | 50066326 | 51457866 | 0.000000 | 0.000000 | 612032776
10-04-2025 1:25:15.000 | 28968377 |  | 28.9684 | -3045124 | 15613544 | 10778213 | 99452042 | 50077614 | 51049248 | 0.000000 | 0.000000 | 607904602
10-04-2025 1:25:10.000 | 28689408 |  | 28.6894 | -3086536 | 15614077 | 10676292 | 99426254 | 50082096 | 50647339 | 0.000000 | 0.000000 | 603737183
10-04-2025 1:25:05.000 | 29324236 |  | 29.3242 | -3100633 | 15614744 | 10909005 | 99445641 | 50080631 | 50243867 | 0.000000 | 0.000000 | 599578247
10-04-2025 1:25:00.000 | 30274863 |  | 30.2749 | -2940219 | 15613250 | 11253293 | 99531723 | 50063511 | 49832217 | 0.000000 | 0.000000 | 595336670
10-04-2025 1:24:55.000 | 30900004 |  | 30.9 | -2987194 | 15614024 | 11483718 | 99535965 | 50042545 | 49408027 | 0.000000 | 0.000000 | 591137390
10-04-2025 1:24:50.000 | 31317770 |  | 31.3178 | -2929754 | 15611814 | 11637734 | 99565277 | 50039341 | 48976655 | 0.000000 | 0.000000 | 587055664
10-04-2025 1:24:45.000 | 30970902 |  | 30.9709 | -3013774 | 15610872 | 11513466 | 99529877 | 50046234 | 48543804 | 0.000000 | 0.000000 | 582916931
10-04-2025 1:24:40.000 | 30322234 |  | 30.3222 | -2958376 | 15610929 | 11273213 | 99527428 | 50052505 | 48117915 | 0.000000 | 0.000000 | 578664368
10-04-2025 1:24:35.000 | 29770072 |  | 29.7701 | -2997473 | 15611746 | 11070714 | 99496925 | 50055832 | 47700942 | 0.000000 | 0.000000 | 574338501
10-04-2025 1:24:30.000 | 28746098 |  | 28.7461 | -3014695 | 15613318 | 10693882 | 99454575 | 50078373 | 47292363 | 0.000000 | 0.000000 | 570107422
10-04-2025 1:24:25.000 | 27882963 |  | 27.883 | -3155214 | 15615819 | 10381068 | 99365837 | 50087685 | 46900864 | 0.000000 | 0.000000 | 565813660
10-04-2025 1:24:20.000 | 29242811 |  | 29.2428 | -3177904 | 15615515 | 10880999 | 99414688 | 50052773 | 46509878 | 0.000000 | 0.000000 | 561428894
10-04-2025 1:24:15.000 | 30298447 |  | 30.2984 | -3244552 | 15612908 | 11273549 | 99431511 | 50032780 | 46095747 | 0.000000 | 0.000000 | 557056824
10-04-2025 1:24:10.000 | 30979990 |  | 30.98 | -3282505 | 15612188 | 11527015 | 99443352 | 50032490 | 45667969 | 0.000000 | 0.000000 | 552621277
10-04-2025 1:24:05.000 | 31312605 |  | 31.3126 | -3266464 | 15612672 | 11647941 | 99460289 | 50035503 | 45238018 | 0.000000 | 0.000000 | 547956604
10-04-2025 1:24:00.000 | 30363322 |  | 30.3633 | -3412737 | 15613109 | 11303761 | 99374275 | 50056911 | 44809956 | 0.000000 | 0.000000 | 543454590
10-04-2025 1:23:55.000 | 30389100 |  | 30.3891 | -3409864 | 15611208 | 11314601 | 99376366 | 50046417 | 44388687 | 0.000000 | 0.000000 | 538654602
10-04-2025 1:23:50.000 | 29421576 |  | 29.4216 | -3284145 | 15613306 | 10952941 | 99382767 | 50068016 | 43968599 | 0.000000 | 0.000000 | 534031189
10-04-2025 1:23:45.000 | 28031926 |  | 28.0319 | -3462281 | 15616287 | 10448662 | 99245857 | 50087639 | 43569097 | 0.000000 | 0.000000 | 529504272
10-04-2025 1:23:40.000 | 29318848 |  | 29.3188 | -3339181 | 15615195 | 10916069 | 99357674 | 50066708 | 43175918 | 0.000000 | 0.000000 | 524845154
10-04-2025 1:23:35.000 | 31479078 |  | 31.4791 | -3396159 | 15612869 | 11713234 | 99423058 | 50032394 | 42757632 | 0.000000 | 0.000000 | 520137268
10-04-2025 1:23:30.000 | 32215779 |  | 32.2158 | -3197283 | 15610017 | 11979347 | 99511124 | 50017445 | 42314946 | 0.000000 | 0.000000 | 515516113
10-04-2025 1:23:25.000 | 31087219 |  | 31.0872 | -3397236 | 15610844 | 11572090 | 99408180 | 50050743 | 41872168 | 0.000000 | 0.000000 | 511072327
10-04-2025 1:23:20.000 | 29884215 |  | 29.8842 | -3707208 | 15614015 | 11140386 | 99239319 | 50072376 | 41447930 | 0.000000 | 0.000000 | 506266632
10-04-2025 1:23:15.000 | 29910832 |  | 29.9108 | -3516552 | 15614333 | 11141042 | 99315971 | 50077705 | 41029688 | 0.000000 | 0.000000 | 501328369
10-04-2025 1:23:10.000 | 29869428 |  | 29.8694 | -3476696 | 15613917 | 11125680 | 99329399 | 50079159 | 40613813 | 0.000000 | 0.000000 | 496488281
10-04-2025 1:23:05.000 | 30225535 |  | 30.2255 | -3807568 | 15615771 | 11269144 | 99215874 | 50079033 | 40197358 | 0.000000 | 0.000000 | 491549011
10-04-2025 1:23:00.000 | 31810836 |  | 31.8108 | -3715093 | 15615025 | 11846954 | 99324936 | 50062672 | 39766804 | 0.000000 | 0.000000 | 486333771
10-04-2025 1:22:55.000 | 33232395 |  | 33.2324 | -3705355 | 15611360 | 12371169 | 99384140 | 50049400 | 39316616 | 0.000000 | 0.000000 | 481210327
10-04-2025 1:22:50.000 | 33909199 |  | 33.9092 | -3844010 | 15609860 | 12628156 | 99363579 | 50032612 | 38851243 | 0.000000 | 0.000000 | 475901978
10-04-2025 1:22:45.000 | 32916906 |  | 32.9169 | -3729266 | 15606196 | 12260778 | 99364342 | 50058365 | 38383084 | 0.000000 | 0.000000 | 470554718
10-04-2025 1:22:40.000 | 29507934 |  | 29.5079 | -4223204 | 15610834 | 11029822 | 98991287 | 50136669 | 37942437 | 0.000000 | 0.000000 | 465288361
10-04-2025 1:22:35.000 | 28616520 |  | 28.6165 | -4401882 | 15614570 | 10711411 | 98837509 | 50145973 | 37540059 | 0.000000 | 0.000000 | 459313965
10-04-2025 1:22:30.000 | 29414359 |  | 29.4144 | -4230402 | 15613660 | 10993915 | 98981552 | 50127270 | 37141399 | 0.000000 | 0.000000 | 453287872
10-04-2025 1:22:25.000 | 30158867 |  | 30.1589 | -4276619 | 15611959 | 11269907 | 99009506 | 50103996 | 36726785 | 0.000000 | 0.000000 | 447392212
10-04-2025 1:22:20.000 | 30142961 |  | 30.143 | -4160361 | 15611646 | 11258992 | 99060905 | 50100403 | 36307734 | 0.000000 | 0.000000 | 441513580
10-04-2025 1:22:15.000 | 28598221 |  | 28.5982 | -3980431 | 15612863 | 10683108 | 99045235 | 50140827 | 35896653 | 0.000000 | 0.000000 | 435917145
10-04-2025 1:22:10.000 | 29350566 |  | 29.3506 | -4307271 | 15615011 | 10975018 | 98940269 | 50133972 | 35499250 | 0.000000 | 0.000000 | 430115570
10-04-2025 1:22:05.000 | 30969113 |  | 30.9691 | -4201008 | 15611117 | 11562952 | 99092438 | 50088215 | 35082500 | 0.000000 | 0.000000 | 424227692
10-04-2025 1:22:00.000 | 30396158 |  | 30.3962 | -3985868 | 15608534 | 11345608 | 99151169 | 50097153 | 34650769 | 0.000000 | 0.000000 | 418497437
10-04-2025 1:21:55.000 | 28123893 |  | 28.1239 | -4273937 | 15613268 | 10524819 | 98864906 | 50129265 | 34243237 | 0.000000 | 0.000000 | 412812164
10-04-2025 1:21:50.000 | 27565486 |  | 27.5655 | -3884582 | 15613907 | 10300364 | 99021599 | 50126156 | 33853228 | 0.000000 | 0.000000 | 407100708
10-04-2025 1:21:45.000 | 26490539 |  | 26.4905 | -3798845 | 15614693 | 990143066 | 98987358 | 50150517 | 33478130 | 0.000000 | 0.000000 | 401834778
10-04-2025 1:21:40.000 | 27402549 |  | 27.4025 | -3868275 | 15619085 | 10235081 | 99018272 | 50116211 | 33110154 | 0.000000 | 0.000000 | 396383850
10-04-2025 1:21:35.000 | 28363326 |  | 28.3633 | -3112067 | 15614453 | 10555784 | 99403442 | 50082958 | 32718225 | 0.000000 | 0.000000 | 391575317
10-04-2025 1:21:30.000 | 28530830 |  | 28.5308 | -3264708 | 15614742 | 10623109 | 99351677 | 50070801 | 32324297 | 0.000000 | 0.000000 | 387278473
10-04-2025 1:21:25.000 | 30195080 |  | 30.1951 | -3128772 | 15612217 | 11232039 | 99467445 | 50043629 | 31918076 | 0.000000 | 0.000000 | 382862793
10-04-2025 1:21:20.000 | 30550727 |  | 30.5507 | -2962398 | 15610839 | 11357264 | 99533165 | 50027248 | 31495183 | 0.000000 | 0.000000 | 378560333
10-04-2025 1:21:15.000 | 29144994 |  | 29.145 | -3156103 | 15613290 | 10847992 | 99418777 | 50055939 | 31079053 | 0.000000 | 0.000000 | 374312775
10-04-2025 1:21:10.000 | 28659322 |  | 28.6593 | -3272664 | 15614210 | 10671173 | 99354317 | 50056293 | 30675798 | 0.000000 | 0.000000 | 369871094
10-04-2025 1:21:05.000 | 29095648 |  | 29.0956 | -3410566 | 15614921 | 10837675 | 99319984 | 50060013 | 30273901 | 0.000000 | 0.000000 | 365330902
10-04-2025 1:21:00.000 | 29611320 |  | 29.6113 | -3148243 | 15613330 | 11016973 | 99439560 | 50046322 | 29863235 | 0.000000 | 0.000000 | 360770844
10-04-2025 1:20:55.000 | 29582422 |  | 29.5824 | -3146354 | 15614071 | 11005415 | 99439140 | 50052540 | 29452239 | 0.000000 | 0.000000 | 356459412
10-04-2025 1:20:50.000 | 30138051 |  | 30.1381 | -2980687 | 15612956 | 11204631 | 99514488 | 50036407 | 29039734 | 0.000000 | 0.000000 | 352044556
10-04-2025 1:20:45.000 | 30740830 |  | 30.7408 | -3047876 | 15612826 | 11428563 | 99512085 | 50032742 | 28618645 | 0.000000 | 0.000000 | 347855957
10-04-2025 1:20:40.000 | 31497180 |  | 31.4972 | -3169270 | 15612396 | 11711890 | 99497581 | 50037750 | 28186729 | 0.000000 | 0.000000 | 343654175
10-04-2025 1:20:35.000 | 31656268 |  | 31.6563 | -3088250 | 15610622 | 11769012 | 99527512 | 50035446 | 27744570 | 0.000000 | 0.000000 | 339367462
10-04-2025 1:20:30.000 | 30705926 |  | 30.7059 | -3103660 | 15612833 | 11417996 | 99493057 | 50063747 | 27307437 | 0.000000 | 0.000000 | 335099182
10-04-2025 1:20:25.000 | 30389154 |  | 30.3892 | -3184453 | 15610805 | 11305963 | 99455444 | 50073196 | 26885251 | 0.000000 | 0.000000 | 330692749
10-04-2025 1:20:20.000 | 30605592 |  | 30.6056 | -3343683 | 15610111 | 11392233 | 99408501 | 50066032 | 26462817 | 0.000000 | 0.000000 | 326014038
10-04-2025 1:20:15.000 | 30421115 |  | 30.4211 | -3472240 | 15611094 | 11328734 | 99354912 | 50067120 | 26039126 | 0.000000 | 0.000000 | 321187317
10-04-2025 1:20:10.000 | 29918035 |  | 29.918 | -3445606 | 15610305 | 11143357 | 99343338 | 50068588 | 25618733 | 0.000000 | 0.000000 | 316391541
10-04-2025 1:20:05.000 | 28447535 |  | 28.4475 | -3383394 | 15613070 | 10600073 | 99300148 | 50096043 | 25209807 | 0.000000 | 0.000000 | 311658539
10-04-2025 1:20:00.000 | 28004582 |  | 28.0046 | -3311646 | 15615854 | 10431841 | 99308052 | 50095024 | 24820369 | 0.000000 | 0.000000 | 306926392
10-04-2025 1:19:55.000 | 29184943 |  | 29.1849 | -3543168 | 15615780 | 10875126 | 99271103 | 50074043 | 24425991 | 0.000000 | 0.000000 | 302110626
10-04-2025 1:19:50.000 | 29962742 |  | 29.9627 | -3253337 | 15615381 | 11149266 | 99415688 | 50049496 | 24014561 | 0.000000 | 0.000000 | 297401184
10-04-2025 1:19:45.000 | 30234023 |  | 30.234 | -3282791 | 15611733 | 11253440 | 99415688 | 50040623 | 23596960 | 0.000000 | 0.000000 | 292901978
10-04-2025 1:19:40.000 | 30280479 |  | 30.2805 | -3460399 | 15612572 | 11275697 | 99353348 | 50041985 | 23174165 | 0.000000 | 0.000000 | 288292267
10-04-2025 1:19:35.000 | 30507258 |  | 30.5073 | -3419398 | 15612174 | 11357700 | 99377708 | 50039299 | 22750830 | 0.000000 | 0.000000 | 283589386
10-04-2025 1:19:30.000 | 28763322 |  | 28.7633 | -3333346 | 15611307 | 10714484 | 99335182 | 50068485 | 22335735 | 0.000000 | 0.000000 | 279059509
10-04-2025 1:19:25.000 | 29075080 |  | 29.0751 | -3460700 | 15613755 | 10831545 | 99299072 | 50044106 | 21938381 | 0.000000 | 0.000000 | 274170380
10-04-2025 1:19:20.000 | 29362949 |  | 29.3629 | -3445072 | 15610902 | 10939747 | 99318741 | 50047966 | 21530903 | 0.000000 | 0.000000 | 269405701
10-04-2025 1:19:15.000 | 29591469 |  | 29.5915 | -3500662 | 15614817 | 11022738 | 99307518 | 50048962 | 21123086 | 0.000000 | 0.000000 | 264393677
10-04-2025 1:19:10.000 | 29621096 |  | 29.6211 | -3667903 | 15612630 | 11042748 | 99242043 | 50041080 | 20713303 | 0.000000 | 0.000000 | 259351379
10-04-2025 1:19:05.000 | 28426422 |  | 28.4264 | -3520630 | 15616245 | 10595339 | 99241760 | 50052654 | 20306826 | 0.000000 | 0.000000 | 254368515
10-04-2025 1:19:00.000 | 29228902 |  | 29.2289 | -3990649 | 15618473 | 10909623 | 99080795 | 50029697 | 19911324 | 0.000000 | 0.000000 | 249240616
10-04-2025 1:18:55.000 | 31301322 |  | 31.3013 | -3533969 | 15612518 | 11654116 | 99368690 | 50010658 | 19489060 | 0.000000 | 0.000000 | 244140610
10-04-2025 1:18:50.000 | 31352209 |  | 31.3522 | -3589127 | 15611092 | 11676378 | 99351112 | 50014595 | 19053197 | 0.000000 | 0.000000 | 239239410
10-04-2025 1:18:45.000 | 30191684 |  | 30.1917 | -3758081 | 15610842 | 11257709 | 99234200 | 50042019 | 18620631 | 0.000000 | 0.000000 | 234270676
10-04-2025 1:18:40.000 | 29369893 |  | 29.3699 | -3898064 | 15612676 | 10961713 | 99130699 | 50055801 | 18206542 | 0.000000 | 0.000000 | 228976974
10-04-2025 1:18:35.000 | 29427283 |  | 29.4273 | -4048941 | 15615134 | 10990587 | 99066658 | 50055126 | 17798843 | 0.000000 | 0.000000 | 223530106
10-04-2025 1:18:30.000 | 29446285 |  | 29.4463 | -3789674 | 15612692 | 10985121 | 99181992 | 50055370 | 17386433 | 0.000000 | 0.000000 | 218292755
10-04-2025 1:18:25.000 | 29244314 |  | 29.2443 | -3936911 | 15615470 | 10915206 | 99105988 | 50063885 | 16977035 | 0.000000 | 0.000000 | 213044540
10-04-2025 1:18:20.000 | 30247188 |  | 30.2472 | -4006724 | 15613552 | 11286809 | 99134018 | 50049564 | 16564841 | 0.000000 | 0.000000 | 207632767
10-04-2025 1:18:15.000 | 30602961 |  | 30.603 | -3634664 | 15613432 | 11400649 | 99302078 | 50027435 | 16140973 | 0.000000 | 0.000000 | 202330444
10-04-2025 1:18:10.000 | 30205102 |  | 30.2051 | -3697641 | 15611507 | 11259564 | 99259010 | 50046875 | 15717394 | 0.000000 | 0.000000 | 197331451
10-04-2025 1:18:05.000 | 29939693 |  | 29.9397 | -3888377 | 15613354 | 11168643 | 99167160 | 50042194 | 15299565 | 0.000000 | 0.000000 | 191985352
10-04-2025 1:18:00.000 | 28727426 |  | 28.7274 | -3759143 | 15613309 | 10719286 | 99154678 | 50062687 | 14887513 | 0.000000 | 0.000000 | 186833572
10-04-2025 1:17:55.000 | 28252873 |  | 28.2529 | -4002015 | 15615839 | 10556985 | 99011612 | 50069492 | 14494334 | 0.000000 | 0.000000 | 181505859
10-04-2025 1:17:50.000 | 30207572 |  | 30.2076 | -3816823 | 15613238 | 11264937 | 99211174 | 50029469 | 14091067 | 0.000000 | 0.000000 | 176002228
10-04-2025 1:17:45.000 | 30198098 |  | 30.1981 | -3567545 | 15613391 | 11250121 | 99309387 | 50029167 | 13670483 | 0.000000 | 0.000000 | 170820328
10-04-2025 1:17:40.000 | 30005059 |  | 30.0051 | -3810511 | 15613747 | 11189443 | 99203232 | 50038506 | 13251624 | 0.000000 | 0.000000 | 165812073
10-04-2025 1:17:35.000 | 30717082 |  | 30.7171 | -3568468 | 15611438 | 11443218 | 99331955 | 50013428 | 12829586 | 0.000000 | 0.000000 | 160552704
10-04-2025 1:17:30.000 | 31047080 |  | 31.0471 | -3789903 | 15613554 | 11571027 | 99263176 | 50026295 | 12402224 | 0.000000 | 0.000000 | 155486633
10-04-2025 1:17:25.000 | 31367697 |  | 31.3677 | -3692701 | 15610414 | 11687692 | 99314186 | 50025902 | 11967567 | 0.000000 | 0.000000 | 150359787
10-04-2025 1:17:20.000 | 30606936 |  | 30.6069 | -3701773 | 15612067 | 11407445 | 99276535 | 50041595 | 11536510 | 0.000000 | 0.000000 | 145202362
10-04-2025 1:17:15.000 | 30088557 |  | 30.0886 | -3669779 | 15609927 | 11217682 | 99264412 | 50053501 | 11116289 | 0.000000 | 0.000000 | 139974014
10-04-2025 1:17:10.000 | 28347922 |  | 28.3479 | -3940644 | 15614630 | 10589038 | 99047592 | 50081318 | 10709410 | 0.000000 | 0.000000 | 134833405
10-04-2025 1:17:05.000 | 28517709 |  | 28.5177 | -3904809 | 15615619 | 10647874 | 99075546 | 50060734 | 10315406 | 0.000000 | 0.000000 | 129444992
10-04-2025 1:17:00.000 | 29259389 |  | 29.2594 | -3734136 | 15613521 | 10913002 | 99195450 | 50048752 | 991213745 | 0.000000 | 0.000000 | 124253540
10-04-2025 1:16:55.000 | 28593586 |  | 28.5936 | -3559264 | 15614157 | 10660674 | 99234154 | 50059700 | 950748230 | 0.000000 | 0.000000 | 119190742
10-04-2025 1:16:50.000 | 29296018 |  | 29.296 | -3818852 | 15615994 | 10929202 | 99161072 | 50041985 | 910993286 | 0.000000 | 0.000000 | 114027451
10-04-2025 1:16:45.000 | 31159090 |  | 31.1591 | -3653856 | 15612988 | 11606378 | 99319466 | 50008560 | 869141724 | 0.000000 | 0.000000 | 108834366
10-04-2025 1:16:40.000 | 31631051 |  | 31.6311 | -3684404 | 15612783 | 11781926 | 99328438 | 50008831 | 825590515 | 0.000000 | 0.000000 | 103706818
10-04-2025 1:16:35.000 | 30797246 |  | 30.7972 | -3899371 | 15612433 | 11484871 | 99207954 | 50024723 | 782099976 | 0.000000 | 0.000000 | 98541405
10-04-2025 1:16:30.000 | 30573287 |  | 30.5733 | -3890718 | 15614964 | 11400674 | 99199966 | 50025208 | 739106934 | 0.000000 | 0.000000 | 93263840
10-04-2025 1:16:25.000 | 30483604 |  | 30.4836 | -3834668 | 15610319 | 11369221 | 99218056 | 50032372 | 696415466 | 0.000000 | 0.000000 | 87986351
10-04-2025 1:16:20.000 | 29798705 |  | 29.7987 | -3889974 | 15611800 | 11120216 | 99158684 | 50041660 | 654356384 | 0.000000 | 0.000000 | 82613983
10-04-2025 1:16:15.000 | 28896971 |  | 28.897 | -3793045 | 15613864 | 10783208 | 99149506 | 50059780 | 613571838 | 0.000000 | 0.000000 | 77229675
10-04-2025 1:16:10.000 | 29391506 |  | 29.3915 | -3689586 | 15612696 | 10961195 | 99221275 | 50055561 | 573240234 | 0.000000 | 0.000000 | 71902626
10-04-2025 1:16:05.000 | 29778396 |  | 29.7784 | -3845449 | 15612645 | 11109657 | 99176483 | 50057919 | 532169983 | 0.000000 | 0.000000 | 66644043
10-04-2025 1:16:00.000 | 30013475 |  | 30.0135 | -3853625 | 15614118 | 11195074 | 99185768 | 50038338 | 490663361 | 0.000000 | 0.000000 | 61290337
10-04-2025 1:15:55.000 | 29589365 |  | 29.5894 | -3618852 | 15611658 | 11030789 | 99260391 | 50046852 | 449214905 | 0.000000 | 0.000000 | 56091534
10-04-2025 1:15:50.000 | 29342100 |  | 29.3421 | -3622167 | 15613585 | 10937847 | 99246651 | 50054935 | 408474487 | 0.000000 | 0.000000 | 50915314
10-04-2025 1:15:45.000 | 29673844 |  | 29.6738 | -3854360 | 15612769 | 11072390 | 99166946 | 50054276 | 367569824 | 0.000000 | 0.000000 | 45807117
10-04-2025 1:15:40.000 | 29753498 |  | 29.7535 | -3578433 | 15610016 | 11088859 | 99284515 | 50046227 | 326228302 | 0.000000 | 0.000000 | 40586567
10-04-2025 1:15:35.000 | 28904809 |  | 28.9048 | -3736371 | 15611899 | 10785220 | 99174858 | 50052273 | 285229858 | 0.000000 | 0.000000 | 35559059
10-04-2025 1:15:30.000 | 28586668 |  | 28.5867 | -3693924 | 15613651 | 10664753 | 99175446 | 50051010 | 245352890 | 0.000000 | 0.000000 | 30386263
10-04-2025 1:15:25.000 | 28438818 |  | 28.4388 | -3734978 | 15614249 | 10611849 | 99148567 | 50044670 | 205655319 | 0.000000 | 0.000000 | 25196516
10-04-2025 1:15:20.000 | 29067072 |  | 29.0671 | -3685423 | 15613518 | 10841207 | 99205772 | 50026886 | 165986267 | 0.000000 | 0.000000 | 19976555
10-04-2025 1:15:15.000 | 29398902 |  | 29.3989 | -3662481 | 15615374 | 10959354 | 99232925 | 50021275 | 125564331 | 0.000000 | 0.000000 | 14862851
10-04-2025 1:15:10.000 | 29821367 |  | 29.8214 | -3396377 | 15614407 | 11102793 | 99357689 | 50013607 | 84644379 | 0.000000 | 0.000000 | 9832610
10-04-2025 1:15:05.000 | 30080361 |  | 30.0804 | -3753097 | 15616495 | 11213099 | 99230606 | 50012218 | 43063950 | 0.000000 | 0.000000 | 4999866
10-04-2025 1:15:00.000 | 31424652 |  | 31.4247 | -3582147 | 15609568 | 11703793 | 99356560 | 49986118 | 74581973 | 0.000000 | 0.000000 | 903959778
10-04-2025 1:14:55.000 | 31316709 |  | 31.3167 | -3593410 | 15609766 | 11664993 | 99348122 | 49996197 | 74142163 | 0.000000 | 0.000000 | 899040771
10-04-2025 1:14:50.000 | 30118998 |  | 30.119 | -3713281 | 15610771 | 11229890 | 99248573 | 50026665 | 73713667 | 0.000000 | 0.000000 | 893994080
10-04-2025 1:14:45.000 | 29230959 |  | 29.231 | -3738475 | 15612477 | 10903719 | 99192047 | 50034729 | 73303535 | 0.000000 | 0.000000 | 888709290
10-04-2025 1:14:40.000 | 29043322 |  | 29.0433 | -3734008 | 15613805 | 10833540 | 99183632 | 50045658 | 72898169 | 0.000000 | 0.000000 | 883509888
10-04-2025 1:14:35.000 | 29179262 |  | 29.1793 | -3604963 | 15612412 | 10878651 | 99245453 | 50044205 | 72493853 | 0.000000 | 0.000000 | 878253174
10-04-2025 1:14:30.000 | 28644004 |  | 28.644 | -3674013 | 15614652 | 10684242 | 99187424 | 50054325 | 72094146 | 0.000000 | 0.000000 | 873166748
10-04-2025 1:14:25.000 | 28977521 |  | 28.9775 | -3678508 | 15614681 | 10805917 | 99203873 | 50049042 | 71697456 | 0.000000 | 0.000000 | 867982361
10-04-2025 1:14:20.000 | 29919832 |  | 29.9198 | -3622125 | 15613096 | 11150105 | 99275169 | 50030334 | 71289863 | 0.000000 | 0.000000 | 862938110
10-04-2025 1:14:15.000 | 30083277 |  | 30.0833 | -3747803 | 15613082 | 11216094 | 99232895 | 50026062 | 70872368 | 0.000000 | 0.000000 | 857860779
10-04-2025 1:14:10.000 | 29604740 |  | 29.6047 | -3684843 | 15613326 | 11037655 | 99234268 | 50033211 | 70455156 | 0.000000 | 0.000000 | 852735352
10-04-2025 1:14:05.000 | 29379807 |  | 29.3798 | -3716481 | 15613607 | 10956796 | 99209389 | 50043186 | 70046328 | 0.000000 | 0.000000 | 847604065
10-04-2025 1:14:00.000 | 29804846 |  | 29.8048 | -3674292 | 15615709 | 11108899 | 99248672 | 50034595 | 69634795 | 0.000000 | 0.000000 | 842519897
10-04-2025 1:13:55.000 | 30346119 |  | 30.3461 | -3603309 | 15613788 | 11306407 | 99302406 | 50020744 | 69218208 | 0.000000 | 0.000000 | 837469055
10-04-2025 1:13:50.000 | 30852324 |  | 30.8523 | -3729596 | 15613505 | 11496831 | 99277245 | 50017971 | 68794448 | 0.000000 | 0.000000 | 832376587
10-04-2025 1:13:45.000 | 31865934 |  | 31.8659 | -3817684 | 15612264 | 11874011 | 99289978 | 50018623 | 68359946 | 0.000000 | 0.000000 | 827168396
10-04-2025 1:13:40.000 | 32615453 |  | 32.6155 | -3980612 | 15610222 | 12157513 | 99263451 | 50008263 | 67913867 | 0.000000 | 0.000000 | 821610352
10-04-2025 1:13:35.000 | 31845061 |  | 31.8451 | -4100000 | 15606754 | 11883058 | 99181358 | 50039997 | 67463867 | 0.000000 | 0.000000 | 816147766
10-04-2025 1:13:30.000 | 30373924 |  | 30.3739 | -4301125 | 15612342 | 11349343 | 99012222 | 50062344 | 67030645 | 0.000000 | 0.000000 | 810200378
10-04-2025 1:13:25.000 | 29126490 |  | 29.1265 | -4531983 | 15611732 | 10906245 | 98811028 | 50084602 | 66615078 | 0.000000 | 0.000000 | 804082825
10-04-2025 1:13:20.000 | 29358041 |  | 29.358 | -4652855 | 15612078 | 10998615 | 98767273 | 50094372 | 66211021 | 0.000000 | 0.000000 | 797720093
10-04-2025 1:13:15.000 | 29753049 |  | 29.753 | -4635577 | 15614203 | 11139310 | 98807953 | 50076267 | 65801279 | 0.000000 | 0.000000 | 791245728
10-04-2025 1:13:10.000 | 29893627 |  | 29.8936 | -4619569 | 15612509 | 11191154 | 98826935 | 50075871 | 65387915 | 0.000000 | 0.000000 | 784841187
10-04-2025 1:13:05.000 | 29229428 |  | 29.2294 | -4598965 | 15611112 | 10948250 | 98784721 | 50085735 | 64975220 | 0.000000 | 0.000000 | 778465027
10-04-2025 1:13:00.000 | 28905072 |  | 28.9051 | -4572056 | 15610498 | 10828551 | 98772034 | 50096153 | 64573745 | 0.000000 | 0.000000 | 772159180
10-04-2025 1:12:55.000 | 29173771 |  | 29.1738 | -4748926 | 15612711 | 10935491 | 98700882 | 50085670 | 64170005 | 0.000000 | 0.000000 | 765631470
10-04-2025 1:12:50.000 | 28964885 |  | 28.9649 | -4615347 | 15611250 | 10852959 | 98754166 | 50074402 | 63762051 | 0.000000 | 0.000000 | 759127991
10-04-2025 1:12:45.000 | 27867410 |  | 27.8674 | -4457873 | 15611949 | 10442567 | 98744568 | 50088585 | 63366738 | 0.000000 | 0.000000 | 752778625
10-04-2025 1:12:40.000 | 25746957 |  | 25.747 | -4256536 | 15615228 | 965579468 | 98660820 | 50110332 | 62992495 | 0.000000 | 0.000000 | 746738831
10-04-2025 1:12:35.000 | 25691334 |  | 25.6913 | -4361460 | 15616666 | 964012329 | 98589432 | 50118816 | 62636021 | 0.000000 | 0.000000 | 740778076
10-04-2025 1:12:30.000 | 26936031 |  | 26.936 | -4044806 | 15619695 | 10074236 | 98891266 | 50074951 | 62274175 | 0.000000 | 0.000000 | 734821472
10-04-2025 1:12:25.000 | 28919016 |  | 28.919 | -3739756 | 15615015 | 10786968 | 99174187 | 50032421 | 61886841 | 0.000000 | 0.000000 | 729524963
10-04-2025 1:12:20.000 | 30273369 |  | 30.2734 | -3503404 | 15611672 | 11275374 | 99337029 | 50004452 | 61474985 | 0.000000 | 0.000000 | 724491882
10-04-2025 1:12:15.000 | 30288779 |  | 30.2888 | -3499037 | 15610847 | 11282096 | 99339333 | 50002087 | 61053940 | 0.000000 | 0.000000 | 719558350
10-04-2025 1:12:10.000 | 29710115 |  | 29.7101 | -3507166 | 15611311 | 11069435 | 99310455 | 50015083 | 60636689 | 0.000000 | 0.000000 | 714626221
10-04-2025 1:12:05.000 | 29127141 |  | 29.1271 | -3645144 | 15613903 | 10859404 | 99226006 | 50025658 | 60225894 | 0.000000 | 0.000000 | 709635925
10-04-2025 1:12:00.000 | 28556309 |  | 28.5563 | -3629434 | 15615446 | 10648727 | 99201965 | 50043087 | 59825620 | 0.000000 | 0.000000 | 704687683
10-04-2025 1:11:55.000 | 29529703 |  | 29.5297 | -3636368 | 15615385 | 11005873 | 99250313 | 50030552 | 59424194 | 0.000000 | 0.000000 | 699755066
10-04-2025 1:11:50.000 | 31381545 |  | 31.3815 | -3577781 | 15612313 | 11685011 | 99356361 | 49999924 | 59005820 | 0.000000 | 0.000000 | 694784302
10-04-2025 1:11:45.000 | 32510244 |  | 32.5102 | -3650114 | 15609195 | 12104821 | 99375603 | 49979698 | 58562451 | 0.000000 | 0.000000 | 689790344
10-04-2025 1:11:40.000 | 32112188 |  | 32.1122 | -3625171 | 15609175 | 11959501 | 99368813 | 49993530 | 58110122 | 0.000000 | 0.000000 | 684805847
10-04-2025 1:11:35.000 | 30032568 |  | 30.0326 | -3487408 | 15609207 | 11188696 | 99332542 | 50037601 | 57674771 | 0.000000 | 0.000000 | 679854065
10-04-2025 1:11:30.000 | 28219744 |  | 28.2197 | -3558537 | 15611186 | 10525721 | 99214287 | 50066132 | 57270757 | 0.000000 | 0.000000 | 674908997
10-04-2025 1:11:25.000 | 28317297 |  | 28.3173 | -3596564 | 15612078 | 10562400 | 99203056 | 50053005 | 56879150 | 0.000000 | 0.000000 | 669769958
10-04-2025 1:11:20.000 | 27538711 |  | 27.5387 | -3220618 | 15614903 | 10257437 | 99323082 | 50051617 | 56490635 | 0.000000 | 0.000000 | 664954041
10-04-2025 1:11:15.000 | 27433430 |  | 27.4334 | -3707923 | 15618444 | 10239338 | 99098907 | 50046635 | 56110454 | 0.000000 | 0.000000 | 660187927
10-04-2025 1:11:10.000 | 29487447 |  | 29.4874 | -3454509 | 15615094 | 10982836 | 99320755 | 50008511 | 55718340 | 0.000000 | 0.000000 | 655158081
10-04-2025 1:11:05.000 | 31725447 |  | 31.7254 | -3372094 | 15609657 | 11807253 | 99439865 | 49962524 | 55297402 | 0.000000 | 0.000000 | 650263794
10-04-2025 1:11:00.000 | 30550932 |  | 30.5509 | -3296365 | 15611221 | 11370392 | 99422943 | 49989044 | 54859756 | 0.000000 | 0.000000 | 645773743
10-04-2025 1:10:55.000 | 29993689 |  | 29.9937 | -3600957 | 15613299 | 11177090 | 99287010 | 49999161 | 54439414 | 0.000000 | 0.000000 | 641050964
10-04-2025 1:10:50.000 | 30312469 |  | 30.3125 | -3508035 | 15613271 | 11288972 | 99336990 | 49997410 | 54021450 | 0.000000 | 0.000000 | 636097229
10-04-2025 1:10:45.000 | 30096867 |  | 30.0969 | -3605638 | 15614722 | 11212852 | 99290016 | 49997471 | 53600132 | 0.000000 | 0.000000 | 631118652
10-04-2025 1:10:40.000 | 29981080 |  | 29.9811 | -3578974 | 15612890 | 11171395 | 99295013 | 50001244 | 53181094 | 0.000000 | 0.000000 | 626215454
10-04-2025 1:10:35.000 | 29757195 |  | 29.7572 | -3652262 | 15613570 | 11091818 | 99255203 | 50003986 | 52765679 | 0.000000 | 0.000000 | 621225830
10-04-2025 1:10:30.000 | 29634631 |  | 29.6346 | -3611474 | 15613688 | 11045233 | 99265594 | 50011127 | 52353115 | 0.000000 | 0.000000 | 616233154
10-04-2025 1:10:25.000 | 30147537 |  | 30.1475 | -3723824 | 15614270 | 11237262 | 99245758 | 50002781 | 51940337 | 0.000000 | 0.000000 | 611160706
10-04-2025 1:10:20.000 | 29934324 |  | 29.9343 | -3391111 | 15613515 | 11145762 | 99364433 | 50003811 | 51520454 | 0.000000 | 0.000000 | 606168396
10-04-2025 1:10:15.000 | 29949871 |  | 29.9499 | -3777390 | 15615713 | 11166464 | 99214005 | 50015308 | 51106758 | 0.000000 | 0.000000 | 601290588
10-04-2025 1:10:10.000 | 32473467 |  | 32.4735 | -3558426 | 15610350 | 12087222 | 99404968 | 49967636 | 50675557 | 0.000000 | 0.000000 | 596070923
10-04-2025 1:10:05.000 | 33216344 |  | 33.2163 | -3609669 | 15607436 | 12364910 | 99414703 | 49965855 | 50219517 | 0.000000 | 0.000000 | 590996582
10-04-2025 1:10:00.000 | 31623621 |  | 31.6236 | -3742948 | 15610260 | 11783793 | 99306831 | 50001740 | 49766411 | 0.000000 | 0.000000 | 585881653
10-04-2025 1:09:55.000 | 29514061 |  | 29.5141 | -3775919 | 15612073 | 11009293 | 99191528 | 50047779 | 49337808 | 0.000000 | 0.000000 | 580666748
10-04-2025 1:09:50.000 | 29029803 |  | 29.0298 | -4120567 | 15615818 | 10846406 | 99007584 | 50057365 | 48937593 | 0.000000 | 0.000000 | 575070313
10-04-2025 1:09:45.000 | 29949756 |  | 29.9498 | -3787572 | 15611874 | 11170179 | 99209808 | 50032372 | 48528823 | 0.000000 | 0.000000 | 569464417
10-04-2025 1:09:40.000 | 29442512 |  | 29.4425 | -3674325 | 15611070 | 10979497 | 99230270 | 50040802 | 48115518 | 0.000000 | 0.000000 | 564172607
10-04-2025 1:09:35.000 | 28710410 |  | 28.7104 | -3886394 | 15612417 | 10719690 | 99096214 | 50038879 | 47710840 | 0.000000 | 0.000000 | 558877808
10-04-2025 1:09:30.000 | 28065371 |  | 28.0654 | -3641893 | 15614913 | 10470054 | 99168541 | 50031956 | 47314980 | 0.000000 | 0.000000 | 553622314
10-04-2025 1:09:25.000 | 27989916 |  | 27.9899 | -3506696 | 15615634 | 10437042 | 99224312 | 50032963 | 46928101 | 0.000000 | 0.000000 | 548589966
10-04-2025 1:09:20.000 | 29253447 |  | 29.2534 | -3635337 | 15616824 | 10903411 | 99236671 | 50011204 | 46533076 | 0.000000 | 0.000000 | 543599121
10-04-2025 1:09:15.000 | 30841555 |  | 30.8416 | -3455331 | 15614385 | 11480272 | 99378258 | 49985214 | 46117344 | 0.000000 | 0.000000 | 538687744
10-04-2025 1:09:10.000 | 31664305 |  | 31.6643 | -3526698 | 15611068 | 11788156 | 99385460 | 49975780 | 45682676 | 0.000000 | 0.000000 | 533874512
10-04-2025 1:09:05.000 | 31096949 |  | 31.0969 | -3242740 | 15612001 | 11567590 | 99460693 | 49988743 | 45243589 | 0.000000 | 0.000000 | 529095886
10-04-2025 1:09:00.000 | 29093875 |  | 29.0939 | -3352596 | 15612092 | 10837043 | 99342598 | 50037682 | 44823896 | 0.000000 | 0.000000 | 524575989
10-04-2025 1:08:55.000 | 28902791 |  | 28.9028 | -3459589 | 15611071 | 10771689 | 99291237 | 50039394 | 44420615 | 0.000000 | 0.000000 | 519871582
10-04-2025 1:08:50.000 | 29216424 |  | 29.2164 | -3428534 | 15612204 | 10883496 | 99318481 | 50026752 | 44016812 | 0.000000 | 0.000000 | 514996704
10-04-2025 1:08:45.000 | 28138359 |  | 28.1384 | -3369835 | 15614354 | 10485591 | 99290504 | 50033108 | 43618965 | 0.000000 | 0.000000 | 510256378
10-04-2025 1:08:40.000 | 28018840 |  | 28.0188 | -3512655 | 15618473 | 10444841 | 99223289 | 50030380 | 43232588 | 0.000000 | 0.000000 | 505507355
10-04-2025 1:08:35.000 | 30306223 |  | 30.3062 | -3241474 | 15615420 | 11275490 | 99432869 | 49984192 | 42831455 | 0.000000 | 0.000000 | 500587067
10-04-2025 1:08:30.000 | 30875189 |  | 30.8752 | -3267965 | 15611730 | 11487540 | 99444511 | 49975193 | 42405454 | 0.000000 | 0.000000 | 496189758
10-04-2025 1:08:25.000 | 31363545 |  | 31.3635 | -3256368 | 15611581 | 11666604 | 99465324 | 49978111 | 41975034 | 0.000000 | 0.000000 | 491606812
10-04-2025 1:08:20.000 | 31682248 |  | 31.6822 | -3590328 | 15612163 | 11797013 | 99364014 | 49986713 | 41536353 | 0.000000 | 0.000000 | 486968170
10-04-2025 1:08:15.000 | 31269604 |  | 31.2696 | -3448935 | 15608422 | 11641656 | 99397224 | 49991741 | 41096753 | 0.000000 | 0.000000 | 482041992
10-04-2025 1:08:10.000 | 29223939 |  | 29.2239 | -3764781 | 15612056 | 10902657 | 99180389 | 50039433 | 40673633 | 0.000000 | 0.000000 | 477319275
10-04-2025 1:08:05.000 | 30286256 |  | 30.2863 | -3869458 | 15615047 | 11293872 | 99193687 | 50017036 | 40264810 | 0.000000 | 0.000000 | 471779510
10-04-2025 1:08:00.000 | 30689053 |  | 30.6891 | -3745192 | 15611613 | 11439918 | 99263565 | 50005581 | 39841365 | 0.000000 | 0.000000 | 466647736
10-04-2025 1:07:55.000 | 30094652 |  | 30.0947 | -3813755 | 15609989 | 11226179 | 99206581 | 50013390 | 39417966 | 0.000000 | 0.000000 | 461448517
10-04-2025 1:07:50.000 | 29064844 |  | 29.0648 | -3563123 | 15613209 | 10834078 | 99256920 | 50022110 | 39003066 | 0.000000 | 0.000000 | 456266113
10-04-2025 1:07:45.000 | 27588867 |  | 27.5889 | -3439566 | 15613266 | 10286837 | 99231789 | 50046154 | 38609849 | 0.000000 | 0.000000 | 451386688
10-04-2025 1:07:40.000 | 28052109 |  | 28.0521 | -3535224 | 15615883 | 10459561 | 99215240 | 50026566 | 38226143 | 0.000000 | 0.000000 | 446401184
10-04-2025 1:07:35.000 | 29133000 |  | 29.133 | -3370797 | 15612925 | 10850957 | 99337280 | 50001209 | 37830159 | 0.000000 | 0.000000 | 441580566
10-04-2025 1:07:30.000 | 29488281 |  | 29.4883 | -3411361 | 15612306 | 10983579 | 99337486 | 49989162 | 37423215 | 0.000000 | 0.000000 | 436839783
10-04-2025 1:07:25.000 | 29138924 |  | 29.1389 | -3407562 | 15613570 | 10854861 | 99323166 | 49994812 | 37013938 | 0.000000 | 0.000000 | 432045715
10-04-2025 1:07:20.000 | 28713775 |  | 28.7138 | -3519919 | 15614732 | 10702363 | 99256989 | 50017685 | 36613645 | 0.000000 | 0.000000 | 427363342
10-04-2025 1:07:15.000 | 29852041 |  | 29.852 | -3540925 | 15615605 | 11120415 | 99303848 | 49997166 | 36209526 | 0.000000 | 0.000000 | 422506744
10-04-2025 1:07:10.000 | 31787184 |  | 31.7872 | -3429966 | 15611619 | 11830118 | 99422867 | 49960262 | 35783091 | 0.000000 | 0.000000 | 417654663
10-04-2025 1:07:05.000 | 31229879 |  | 31.2299 | -3247786 | 15610078 | 11618137 | 99463585 | 49977272 | 35341226 | 0.000000 | 0.000000 | 413000916
10-04-2025 1:07:00.000 | 30155283 |  | 30.1553 | -3330324 | 15609648 | 11227612 | 99395683 | 49998917 | 34914358 | 0.000000 | 0.000000 | 408337402
10-04-2025 1:06:55.000 | 29604719 |  | 29.6047 | -3449774 | 15612765 | 11027107 | 99327904 | 50002861 | 34497446 | 0.000000 | 0.000000 | 403631134
10-04-2025 1:06:50.000 | 29217389 |  | 29.2174 | -3156554 | 15610292 | 10875104 | 99421463 | 50023285 | 34089780 | 0.000000 | 0.000000 | 398931122
10-04-2025 1:06:45.000 | 29347508 |  | 29.3475 | -3547091 | 15614347 | 10938080 | 99277489 | 50021530 | 33687988 | 0.000000 | 0.000000 | 394105042
10-04-2025 1:06:40.000 | 30185648 |  | 30.1856 | -3601848 | 15612354 | 11248210 | 99295609 | 50003792 | 33275935 | 0.000000 | 0.000000 | 389199188
10-04-2025 1:06:35.000 | 30060164 |  | 30.0602 | -3463706 | 15610805 | 11196349 | 99342690 | 49991245 | 32855981 | 0.000000 | 0.000000 | 384339264
10-04-2025 1:06:30.000 | 28257449 |  | 28.2574 | -3239427 | 15611614 | 10524691 | 99349297 | 50019886 | 32445518 | 0.000000 | 0.000000 | 379814056
10-04-2025 1:06:25.000 | 27454289 |  | 27.4543 | -3111142 | 15614056 | 10223740 | 99364037 | 50030392 | 32059717 | 0.000000 | 0.000000 | 375218811
10-04-2025 1:06:20.000 | 26766748 |  | 26.7667 | -3489764 | 15616911 | 998707336 | 99160774 | 50037003 | 31683257 | 0.000000 | 0.000000 | 370766754
10-04-2025 1:06:15.000 | 27965764 |  | 27.9658 | -3310677 | 15615513 | 10417767 | 99306549 | 49997856 | 31303511 | 0.000000 | 0.000000 | 366093872
10-04-2025 1:06:10.000 | 29098396 |  | 29.0984 | -3269507 | 15613060 | 10834076 | 99374672 | 49980537 | 30910305 | 0.000000 | 0.000000 | 361446869
10-04-2025 1:06:05.000 | 30569789 |  | 30.5698 | -3473926 | 15616337 | 11380105 | 99360497 | 49957283 | 30499126 | 0.000000 | 0.000000 | 356687805
10-04-2025 1:06:00.000 | 32023881 |  | 32.0239 | -3156495 | 15612883 | 11905647 | 99517738 | 49923103 | 30067900 | 0.000000 | 0.000000 | 352012421
10-04-2025 1:05:55.000 | 31910738 |  | 31.9107 | -3130638 | 15610242 | 11865067 | 99522209 | 49939919 | 29621877 | 0.000000 | 0.000000 | 347703308
10-04-2025 1:05:50.000 | 31380588 |  | 31.3806 | -3289362 | 15610299 | 11675372 | 99455109 | 49963898 | 29180662 | 0.000000 | 0.000000 | 343224670
10-04-2025 1:05:45.000 | 30500271 |  | 30.5003 | -3313964 | 15608733 | 11353735 | 99414894 | 49979031 | 28747405 | 0.000000 | 0.000000 | 338574341
10-04-2025 1:05:40.000 | 29411156 |  | 29.4112 | -3465312 | 15610008 | 10959713 | 99313034 | 49989223 | 28329827 | 0.000000 | 0.000000 | 333795074
10-04-2025 1:05:35.000 | 27467457 |  | 27.4675 | -3287548 | 15611018 | 10237375 | 99291336 | 50021774 | 27930215 | 0.000000 | 0.000000 | 329186981
10-04-2025 1:05:30.000 | 27196154 |  | 27.1962 | -3668443 | 15613852 | 10153062 | 99102486 | 50031181 | 27550876 | 0.000000 | 0.000000 | 324430756
10-04-2025 1:05:25.000 | 28756455 |  | 28.7565 | -3755504 | 15614854 | 10728029 | 99157982 | 49990292 | 27166560 | 0.000000 | 0.000000 | 319247864
10-04-2025 1:05:20.000 | 29515914 |  | 29.5159 | -3271208 | 15612228 | 10988362 | 99391449 | 49973209 | 26762727 | 0.000000 | 0.000000 | 314317383
10-04-2025 1:05:15.000 | 29296066 |  | 29.2961 | -3322600 | 15612757 | 10908656 | 99362999 | 49967262 | 26355671 | 0.000000 | 0.000000 | 309780945
10-04-2025 1:05:10.000 | 28744965 |  | 28.745 | -3181970 | 15613390 | 10700023 | 99392883 | 49971577 | 25949780 | 0.000000 | 0.000000 | 305341827
10-04-2025 1:05:05.000 | 28957633 |  | 28.9576 | -3127471 | 15612212 | 10776897 | 99421837 | 49977306 | 25549421 | 0.000000 | 0.000000 | 300880157
10-04-2025 1:05:00.000 | 29038338 |  | 29.0383 | -3136555 | 15614557 | 10805070 | 99421700 | 49974075 | 25147288 | 0.000000 | 0.000000 | 296528778
10-04-2025 1:04:55.000 | 29094396 |  | 29.0944 | -3236953 | 15614820 | 10830725 | 99386780 | 49975822 | 24743115 | 0.000000 | 0.000000 | 292229187
10-04-2025 1:04:50.000 | 29752424 |  | 29.7524 | -3147738 | 15613616 | 11069517 | 99445000 | 49970848 | 24336702 | 0.000000 | 0.000000 | 287780212
10-04-2025 1:04:45.000 | 31009035 |  | 31.009 | -3302847 | 15613311 | 11536718 | 99437538 | 49955017 | 23917585 | 0.000000 | 0.000000 | 283234985
10-04-2025 1:04:40.000 | 31618893 |  | 31.6189 | -2916894 | 15613137 | 11747390 | 99577179 | 49939777 | 23482449 | 0.000000 | 0.000000 | 278767426
10-04-2025 1:04:35.000 | 31637584 |  | 31.6376 | -2968062 | 15611741 | 11756711 | 99562828 | 49963665 | 23042708 | 0.000000 | 0.000000 | 274693268
10-04-2025 1:04:30.000 | 32061418 |  | 32.0614 | -3259170 | 15613838 | 11921821 | 99487297 | 49976826 | 22601604 | 0.000000 | 0.000000 | 270365784
10-04-2025 1:04:25.000 | 33421133 |  | 33.4211 | -3369372 | 15611326 | 12428362 | 99495651 | 49958694 | 22148813 | 0.000000 | 0.000000 | 265699738
10-04-2025 1:04:20.000 | 33357402 |  | 33.3574 | -3419716 | 15608885 | 12407941 | 99478615 | 49965202 | 21681609 | 0.000000 | 0.000000 | 261044464
10-04-2025 1:04:15.000 | 32087281 |  | 32.0873 | -3442291 | 15606984 | 11943168 | 99429482 | 50003979 | 21225708 | 0.000000 | 0.000000 | 256278992
10-04-2025 1:04:10.000 | 30060615 |  | 30.0606 | -3991014 | 15613231 | 11219102 | 99130150 | 50047348 | 20793672 | 0.000000 | 0.000000 | 251072342
10-04-2025 1:04:05.000 | 29641748 |  | 29.6417 | -3953976 | 15613441 | 11063236 | 99122025 | 50054249 | 20378090 | 0.000000 | 0.000000 | 245534012
10-04-2025 1:04:00.000 | 29672053 |  | 29.6721 | -3940214 | 15612825 | 11074895 | 99129807 | 50051529 | 19965957 | 0.000000 | 0.000000 | 240013062
10-04-2025 1:03:55.000 | 30284609 |  | 30.2846 | -3927237 | 15612079 | 11298604 | 99169640 | 50047993 | 19551067 | 0.000000 | 0.000000 | 234521774
10-04-2025 1:03:50.000 | 30206498 |  | 30.2065 | -4047225 | 15612162 | 11276149 | 99114304 | 50045410 | 19130464 | 0.000000 | 0.000000 | 229026199
10-04-2025 1:03:45.000 | 30012363 |  | 30.0124 | -3953324 | 15612469 | 11200297 | 99143578 | 50044430 | 18710780 | 0.000000 | 0.000000 | 223496796
10-04-2025 1:03:40.000 | 29071861 |  | 29.0719 | -3816730 | 15614027 | 10847548 | 99149185 | 50061592 | 18296525 | 0.000000 | 0.000000 | 218165863
10-04-2025 1:03:35.000 | 29402666 |  | 29.4027 | -3732638 | 15613652 | 10964889 | 99203812 | 50063534 | 17893645 | 0.000000 | 0.000000 | 212869522
10-04-2025 1:03:30.000 | 30235584 |  | 30.2356 | -3931170 | 15615063 | 11279158 | 99165337 | 50052479 | 17480248 | 0.000000 | 0.000000 | 207534775
10-04-2025 1:03:25.000 | 31335285 |  | 31.3353 | -3809787 | 15613074 | 11677703 | 99268990 | 50026035 | 17052380 | 0.000000 | 0.000000 | 202157501
10-04-2025 1:03:20.000 | 31291059 |  | 31.2911 | -3585123 | 15611562 | 11652975 | 99350037 | 50020550 | 16616942 | 0.000000 | 0.000000 | 196917847
10-04-2025 1:03:15.000 | 30298785 |  | 30.2988 | -3744458 | 15612090 | 11295725 | 99244980 | 50037189 | 16187266 | 0.000000 | 0.000000 | 191903259
10-04-2025 1:03:10.000 | 30327900 |  | 30.3279 | -3847582 | 15613689 | 11309293 | 99204834 | 50040848 | 15764916 | 0.000000 | 0.000000 | 186627853
10-04-2025 1:03:05.000 | 30406258 |  | 30.4063 | -3642127 | 15611737 | 11330455 | 99290237 | 50042778 | 15340853 | 0.000000 | 0.000000 | 181441284
10-04-2025 1:03:00.000 | 29834385 |  | 29.8344 | -3637474 | 15610912 | 11121111 | 99264931 | 50047379 | 14921959 | 0.000000 | 0.000000 | 176349426
10-04-2025 1:02:55.000 | 29061146 |  | 29.0611 | -3587813 | 15610984 | 10834806 | 99246513 | 50055969 | 14510767 | 0.000000 | 0.000000 | 171272720
10-04-2025 1:02:50.000 | 27849674 |  | 27.8497 | -3777398 | 15612043 | 10399521 | 99092651 | 50071899 | 14115945 | 0.000000 | 0.000000 | 166238968
10-04-2025 1:02:45.000 | 28008516 |  | 28.0085 | -3696852 | 15613923 | 10452959 | 99140144 | 50058929 | 13726107 | 0.000000 | 0.000000 | 161016235
10-04-2025 1:02:40.000 | 28665576 |  | 28.6656 | -3496558 | 15613743 | 10683875 | 99264275 | 50042366 | 13332826 | 0.000000 | 0.000000 | 156020111
10-04-2025 1:02:35.000 | 28781518 |  | 28.7815 | -3522363 | 15614851 | 10727306 | 99259430 | 50038216 | 12934010 | 0.000000 | 0.000000 | 151155762
10-04-2025 1:02:30.000 | 29344018 |  | 29.344 | -3473766 | 15612632 | 10932275 | 99306580 | 50029926 | 12530299 | 0.000000 | 0.000000 | 146397400
10-04-2025 1:02:25.000 | 29639125 |  | 29.6391 | -3507754 | 15612604 | 11042515 | 99306953 | 50022644 | 12121655 | 0.000000 | 0.000000 | 141536728
10-04-2025 1:02:20.000 | 29671355 |  | 29.6714 | -3307156 | 15611338 | 11046364 | 99384567 | 50024120 | 11706598 | 0.000000 | 0.000000 | 136809006
10-04-2025 1:02:15.000 | 29321912 |  | 29.3219 | -3484091 | 15611811 | 10925249 | 99301453 | 50034775 | 11298645 | 0.000000 | 0.000000 | 132052597
10-04-2025 1:02:10.000 | 29213650 |  | 29.2137 | -3408267 | 15613110 | 10882466 | 99326309 | 50028912 | 10892982 | 0.000000 | 0.000000 | 127136940
10-04-2025 1:02:05.000 | 29721232 |  | 29.7212 | -3476363 | 15614830 | 11069561 | 99322891 | 50028507 | 10485280 | 0.000000 | 0.000000 | 122304771
10-04-2025 1:02:00.000 | 30654295 |  | 30.6543 | -3573947 | 15613313 | 11417827 | 99327202 | 50011395 | 10068109 | 0.000000 | 0.000000 | 117419037
10-04-2025 1:01:55.000 | 31758994 |  | 31.759 | -3561820 | 15611157 | 11824141 | 99376976 | 49994839 | 963450012 | 0.000000 | 0.000000 | 112343666
10-04-2025 1:01:50.000 | 30598773 |  | 30.5988 | -3601702 | 15610777 | 11399827 | 99314362 | 50017071 | 919913330 | 0.000000 | 0.000000 | 107376427
10-04-2025 1:01:45.000 | 29891094 |  | 29.8911 | -3791229 | 15612457 | 11147672 | 99205223 | 50039410 | 878104004 | 0.000000 | 0.000000 | 102205658
10-04-2025 1:01:40.000 | 30027311 |  | 30.0273 | -3770911 | 15612106 | 11196938 | 99220657 | 50035675 | 836591248 | 0.000000 | 0.000000 | 96909737
10-04-2025 1:01:35.000 | 29779676 |  | 29.7797 | -3828573 | 15611933 | 11109124 | 99183678 | 50043987 | 794977783 | 0.000000 | 0.000000 | 91727737
10-04-2025 1:01:30.000 | 29844381 |  | 29.8444 | -3725843 | 15612637 | 11127134 | 99229713 | 50033531 | 753665344 | 0.000000 | 0.000000 | 86424545
10-04-2025 1:01:25.000 | 28540701 |  | 28.5407 | -3503139 | 15611631 | 10640624 | 99255127 | 50048340 | 712873413 | 0.000000 | 0.000000 | 81408981
10-04-2025 1:01:20.000 | 27567715 |  | 27.5677 | -3628900 | 15613874 | 10288010 | 99144699 | 50059441 | 674096619 | 0.000000 | 0.000000 | 76404129
10-04-2025 1:01:15.000 | 28766203 |  | 28.7662 | -3713956 | 15615938 | 10729192 | 99176826 | 50037457 | 635069092 | 0.000000 | 0.000000 | 71283226
10-04-2025 1:01:10.000 | 28886441 |  | 28.8864 | -3447429 | 15612592 | 10763134 | 99295364 | 50025944 | 594758484 | 0.000000 | 0.000000 | 66427399
10-04-2025 1:01:05.000 | 29110578 |  | 29.1106 | -3456084 | 15614580 | 10844885 | 99302612 | 50024006 | 554486694 | 0.000000 | 0.000000 | 61629776
10-04-2025 1:01:00.000 | 29276646 |  | 29.2766 | -3538539 | 15614355 | 10909230 | 99277481 | 50025223 | 513957031 | 0.000000 | 0.000000 | 56868652
10-04-2025 1:00:55.000 | 29993557 |  | 29.9936 | -3332293 | 15614164 | 11164042 | 99388489 | 50016045 | 472864105 | 0.000000 | 0.000000 | 52105850
10-04-2025 1:00:50.000 | 31431988 |  | 31.432 | -3615721 | 15613476 | 11704904 | 99344864 | 49997196 | 430604370 | 0.000000 | 0.000000 | 47363789
10-04-2025 1:00:45.000 | 32831680 |  | 32.8317 | -3234588 | 15613509 | 12204491 | 99518188 | 49986855 | 386266296 | 0.000000 | 0.000000 | 42505661
10-04-2025 1:00:40.000 | 32578959 |  | 32.579 | -3188933 | 15608602 | 12112900 | 99524361 | 49995617 | 340856201 | 0.000000 | 0.000000 | 38054020
10-04-2025 1:00:35.000 | 31878230 |  | 31.8782 | -3420835 | 15611688 | 11861915 | 99429161 | 50022057 | 295937592 | 0.000000 | 0.000000 | 33448917
10-04-2025 1:00:30.000 | 31208002 |  | 31.208 | -3317677 | 15612385 | 11610518 | 99439667 | 50037468 | 252008163 | 0.000000 | 0.000000 | 28720879
10-04-2025 1:00:25.000 | 30367361 |  | 30.3674 | -3326705 | 15610914 | 11302860 | 99405304 | 50058208 | 209154587 | 0.000000 | 0.000000 | 24068375
10-04-2025 1:00:20.000 | 29915107 |  | 29.9151 | -3422255 | 15614488 | 11138296 | 99351997 | 50068134 | 167409576 | 0.000000 | 0.000000 | 19366016
10-04-2025 1:00:15.000 | 29692928 |  | 29.6929 | -3457602 | 15613204 | 11059342 | 99328842 | 50070313 | 126117409 | 0.000000 | 0.000000 | 14629728
10-04-2025 1:00:10.000 | 30393273 |  | 30.3933 | -3449238 | 15613568 | 11315371 | 99362190 | 50062328 | 84385719 | 0.000000 | 0.000000 | 9831635
10-04-2025 1:00:05.000 | 30396547 |  | 30.3965 | -3626913 | 15613490 | 11324711 | 99295647 | 50060669 | 42249508 | 0.000000 | 0.000000 | 5000210
10-04-2025 1:00:00.000 | 30745377 |  | 30.7454 | -3433840 | 15614183 | 11444110 | 99382080 | 50059086 | 75026230 | 0.000000 | 0.000000 | 715840820
10-04-2025 0:59:55.000 | 31441805 |  | 31.4418 | -3347684 | 15611201 | 11698831 | 99437958 | 50062687 | 74596807 | 0.000000 | 0.000000 | 711176270
10-04-2025 0:59:50.000 | 31767289 |  | 31.7673 | -3234626 | 15609837 | 11814729 | 99485603 | 50061680 | 74155562 | 0.000000 | 0.000000 | 706478943
10-04-2025 0:59:45.000 | 30841555 |  | 30.8416 | -3409140 | 15612537 | 11479891 | 99394615 | 50076420 | 73721001 | 0.000000 | 0.000000 | 701846619
10-04-2025 0:59:40.000 | 30699375 |  | 30.6994 | -3492014 | 15612655 | 11430781 | 99359276 | 50081322 | 73292778 | 0.000000 | 0.000000 | 697088379
10-04-2025 0:59:35.000 | 29851451 |  | 29.8515 | -3506202 | 15615623 | 11117449 | 99317268 | 50096828 | 72870254 | 0.000000 | 0.000000 | 692329163
10-04-2025 0:59:30.000 | 30123762 |  | 30.1238 | -3441071 | 15613823 | 11215929 | 99353882 | 50098515 | 72454404 | 0.000000 | 0.000000 | 687510437
10-04-2025 0:59:25.000 | 31308264 |  | 31.3083 | -3500215 | 15613844 | 11653447 | 99380852 | 50087292 | 72028159 | 0.000000 | 0.000000 | 682704651
10-04-2025 0:59:20.000 | 31883408 |  | 31.8834 | -2973934 | 15610185 | 11847963 | 99567802 | 50074230 | 71590806 | 0.000000 | 0.000000 | 678011963
10-04-2025 0:59:15.000 | 28761807 |  | 28.7618 | -3227535 | 15614681 | 10706345 | 99376266 | 50148159 | 71160337 | 0.000000 | 0.000000 | 674119446
10-04-2025 0:59:10.000 | 29106443 |  | 29.1064 | -3160842 | 15616161 | 10829277 | 99415512 | 50152393 | 70763521 | 0.000000 | 0.000000 | 669687317
10-04-2025 0:59:05.000 | 31000182 |  | 31.0002 | -3232417 | 15614077 | 11530389 | 99460770 | 50113914 | 70353506 | 0.000000 | 0.000000 | 665206055
10-04-2025 0:59:00.000 | 32758199 |  | 32.7582 | -3051086 | 15610160 | 12172487 | 99569054 | 50080570 | 69908545 | 0.000000 | 0.000000 | 660831726
10-04-2025 0:58:55.000 | 32152508 |  | 32.1525 | -3043574 | 15608765 | 11951893 | 99554955 | 50101509 | 69453672 | 0.000000 | 0.000000 | 656563416
10-04-2025 0:58:50.000 | 30840740 |  | 30.8407 | -3103476 | 15610469 | 11468407 | 99497505 | 50131954 | 69014482 | 0.000000 | 0.000000 | 652220642
10-04-2025 0:58:45.000 | 29506680 |  | 29.5067 | -3417173 | 15612687 | 10988994 | 99336075 | 50157959 | 68596670 | 0.000000 | 0.000000 | 647683044
10-04-2025 0:58:40.000 | 29535988 |  | 29.536 | -3549260 | 15614000 | 11004657 | 99285721 | 50162548 | 68188330 | 0.000000 | 0.000000 | 642911743
10-04-2025 0:58:35.000 | 30102369 |  | 30.1024 | -3536640 | 15613489 | 11212520 | 99316902 | 50148670 | 67773794 | 0.000000 | 0.000000 | 638029480
10-04-2025 0:58:30.000 | 30522205 |  | 30.5222 | -3360342 | 15612411 | 11360076 | 99399406 | 50137016 | 67350171 | 0.000000 | 0.000000 | 633243652
10-04-2025 0:58:25.000 | 30091484 |  | 30.0915 | -3444096 | 15614058 | 11204519 | 99351379 | 50146473 | 66929243 | 0.000000 | 0.000000 | 628528137
10-04-2025 0:58:20.000 | 30297457 |  | 30.2975 | -3331196 | 15612460 | 11276788 | 99400978 | 50149395 | 66509702 | 0.000000 | 0.000000 | 623850769
10-04-2025 0:58:15.000 | 30224281 |  | 30.2243 | -3462195 | 15613958 | 11254209 | 99350304 | 50142139 | 66088745 | 0.000000 | 0.000000 | 619133545
10-04-2025 0:58:10.000 | 29961914 |  | 29.9619 | -3396070 | 15612943 | 11155311 | 99363754 | 50144722 | 65667783 | 0.000000 | 0.000000 | 614438599
10-04-2025 0:58:05.000 | 29236578 |  | 29.2366 | -3334751 | 15612345 | 10887063 | 99355782 | 50158695 | 65255054 | 0.000000 | 0.000000 | 609791443
10-04-2025 0:58:00.000 | 27926590 |  | 27.9266 | -3571732 | 15613642 | 10417952 | 99192017 | 50173927 | 64858223 | 0.000000 | 0.000000 | 605121399
10-04-2025 0:57:55.000 | 29087365 |  | 29.0874 | -3289241 | 15610396 | 10831187 | 99366699 | 50148117 | 64461465 | 0.000000 | 0.000000 | 600277771
10-04-2025 0:57:50.000 | 29264100 |  | 29.2641 | -3304555 | 15612402 | 10895809 | 99368469 | 50137070 | 64055737 | 0.000000 | 0.000000 | 595518677
10-04-2025 0:57:45.000 | 27954990 |  | 27.955 | -2998585 | 15611464 | 10403464 | 99429634 | 50151558 | 63656421 | 0.000000 | 0.000000 | 591072327
10-04-2025 0:57:40.000 | 26124572 |  | 26.1246 | -3059127 | 15614000 | 973152222 | 99321381 | 50174622 | 63280952 | 0.000000 | 0.000000 | 586763184
10-04-2025 0:57:35.000 | 25943125 |  | 25.9431 | -3074627 | 15619001 | 966226868 | 99305031 | 50182583 | 62920996 | 0.000000 | 0.000000 | 582489685
10-04-2025 0:57:30.000 | 28575330 |  | 28.5753 | -3018080 | 15618452 | 10626930 | 99446861 | 50111126 | 62548618 | 0.000000 | 0.000000 | 578183167
10-04-2025 0:57:25.000 | 29911230 |  | 29.9112 | -2493484 | 15612784 | 11103920 | 99654335 | 50081146 | 62138486 | 0.000000 | 0.000000 | 574557983
10-04-2025 0:57:20.000 | 29614998 |  | 29.615 | -2463570 | 15611773 | 10995234 | 99655785 | 50091618 | 61724111 | 0.000000 | 0.000000 | 571138184
10-04-2025 0:57:15.000 | 29583584 |  | 29.5836 | -2600327 | 15614194 | 10985809 | 99615921 | 50094818 | 61315923 | 0.000000 | 0.000000 | 567658752
10-04-2025 0:57:10.000 | 30559336 |  | 30.5593 | -2620542 | 15612591 | 11347411 | 99634338 | 50074390 | 60896602 | 0.000000 | 0.000000 | 564000549
10-04-2025 0:57:05.000 | 30398465 |  | 30.3985 | -2544730 | 15610940 | 11287305 | 99651443 | 50063900 | 60470952 | 0.000000 | 0.000000 | 560398438
10-04-2025 0:57:00.000 | 29053484 |  | 29.0535 | -2558598 | 15611918 | 10790653 | 99614471 | 50091343 | 60053257 | 0.000000 | 0.000000 | 556935303
10-04-2025 0:56:55.000 | 27590639 |  | 27.5906 | -2444558 | 15614917 | 10247344 | 99609787 | 50116142 | 59656157 | 0.000000 | 0.000000 | 553493713
10-04-2025 0:56:50.000 | 28347646 |  | 28.3476 | -2484610 | 15614834 | 10527208 | 99618095 | 50100422 | 59271675 | 0.000000 | 0.000000 | 550118835
10-04-2025 0:56:45.000 | 29581951 |  | 29.582 | -2514716 | 15615376 | 10982206 | 99640625 | 50069668 | 58870044 | 0.000000 | 0.000000 | 546698669
10-04-2025 0:56:40.000 | 31186926 |  | 31.1869 | -2577211 | 15612094 | 11577965 | 99660294 | 50043552 | 58449370 | 0.000000 | 0.000000 | 543276184
10-04-2025 0:56:35.000 | 31629607 |  | 31.6296 | -2611354 | 15610109 | 11742782 | 99660919 | 50046032 | 58011592 | 0.000000 | 0.000000 | 539754700
10-04-2025 0:56:30.000 | 31126699 |  | 31.1267 | -2635911 | 15610574 | 11558151 | 99643356 | 50054859 | 57572764 | 0.000000 | 0.000000 | 536122742
10-04-2025 0:56:25.000 | 29886809 |  | 29.8868 | -2534741 | 15613257 | 11096272 | 99642281 | 50074390 | 57149736 | 0.000000 | 0.000000 | 532497681
10-04-2025 0:56:20.000 | 29861953 |  | 29.862 | -2560307 | 15612366 | 11088533 | 99634460 | 50073868 | 56735444 | 0.000000 | 0.000000 | 528812622
10-04-2025 0:56:15.000 | 29527660 |  | 29.5277 | -2525004 | 15612832 | 10963994 | 99636368 | 50088688 | 56322524 | 0.000000 | 0.000000 | 525312561
10-04-2025 0:56:10.000 | 29763309 |  | 29.7633 | -2476168 | 15615113 | 11047499 | 99655716 | 50081955 | 55912505 | 0.000000 | 0.000000 | 521750549
10-04-2025 0:56:05.000 | 30543896 |  | 30.5439 | -2661094 | 15615465 | 11341841 | 99622620 | 50075317 | 55495088 | 0.000000 | 0.000000 | 518208069
10-04-2025 0:56:00.000 | 32183846 |  | 32.1838 | -2592889 | 15612306 | 11945358 | 99677032 | 50047756 | 55060864 | 0.000000 | 0.000000 | 514496338
10-04-2025 0:55:55.000 | 31369521 |  | 31.3695 | -2707589 | 15610534 | 11649836 | 99629578 | 50071396 | 54618364 | 0.000000 | 0.000000 | 510971497
10-04-2025 0:55:50.000 | 31144527 |  | 31.1445 | -2699709 | 15613581 | 11564501 | 99626404 | 50071732 | 54183442 | 0.000000 | 0.000000 | 507055298
10-04-2025 0:55:45.000 | 30062814 |  | 30.0628 | -2624724 | 15612891 | 11164342 | 99621033 | 50092419 | 53755449 | 0.000000 | 0.000000 | 503332153
10-04-2025 0:55:40.000 | 29946303 |  | 29.9463 | -2603107 | 15612773 | 11120641 | 99624321 | 50104034 | 53340996 | 0.000000 | 0.000000 | 499621826
10-04-2025 0:55:35.000 | 30088170 |  | 30.0882 | -2812473 | 15616441 | 11177418 | 99565971 | 50101334 | 52928418 | 0.000000 | 0.000000 | 495813049
10-04-2025 0:55:30.000 | 31352428 |  | 31.3524 | -2785537 | 15611825 | 11645344 | 99607643 | 50074123 | 52503159 | 0.000000 | 0.000000 | 491965759
10-04-2025 0:55:25.000 | 31186922 |  | 31.1869 | -2726818 | 15611411 | 11582983 | 99619934 | 50072289 | 52067520 | 0.000000 | 0.000000 | 488196014
10-04-2025 0:55:20.000 | 30425688 |  | 30.4257 | -2682700 | 15610413 | 11301136 | 99613533 | 50079231 | 51635718 | 0.000000 | 0.000000 | 484420563
10-04-2025 0:55:15.000 | 29839102 |  | 29.8391 | -2672257 | 15611900 | 11084083 | 99601387 | 50094738 | 51213545 | 0.000000 | 0.000000 | 480680878
10-04-2025 0:55:10.000 | 28576277 |  | 28.5763 | -2801844 | 15613231 | 10622533 | 99522766 | 50114326 | 50808203 | 0.000000 | 0.000000 | 476965454
10-04-2025 0:55:05.000 | 29039035 |  | 29.039 | -2868010 | 15613283 | 10795253 | 99515823 | 50087296 | 50408940 | 0.000000 | 0.000000 | 473006287
10-04-2025 0:55:00.000 | 28482686 |  | 28.4827 | -2618561 | 15613964 | 10581714 | 99580055 | 50080776 | 50007051 | 0.000000 | 0.000000 | 469237976
10-04-2025 0:54:55.000 | 29086500 |  | 29.0865 | -2769059 | 15612660 | 10809812 | 99549896 | 50072987 | 49610752 | 0.000000 | 0.000000 | 465479553
10-04-2025 0:54:50.000 | 29667477 |  | 29.6675 | -2907540 | 15614063 | 11027297 | 99523193 | 50063625 | 49203936 | 0.000000 | 0.000000 | 461595337
10-04-2025 0:54:45.000 | 30648033 |  | 30.648 | -2759773 | 15611711 | 11385070 | 99597023 | 50046124 | 48786572 | 0.000000 | 0.000000 | 457760590
10-04-2025 0:54:40.000 | 31728447 |  | 31.7284 | -2860550 | 15608425 | 11788748 | 99596046 | 50033497 | 48355181 | 0.000000 | 0.000000 | 453816315
10-04-2025 0:54:35.000 | 31370533 |  | 31.3705 | -2948637 | 15610781 | 11658514 | 99561165 | 50049484 | 47914922 | 0.000000 | 0.000000 | 449805969
10-04-2025 0:54:30.000 | 30379518 |  | 30.3795 | -2873890 | 15611899 | 11290193 | 99555527 | 50069763 | 47484004 | 0.000000 | 0.000000 | 445735199
10-04-2025 0:54:25.000 | 29420547 |  | 29.4205 | -3071652 | 15613522 | 10943406 | 99459396 | 50090221 | 47070015 | 0.000000 | 0.000000 | 441641815
10-04-2025 0:54:20.000 | 29632332 |  | 29.6323 | -3089742 | 15613096 | 11022069 | 99460785 | 50084644 | 46658687 | 0.000000 | 0.000000 | 437511200
10-04-2025 0:54:15.000 | 30041744 |  | 30.0417 | -2934579 | 15611694 | 11168145 | 99526283 | 50080181 | 46245464 | 0.000000 | 0.000000 | 433280670
10-04-2025 0:54:10.000 | 30433352 |  | 30.4334 | -3127832 | 15611160 | 11322251 | 99475998 | 50076054 | 45827915 | 0.000000 | 0.000000 | 429064545
10-04-2025 0:54:05.000 | 30657207 |  | 30.6572 | -2905995 | 15611070 | 11393674 | 99553749 | 50063126 | 45403662 | 0.000000 | 0.000000 | 424758789
10-04-2025 0:54:00.000 | 29999766 |  | 29.9998 | -2805226 | 15611485 | 11148571 | 99565659 | 50067852 | 44980684 | 0.000000 | 0.000000 | 420665833
10-04-2025 0:53:55.000 | 28753469 |  | 28.7535 | -2846877 | 15612547 | 10690100 | 99513428 | 50092258 | 44571499 | 0.000000 | 0.000000 | 416744995
10-04-2025 0:53:50.000 | 28640813 |  | 28.6408 | -2913646 | 15614952 | 10649149 | 99486526 | 50096958 | 44174971 | 0.000000 | 0.000000 | 412877167
10-04-2025 0:53:45.000 | 30340021 |  | 30.34 | -3052052 | 15612697 | 11282021 | 99497841 | 50063671 | 43769004 | 0.000000 | 0.000000 | 408749481
10-04-2025 0:53:40.000 | 30711557 |  | 30.7116 | -2722658 | 15612037 | 11407411 | 99609337 | 50048302 | 43343198 | 0.000000 | 0.000000 | 404650787
10-04-2025 0:53:35.000 | 29740988 |  | 29.741 | -2772372 | 15612420 | 11050834 | 99568336 | 50064377 | 42921372 | 0.000000 | 0.000000 | 400830811
10-04-2025 0:53:30.000 | 29323527 |  | 29.3235 | -2720767 | 15613810 | 10894584 | 99572311 | 50077385 | 42513799 | 0.000000 | 0.000000 | 397050049
10-04-2025 0:53:25.000 | 29589234 |  | 29.5892 | -2728695 | 15615083 | 10991797 | 99577477 | 50074646 | 42105386 | 0.000000 | 0.000000 | 393193848
10-04-2025 0:53:20.000 | 29686111 |  | 29.6861 | -2730431 | 15612717 | 11029016 | 99579681 | 50070011 | 41694448 | 0.000000 | 0.000000 | 389382477
10-04-2025 0:53:15.000 | 29948287 |  | 29.9483 | -2728093 | 15612755 | 11125464 | 99587662 | 50065613 | 41279316 | 0.000000 | 0.000000 | 385585327
10-04-2025 0:53:10.000 | 30243559 |  | 30.2436 | -2774410 | 15613885 | 11234453 | 99581863 | 50065559 | 40860063 | 0.000000 | 0.000000 | 381742920
10-04-2025 0:53:05.000 | 31554191 |  | 31.5542 | -2937814 | 15613421 | 11724116 | 99569382 | 50047794 | 40434995 | 0.000000 | 0.000000 | 377746460
10-04-2025 0:53:00.000 | 32128422 |  | 32.1284 | -2952317 | 15609174 | 11938851 | 99580460 | 50046825 | 39991995 | 0.000000 | 0.000000 | 373730835
10-04-2025 0:52:55.000 | 32124889 |  | 32.1249 | -2911440 | 15608367 | 11936267 | 99591835 | 50057526 | 39546018 | 0.000000 | 0.000000 | 369535645
10-04-2025 0:52:50.000 | 29638086 |  | 29.6381 | -3011938 | 15613033 | 11020261 | 99487595 | 50100731 | 39114458 | 0.000000 | 0.000000 | 365467407
10-04-2025 0:52:45.000 | 28755395 |  | 28.7554 | -3062096 | 15612795 | 10698715 | 99437798 | 50110535 | 38709263 | 0.000000 | 0.000000 | 361287903
10-04-2025 0:52:40.000 | 27990418 |  | 27.9904 | -3053958 | 15613506 | 10416971 | 99410042 | 50115784 | 38314805 | 0.000000 | 0.000000 | 356982666
10-04-2025 0:52:35.000 | 28786736 |  | 28.7867 | -3027696 | 15614058 | 10709119 | 99451439 | 50095356 | 37923289 | 0.000000 | 0.000000 | 352751068
10-04-2025 0:52:30.000 | 29381771 |  | 29.3818 | -3079525 | 15613203 | 10929692 | 99455223 | 50077454 | 37519136 | 0.000000 | 0.000000 | 348550568
10-04-2025 0:52:25.000 | 28911086 |  | 28.9111 | -2896454 | 15611457 | 10750895 | 99501892 | 50068863 | 37110178 | 0.000000 | 0.000000 | 344354614
10-04-2025 0:52:20.000 | 27783586 |  | 27.7836 | -2862763 | 15615077 | 10332681 | 99473351 | 50096416 | 36711968 | 0.000000 | 0.000000 | 340456238
10-04-2025 0:52:15.000 | 27778115 |  | 27.7781 | -2676774 | 15615699 | 10323531 | 99538918 | 50077438 | 36328645 | 0.000000 | 0.000000 | 336557373
10-04-2025 0:52:10.000 | 29090941 |  | 29.0909 | -2791729 | 15613462 | 10812939 | 99542686 | 50057671 | 35936765 | 0.000000 | 0.000000 | 332799225
10-04-2025 0:52:05.000 | 29285912 |  | 29.2859 | -2532274 | 15613801 | 10874099 | 99628250 | 50042633 | 35529465 | 0.000000 | 0.000000 | 329128845
10-04-2025 0:52:00.000 | 29098473 |  | 29.0985 | -2550240 | 15612829 | 10806587 | 99618149 | 50043697 | 35123262 | 0.000000 | 0.000000 | 325618744
10-04-2025 0:51:55.000 | 28982484 |  | 28.9825 | -2588194 | 15612474 | 10765338 | 99603630 | 50049469 | 34721719 | 0.000000 | 0.000000 | 322028290
10-04-2025 0:51:50.000 | 29277434 |  | 29.2774 | -2499152 | 15610700 | 10872861 | 99637657 | 50053860 | 34320183 | 0.000000 | 0.000000 | 318473877
10-04-2025 0:51:45.000 | 29452385 |  | 29.4524 | -2664869 | 15614722 | 10939067 | 99593163 | 50038872 | 33914849 | 0.000000 | 0.000000 | 314796997
10-04-2025 0:51:40.000 | 29226660 |  | 29.2267 | -2387585 | 15612383 | 10849685 | 99667984 | 50041481 | 33505093 | 0.000000 | 0.000000 | 311322540
10-04-2025 0:51:35.000 | 29103305 |  | 29.1033 | -2477368 | 15613610 | 10805249 | 99639656 | 50053387 | 33100991 | 0.000000 | 0.000000 | 307998108
10-04-2025 0:51:30.000 | 30082566 |  | 30.0826 | -2515295 | 15614316 | 11166731 | 99652267 | 50039101 | 32693096 | 0.000000 | 0.000000 | 304452911
10-04-2025 0:51:25.000 | 31384688 |  | 31.3847 | -2490134 | 15611801 | 11648372 | 99686722 | 50024422 | 32268669 | 0.000000 | 0.000000 | 300995300
10-04-2025 0:51:20.000 | 31653945 |  | 31.6539 | -2477725 | 15609522 | 11748937 | 99695045 | 50017525 | 31829917 | 0.000000 | 0.000000 | 297454102
10-04-2025 0:51:15.000 | 29941980 |  | 29.942 | -2345336 | 15611926 | 11111293 | 99694633 | 50050632 | 31399126 | 0.000000 | 0.000000 | 294090637
10-04-2025 0:51:10.000 | 28181422 |  | 28.1814 | -2554832 | 15614957 | 10467946 | 99591583 | 50074467 | 30994724 | 0.000000 | 0.000000 | 290853943
10-04-2025 0:51:05.000 | 29597777 |  | 29.5978 | -2284485 | 15612540 | 10983381 | 99703453 | 50061806 | 30594470 | 0.000000 | 0.000000 | 287422241
10-04-2025 0:51:00.000 | 30196641 |  | 30.1966 | -2329066 | 15612453 | 11204734 | 99703873 | 50045818 | 30183162 | 0.000000 | 0.000000 | 284120544
10-04-2025 0:50:55.000 | 30124453 |  | 30.1245 | -2348062 | 15612823 | 11179019 | 99697601 | 50039150 | 29762637 | 0.000000 | 0.000000 | 280866730
10-04-2025 0:50:50.000 | 30045029 |  | 30.045 | -2383839 | 15613020 | 11150085 | 99686722 | 50043236 | 29343958 | 0.000000 | 0.000000 | 277606720
10-04-2025 0:50:45.000 | 30147180 |  | 30.1472 | -2531754 | 15610502 | 11195037 | 99649223 | 50046276 | 28927041 | 0.000000 | 0.000000 | 274172119
10-04-2025 0:50:40.000 | 30002129 |  | 30.0021 | -2393651 | 15613081 | 11135421 | 99683250 | 50038994 | 28508831 | 0.000000 | 0.000000 | 270717865
10-04-2025 0:50:35.000 | 28770982 |  | 28.771 | -2426749 | 15612126 | 10683262 | 99646164 | 50068645 | 28098589 | 0.000000 | 0.000000 | 267481689
10-04-2025 0:50:30.000 | 28844188 |  | 28.8442 | -2613719 | 15614983 | 10713533 | 99591957 | 50070850 | 27701599 | 0.000000 | 0.000000 | 264010712
10-04-2025 0:50:25.000 | 29973422 |  | 29.9734 | -2466593 | 15613192 | 11126361 | 99663109 | 50054142 | 27295261 | 0.000000 | 0.000000 | 260461578
10-04-2025 0:50:20.000 | 30354230 |  | 30.3542 | -2561489 | 15613257 | 11269440 | 99645836 | 50044460 | 26877363 | 0.000000 | 0.000000 | 256993286
10-04-2025 0:50:15.000 | 31515279 |  | 31.5153 | -2637315 | 15612138 | 11699535 | 99651680 | 50029716 | 26448809 | 0.000000 | 0.000000 | 253403564
10-04-2025 0:50:10.000 | 31014207 |  | 31.0142 | -2391381 | 15608635 | 11510693 | 99704056 | 50032021 | 26009570 | 0.000000 | 0.000000 | 249857208
10-04-2025 0:50:05.000 | 29469383 |  | 29.4694 | -2587247 | 15612566 | 10944795 | 99616821 | 50066299 | 25588704 | 0.000000 | 0.000000 | 246486450
10-04-2025 0:50:00.000 | 29254436 |  | 29.2544 | -2710237 | 15613093 | 10869459 | 99573601 | 50075703 | 25180173 | 0.000000 | 0.000000 | 242830444
10-04-2025 0:49:55.000 | 29600178 |  | 29.6002 | -2324613 | 15612310 | 10985553 | 99693039 | 50067375 | 24771863 | 0.000000 | 0.000000 | 239170959
10-04-2025 0:49:50.000 | 29694529 |  | 29.6945 | -2525013 | 15615201 | 11023709 | 99640419 | 50072075 | 24362905 | 0.000000 | 0.000000 | 235703079
10-04-2025 0:49:45.000 | 30383313 |  | 30.3833 | -2463499 | 15615502 | 11275632 | 99672905 | 50064735 | 23946619 | 0.000000 | 0.000000 | 232250916
10-04-2025 0:49:40.000 | 31660070 |  | 31.6601 | -2530742 | 15612156 | 11751877 | 99682045 | 50044495 | 23518687 | 0.000000 | 0.000000 | 228779312
10-04-2025 0:49:35.000 | 32577787 |  | 32.5778 | -2396512 | 15609723 | 12085697 | 99730522 | 50028088 | 23072664 | 0.000000 | 0.000000 | 225273224
10-04-2025 0:49:30.000 | 31476195 |  | 31.4762 | -2496357 | 15612365 | 11681526 | 99686974 | 50064362 | 22623999 | 0.000000 | 0.000000 | 221907578
10-04-2025 0:49:25.000 | 30203475 |  | 30.2035 | -2740219 | 15613497 | 11220383 | 99590973 | 50094826 | 22194724 | 0.000000 | 0.000000 | 218405731
10-04-2025 0:49:20.000 | 30941619 |  | 30.9416 | -2665082 | 15613480 | 11488843 | 99631111 | 50075966 | 21772185 | 0.000000 | 0.000000 | 214618881
10-04-2025 0:49:15.000 | 30851650 |  | 30.8516 | -3099117 | 15611796 | 11472650 | 99499252 | 50084301 | 21340620 | 0.000000 | 0.000000 | 210857956
10-04-2025 0:49:10.000 | 30935320 |  | 30.9353 | -2797022 | 15612695 | 11492517 | 99593742 | 50071732 | 20909883 | 0.000000 | 0.000000 | 206660919
10-04-2025 0:49:05.000 | 30679500 |  | 30.6795 | -2855005 | 15609547 | 11401733 | 99569794 | 50087391 | 20483379 | 0.000000 | 0.000000 | 202805588
10-04-2025 0:49:00.000 | 29813189 |  | 29.8132 | -2693225 | 15612257 | 11074503 | 99594444 | 50092773 | 20062504 | 0.000000 | 0.000000 | 198895859
10-04-2025 0:48:55.000 | 28833855 |  | 28.8339 | -2807656 | 15614134 | 10718916 | 99529266 | 50108906 | 19654427 | 0.000000 | 0.000000 | 195183975
10-04-2025 0:48:50.000 | 28913648 |  | 28.9136 | -2718555 | 15616244 | 10743168 | 99560890 | 50101936 | 19256580 | 0.000000 | 0.000000 | 191206299
10-04-2025 0:48:45.000 | 29662078 |  | 29.6621 | -2994534 | 15615301 | 11028621 | 99494270 | 50097088 | 18850646 | 0.000000 | 0.000000 | 187461441
10-04-2025 0:48:40.000 | 31904230 |  | 31.9042 | -2839242 | 15610341 | 11850876 | 99606354 | 50055332 | 18423392 | 0.000000 | 0.000000 | 183363205
10-04-2025 0:48:35.000 | 31651854 |  | 31.6519 | -2858794 | 15609120 | 11760311 | 99594597 | 50059776 | 17980626 | 0.000000 | 0.000000 | 179368225
10-04-2025 0:48:30.000 | 30493045 |  | 30.493 | -2955565 | 15609066 | 11336844 | 99533554 | 50095375 | 17548889 | 0.000000 | 0.000000 | 175262848
10-04-2025 0:48:25.000 | 29058641 |  | 29.0586 | -2832461 | 15612752 | 10802727 | 99528297 | 50112953 | 17135015 | 0.000000 | 0.000000 | 171016800
10-04-2025 0:48:20.000 | 28085994 |  | 28.086 | -3058857 | 15615889 | 10450533 | 99412148 | 50132481 | 16739054 | 0.000000 | 0.000000 | 166972076
10-04-2025 0:48:15.000 | 29981777 |  | 29.9818 | -3079610 | 15615753 | 11148575 | 99476608 | 50093563 | 16340487 | 0.000000 | 0.000000 | 162671387
10-04-2025 0:48:10.000 | 32443809 |  | 32.4438 | -3015699 | 15609367 | 12057028 | 99570778 | 50055786 | 15909210 | 0.000000 | 0.000000 | 158404678
10-04-2025 0:48:05.000 | 32232803 |  | 32.2328 | -2938006 | 15608576 | 11978010 | 99587158 | 50057152 | 15458126 | 0.000000 | 0.000000 | 154238998
10-04-2025 0:48:00.000 | 30408164 |  | 30.4082 | -3006022 | 15610546 | 11306561 | 99514931 | 50097733 | 15021567 | 0.000000 | 0.000000 | 150041885
10-04-2025 0:47:55.000 | 29094338 |  | 29.0943 | -3216572 | 15614373 | 10827760 | 99394409 | 50122360 | 14606063 | 0.000000 | 0.000000 | 145806412
10-04-2025 0:47:50.000 | 28963625 |  | 28.9636 | -2816439 | 15612960 | 10766669 | 99530540 | 50111191 | 14202997 | 0.000000 | 0.000000 | 141401932
10-04-2025 0:47:45.000 | 28241559 |  | 28.2416 | -2787263 | 15616598 | 10497070 | 99516510 | 50124741 | 13806180 | 0.000000 | 0.000000 | 137496002
10-04-2025 0:47:40.000 | 29733480 |  | 29.7335 | -2866851 | 15614577 | 11050325 | 99538391 | 50097401 | 13410197 | 0.000000 | 0.000000 | 133520233
10-04-2025 0:47:35.000 | 31675213 |  | 31.6752 | -2803386 | 15611848 | 11765055 | 99610634 | 50056404 | 12986649 | 0.000000 | 0.000000 | 129504852
10-04-2025 0:47:30.000 | 31360568 |  | 31.3606 | -2841122 | 15609284 | 11652087 | 99592133 | 50069462 | 12545934 | 0.000000 | 0.000000 | 125705711
10-04-2025 0:47:25.000 | 30528984 |  | 30.529 | -2804549 | 15612123 | 11342554 | 99580688 | 50083004 | 12117056 | 0.000000 | 0.000000 | 121629440
10-04-2025 0:47:20.000 | 28379270 |  | 28.3793 | -3104632 | 15615361 | 10561219 | 99406921 | 50125084 | 11706383 | 0.000000 | 0.000000 | 117736046
10-04-2025 0:47:15.000 | 29764023 |  | 29.764 | -2701858 | 15615842 | 11054913 | 99590515 | 50103519 | 11304602 | 0.000000 | 0.000000 | 113756828
10-04-2025 0:47:10.000 | 31544389 |  | 31.5444 | -2721662 | 15611836 | 11713333 | 99629852 | 50070530 | 10881102 | 0.000000 | 0.000000 | 109916687
10-04-2025 0:47:05.000 | 31828926 |  | 31.8289 | -2657724 | 15609863 | 11818683 | 99653198 | 50074505 | 10439264 | 0.000000 | 0.000000 | 106156418
10-04-2025 0:47:00.000 | 30201631 |  | 30.2016 | -2748998 | 15610900 | 11221034 | 99588310 | 50110043 | 10003998 | 0.000000 | 0.000000 | 102519676
10-04-2025 0:46:55.000 | 29757213 |  | 29.7572 | -2738007 | 15614699 | 11054208 | 99579361 | 50121071 | 958858337 | 0.000000 | 0.000000 | 98660591
10-04-2025 0:46:50.000 | 29424904 |  | 29.4249 | -2825298 | 15614142 | 10935033 | 99542198 | 50125423 | 917769226 | 0.000000 | 0.000000 | 94883644
10-04-2025 0:46:45.000 | 29861971 |  | 29.862 | -2810538 | 15614201 | 11095454 | 99560013 | 50124290 | 876605164 | 0.000000 | 0.000000 | 91031403
10-04-2025 0:46:40.000 | 30149643 |  | 30.1496 | -3004315 | 15614108 | 11208502 | 99507195 | 50121189 | 835046387 | 0.000000 | 0.000000 | 87009270
10-04-2025 0:46:35.000 | 31786234 |  | 31.7862 | -2959763 | 15611268 | 11811212 | 99569283 | 50093243 | 791897888 | 0.000000 | 0.000000 | 82901848
10-04-2025 0:46:30.000 | 32102957 |  | 32.103 | -3087572 | 15610462 | 11932459 | 99540680 | 50101971 | 747422729 | 0.000000 | 0.000000 | 78846626
10-04-2025 0:46:25.000 | 30468242 |  | 30.4682 | -2918833 | 15609159 | 11326581 | 99544258 | 50130451 | 703424988 | 0.000000 | 0.000000 | 74708130
10-04-2025 0:46:20.000 | 29023639 |  | 29.0236 | -2906779 | 15612423 | 10791709 | 99502220 | 50156811 | 662020325 | 0.000000 | 0.000000 | 70544670
10-04-2025 0:46:15.000 | 28267447 |  | 28.2674 | -3132655 | 15614201 | 10521340 | 99391525 | 50168427 | 622588135 | 0.000000 | 0.000000 | 66347351
10-04-2025 0:46:10.000 | 28943904 |  | 28.9439 | -2943592 | 15614200 | 10762310 | 99486832 | 50149380 | 582940613 | 0.000000 | 0.000000 | 62155682
10-04-2025 0:46:05.000 | 29598371 |  | 29.5984 | -2777398 | 15613342 | 10999147 | 99562622 | 50138187 | 542095154 | 0.000000 | 0.000000 | 58174507
10-04-2025 0:46:00.000 | 30620662 |  | 30.6207 | -2847929 | 15613009 | 11376560 | 99570274 | 50123585 | 500432312 | 0.000000 | 0.000000 | 54185879
10-04-2025 0:45:55.000 | 30634154 |  | 30.6342 | -2728246 | 15611162 | 11379111 | 99605766 | 50113922 | 457931854 | 0.000000 | 0.000000 | 50237762
10-04-2025 0:45:50.000 | 29986711 |  | 29.9867 | -2780348 | 15613487 | 11140519 | 99572906 | 50126419 | 415444183 | 0.000000 | 0.000000 | 46436989
10-04-2025 0:45:45.000 | 30165916 |  | 30.1659 | -2867511 | 15612902 | 11210975 | 99551239 | 50132946 | 373643280 | 0.000000 | 0.000000 | 42554436
10-04-2025 0:45:40.000 | 30985521 |  | 30.9855 | -3118890 | 15611114 | 11522776 | 99497231 | 50118481 | 331425659 | 0.000000 | 0.000000 | 38348503
10-04-2025 0:45:35.000 | 31927557 |  | 31.9276 | -3122923 | 15608807 | 11870841 | 99525040 | 50101025 | 287355133 | 0.000000 | 0.000000 | 33980854
10-04-2025 0:45:30.000 | 29752307 |  | 29.7523 | -3205133 | 15607981 | 11074479 | 99424744 | 50161934 | 244141953 | 0.000000 | 0.000000 | 29770073
10-04-2025 0:45:25.000 | 29326914 |  | 29.3269 | -3662562 | 15612554 | 10933944 | 99229164 | 50170048 | 203548325 | 0.000000 | 0.000000 | 24950590
10-04-2025 0:45:20.000 | 30478965 |  | 30.479 | -3724729 | 15612781 | 11359089 | 99261536 | 50138409 | 162004013 | 0.000000 | 0.000000 | 19752203
10-04-2025 0:45:15.000 | 30465037 |  | 30.465 | -3358168 | 15611214 | 11339521 | 99397949 | 50137154 | 119375969 | 0.000000 | 0.000000 | 14803961
10-04-2025 0:45:10.000 | 28188721 |  | 28.1887 | -3362014 | 15614214 | 10501617 | 99296257 | 50175835 | 78511612 | 0.000000 | 0.000000 | 10066929
10-04-2025 0:45:05.000 | 27868541 |  | 27.8685 | -3670526 | 15617287 | 10396698 | 99143768 | 50185764 | 40059464 | 0.000000 | 0.000000 | 5241637
10-04-2025 0:45:00.000 | 30587730 |  | 30.5877 | -3723266 | 15613342 | 11398972 | 99267296 | 50119587 | 74446816 | 0.000000 | 0.000000 | 645277039
10-04-2025 0:44:55.000 | 31465990 |  | 31.466 | -3502704 | 15608412 | 11715253 | 99386124 | 50100380 | 74010430 | 0.000000 | 0.000000 | 640205139
10-04-2025 0:44:50.000 | 29180230 |  | 29.1802 | -3301214 | 15610413 | 10865718 | 99366135 | 50136353 | 73585586 | 0.000000 | 0.000000 | 635332947
10-04-2025 0:44:45.000 | 26692465 |  | 26.6925 | -3362598 | 15613428 | 995441284 | 99215828 | 50181179 | 73195229 | 0.000000 | 0.000000 | 630746155
10-04-2025 0:44:40.000 | 26821770 |  | 26.8218 | -3260034 | 15618306 | 999294495 | 99269432 | 50171986 | 72826494 | 0.000000 | 0.000000 | 625986389
10-04-2025 0:44:35.000 | 28278449 |  | 28.2784 | -3186721 | 15617815 | 10524701 | 99371025 | 50142433 | 72448970 | 0.000000 | 0.000000 | 621453979
10-04-2025 0:44:30.000 | 30188934 |  | 30.1889 | -2907841 | 15612232 | 11220858 | 99539314 | 50105541 | 72044395 | 0.000000 | 0.000000 | 617348145
10-04-2025 0:44:25.000 | 32088012 |  | 32.088 | -2967430 | 15611680 | 11922406 | 99575119 | 50066364 | 71613555 | 0.000000 | 0.000000 | 613129089
10-04-2025 0:44:20.000 | 31353393 |  | 31.3534 | -2901883 | 15609213 | 11651108 | 99574417 | 50089767 | 71169531 | 0.000000 | 0.000000 | 609053772
10-04-2025 0:44:15.000 | 30032887 |  | 30.0329 | -2946138 | 15612043 | 11164083 | 99522293 | 50112377 | 70741802 | 0.000000 | 0.000000 | 604922241
10-04-2025 0:44:10.000 | 28528262 |  | 28.5283 | -3009199 | 15615780 | 10611699 | 99448288 | 50136898 | 70333296 | 0.000000 | 0.000000 | 600802368
10-04-2025 0:44:05.000 | 28748328 |  | 28.7483 | -2987638 | 15615779 | 10691132 | 99464325 | 50130306 | 69936089 | 0.000000 | 0.000000 | 596668518
10-04-2025 0:44:00.000 | 30042279 |  | 30.0423 | -2841046 | 15614058 | 11163356 | 99555817 | 50109268 | 69528857 | 0.000000 | 0.000000 | 592631775
10-04-2025 0:43:55.000 | 30868635 |  | 30.8686 | -2868432 | 15612479 | 11468767 | 99571037 | 50092991 | 69107075 | 0.000000 | 0.000000 | 588757813
10-04-2025 0:43:50.000 | 31675635 |  | 31.6756 | -2895099 | 15612745 | 11766515 | 99584915 | 50089581 | 68670137 | 0.000000 | 0.000000 | 584717834
10-04-2025 0:43:45.000 | 30824199 |  | 30.8242 | -2807385 | 15609477 | 11452859 | 99587807 | 50100910 | 68235073 | 0.000000 | 0.000000 | 580709351
10-04-2025 0:43:40.000 | 29988186 |  | 29.9882 | -3021603 | 15611841 | 11151854 | 99496208 | 50128574 | 67814395 | 0.000000 | 0.000000 | 576651733
10-04-2025 0:43:35.000 | 29245561 |  | 29.2456 | -3002822 | 15613078 | 10876173 | 99477013 | 50130169 | 67403530 | 0.000000 | 0.000000 | 572435059
10-04-2025 0:43:30.000 | 28792379 |  | 28.7924 | -2712661 | 15613994 | 10698387 | 99559113 | 50131245 | 67000552 | 0.000000 | 0.000000 | 568480591
10-04-2025 0:43:25.000 | 29304996 |  | 29.305 | -3054873 | 15614621 | 10899550 | 99461044 | 50119461 | 66599312 | 0.000000 | 0.000000 | 564496277
10-04-2025 0:43:20.000 | 30092072 |  | 30.0921 | -2889436 | 15614028 | 11183257 | 99542175 | 50090538 | 66184585 | 0.000000 | 0.000000 | 560297546
10-04-2025 0:43:15.000 | 29257455 |  | 29.2575 | -2716585 | 15613024 | 10871537 | 99571701 | 50112953 | 65766309 | 0.000000 | 0.000000 | 556471252
10-04-2025 0:43:10.000 | 28238900 |  | 28.2389 | -2905479 | 15615426 | 10500306 | 99474854 | 50126404 | 65367749 | 0.000000 | 0.000000 | 552633728
10-04-2025 0:43:05.000 | 29475652 |  | 29.4757 | -2766814 | 15613651 | 10952787 | 99562332 | 50106728 | 64966890 | 0.000000 | 0.000000 | 548744141
10-04-2025 0:43:00.000 | 30619473 |  | 30.6195 | -2841034 | 15614627 | 11374928 | 99572304 | 50084171 | 64552544 | 0.000000 | 0.000000 | 544832458
10-04-2025 0:42:55.000 | 30983363 |  | 30.9834 | -2805938 | 15611617 | 11509589 | 99592422 | 50086319 | 64120356 | 0.000000 | 0.000000 | 540993652
10-04-2025 0:42:50.000 | 30758959 |  | 30.759 | -2914073 | 15612457 | 11429907 | 99554222 | 50081795 | 63690972 | 0.000000 | 0.000000 | 537047974
10-04-2025 0:42:45.000 | 30905039 |  | 30.905 | -2875901 | 15611039 | 11483645 | 99569817 | 50084091 | 63261714 | 0.000000 | 0.000000 | 533042358
10-04-2025 0:42:40.000 | 29932842 |  | 29.9328 | -2767997 | 15611082 | 11121595 | 99575157 | 50100632 | 62837231 | 0.000000 | 0.000000 | 529185486
10-04-2025 0:42:35.000 | 29021461 |  | 29.0215 | -2802219 | 15613377 | 10786078 | 99537071 | 50113167 | 62427739 | 0.000000 | 0.000000 | 525339966
10-04-2025 0:42:30.000 | 28252867 |  | 28.2529 | -2729744 | 15612823 | 10502246 | 99536491 | 50120846 | 62028823 | 0.000000 | 0.000000 | 521554016
10-04-2025 0:42:25.000 | 28905945 |  | 28.9059 | -2571503 | 15613025 | 10736044 | 99606628 | 50104115 | 61633105 | 0.000000 | 0.000000 | 517812500
10-04-2025 0:42:20.000 | 29216678 |  | 29.2167 | -2538450 | 15612986 | 10849823 | 99624687 | 50104401 | 61230742 | 0.000000 | 0.000000 | 514203552
10-04-2025 0:42:15.000 | 30071566 |  | 30.0716 | -2538372 | 15614111 | 11163379 | 99645630 | 50094193 | 60820986 | 0.000000 | 0.000000 | 510587494
10-04-2025 0:42:10.000 | 31475176 |  | 31.4752 | -2729639 | 15611464 | 11688704 | 99626060 | 50065506 | 60397979 | 0.000000 | 0.000000 | 506860016
10-04-2025 0:42:05.000 | 31698762 |  | 31.6988 | -2578019 | 15610232 | 11766936 | 99670914 | 50060383 | 59957334 | 0.000000 | 0.000000 | 503050995
10-04-2025 0:42:00.000 | 29735848 |  | 29.7358 | -2484831 | 15612700 | 11039357 | 99652672 | 50101936 | 59526543 | 0.000000 | 0.000000 | 499477478
10-04-2025 0:41:55.000 | 28554482 |  | 28.5545 | -2613575 | 15613250 | 10608281 | 99583733 | 50117027 | 59126567 | 0.000000 | 0.000000 | 495920929
10-04-2025 0:41:50.000 | 28931031 |  | 28.931 | -2568209 | 15612192 | 10745803 | 99608307 | 50103699 | 58730786 | 0.000000 | 0.000000 | 492224518
10-04-2025 0:41:45.000 | 29596631 |  | 29.5966 | -2233288 | 15611466 | 10982708 | 99716515 | 50086796 | 58324629 | 0.000000 | 0.000000 | 488693726
10-04-2025 0:41:40.000 | 29273648 |  | 29.2736 | -2391548 | 15613449 | 10865327 | 99667946 | 50097485 | 57916025 | 0.000000 | 0.000000 | 485477539
10-04-2025 0:41:35.000 | 30260266 |  | 30.2603 | -2363991 | 15612325 | 11229146 | 99696236 | 50078274 | 57505894 | 0.000000 | 0.000000 | 482096191
10-04-2025 0:41:30.000 | 30239621 |  | 30.2396 | -2376586 | 15611778 | 11222346 | 99692589 | 50074661 | 57082505 | 0.000000 | 0.000000 | 478821747
10-04-2025 0:41:25.000 | 29901895 |  | 29.9019 | -2255068 | 15612097 | 11093904 | 99716835 | 50072754 | 56662251 | 0.000000 | 0.000000 | 475589325
10-04-2025 0:41:20.000 | 29694484 |  | 29.6945 | -2416623 | 15612859 | 11022313 | 99670479 | 50093979 | 56247515 | 0.000000 | 0.000000 | 472420380
10-04-2025 0:41:15.000 | 30267262 |  | 30.2673 | -2423023 | 15614574 | 11231936 | 99681099 | 50079277 | 55832773 | 0.000000 | 0.000000 | 469030334
10-04-2025 0:41:10.000 | 30665992 |  | 30.666 | -2222293 | 15612497 | 11374574 | 99738449 | 50062347 | 55409536 | 0.000000 | 0.000000 | 465766785
10-04-2025 0:41:05.000 | 30065471 |  | 30.0655 | -2158171 | 15613302 | 11150889 | 99743355 | 50081188 | 54986138 | 0.000000 | 0.000000 | 462709442
10-04-2025 0:41:00.000 | 29712715 |  | 29.7127 | -2358340 | 15614611 | 11025643 | 99686493 | 50089233 | 54571514 | 0.000000 | 0.000000 | 459664856
10-04-2025 0:40:55.000 | 31123979 |  | 31.124 | -2344210 | 15613116 | 11546376 | 99717560 | 50074059 | 54152388 | 0.000000 | 0.000000 | 456386047
10-04-2025 0:40:50.000 | 31432156 |  | 31.4322 | -2409851 | 15611571 | 11663801 | 99707390 | 50073814 | 53717017 | 0.000000 | 0.000000 | 453162476
10-04-2025 0:40:45.000 | 30975879 |  | 30.9759 | -2372384 | 15609674 | 11494979 | 99708000 | 50072433 | 53283682 | 0.000000 | 0.000000 | 449787872
10-04-2025 0:40:40.000 | 29860063 |  | 29.8601 | -2354802 | 15612029 | 11084229 | 99690491 | 50098198 | 52857280 | 0.000000 | 0.000000 | 446566010
10-04-2025 0:40:35.000 | 27881758 |  | 27.8818 | -2433172 | 15613550 | 10354247 | 99621384 | 50134384 | 52455601 | 0.000000 | 0.000000 | 443353516
10-04-2025 0:40:30.000 | 28916377 |  | 28.9164 | -2616369 | 15614096 | 10741207 | 99593163 | 50109119 | 52064707 | 0.000000 | 0.000000 | 439879517
10-04-2025 0:40:25.000 | 30036611 |  | 30.0366 | -2431012 | 15614468 | 11148438 | 99674080 | 50077194 | 51654609 | 0.000000 | 0.000000 | 436323090
10-04-2025 0:40:20.000 | 29770814 |  | 29.7708 | -2356129 | 15611935 | 11049760 | 99688286 | 50094086 | 51239028 | 0.000000 | 0.000000 | 433068817
10-04-2025 0:40:15.000 | 30271715 |  | 30.2717 | -2458923 | 15613444 | 11235103 | 99671722 | 50078178 | 50825313 | 0.000000 | 0.000000 | 429634460
10-04-2025 0:40:10.000 | 31024488 |  | 31.0245 | -2475930 | 15610458 | 11515078 | 99683067 | 50063492 | 50399023 | 0.000000 | 0.000000 | 426228149
10-04-2025 0:40:05.000 | 29935857 |  | 29.9359 | -2490458 | 15612520 | 11113540 | 99655731 | 50077869 | 49973188 | 0.000000 | 0.000000 | 422827606
10-04-2025 0:40:00.000 | 28802533 |  | 28.8025 | -2585730 | 15613652 | 10698215 | 99599449 | 50099834 | 49563574 | 0.000000 | 0.000000 | 419314514
10-04-2025 0:39:55.000 | 28849756 |  | 28.8498 | -2739925 | 15615778 | 10719060 | 99552040 | 50104313 | 49162539 | 0.000000 | 0.000000 | 415677399
10-04-2025 0:39:50.000 | 29355936 |  | 29.3559 | -2404313 | 15613283 | 10896412 | 99666283 | 50090454 | 48757817 | 0.000000 | 0.000000 | 412090576
10-04-2025 0:39:45.000 | 29750648 |  | 29.7506 | -2351753 | 15613308 | 11040297 | 99689018 | 50091469 | 48348477 | 0.000000 | 0.000000 | 408618347
10-04-2025 0:39:40.000 | 29944492 |  | 29.9445 | -2393696 | 15612908 | 11112714 | 99682022 | 50086224 | 47936475 | 0.000000 | 0.000000 | 405250214
10-04-2025 0:39:35.000 | 31026600 |  | 31.0266 | -2732726 | 15611465 | 11522864 | 99614365 | 50077190 | 47514971 | 0.000000 | 0.000000 | 401774292
10-04-2025 0:39:30.000 | 31879570 |  | 31.8796 | -2595286 | 15608521 | 11836085 | 99670265 | 50063175 | 47077510 | 0.000000 | 0.000000 | 397981384
10-04-2025 0:39:25.000 | 30746816 |  | 30.7468 | -2666076 | 15608202 | 11421941 | 99626167 | 50084366 | 46640522 | 0.000000 | 0.000000 | 394316315
10-04-2025 0:39:20.000 | 28734283 |  | 28.7343 | -2526709 | 15613424 | 10671760 | 99615608 | 50117393 | 46222886 | 0.000000 | 0.000000 | 390577118
10-04-2025 0:39:15.000 | 28311174 |  | 28.3112 | -2732583 | 15616001 | 10521013 | 99537430 | 50129200 | 45831973 | 0.000000 | 0.000000 | 386896362
10-04-2025 0:39:10.000 | 29246600 |  | 29.2466 | -2667043 | 15614003 | 10864326 | 99586777 | 50112461 | 45435093 | 0.000000 | 0.000000 | 383219116
10-04-2025 0:39:05.000 | 31261432 |  | 31.2614 | -2727316 | 15612999 | 11608514 | 99621597 | 50080322 | 45019180 | 0.000000 | 0.000000 | 379448364
10-04-2025 0:39:00.000 | 31343447 |  | 31.3434 | -2638478 | 15610486 | 11637758 | 99647560 | 50073612 | 44582188 | 0.000000 | 0.000000 | 375820465
10-04-2025 0:38:55.000 | 31161791 |  | 31.1618 | -2819466 | 15613643 | 11573901 | 99593178 | 50079845 | 44147407 | 0.000000 | 0.000000 | 372069916
10-04-2025 0:38:50.000 | 30321049 |  | 30.321 | -2566110 | 15611891 | 11257668 | 99643791 | 50093960 | 43716167 | 0.000000 | 0.000000 | 368471741
10-04-2025 0:38:45.000 | 29123135 |  | 29.1231 | -2546469 | 15612434 | 10816466 | 99619911 | 50106728 | 43302461 | 0.000000 | 0.000000 | 364873627
10-04-2025 0:38:40.000 | 28159156 |  | 28.1592 | -2611805 | 15615268 | 10461227 | 99572617 | 50123001 | 42903906 | 0.000000 | 0.000000 | 361325653
10-04-2025 0:38:35.000 | 29027033 |  | 29.027 | -2599426 | 15615647 | 10779984 | 99601418 | 50103451 | 42511553 | 0.000000 | 0.000000 | 357566986
10-04-2025 0:38:30.000 | 29741676 |  | 29.7417 | -2667622 | 15612862 | 11048146 | 99600166 | 50086845 | 42104893 | 0.000000 | 0.000000 | 353968658
10-04-2025 0:38:25.000 | 30396586 |  | 30.3966 | -2676996 | 15610714 | 11290463 | 99614433 | 50072002 | 41689961 | 0.000000 | 0.000000 | 350273682
10-04-2025 0:38:20.000 | 29982436 |  | 29.9824 | -2701020 | 15611642 | 11137683 | 99596672 | 50072620 | 41268184 | 0.000000 | 0.000000 | 346563812
10-04-2025 0:38:15.000 | 29314791 |  | 29.3148 | -2851548 | 15614098 | 10895399 | 99530228 | 50085209 | 40854880 | 0.000000 | 0.000000 | 342837952
10-04-2025 0:38:10.000 | 29413863 |  | 29.4139 | -2753310 | 15614755 | 10928438 | 99564758 | 50096058 | 40444675 | 0.000000 | 0.000000 | 339117371
10-04-2025 0:38:05.000 | 29980594 |  | 29.9806 | -2734859 | 15613759 | 11136938 | 99586517 | 50081512 | 40034275 | 0.000000 | 0.000000 | 335304657
10-04-2025 0:38:00.000 | 31357430 |  | 31.3574 | -2874558 | 15612406 | 11649866 | 99582451 | 50065842 | 39612739 | 0.000000 | 0.000000 | 331394897
10-04-2025 0:37:55.000 | 30638539 |  | 30.6385 | -2821295 | 15610860 | 11384001 | 99578712 | 50080257 | 39179036 | 0.000000 | 0.000000 | 327525604
10-04-2025 0:37:50.000 | 29917971 |  | 29.918 | -2737550 | 15611005 | 11116023 | 99583984 | 50086315 | 38759033 | 0.000000 | 0.000000 | 323634857
10-04-2025 0:37:45.000 | 29336436 |  | 29.3364 | -2669076 | 15613028 | 10897634 | 99588669 | 50097057 | 38344268 | 0.000000 | 0.000000 | 319767120
10-04-2025 0:37:40.000 | 28759611 |  | 28.7596 | -2617566 | 15613479 | 10685059 | 99588364 | 50101868 | 37940674 | 0.000000 | 0.000000 | 316032623
10-04-2025 0:37:35.000 | 29197650 |  | 29.1976 | -2830400 | 15616694 | 10849652 | 99533424 | 50095966 | 37538467 | 0.000000 | 0.000000 | 312269928
10-04-2025 0:37:30.000 | 30107416 |  | 30.1074 | -2651325 | 15613185 | 11181434 | 99614494 | 50070389 | 37124924 | 0.000000 | 0.000000 | 308514648
10-04-2025 0:37:25.000 | 30953258 |  | 30.9533 | -2746700 | 15611537 | 11496680 | 99608597 | 50071301 | 36703521 | 0.000000 | 0.000000 | 304814667
10-04-2025 0:37:20.000 | 31816512 |  | 31.8165 | -2900069 | 15610396 | 11821168 | 99587158 | 50065098 | 36268086 | 0.000000 | 0.000000 | 300925354
10-04-2025 0:37:15.000 | 31452588 |  | 31.4526 | -2840682 | 15610819 | 11684688 | 99594627 | 50066380 | 35825977 | 0.000000 | 0.000000 | 296848022
10-04-2025 0:37:10.000 | 30029164 |  | 30.0292 | -3030020 | 15610001 | 11167025 | 99494789 | 50114204 | 35397031 | 0.000000 | 0.000000 | 292962433
10-04-2025 0:37:05.000 | 29739373 |  | 29.7394 | -3236771 | 15612520 | 11067631 | 99412926 | 50105507 | 34983911 | 0.000000 | 0.000000 | 288461334
10-04-2025 0:37:00.000 | 30221430 |  | 30.2214 | -3181877 | 15612902 | 11241649 | 99450317 | 50103283 | 34568604 | 0.000000 | 0.000000 | 283904175
10-04-2025 0:36:55.000 | 30107432 |  | 30.1074 | -3415903 | 15611613 | 11210214 | 99362518 | 50101311 | 34150698 | 0.000000 | 0.000000 | 279345825
10-04-2025 0:36:50.000 | 30179379 |  | 30.1794 | -3215835 | 15611586 | 11228706 | 99437065 | 50099171 | 33731045 | 0.000000 | 0.000000 | 274656433
10-04-2025 0:36:45.000 | 29345242 |  | 29.3452 | -3360001 | 15610833 | 10929343 | 99350876 | 50119286 | 33318157 | 0.000000 | 0.000000 | 270155701
10-04-2025 0:36:40.000 | 29204166 |  | 29.2042 | -3497214 | 15613665 | 10880535 | 99290611 | 50119881 | 32913237 | 0.000000 | 0.000000 | 265362732
10-04-2025 0:36:35.000 | 29565793 |  | 29.5658 | -3464139 | 15612417 | 11013821 | 99320580 | 50113850 | 32505798 | 0.000000 | 0.000000 | 260638580
10-04-2025 0:36:30.000 | 29210088 |  | 29.2101 | -3187673 | 15611949 | 10871456 | 99409805 | 50104759 | 32095967 | 0.000000 | 0.000000 | 255995087
10-04-2025 0:36:25.000 | 28145742 |  | 28.1457 | -3200932 | 15611979 | 10480441 | 99359512 | 50111645 | 31697495 | 0.000000 | 0.000000 | 251515625
10-04-2025 0:36:20.000 | 26190738 |  | 26.1907 | -3139791 | 15614289 | 975888733 | 99289070 | 50140186 | 31318093 | 0.000000 | 0.000000 | 247113586
10-04-2025 0:36:15.000 | 26625055 |  | 26.6251 | -3077292 | 15618600 | 991254272 | 99338692 | 50137436 | 30953914 | 0.000000 | 0.000000 | 242736115
10-04-2025 0:36:10.000 | 29003781 |  | 29.0038 | -3145281 | 15618406 | 10789799 | 99417130 | 50073116 | 30573813 | 0.000000 | 0.000000 | 238402969
10-04-2025 0:36:05.000 | 30411004 |  | 30.411 | -2524106 | 15612458 | 11289042 | 99657318 | 50046860 | 30155923 | 0.000000 | 0.000000 | 234645142
10-04-2025 0:36:00.000 | 30022467 |  | 30.0225 | -2411282 | 15612586 | 11142509 | 99679016 | 50045506 | 29734978 | 0.000000 | 0.000000 | 231143616
10-04-2025 0:35:55.000 | 29965920 |  | 29.9659 | -2466792 | 15613261 | 11122699 | 99662888 | 50051647 | 29317590 | 0.000000 | 0.000000 | 227815720
10-04-2025 0:35:50.000 | 30335672 |  | 30.3357 | -2673998 | 15612507 | 11265920 | 99613754 | 50046303 | 28899155 | 0.000000 | 0.000000 | 224314926
10-04-2025 0:35:45.000 | 30335824 |  | 30.3358 | -2470882 | 15611034 | 11261335 | 99669930 | 50045200 | 28474070 | 0.000000 | 0.000000 | 220844360
10-04-2025 0:35:40.000 | 29574465 |  | 29.5745 | -2522012 | 15610981 | 10982308 | 99638367 | 50056728 | 28056726 | 0.000000 | 0.000000 | 217355331
10-04-2025 0:35:35.000 | 29014746 |  | 29.0147 | -2592098 | 15612424 | 10777351 | 99603317 | 50063347 | 27649001 | 0.000000 | 0.000000 | 213756760
10-04-2025 0:35:30.000 | 29154969 |  | 29.155 | -2473055 | 15613751 | 10824138 | 99642174 | 50068298 | 27245627 | 0.000000 | 0.000000 | 210221466
10-04-2025 0:35:25.000 | 29092836 |  | 29.0928 | -2496933 | 15614054 | 10802228 | 99633713 | 50073067 | 26842561 | 0.000000 | 0.000000 | 206818100
10-04-2025 0:35:20.000 | 29779697 |  | 29.7797 | -2564408 | 15613068 | 11057435 | 99631279 | 50056545 | 26434670 | 0.000000 | 0.000000 | 203239288
10-04-2025 0:35:15.000 | 30602422 |  | 30.6024 | -2580087 | 15612576 | 11362178 | 99646477 | 50039085 | 26015574 | 0.000000 | 0.000000 | 199611343
10-04-2025 0:35:10.000 | 30389406 |  | 30.3894 | -2492502 | 15610069 | 11282483 | 99665337 | 50041389 | 25590142 | 0.000000 | 0.000000 | 196124405
10-04-2025 0:35:05.000 | 29132277 |  | 29.1323 | -2504489 | 15613438 | 10817081 | 99632500 | 50061138 | 25175417 | 0.000000 | 0.000000 | 192613281
10-04-2025 0:35:00.000 | 28299326 |  | 28.2993 | -2442990 | 15615017 | 10508151 | 99629456 | 50065392 | 24777510 | 0.000000 | 0.000000 | 189123596
10-04-2025 0:34:55.000 | 29643150 |  | 29.6431 | -2537595 | 15612822 | 11006877 | 99635590 | 50049358 | 24377983 | 0.000000 | 0.000000 | 185605209
10-04-2025 0:34:50.000 | 30418162 |  | 30.4182 | -2516260 | 15612418 | 11291838 | 99659599 | 50025291 | 23960825 | 0.000000 | 0.000000 | 182073044
10-04-2025 0:34:45.000 | 30089795 |  | 30.0898 | -2395475 | 15610186 | 11168876 | 99684601 | 50031311 | 23538923 | 0.000000 | 0.000000 | 178580826
10-04-2025 0:34:40.000 | 29368648 |  | 29.3686 | -2569127 | 15611724 | 10908500 | 99619560 | 50051479 | 23128655 | 0.000000 | 0.000000 | 175106964
10-04-2025 0:34:35.000 | 29599760 |  | 29.5998 | -2405672 | 15610336 | 10989583 | 99671356 | 50035194 | 22721785 | 0.000000 | 0.000000 | 171419220
10-04-2025 0:34:30.000 | 29290313 |  | 29.2903 | -2507681 | 15612861 | 10876342 | 99635506 | 50046890 | 22313435 | 0.000000 | 0.000000 | 167991211
10-04-2025 0:34:25.000 | 29227389 |  | 29.2274 | -2622168 | 15613265 | 10857223 | 99599968 | 50047100 | 21905498 | 0.000000 | 0.000000 | 164388351
10-04-2025 0:34:20.000 | 29419895 |  | 29.4199 | -2525575 | 15613375 | 10923950 | 99633553 | 50042557 | 21496262 | 0.000000 | 0.000000 | 160793549
10-04-2025 0:34:15.000 | 29586160 |  | 29.5862 | -2541933 | 15612573 | 10986591 | 99632950 | 50038952 | 21085469 | 0.000000 | 0.000000 | 157348724
10-04-2025 0:34:10.000 | 29586439 |  | 29.5864 | -2564587 | 15612438 | 10987747 | 99626419 | 50031181 | 20673896 | 0.000000 | 0.000000 | 153779922
10-04-2025 0:34:05.000 | 28472666 |  | 28.4727 | -2479394 | 15612346 | 10574125 | 99623001 | 50045647 | 20266124 | 0.000000 | 0.000000 | 150299774
10-04-2025 0:34:00.000 | 28084063 |  | 28.0841 | -2516438 | 15616758 | 10429745 | 99600960 | 50049915 | 19874517 | 0.000000 | 0.000000 | 146700806
10-04-2025 0:33:55.000 | 28769691 |  | 28.7697 | -2452651 | 15616078 | 10680266 | 99638580 | 50033352 | 19482693 | 0.000000 | 0.000000 | 143259659
10-04-2025 0:33:50.000 | 30229820 |  | 30.2298 | -2534662 | 15615665 | 11221893 | 99650330 | 49994511 | 19073391 | 0.000000 | 0.000000 | 139944305
10-04-2025 0:33:45.000 | 31101604 |  | 31.1016 | -2217010 | 15612123 | 11535439 | 99746902 | 49980953 | 18641620 | 0.000000 | 0.000000 | 136674316
10-04-2025 0:33:40.000 | 30091957 |  | 30.092 | -2331308 | 15612602 | 11165599 | 99701241 | 50009968 | 18214951 | 0.000000 | 0.000000 | 133583969
10-04-2025 0:33:35.000 | 29814555 |  | 29.8146 | -2353927 | 15614543 | 11063114 | 99689774 | 50015835 | 17798982 | 0.000000 | 0.000000 | 130380524
10-04-2025 0:33:30.000 | 30335357 |  | 30.3354 | -2369879 | 15613389 | 11255950 | 99696236 | 49996716 | 17380737 | 0.000000 | 0.000000 | 127113800
10-04-2025 0:33:25.000 | 30242207 |  | 30.2422 | -2302406 | 15613114 | 11220638 | 99711449 | 50009232 | 16960232 | 0.000000 | 0.000000 | 123838585
10-04-2025 0:33:20.000 | 30142174 |  | 30.1422 | -2323516 | 15612414 | 11184264 | 99704208 | 50008751 | 16541672 | 0.000000 | 0.000000 | 120648415
10-04-2025 0:33:15.000 | 30404256 |  | 30.4043 | -2102310 | 15610046 | 11277921 | 99761803 | 49998936 | 16119695 | 0.000000 | 0.000000 | 117537971
10-04-2025 0:33:10.000 | 29320043 |  | 29.32 | -2213983 | 15612150 | 10879066 | 99716118 | 50018173 | 15706252 | 0.000000 | 0.000000 | 114327019
10-04-2025 0:33:05.000 | 29173270 |  | 29.1733 | -2384185 | 15612535 | 10829609 | 99667717 | 50034836 | 15301960 | 0.000000 | 0.000000 | 111074020
10-04-2025 0:33:00.000 | 30469506 |  | 30.4695 | -2602901 | 15614172 | 11312268 | 99637100 | 50004185 | 14890885 | 0.000000 | 0.000000 | 107644371
10-04-2025 0:32:55.000 | 30902654 |  | 30.9027 | -2333199 | 15610250 | 11466855 | 99716187 | 49984234 | 14460891 | 0.000000 | 0.000000 | 104275986
10-04-2025 0:32:50.000 | 29666207 |  | 29.6662 | -2301170 | 15610163 | 11010712 | 99700508 | 50012108 | 14036440 | 0.000000 | 0.000000 | 101195862
10-04-2025 0:32:45.000 | 28818834 |  | 28.8188 | -2407923 | 15612636 | 10699368 | 99652756 | 50010406 | 13629352 | 0.000000 | 0.000000 | 97977173
10-04-2025 0:32:40.000 | 28196814 |  | 28.1968 | -2378267 | 15614318 | 10468453 | 99646179 | 50013790 | 13233599 | 0.000000 | 0.000000 | 94661858
10-04-2025 0:32:35.000 | 28493078 |  | 28.4931 | -2299220 | 15616319 | 10574076 | 99676003 | 50004456 | 12839956 | 0.000000 | 0.000000 | 91310196
10-04-2025 0:32:30.000 | 28989152 |  | 28.9892 | -2305860 | 15615093 | 10757509 | 99685143 | 50004509 | 12441658 | 0.000000 | 0.000000 | 88194130
10-04-2025 0:32:25.000 | 30145313 |  | 30.1453 | -2158313 | 15612952 | 11182590 | 99744675 | 49978710 | 12033429 | 0.000000 | 0.000000 | 84958153
10-04-2025 0:32:20.000 | 30813670 |  | 30.8137 | -1933960 | 15612414 | 11422761 | 99803619 | 49954136 | 11609504 | 0.000000 | 0.000000 | 81970818
10-04-2025 0:32:15.000 | 29885486 |  | 29.8855 | -2199966 | 15612353 | 11087357 | 99730148 | 49973164 | 11185984 | 0.000000 | 0.000000 | 79237877
10-04-2025 0:32:10.000 | 29312453 |  | 29.3125 | -2311707 | 15613310 | 10877596 | 99690460 | 49994247 | 10775104 | 0.000000 | 0.000000 | 76297073
10-04-2025 0:32:05.000 | 29295957 |  | 29.296 | -2194633 | 15612861 | 10869091 | 99720581 | 49992992 | 10370669 | 0.000000 | 0.000000 | 73054398
10-04-2025 0:32:00.000 | 29579828 |  | 29.5798 | -2484712 | 15615989 | 10979056 | 99649055 | 49987728 | 996394592 | 0.000000 | 0.000000 | 69855415
10-04-2025 0:31:55.000 | 30300867 |  | 30.3009 | -2310187 | 15613171 | 11242031 | 99710625 | 49977428 | 954647278 | 0.000000 | 0.000000 | 66668495
10-04-2025 0:31:50.000 | 31205332 |  | 31.2053 | -2087663 | 15611439 | 11571912 | 99776962 | 49955944 | 912021667 | 0.000000 | 0.000000 | 63571541
10-04-2025 0:31:45.000 | 30297924 |  | 30.2979 | -1993330 | 15612373 | 11233342 | 99784279 | 49970806 | 868876404 | 0.000000 | 0.000000 | 60759426
10-04-2025 0:31:40.000 | 29350420 |  | 29.3504 | -2056836 | 15611567 | 10886648 | 99755348 | 49986553 | 827410034 | 0.000000 | 0.000000 | 57998192
10-04-2025 0:31:35.000 | 28905260 |  | 28.9053 | -2121620 | 15614014 | 10722467 | 99731712 | 49986824 | 787300537 | 0.000000 | 0.000000 | 54961517
10-04-2025 0:31:30.000 | 28852742 |  | 28.8527 | -2019894 | 15614448 | 10699932 | 99755852 | 49968555 | 747289917 | 0.000000 | 0.000000 | 51988365
10-04-2025 0:31:25.000 | 28843197 |  | 28.8432 | -1886210 | 15613990 | 10694733 | 99786858 | 49972614 | 707523254 | 0.000000 | 0.000000 | 49245411
10-04-2025 0:31:20.000 | 30457674 |  | 30.4577 | -2178563 | 15612723 | 11298466 | 99745171 | 49942516 | 666947632 | 0.000000 | 0.000000 | 46268764
10-04-2025 0:31:15.000 | 30737709 |  | 30.7377 | -2075952 | 15612928 | 11397567 | 99772713 | 49926277 | 624282654 | 0.000000 | 0.000000 | 43247849
10-04-2025 0:31:10.000 | 29527672 |  | 29.5277 | -1878839 | 15612137 | 10946386 | 99798172 | 49946541 | 582179626 | 0.000000 | 0.000000 | 40474453
10-04-2025 0:31:05.000 | 28974713 |  | 28.9747 | -2485506 | 15616934 | 10758726 | 99634094 | 49967178 | 541620117 | 0.000000 | 0.000000 | 37681629
10-04-2025 0:31:00.000 | 30411168 |  | 30.4112 | -2199799 | 15612876 | 11279971 | 99739403 | 49951019 | 500272278 | 0.000000 | 0.000000 | 34586468
10-04-2025 0:30:55.000 | 32166756 |  | 32.1668 | -2122637 | 15614120 | 11924897 | 99782982 | 49923786 | 456926208 | 0.000000 | 0.000000 | 31330982
10-04-2025 0:30:50.000 | 31687068 |  | 31.6871 | -1888941 | 15609409 | 11745361 | 99822792 | 49933918 | 412229309 | 0.000000 | 0.000000 | 28681040
10-04-2025 0:30:45.000 | 30785197 |  | 30.7852 | -1856609 | 15610367 | 11411034 | 99818642 | 49953594 | 368886902 | 0.000000 | 0.000000 | 25989367
10-04-2025 0:30:40.000 | 28777871 |  | 28.7779 | -2178769 | 15614222 | 10676610 | 99714630 | 49996571 | 327328888 | 0.000000 | 0.000000 | 23280394
10-04-2025 0:30:35.000 | 28411070 |  | 28.4111 | -2011027 | 15614627 | 10538082 | 99750427 | 49996689 | 287683685 | 0.000000 | 0.000000 | 20341326
10-04-2025 0:30:30.000 | 30067756 |  | 30.0678 | -2269354 | 15613291 | 11154647 | 99716393 | 49965874 | 247510345 | 0.000000 | 0.000000 | 17326576
10-04-2025 0:30:25.000 | 30878404 |  | 30.8784 | -2173042 | 15612300 | 11452620 | 99753288 | 49938549 | 205225250 | 0.000000 | 0.000000 | 14167853
10-04-2025 0:30:20.000 | 30103902 |  | 30.1039 | -2018083 | 15610898 | 11163606 | 99776054 | 49945747 | 162783478 | 0.000000 | 0.000000 | 11189555
10-04-2025 0:30:15.000 | 28521936 |  | 28.5219 | -1957075 | 15613250 | 10576588 | 99765419 | 49974174 | 121649956 | 0.000000 | 0.000000 | 8436200
10-04-2025 0:30:10.000 | 29103658 |  | 29.1037 | -2119294 | 15614074 | 10795039 | 99735924 | 49968849 | 81970291 | 0.000000 | 0.000000 | 5601573
10-04-2025 0:30:05.000 | 29668488 |  | 29.6685 | -2167807 | 15614521 | 11005415 | 99734123 | 49952599 | 41201225 | 0.000000 | 0.000000 | 2735364
10-04-2025 0:30:00.000 | 29456938 |  | 29.4569 | -1869349 | 15611392 | 10920673 | 99799248 | 49953827 | 86922568 | 0.000000 | 0.000000 | 491508453
10-04-2025 0:29:55.000 | 29466211 |  | 29.4662 | -2133383 | 15612677 | 10930194 | 99738930 | 49957840 | 86513623 | 0.000000 | 0.000000 | 488759308
10-04-2025 0:29:50.000 | 30443064 |  | 30.4431 | -2049712 | 15613222 | 11286899 | 99774109 | 49934242 | 86097764 | 0.000000 | 0.000000 | 485745728
10-04-2025 0:29:45.000 | 29750660 |  | 29.7507 | -2097140 | 15612197 | 11034978 | 99752480 | 49943592 | 85677100 | 0.000000 | 0.000000 | 482980591
10-04-2025 0:29:40.000 | 28990709 |  | 28.9907 | -1798207 | 15613229 | 10747395 | 99808189 | 49954960 | 85268936 | 0.000000 | 0.000000 | 480305634
10-04-2025 0:29:35.000 | 29005309 |  | 29.0053 | -1943865 | 15614290 | 10754946 | 99776184 | 49960506 | 84867734 | 0.000000 | 0.000000 | 477637421
10-04-2025 0:29:30.000 | 29179047 |  | 29.179 | -1946241 | 15613567 | 10818120 | 99778297 | 49964241 | 84464414 | 0.000000 | 0.000000 | 474962494
10-04-2025 0:29:25.000 | 29325760 |  | 29.3258 | -1770334 | 15613635 | 10869178 | 99818283 | 49960400 | 84060928 | 0.000000 | 0.000000 | 472333496
10-04-2025 0:29:20.000 | 29557729 |  | 29.5577 | -2064913 | 15612611 | 10961472 | 99756866 | 49960857 | 83653594 | 0.000000 | 0.000000 | 469813965
10-04-2025 0:29:15.000 | 30075338 |  | 30.0753 | -1872107 | 15614456 | 11146283 | 99806824 | 49937988 | 83241064 | 0.000000 | 0.000000 | 467087341
10-04-2025 0:29:10.000 | 30185426 |  | 30.1854 | -1942971 | 15610995 | 11191677 | 99793480 | 49941727 | 82821074 | 0.000000 | 0.000000 | 464605927
10-04-2025 0:29:05.000 | 30422666 |  | 30.4227 | -1989671 | 15610873 | 11280635 | 99786819 | 49943119 | 82402100 | 0.000000 | 0.000000 | 461897705
10-04-2025 0:29:00.000 | 29957424 |  | 29.9574 | -1752238 | 15609679 | 11105531 | 99829376 | 49941151 | 81981816 | 0.000000 | 0.000000 | 459180481
10-04-2025 0:28:55.000 | 29287203 |  | 29.2872 | -1782836 | 15612299 | 10855630 | 99815231 | 49950619 | 81570698 | 0.000000 | 0.000000 | 456618073
10-04-2025 0:28:50.000 | 28864697 |  | 28.8647 | -1714081 | 15613646 | 10697810 | 99824142 | 49972271 | 81166445 | 0.000000 | 0.000000 | 454185120
10-04-2025 0:28:45.000 | 29724594 |  | 29.7246 | -1893074 | 15615479 | 11017899 | 99797813 | 49959209 | 80763247 | 0.000000 | 0.000000 | 451670135
10-04-2025 0:28:40.000 | 31142455 |  | 31.1425 | -1774839 | 15610835 | 11541537 | 99837997 | 49935036 | 80341855 | 0.000000 | 0.000000 | 449175232
10-04-2025 0:28:35.000 | 31390852 |  | 31.3909 | -1749922 | 15609957 | 11633556 | 99844978 | 49928093 | 79906577 | 0.000000 | 0.000000 | 446573059
10-04-2025 0:28:30.000 | 30244084 |  | 30.2441 | -1890021 | 15611173 | 11211823 | 99805305 | 49958660 | 79474883 | 0.000000 | 0.000000 | 444096863
10-04-2025 0:28:25.000 | 29858771 |  | 29.8588 | -1700737 | 15610335 | 11067004 | 99838173 | 49970825 | 79059580 | 0.000000 | 0.000000 | 441491638
10-04-2025 0:28:20.000 | 29388174 |  | 29.3882 | -1683023 | 15610446 | 10891984 | 99836418 | 49971809 | 78648345 | 0.000000 | 0.000000 | 438921143
10-04-2025 0:28:15.000 | 28004986 |  | 28.005 | -1690658 | 15613272 | 10379984 | 99818268 | 49978630 | 78247358 | 0.000000 | 0.000000 | 436583191
10-04-2025 0:28:10.000 | 27822432 |  | 27.8224 | -1806586 | 15614989 | 10315132 | 99789848 | 49973099 | 77859692 | 0.000000 | 0.000000 | 434289063
10-04-2025 0:28:05.000 | 28039777 |  | 28.0398 | -1821321 | 15615054 | 10394576 | 99789711 | 49955555 | 77470576 | 0.000000 | 0.000000 | 431792603
10-04-2025 0:28:00.000 | 28742775 |  | 28.7428 | -1888425 | 15618630 | 10653469 | 99784866 | 49940891 | 77078423 | 0.000000 | 0.000000 | 429223114
10-04-2025 0:27:55.000 | 29684084 |  | 29.6841 | -1626586 | 15612570 | 10998733 | 99850204 | 49929440 | 76673779 | 0.000000 | 0.000000 | 426931702
10-04-2025 0:27:50.000 | 29963219 |  | 29.9632 | -1737199 | 15613085 | 11103237 | 99832352 | 49914124 | 76262485 | 0.000000 | 0.000000 | 424578430
10-04-2025 0:27:45.000 | 30052611 |  | 30.0526 | -1666014 | 15612726 | 11135206 | 99846695 | 49910217 | 75845410 | 0.000000 | 0.000000 | 422234192
10-04-2025 0:27:40.000 | 29490328 |  | 29.4903 | -1804992 | 15613529 | 10930394 | 99813217 | 49929569 | 75430825 | 0.000000 | 0.000000 | 419972717
10-04-2025 0:27:35.000 | 30625783 |  | 30.6258 | -2016763 | 15612957 | 11354558 | 99783882 | 49911304 | 75017764 | 0.000000 | 0.000000 | 417322571
10-04-2025 0:27:30.000 | 31324654 |  | 31.3247 | -1730351 | 15612846 | 11606305 | 99847778 | 49899765 | 74582686 | 0.000000 | 0.000000 | 414623230
10-04-2025 0:27:25.000 | 30146391 |  | 30.1464 | -1846234 | 15614172 | 11172522 | 99812996 | 49924324 | 74153296 | 0.000000 | 0.000000 | 412270966
10-04-2025 0:27:20.000 | 30757234 |  | 30.7572 | -1877011 | 15613562 | 11399957 | 99814308 | 49931068 | 73732363 | 0.000000 | 0.000000 | 409638977
10-04-2025 0:27:15.000 | 32207090 |  | 32.2071 | -1979783 | 15612785 | 11937107 | 99811600 | 49907383 | 73298120 | 0.000000 | 0.000000 | 406922424
10-04-2025 0:27:10.000 | 32200955 |  | 32.201 | -1945169 | 15609954 | 11935588 | 99818047 | 49907303 | 72848833 | 0.000000 | 0.000000 | 404278870
10-04-2025 0:27:05.000 | 30902752 |  | 30.9028 | -1978371 | 15610189 | 11457749 | 99795708 | 49958050 | 72405249 | 0.000000 | 0.000000 | 401710480
10-04-2025 0:27:00.000 | 30657365 |  | 30.6574 | -2140970 | 15612014 | 11369899 | 99757042 | 49949726 | 71980459 | 0.000000 | 0.000000 | 398754120
10-04-2025 0:26:55.000 | 30456340 |  | 30.4563 | -2191629 | 15611225 | 11297897 | 99742088 | 49953106 | 71556035 | 0.000000 | 0.000000 | 395719666
10-04-2025 0:26:50.000 | 29771854 |  | 29.7719 | -2327733 | 15612311 | 11048413 | 99695747 | 49971031 | 71136772 | 0.000000 | 0.000000 | 392667450
10-04-2025 0:26:45.000 | 29492297 |  | 29.4923 | -2338135 | 15612472 | 10945352 | 99687210 | 49975159 | 70725215 | 0.000000 | 0.000000 | 389399658
10-04-2025 0:26:40.000 | 28702371 |  | 28.7024 | -2371734 | 15613651 | 10654834 | 99660339 | 49980881 | 70321040 | 0.000000 | 0.000000 | 386168518
10-04-2025 0:26:35.000 | 28351160 |  | 28.3512 | -2590427 | 15616193 | 10530585 | 99585175 | 49975887 | 69926670 | 0.000000 | 0.000000 | 382724548
10-04-2025 0:26:30.000 | 29420979 |  | 29.421 | -2335465 | 15615350 | 10917017 | 99686417 | 49958084 | 69527925 | 0.000000 | 0.000000 | 379297394
10-04-2025 0:26:25.000 | 29958172 |  | 29.9582 | -2193602 | 15613359 | 11112880 | 99733002 | 49947708 | 69117412 | 0.000000 | 0.000000 | 376151978
10-04-2025 0:26:20.000 | 30495605 |  | 30.4956 | -2296947 | 15612757 | 11313778 | 99717545 | 49945095 | 68700166 | 0.000000 | 0.000000 | 373034760
10-04-2025 0:26:15.000 | 31218611 |  | 31.2186 | -2376263 | 15611752 | 11583325 | 99711563 | 49933971 | 68269248 | 0.000000 | 0.000000 | 369837799
10-04-2025 0:26:10.000 | 30882852 |  | 30.8829 | -2357836 | 15610772 | 11459817 | 99709816 | 49938961 | 67834521 | 0.000000 | 0.000000 | 366523621
10-04-2025 0:26:05.000 | 29813021 |  | 29.813 | -2456319 | 15612473 | 11067031 | 99662308 | 49971611 | 67411528 | 0.000000 | 0.000000 | 363283722
10-04-2025 0:26:00.000 | 29983145 |  | 29.9831 | -2496596 | 15612109 | 11131527 | 99655128 | 49969204 | 66998340 | 0.000000 | 0.000000 | 359825134
10-04-2025 0:25:55.000 | 30448293 |  | 30.4483 | -2350551 | 15612518 | 11297883 | 99703346 | 49958813 | 66578247 | 0.000000 | 0.000000 | 356333191
10-04-2025 0:25:50.000 | 30297486 |  | 30.2975 | -2401823 | 15612206 | 11244045 | 99687248 | 49957600 | 66156104 | 0.000000 | 0.000000 | 352944824
10-04-2025 0:25:45.000 | 30221951 |  | 30.222 | -2507899 | 15613679 | 11218363 | 99657463 | 49955032 | 65734556 | 0.000000 | 0.000000 | 349588196
10-04-2025 0:25:40.000 | 30453703 |  | 30.4537 | -2493343 | 15612098 | 11304399 | 99666512 | 49958691 | 65312432 | 0.000000 | 0.000000 | 346228638
10-04-2025 0:25:35.000 | 30736135 |  | 30.7361 | -2444520 | 15612644 | 11406899 | 99685219 | 49956188 | 64888384 | 0.000000 | 0.000000 | 342779938
10-04-2025 0:25:30.000 | 30606156 |  | 30.6062 | -2486431 | 15613345 | 11359188 | 99671631 | 49957321 | 64462354 | 0.000000 | 0.000000 | 339301514
10-04-2025 0:25:25.000 | 30526557 |  | 30.5266 | -2688645 | 15613345 | 11336936 | 99614380 | 49958664 | 64038408 | 0.000000 | 0.000000 | 335752106
10-04-2025 0:25:20.000 | 30811199 |  | 30.8112 | -2492208 | 15612837 | 11435957 | 99674469 | 49948372 | 63614048 | 0.000000 | 0.000000 | 332047516
10-04-2025 0:25:15.000 | 31088480 |  | 31.0885 | -2336355 | 15612319 | 11533870 | 99718803 | 49947563 | 63184355 | 0.000000 | 0.000000 | 328637909
10-04-2025 0:25:10.000 | 31102371 |  | 31.1024 | -2430838 | 15611739 | 11541716 | 99695976 | 49949810 | 62752568 | 0.000000 | 0.000000 | 325306213
10-04-2025 0:25:05.000 | 30889883 |  | 30.8899 | -2253677 | 15609308 | 11460640 | 99734909 | 49940720 | 62322158 | 0.000000 | 0.000000 | 321976563
10-04-2025 0:25:00.000 | 29895061 |  | 29.8951 | -2428583 | 15610995 | 11097600 | 99671654 | 49961426 | 61898394 | 0.000000 | 0.000000 | 318768829
10-04-2025 0:24:55.000 | 28788139 |  | 28.7881 | -2600166 | 15613504 | 10694558 | 99594589 | 49980576 | 61488823 | 0.000000 | 0.000000 | 315381500
10-04-2025 0:24:50.000 | 28796871 |  | 28.7969 | -2576121 | 15613253 | 10696271 | 99602249 | 49986919 | 61087817 | 0.000000 | 0.000000 | 311753693
10-04-2025 0:24:45.000 | 28373953 |  | 28.374 | -2537456 | 15614237 | 10538086 | 99602509 | 49999954 | 60691279 | 0.000000 | 0.000000 | 308222198
10-04-2025 0:24:40.000 | 29134346 |  | 29.1343 | -2456115 | 15614907 | 10815460 | 99646530 | 49988514 | 60294292 | 0.000000 | 0.000000 | 304728180
10-04-2025 0:24:35.000 | 30375938 |  | 30.3759 | -2303021 | 15614371 | 11268408 | 99713821 | 49962883 | 59881465 | 0.000000 | 0.000000 | 301345825
10-04-2025 0:24:30.000 | 30650752 |  | 30.6508 | -2265794 | 15611667 | 11371254 | 99727882 | 49959599 | 59456865 | 0.000000 | 0.000000 | 298203278
10-04-2025 0:24:25.000 | 31404506 |  | 31.4045 | -2294134 | 15610716 | 11650146 | 99734238 | 49947281 | 59025918 | 0.000000 | 0.000000 | 294997894
10-04-2025 0:24:20.000 | 30816600 |  | 30.8166 | -2408855 | 15610321 | 11437100 | 99695885 | 49959023 | 58589570 | 0.000000 | 0.000000 | 291783813
10-04-2025 0:24:15.000 | 29525732 |  | 29.5257 | -2569038 | 15611564 | 10965222 | 99623596 | 49990307 | 58167524 | 0.000000 | 0.000000 | 288527100
10-04-2025 0:24:10.000 | 28354736 |  | 28.3547 | -2569781 | 15613636 | 10532604 | 99591827 | 49999634 | 57764995 | 0.000000 | 0.000000 | 284967499
10-04-2025 0:24:05.000 | 28013197 |  | 28.0132 | -2655597 | 15616545 | 10407878 | 99553673 | 50007530 | 57374346 | 0.000000 | 0.000000 | 281360992
10-04-2025 0:24:00.000 | 29721016 |  | 29.721 | -2436756 | 15616994 | 11029218 | 99665588 | 49973133 | 56980244 | 0.000000 | 0.000000 | 277666016
10-04-2025 0:23:55.000 | 31583268 |  | 31.5833 | -2364573 | 15610727 | 11718007 | 99720909 | 49936749 | 56555449 | 0.000000 | 0.000000 | 274356934
10-04-2025 0:23:50.000 | 31028063 |  | 31.0281 | -2386821 | 15610880 | 11513816 | 99705437 | 49949516 | 56119888 | 0.000000 | 0.000000 | 271033142
10-04-2025 0:23:45.000 | 30732025 |  | 30.732 | -2568258 | 15612945 | 11408457 | 99652626 | 49949398 | 55691162 | 0.000000 | 0.000000 | 267572784
10-04-2025 0:23:40.000 | 30152367 |  | 30.1524 | -2299678 | 15612312 | 11187727 | 99710419 | 49960640 | 55266846 | 0.000000 | 0.000000 | 264145966
10-04-2025 0:23:35.000 | 29960102 |  | 29.9601 | -2496940 | 15615236 | 11120265 | 99654503 | 49976234 | 54849390 | 0.000000 | 0.000000 | 260845978
10-04-2025 0:23:30.000 | 30793857 |  | 30.7939 | -2440094 | 15613171 | 11427412 | 99687523 | 49967319 | 54429937 | 0.000000 | 0.000000 | 257430939
10-04-2025 0:23:25.000 | 31610914 |  | 31.6109 | -2626359 | 15612038 | 11735466 | 99656631 | 49961071 | 53998838 | 0.000000 | 0.000000 | 253944016
10-04-2025 0:23:20.000 | 32029326 |  | 32.0293 | -2501609 | 15610234 | 11886436 | 99696381 | 49951622 | 53557031 | 0.000000 | 0.000000 | 250294815
10-04-2025 0:23:15.000 | 31260537 |  | 31.2605 | -2384671 | 15610063 | 11600062 | 99710304 | 49976730 | 53113730 | 0.000000 | 0.000000 | 246890533
10-04-2025 0:23:10.000 | 30098492 |  | 30.0985 | -2657097 | 15614496 | 11177587 | 99612595 | 50004631 | 52687441 | 0.000000 | 0.000000 | 243378769
10-04-2025 0:23:05.000 | 30545160 |  | 30.5452 | -2598768 | 15613409 | 11340295 | 99640030 | 49996552 | 52266201 | 0.000000 | 0.000000 | 239697266
10-04-2025 0:23:00.000 | 31229695 |  | 31.2297 | -2823871 | 15614676 | 11599714 | 99593674 | 49987644 | 51838101 | 0.000000 | 0.000000 | 235845947
10-04-2025 0:22:55.000 | 31505475 |  | 31.5055 | -2656145 | 15611290 | 11697422 | 99646500 | 49984478 | 51402563 | 0.000000 | 0.000000 | 232143982
10-04-2025 0:22:50.000 | 31387811 |  | 31.3878 | -2694076 | 15612579 | 11654542 | 99633667 | 49979134 | 50966025 | 0.000000 | 0.000000 | 228325668
10-04-2025 0:22:45.000 | 31093150 |  | 31.0932 | -2883931 | 15612941 | 11551450 | 99572617 | 49989388 | 50530767 | 0.000000 | 0.000000 | 224546112
10-04-2025 0:22:40.000 | 30727057 |  | 30.7271 | -2917888 | 15611505 | 11419784 | 99552139 | 49993614 | 50099570 | 0.000000 | 0.000000 | 220637817
10-04-2025 0:22:35.000 | 30059580 |  | 30.0596 | -2851784 | 15612572 | 11170527 | 99552986 | 50006062 | 49676470 | 0.000000 | 0.000000 | 216631531
10-04-2025 0:22:30.000 | 29609777 |  | 29.6098 | -2829011 | 15612123 | 11005214 | 99546677 | 50016617 | 49263540 | 0.000000 | 0.000000 | 212672806
10-04-2025 0:22:25.000 | 29730611 |  | 29.7306 | -2946094 | 15612597 | 11052599 | 99512619 | 50011147 | 48852456 | 0.000000 | 0.000000 | 208640137
10-04-2025 0:22:20.000 | 29759193 |  | 29.7592 | -2709858 | 15610353 | 11056775 | 99587967 | 50000771 | 48438091 | 0.000000 | 0.000000 | 204663330
10-04-2025 0:22:15.000 | 28100793 |  | 28.1008 | -2645574 | 15611377 | 10443057 | 99559753 | 50018600 | 48033042 | 0.000000 | 0.000000 | 200974319
10-04-2025 0:22:10.000 | 27156734 |  | 27.1567 | -2507458 | 15615051 | 10088666 | 99576439 | 50021088 | 47648252 | 0.000000 | 0.000000 | 197386566
10-04-2025 0:22:05.000 | 25864355 |  | 25.8644 | -2259641 | 15614796 | 960548218 | 99620537 | 50038574 | 47277681 | 0.000000 | 0.000000 | 194052277
10-04-2025 0:22:00.000 | 26091318 |  | 26.0913 | -2360438 | 15621821 | 968831665 | 99593269 | 50041790 | 46921196 | 0.000000 | 0.000000 | 190804459
10-04-2025 0:21:55.000 | 30563031 |  | 30.563 | -2088618 | 15617973 | 11330688 | 99767311 | 49946251 | 46536396 | 0.000000 | 0.000000 | 187529373
10-04-2025 0:21:50.000 | 33123336 |  | 33.1233 | -1820073 | 15611441 | 12272303 | 99849373 | 49908058 | 46096758 | 0.000000 | 0.000000 | 184772903
10-04-2025 0:21:45.000 | 32856961 |  | 32.857 | -1648292 | 15609200 | 12172560 | 99874405 | 49923775 | 45634961 | 0.000000 | 0.000000 | 182299652
10-04-2025 0:21:40.000 | 32430926 |  | 32.4309 | -1992691 | 15609597 | 12022115 | 99811760 | 49944344 | 45183706 | 0.000000 | 0.000000 | 179760468
10-04-2025 0:21:35.000 | 32224086 |  | 32.2241 | -2373549 | 15609014 | 11954988 | 99729828 | 49957035 | 44734917 | 0.000000 | 0.000000 | 176695038
10-04-2025 0:21:30.000 | 31256438 |  | 31.2564 | -2183708 | 15607530 | 11595624 | 99756836 | 49987297 | 44289229 | 0.000000 | 0.000000 | 173582153
10-04-2025 0:21:25.000 | 29662002 |  | 29.662 | -2590019 | 15611004 | 11016910 | 99620949 | 50013832 | 43867285 | 0.000000 | 0.000000 | 170177948
10-04-2025 0:21:20.000 | 28243770 |  | 28.2438 | -2556535 | 15612805 | 10492390 | 99592834 | 50025562 | 43463027 | 0.000000 | 0.000000 | 166629578
10-04-2025 0:21:15.000 | 26971824 |  | 26.9718 | -2562162 | 15614645 | 10022690 | 99551834 | 50036461 | 43076938 | 0.000000 | 0.000000 | 163100922
10-04-2025 0:21:10.000 | 26318752 |  | 26.3188 | -2293672 | 15614611 | 977355103 | 99622398 | 50047611 | 42707876 | 0.000000 | 0.000000 | 159690201
10-04-2025 0:21:05.000 | 27397695 |  | 27.3977 | -2641324 | 15616706 | 10180838 | 99538498 | 50016144 | 42341138 | 0.000000 | 0.000000 | 156321106
10-04-2025 0:21:00.000 | 29809035 |  | 29.809 | -2184441 | 15615157 | 11055432 | 99732567 | 49964588 | 41943140 | 0.000000 | 0.000000 | 152833084
10-04-2025 0:20:55.000 | 29637715 |  | 29.6377 | -2013821 | 15614655 | 10988560 | 99769951 | 49969734 | 41529331 | 0.000000 | 0.000000 | 150082916
10-04-2025 0:20:50.000 | 30317660 |  | 30.3177 | -1958522 | 15610994 | 11240588 | 99791992 | 49959743 | 41115049 | 0.000000 | 0.000000 | 147359283
10-04-2025 0:20:45.000 | 30984377 |  | 30.9844 | -2252840 | 15609908 | 11494745 | 99736717 | 49934879 | 40690095 | 0.000000 | 0.000000 | 144362579
10-04-2025 0:20:40.000 | 29361553 |  | 29.3616 | -1714527 | 15612925 | 10880498 | 99829941 | 49961132 | 40264275 | 0.000000 | 0.000000 | 141586136
10-04-2025 0:20:35.000 | 27539357 |  | 27.5394 | -1883662 | 15615599 | 10210993 | 99766899 | 49999771 | 39871270 | 0.000000 | 0.000000 | 139234634
10-04-2025 0:20:30.000 | 29175797 |  | 29.1758 | -1858578 | 15613397 | 10815549 | 99797714 | 49964710 | 39479392 | 0.000000 | 0.000000 | 136569962
10-04-2025 0:20:25.000 | 30874236 |  | 30.8742 | -1839607 | 15610979 | 11444170 | 99822960 | 49933033 | 39065273 | 0.000000 | 0.000000 | 134046341
10-04-2025 0:20:20.000 | 31570605 |  | 31.5706 | -1796294 | 15610704 | 11700219 | 99838524 | 49928280 | 38631394 | 0.000000 | 0.000000 | 131470230
10-04-2025 0:20:15.000 | 29859863 |  | 29.8599 | -1763930 | 15610873 | 11066953 | 99825974 | 49957985 | 38201702 | 0.000000 | 0.000000 | 129058823
10-04-2025 0:20:10.000 | 28809854 |  | 28.8099 | -1954766 | 15611674 | 10683353 | 99770607 | 49980087 | 37796487 | 0.000000 | 0.000000 | 126507652
10-04-2025 0:20:05.000 | 28932348 |  | 28.9323 | -1848094 | 15613917 | 10724661 | 99796616 | 49982235 | 37396567 | 0.000000 | 0.000000 | 123816299
10-04-2025 0:20:00.000 | 30111936 |  | 30.1119 | -1849813 | 15613326 | 11160388 | 99811844 | 49960712 | 36990254 | 0.000000 | 0.000000 | 121078049
10-04-2025 0:19:55.000 | 30535359 |  | 30.5354 | -1851865 | 15613542 | 11317537 | 99816605 | 49957115 | 36568694 | 0.000000 | 0.000000 | 118566071
10-04-2025 0:19:50.000 | 31480021 |  | 31.48 | -1732117 | 15611847 | 11663552 | 99848969 | 49951359 | 36136753 | 0.000000 | 0.000000 | 116038239
10-04-2025 0:19:45.000 | 31228941 |  | 31.2289 | -1699940 | 15611668 | 11570637 | 99852173 | 49961040 | 35702266 | 0.000000 | 0.000000 | 113535553
10-04-2025 0:19:40.000 | 31084203 |  | 31.0842 | -1901851 | 15614770 | 11518553 | 99813354 | 49982937 | 35270032 | 0.000000 | 0.000000 | 111077393
10-04-2025 0:19:35.000 | 31428104 |  | 31.4281 | -1657395 | 15612310 | 11643088 | 99861237 | 49984169 | 34834915 | 0.000000 | 0.000000 | 108664894
10-04-2025 0:19:30.000 | 31331357 |  | 31.3314 | -1914252 | 15617325 | 11608590 | 99813881 | 50008392 | 34398792 | 0.000000 | 0.000000 | 106237785
10-04-2025 0:19:25.000 | 32259266 |  | 32.2593 | -1981826 | 15617164 | 11952500 | 99811821 | 50014980 | 33958970 | 0.000000 | 0.000000 | 103611832
10-04-2025 0:19:20.000 | 34170828 |  | 34.1708 | -1954593 | 15617323 | 12657089 | 99836807 | 49991096 | 33500225 | 0.000000 | 0.000000 | 100908493
10-04-2025 0:19:15.000 | 36083590 |  | 36.0836 | -1678276 | 15616228 | 13360303 | 99892014 | 49964939 | 33013259 | 0.000000 | 0.000000 | 98210686
10-04-2025 0:19:10.000 | 37458379 |  | 37.4584 | -1519492 | 15614626 | 13864980 | 99917824 | 49958126 | 32502043 | 0.000000 | 0.000000 | 95993912
10-04-2025 0:19:05.000 | 37909055 |  | 37.9091 | -1491196 | 15614570 | 14032080 | 99922722 | 49970531 | 31980396 | 0.000000 | 0.000000 | 93902237
10-04-2025 0:19:00.000 | 39159832 |  | 39.1598 | -1828019 | 15614036 | 14498971 | 99891220 | 49954826 | 31445000 | 0.000000 | 0.000000 | 91691734
10-04-2025 0:18:55.000 | 39908219 |  | 39.9082 | -1677786 | 15610412 | 14776327 | 99911743 | 49947590 | 30897646 | 0.000000 | 0.000000 | 89236832
10-04-2025 0:18:50.000 | 38845715 |  | 38.8457 | -1807119 | 15613980 | 14382953 | 99891968 | 49979103 | 30350112 | 0.000000 | 0.000000 | 86779510
10-04-2025 0:18:45.000 | 39483297 |  | 39.4833 | -1739703 | 15617864 | 14613756 | 99903069 | 49993027 | 29806924 | 0.000000 | 0.000000 | 84269623
10-04-2025 0:18:40.000 | 40946395 |  | 40.9464 | -1796554 | 15616521 | 15156179 | 99903885 | 49973595 | 29251108 | 0.000000 | 0.000000 | 81793884
10-04-2025 0:18:35.000 | 42253426 |  | 42.2534 | -1559376 | 15616178 | 15635195 | 99931969 | 49972874 | 28670186 | 0.000000 | 0.000000 | 79560356
10-04-2025 0:18:30.000 | 44056277 |  | 44.0563 | -1448137 | 15614523 | 16302208 | 99946022 | 49960514 | 28073447 | 0.000000 | 0.000000 | 77414474
10-04-2025 0:18:25.000 | 44781848 |  | 44.7818 | -1477350 | 15613299 | 16571868 | 99945625 | 49951557 | 27457754 | 0.000000 | 0.000000 | 75438293
10-04-2025 0:18:20.000 | 45247027 |  | 45.247 | -1305857 | 15609715 | 16745002 | 99958382 | 49947853 | 26829436 | 0.000000 | 0.000000 | 73482132
10-04-2025 0:18:15.000 | 45058801 |  | 45.0588 | -1713038 | 15610300 | 16680576 | 99927811 | 49968250 | 26202034 | 0.000000 | 0.000000 | 71520348
10-04-2025 0:18:10.000 | 43376047 |  | 43.376 | -1231224 | 15612024 | 16050630 | 99959740 | 50010464 | 25584224 | 0.000000 | 0.000000 | 69514008
10-04-2025 0:18:05.000 | 43520125 |  | 43.5201 | -1484138 | 15619217 | 16099026 | 99941902 | 50039688 | 24983928 | 0.000000 | 0.000000 | 67543579
10-04-2025 0:18:00.000 | 45409074 |  | 45.4091 | -1531272 | 15618745 | 16798202 | 99943192 | 50018837 | 24371958 | 0.000000 | 0.000000 | 65384926
10-04-2025 0:17:55.000 | 47480238 |  | 47.4802 | -1276743 | 15617656 | 17561537 | 99963867 | 49986233 | 23728567 | 0.000000 | 0.000000 | 63301640
10-04-2025 0:17:50.000 | 49066836 |  | 49.0668 | -1024191 | 15614063 | 18149482 | 99978226 | 49980301 | 23059575 | 0.000000 | 0.000000 | 61660591
10-04-2025 0:17:45.000 | 50049813 |  | 50.0498 | -1253528 | 15611771 | 18517922 | 99968651 | 49970737 | 22375894 | 0.000000 | 0.000000 | 60048870
10-04-2025 0:17:40.000 | 50118027 |  | 50.118 | -1065634 | 15607995 | 18546013 | 99977402 | 49979702 | 21675261 | 0.000000 | 0.000000 | 58501102
10-04-2025 0:17:35.000 | 50022543 |  | 50.0225 | -1391852 | 15609161 | 18512134 | 99961311 | 49997154 | 20980173 | 0.000000 | 0.000000 | 56849461
10-04-2025 0:17:30.000 | 48777867 |  | 48.7779 | -1265715 | 15609801 | 18049935 | 99966354 | 50013653 | 20291794 | 0.000000 | 0.000000 | 55047852
10-04-2025 0:17:25.000 | 47661496 |  | 47.6615 | -1304218 | 15613252 | 17633734 | 99962578 | 50020317 | 19619941 | 0.000000 | 0.000000 | 53268063
10-04-2025 0:17:20.000 | 46896230 |  | 46.8962 | -1172945 | 15616823 | 17345793 | 99968735 | 50023972 | 18963833 | 0.000000 | 0.000000 | 51499100
10-04-2025 0:17:15.000 | 46546930 |  | 46.5469 | -1213208 | 15618342 | 17215320 | 99966049 | 50023411 | 18316538 | 0.000000 | 0.000000 | 49884247
10-04-2025 0:17:10.000 | 49026586 |  | 49.0266 | -1261376 | 15614979 | 18136616 | 99966919 | 49978058 | 17656848 | 0.000000 | 0.000000 | 48047161
10-04-2025 0:17:05.000 | 50817117 |  | 50.8171 | -1154879 | 15609583 | 18803184 | 99974190 | 49947231 | 16964669 | 0.000000 | 0.000000 | 46279854
10-04-2025 0:17:00.000 | 50249219 |  | 50.2492 | -1121600 | 15611724 | 18590901 | 99975098 | 49963547 | 16262126 | 0.000000 | 0.000000 | 44682301
10-04-2025 0:16:55.000 | 49424031 |  | 49.424 | -1411333 | 15611725 | 18288530 | 99959251 | 49983101 | 15569590 | 0.000000 | 0.000000 | 43080784
10-04-2025 0:16:50.000 | 49122793 |  | 49.1228 | -1262926 | 15613049 | 18173546 | 99966965 | 49977760 | 14882319 | 0.000000 | 0.000000 | 41180332
10-04-2025 0:16:45.000 | 48457563 |  | 48.4576 | -1239898 | 15610709 | 17930198 | 99967278 | 49989594 | 14201632 | 0.000000 | 0.000000 | 39595314
10-04-2025 0:16:40.000 | 47439797 |  | 47.4398 | -1131230 | 15612979 | 17550569 | 99971581 | 50011845 | 13535229 | 0.000000 | 0.000000 | 37957554
10-04-2025 0:16:35.000 | 48101949 |  | 48.1019 | -1248868 | 15612101 | 17797593 | 99966316 | 50010841 | 12873312 | 0.000000 | 0.000000 | 36302635
10-04-2025 0:16:30.000 | 48542691 |  | 48.5427 | -1167970 | 15611978 | 17959662 | 99971069 | 49992081 | 12203950 | 0.000000 | 0.000000 | 34353764
10-04-2025 0:16:25.000 | 47704254 |  | 47.7043 | -1293388 | 15615257 | 17647596 | 99963264 | 50007687 | 11537523 | 0.000000 | 0.000000 | 32669220
10-04-2025 0:16:20.000 | 48550004 |  | 48.55 | -1256718 | 15614317 | 17960460 | 99966515 | 49992561 | 10870349 | 0.000000 | 0.000000 | 30912453
10-04-2025 0:16:15.000 | 49129504 |  | 49.1295 | -1269129 | 15615770 | 18173029 | 99966652 | 49971508 | 10193602 | 0.000000 | 0.000000 | 29098959
10-04-2025 0:16:10.000 | 48987543 |  | 48.9875 | -1111378 | 15615396 | 18120148 | 99974274 | 49972115 | 950903748 | 0.000000 | 0.000000 | 27532932
10-04-2025 0:16:05.000 | 50153293 |  | 50.1533 | -1071241 | 15612563 | 18553907 | 99977196 | 49963886 | 882337708 | 0.000000 | 0.000000 | 25994303
10-04-2025 0:16:00.000 | 50696480 |  | 50.6965 | -1281444 | 15612796 | 18755942 | 99968071 | 49961510 | 812084229 | 0.000000 | 0.000000 | 24455042
10-04-2025 0:15:55.000 | 50588160 |  | 50.5882 | -1162096 | 15611395 | 18716354 | 99973625 | 49977001 | 741411011 | 0.000000 | 0.000000 | 22810827
10-04-2025 0:15:50.000 | 49948152 |  | 49.9482 | -1426457 | 15609155 | 18485074 | 99959244 | 49992657 | 671671997 | 0.000000 | 0.000000 | 21163994
10-04-2025 0:15:45.000 | 49750273 |  | 49.7503 | -1304747 | 15608402 | 18411350 | 99965630 | 49985489 | 602239380 | 0.000000 | 0.000000 | 19231096
10-04-2025 0:15:40.000 | 48150055 |  | 48.1501 | -1371152 | 15609471 | 17819198 | 99959480 | 50014328 | 533973572 | 0.000000 | 0.000000 | 17382353
10-04-2025 0:15:35.000 | 46055438 |  | 46.0554 | -1385276 | 15616019 | 17037848 | 99954796 | 50034309 | 468610229 | 0.000000 | 0.000000 | 15421676
10-04-2025 0:15:30.000 | 46257902 |  | 46.2579 | -1404476 | 15618168 | 17110563 | 99953941 | 50024803 | 404345337 | 0.000000 | 0.000000 | 13591955
10-04-2025 0:15:25.000 | 47850113 |  | 47.8501 | -1516933 | 15614016 | 17704613 | 99949791 | 49994034 | 339328827 | 0.000000 | 0.000000 | 11612015
10-04-2025 0:15:20.000 | 48556875 |  | 48.5569 | -1631636 | 15612030 | 17970098 | 99943588 | 49967087 | 272243561 | 0.000000 | 0.000000 | 9609579
10-04-2025 0:15:15.000 | 48715633 |  | 48.7156 | -1674536 | 15613896 | 18026791 | 99940971 | 49970943 | 204505600 | 0.000000 | 0.000000 | 7272265
10-04-2025 0:15:10.000 | 48959523 |  | 48.9595 | -1896024 | 15612729 | 18121154 | 99925095 | 49974548 | 136930710 | 0.000000 | 0.000000 | 4854575
10-04-2025 0:15:05.000 | 49026094 |  | 49.0261 | -1884716 | 15616278 | 18141521 | 99926186 | 49956821 | 68759857 | 0.000000 | 0.000000 | 2294488
10-04-2025 0:15:00.000 | 49765852 |  | 49.7659 | -1575375 | 15613414 | 18414192 | 99949936 | 49961639 | 12269909 | 0.000000 | 0.000000 | 951880676
10-04-2025 0:14:55.000 | 50472867 |  | 50.4729 | -2005901 | 15614157 | 18680344 | 99921120 | 49965336 | 12200379 | 0.000000 | 0.000000 | 949416565
10-04-2025 0:14:50.000 | 50894957 |  | 50.895 | -1975805 | 15609779 | 18840836 | 99924728 | 49966572 | 12129555 | 0.000000 | 0.000000 | 946828308
10-04-2025 0:14:45.000 | 50741840 |  | 50.7418 | -1903208 | 15609361 | 18783580 | 99929733 | 49979778 | 12058843 | 0.000000 | 0.000000 | 944152893
10-04-2025 0:14:40.000 | 49587441 |  | 49.5874 | -1919010 | 15613302 | 18352607 | 99925201 | 49999714 | 11988990 | 0.000000 | 0.000000 | 941396423
10-04-2025 0:14:35.000 | 49657680 |  | 49.6577 | -1993496 | 15613610 | 18379298 | 99919518 | 50011288 | 11920309 | 0.000000 | 0.000000 | 938668579
10-04-2025 0:14:30.000 | 50532965 |  | 50.533 | -2050997 | 15611215 | 18706692 | 99917732 | 49994976 | 11851093 | 0.000000 | 0.000000 | 935726746
10-04-2025 0:14:25.000 | 51209449 |  | 51.2094 | -2206696 | 15610705 | 18959536 | 99907288 | 50000092 | 11780404 | 0.000000 | 0.000000 | 932780396
10-04-2025 0:14:20.000 | 51383871 |  | 51.3839 | -2350417 | 15609782 | 19027949 | 99895546 | 50005859 | 11709222 | 0.000000 | 0.000000 | 929565735
10-04-2025 0:14:15.000 | 50933219 |  | 50.9332 | -2256805 | 15607545 | 18863093 | 99901978 | 50021870 | 11638018 | 0.000000 | 0.000000 | 926242493
10-04-2025 0:14:10.000 | 49074242 |  | 49.0742 | -2389950 | 15610405 | 18174401 | 99881622 | 50054691 | 11568476 | 0.000000 | 0.000000 | 922897949
10-04-2025 0:14:05.000 | 48448090 |  | 48.4481 | -2593134 | 15611576 | 17945402 | 99857063 | 50067539 | 11500823 | 0.000000 | 0.000000 | 919453369
10-04-2025 0:14:00.000 | 48402250 |  | 48.4023 | -2507632 | 15612037 | 17926522 | 99866066 | 50069202 | 11433579 | 0.000000 | 0.000000 | 915787048
10-04-2025 0:13:55.000 | 46848973 |  | 46.849 | -2373429 | 15615893 | 17345898 | 99871918 | 50083393 | 11367421 | 0.000000 | 0.000000 | 912340454
10-04-2025 0:13:50.000 | 47540340 |  | 47.5403 | -2581735 | 15615938 | 17605365 | 99852867 | 50069141 | 11302277 | 0.000000 | 0.000000 | 908881653
10-04-2025 0:13:45.000 | 49452504 |  | 49.4525 | -2696563 | 15615711 | 18313801 | 99851662 | 50044033 | 11235063 | 0.000000 | 0.000000 | 905375488
10-04-2025 0:13:40.000 | 51622203 |  | 51.6222 | -2546379 | 15608107 | 19121589 | 99878563 | 49998741 | 11165074 | 0.000000 | 0.000000 | 901646484
10-04-2025 0:13:35.000 | 50709266 |  | 50.7093 | -2957636 | 15608434 | 18791718 | 99830338 | 50021736 | 11093633 | 0.000000 | 0.000000 | 897894897
10-04-2025 0:13:30.000 | 49162207 |  | 49.1622 | -2727970 | 15610187 | 18213633 | 99846405 | 50056683 | 11023539 | 0.000000 | 0.000000 | 893953674
10-04-2025 0:13:25.000 | 47886496 |  | 47.8865 | -3032167 | 15611656 | 17747650 | 99800133 | 50078911 | 10956303 | 0.000000 | 0.000000 | 890078552
10-04-2025 0:13:20.000 | 47156266 |  | 47.1563 | -2760759 | 15612777 | 17470719 | 99829063 | 50063751 | 10890074 | 0.000000 | 0.000000 | 885853333
10-04-2025 0:13:15.000 | 47371402 |  | 47.3714 | -2750932 | 15615759 | 17546575 | 99831810 | 50064514 | 10824194 | 0.000000 | 0.000000 | 882029785
10-04-2025 0:13:10.000 | 47994051 |  | 47.9941 | -2795599 | 15613591 | 17779725 | 99830788 | 50057556 | 10758149 | 0.000000 | 0.000000 | 878357361
10-04-2025 0:13:05.000 | 48130926 |  | 48.1309 | -2594023 | 15612784 | 17826827 | 99855080 | 50056213 | 10691266 | 0.000000 | 0.000000 | 874577942
10-04-2025 0:13:00.000 | 48533500 |  | 48.5335 | -2591138 | 15610455 | 17978552 | 99857788 | 50038105 | 10623945 | 0.000000 | 0.000000 | 870989685
10-04-2025 0:12:55.000 | 46836758 |  | 46.8368 | -2568590 | 15612053 | 17349620 | 99849960 | 50057583 | 10557400 | 0.000000 | 0.000000 | 867590759
10-04-2025 0:12:50.000 | 46231688 |  | 46.2317 | -2613073 | 15617552 | 17120962 | 99840652 | 50068619 | 10493052 | 0.000000 | 0.000000 | 864015503
10-04-2025 0:12:45.000 | 47388379 |  | 47.3884 | -2170681 | 15617150 | 17540541 | 99895256 | 50037949 | 10428386 | 0.000000 | 0.000000 | 860466064
10-04-2025 0:12:40.000 | 48722035 |  | 48.722 | -2187587 | 15613843 | 18037411 | 99899353 | 50006100 | 10362036 | 0.000000 | 0.000000 | 857393494
10-04-2025 0:12:35.000 | 49546207 |  | 49.5462 | -2226441 | 15612393 | 18343521 | 99899185 | 49986275 | 10293660 | 0.000000 | 0.000000 | 854367798
10-04-2025 0:12:30.000 | 49908633 |  | 49.9086 | -2504725 | 15611663 | 18483920 | 99874306 | 49986164 | 10224607 | 0.000000 | 0.000000 | 851241638
10-04-2025 0:12:25.000 | 49818188 |  | 49.8182 | -2289672 | 15613671 | 18443729 | 99894547 | 49982525 | 10155366 | 0.000000 | 0.000000 | 847816223
10-04-2025 0:12:20.000 | 49368852 |  | 49.3689 | -2378887 | 15613605 | 18280386 | 99884109 | 49998825 | 10086459 | 0.000000 | 0.000000 | 844668823
10-04-2025 0:12:15.000 | 50068625 |  | 50.0686 | -2188861 | 15612571 | 18535702 | 99904579 | 49983906 | 10017552 | 0.000000 | 0.000000 | 841497986
10-04-2025 0:12:10.000 | 49842297 |  | 49.8423 | -2165623 | 15609138 | 18456357 | 99905739 | 49974861 | 99479854 | 0.000000 | 0.000000 | 838483032
10-04-2025 0:12:05.000 | 48521195 |  | 48.5212 | -2205558 | 15611674 | 17965184 | 99896851 | 49998787 | 98792236 | 0.000000 | 0.000000 | 835375732
10-04-2025 0:12:00.000 | 47891895 |  | 47.8919 | -2350028 | 15613028 | 17734392 | 99879829 | 50016815 | 98124053 | 0.000000 | 0.000000 | 832231873
10-04-2025 0:11:55.000 | 48322383 |  | 48.3224 | -2470933 | 15614503 | 17893148 | 99869522 | 50011562 | 97458076 | 0.000000 | 0.000000 | 828905151
10-04-2025 0:11:50.000 | 49159613 |  | 49.1596 | -2437516 | 15612971 | 18203684 | 99877296 | 49996716 | 96780332 | 0.000000 | 0.000000 | 825550110
10-04-2025 0:11:45.000 | 48976156 |  | 48.9762 | -2300429 | 15614008 | 18132277 | 99889870 | 49995750 | 96098887 | 0.000000 | 0.000000 | 822270081
10-04-2025 0:11:40.000 | 48618492 |  | 48.6185 | -2258166 | 15614957 | 17998864 | 99892311 | 50007126 | 95420352 | 0.000000 | 0.000000 | 819231567
10-04-2025 0:11:35.000 | 49958680 |  | 49.9587 | -2552712 | 15611704 | 18502518 | 99869713 | 49993732 | 94738262 | 0.000000 | 0.000000 | 815946716
10-04-2025 0:11:30.000 | 50350488 |  | 50.3505 | -2406750 | 15611758 | 18644263 | 99885956 | 49988747 | 94040293 | 0.000000 | 0.000000 | 812490051
10-04-2025 0:11:25.000 | 49981621 |  | 49.9816 | -2372159 | 15611521 | 18507754 | 99887566 | 50007996 | 93341240 | 0.000000 | 0.000000 | 809159729
10-04-2025 0:11:20.000 | 50106996 |  | 50.107 | -2461558 | 15611890 | 18555149 | 99879547 | 50007645 | 92650771 | 0.000000 | 0.000000 | 805684814
10-04-2025 0:11:15.000 | 49725129 |  | 49.7251 | -2489171 | 15609915 | 18416953 | 99874939 | 50004311 | 91957402 | 0.000000 | 0.000000 | 802191711
10-04-2025 0:11:10.000 | 49400949 |  | 49.4009 | -2478423 | 15609589 | 18297371 | 99874390 | 50015106 | 91266152 | 0.000000 | 0.000000 | 798709351
10-04-2025 0:11:05.000 | 47887277 |  | 47.8873 | -2363211 | 15610759 | 17736077 | 99878456 | 50033276 | 90587920 | 0.000000 | 0.000000 | 795335999
10-04-2025 0:11:00.000 | 46491934 |  | 46.4919 | -2361110 | 15613564 | 17216564 | 99871292 | 50040905 | 89931572 | 0.000000 | 0.000000 | 792095215
10-04-2025 0:10:55.000 | 45795410 |  | 45.7954 | -2210774 | 15614815 | 16955188 | 99883682 | 50048260 | 89289951 | 0.000000 | 0.000000 | 788923645
10-04-2025 0:10:50.000 | 46140305 |  | 46.1403 | -2477870 | 15618046 | 17084153 | 99856110 | 50036396 | 88657090 | 0.000000 | 0.000000 | 785597961
10-04-2025 0:10:45.000 | 48459391 |  | 48.4594 | -2070765 | 15613690 | 17938274 | 99908821 | 49977589 | 88002236 | 0.000000 | 0.000000 | 782340332
10-04-2025 0:10:40.000 | 49383563 |  | 49.3836 | -2209414 | 15612868 | 18282616 | 99900070 | 49968559 | 87323457 | 0.000000 | 0.000000 | 779316589
10-04-2025 0:10:35.000 | 50056766 |  | 50.0568 | -2441852 | 15611254 | 18537021 | 99881233 | 49946396 | 86634453 | 0.000000 | 0.000000 | 776049316
10-04-2025 0:10:30.000 | 49833590 |  | 49.8336 | -2615179 | 15611604 | 18457456 | 99862587 | 49952606 | 85937930 | 0.000000 | 0.000000 | 772542725
10-04-2025 0:10:25.000 | 48721188 |  | 48.7212 | -1870724 | 15615253 | 18029910 | 99926369 | 49976387 | 85250820 | 0.000000 | 0.000000 | 769141602
10-04-2025 0:10:20.000 | 48135074 |  | 48.1351 | -1843238 | 15614255 | 17814595 | 99926765 | 49990143 | 84579805 | 0.000000 | 0.000000 | 766722229
10-04-2025 0:10:15.000 | 49187316 |  | 49.1873 | -1931078 | 15616565 | 18201603 | 99923019 | 49968575 | 83907363 | 0.000000 | 0.000000 | 763977905
10-04-2025 0:10:10.000 | 49956000 |  | 49.956 | -1769323 | 15612218 | 18488622 | 99937340 | 49960442 | 83221592 | 0.000000 | 0.000000 | 761368896
10-04-2025 0:10:05.000 | 50167359 |  | 50.1674 | -1857372 | 15613189 | 18567531 | 99931534 | 49968090 | 82522803 | 0.000000 | 0.000000 | 758956787
10-04-2025 0:10:00.000 | 50072051 |  | 50.0721 | -1764177 | 15611307 | 18532328 | 99937988 | 49972145 | 81827544 | 0.000000 | 0.000000 | 756421387
10-04-2025 0:09:55.000 | 49444859 |  | 49.4449 | -1869058 | 15614095 | 18298831 | 99928635 | 49984203 | 81138052 | 0.000000 | 0.000000 | 753865967
10-04-2025 0:09:50.000 | 49926117 |  | 49.9261 | -1979057 | 15611779 | 18481102 | 99921524 | 49986362 | 80448672 | 0.000000 | 0.000000 | 751202271
10-04-2025 0:09:45.000 | 50157441 |  | 50.1574 | -2077972 | 15611847 | 18568186 | 99914291 | 49996304 | 79754790 | 0.000000 | 0.000000 | 748321899
10-04-2025 0:09:40.000 | 49165402 |  | 49.1654 | -2006650 | 15612916 | 18199338 | 99916817 | 50012642 | 79062754 | 0.000000 | 0.000000 | 745627075
10-04-2025 0:09:35.000 | 49278852 |  | 49.2789 | -2249652 | 15613848 | 18243666 | 99895958 | 50015724 | 78379150 | 0.000000 | 0.000000 | 742773010
10-04-2025 0:09:30.000 | 50337445 |  | 50.3374 | -2354316 | 15611788 | 18640198 | 99890808 | 50000774 | 77688521 | 0.000000 | 0.000000 | 739673584
10-04-2025 0:09:25.000 | 49496309 |  | 49.4963 | -1990990 | 15612704 | 18321487 | 99919197 | 50019588 | 76990098 | 0.000000 | 0.000000 | 736813599
10-04-2025 0:09:20.000 | 49858164 |  | 49.8582 | -2396861 | 15615068 | 18459174 | 99884644 | 50023430 | 76302949 | 0.000000 | 0.000000 | 733762817
10-04-2025 0:09:15.000 | 49916832 |  | 49.9168 | -2251188 | 15611659 | 18481932 | 99898460 | 50007523 | 75609766 | 0.000000 | 0.000000 | 730627014
10-04-2025 0:09:10.000 | 49399906 |  | 49.3999 | -2311808 | 15613436 | 18290331 | 99890678 | 50021465 | 74916343 | 0.000000 | 0.000000 | 727526550
10-04-2025 0:09:05.000 | 50051125 |  | 50.0511 | -2434391 | 15612705 | 18533905 | 99881927 | 50018852 | 74228145 | 0.000000 | 0.000000 | 724136230
10-04-2025 0:09:00.000 | 49715055 |  | 49.7151 | -2506992 | 15611577 | 18411843 | 99873100 | 50041561 | 73536528 | 0.000000 | 0.000000 | 720720093
10-04-2025 0:08:55.000 | 50276156 |  | 50.2762 | -2971948 | 15611537 | 18628595 | 99825745 | 50049160 | 72843218 | 0.000000 | 0.000000 | 717001343
10-04-2025 0:08:50.000 | 50243730 |  | 50.2437 | -2779920 | 15611567 | 18612332 | 99847290 | 50052425 | 72143501 | 0.000000 | 0.000000 | 712938293
10-04-2025 0:08:45.000 | 48986250 |  | 48.9862 | -2360043 | 15610459 | 18141501 | 99884148 | 50076176 | 71447695 | 0.000000 | 0.000000 | 709440613
10-04-2025 0:08:40.000 | 49535266 |  | 49.5353 | -3326454 | 15612826 | 18361699 | 99775284 | 50083698 | 70768667 | 0.000000 | 0.000000 | 705574402
10-04-2025 0:08:35.000 | 49232020 |  | 49.232 | -3048988 | 15614233 | 18241794 | 99808777 | 50075890 | 70082529 | 0.000000 | 0.000000 | 701093872
10-04-2025 0:08:30.000 | 49030988 |  | 49.031 | -3373393 | 15614942 | 18174490 | 99764160 | 50085426 | 69398940 | 0.000000 | 0.000000 | 696729675
10-04-2025 0:08:25.000 | 49959285 |  | 49.9593 | -3240096 | 15611446 | 18517562 | 99790352 | 50083992 | 68710767 | 0.000000 | 0.000000 | 692223938
10-04-2025 0:08:20.000 | 50476949 |  | 50.4769 | -3498791 | 15610459 | 18716165 | 99760635 | 50082531 | 68015024 | 0.000000 | 0.000000 | 687565552
10-04-2025 0:08:15.000 | 50997016 |  | 50.997 | -3585979 | 15609635 | 18911331 | 99753685 | 50085369 | 67309438 | 0.000000 | 0.000000 | 682645569
10-04-2025 0:08:10.000 | 49259656 |  | 49.2597 | -3548171 | 15613059 | 18266024 | 99741592 | 50117989 | 66613081 | 0.000000 | 0.000000 | 677705933
10-04-2025 0:08:05.000 | 49910742 |  | 49.9107 | -3884266 | 15613748 | 18514136 | 99698540 | 50122337 | 65926006 | 0.000000 | 0.000000 | 672479736
10-04-2025 0:08:00.000 | 50328387 |  | 50.3284 | -3474050 | 15611873 | 18659077 | 99762604 | 50107651 | 65230024 | 0.000000 | 0.000000 | 667254639
10-04-2025 0:07:55.000 | 49829023 |  | 49.829 | -3286737 | 15614063 | 18467743 | 99783173 | 50113514 | 64531567 | 0.000000 | 0.000000 | 662522827
10-04-2025 0:07:50.000 | 48917445 |  | 48.9174 | -3338436 | 15614342 | 18132728 | 99767929 | 50152534 | 63847734 | 0.000000 | 0.000000 | 658149902
10-04-2025 0:07:45.000 | 49910289 |  | 49.9103 | -3843635 | 15612783 | 18514197 | 99704781 | 50130905 | 63166948 | 0.000000 | 0.000000 | 653129639
10-04-2025 0:07:40.000 | 51492523 |  | 51.4925 | -3802335 | 15610984 | 19098457 | 99728477 | 50101231 | 62461299 | 0.000000 | 0.000000 | 647831909
10-04-2025 0:07:35.000 | 50665426 |  | 50.6654 | -3659997 | 15608901 | 18791853 | 99740097 | 50129639 | 61748257 | 0.000000 | 0.000000 | 642687073
10-04-2025 0:07:30.000 | 48998598 |  | 48.9986 | -3897024 | 15611139 | 18181984 | 99685211 | 50167850 | 61057534 | 0.000000 | 0.000000 | 637471680
10-04-2025 0:07:25.000 | 49055125 |  | 49.0551 | -3993547 | 15610889 | 18205295 | 99670265 | 50156750 | 60377026 | 0.000000 | 0.000000 | 631879028
10-04-2025 0:07:20.000 | 48240750 |  | 48.2407 | -3987542 | 15611949 | 17903709 | 99660110 | 50169575 | 59696392 | 0.000000 | 0.000000 | 626408325
10-04-2025 0:07:15.000 | 46668129 |  | 46.6681 | -4010631 | 15615168 | 17321699 | 99632751 | 50188622 | 59034438 | 0.000000 | 0.000000 | 620977417
10-04-2025 0:07:10.000 | 47284773 |  | 47.2848 | -3845537 | 15614142 | 17544526 | 99670929 | 50180073 | 58385415 | 0.000000 | 0.000000 | 615453003
10-04-2025 0:07:05.000 | 48744598 |  | 48.7446 | -4045118 | 15613473 | 18089454 | 99657433 | 50155270 | 57725176 | 0.000000 | 0.000000 | 609953247
10-04-2025 0:07:00.000 | 49881020 |  | 49.881 | -4507305 | 15610981 | 18525879 | 99594223 | 50136330 | 57044365 | 0.000000 | 0.000000 | 604078308
10-04-2025 0:06:55.000 | 50409129 |  | 50.4091 | -4172715 | 15610899 | 18709897 | 99659149 | 50121967 | 56342261 | 0.000000 | 0.000000 | 597925110
10-04-2025 0:06:50.000 | 49122758 |  | 49.1228 | -3944735 | 15609706 | 18230702 | 99679115 | 50161022 | 55649043 | 0.000000 | 0.000000 | 592294128
10-04-2025 0:06:45.000 | 46675891 |  | 46.6759 | -4272124 | 15614158 | 17334254 | 99583748 | 50189369 | 54986714 | 0.000000 | 0.000000 | 586658630
10-04-2025 0:06:40.000 | 47436164 |  | 47.4362 | -4576053 | 15618196 | 17619933 | 99537926 | 50171642 | 54334619 | 0.000000 | 0.000000 | 580528931
10-04-2025 0:06:35.000 | 48905656 |  | 48.9057 | -4428414 | 15614589 | 18159644 | 99592537 | 50145378 | 53664609 | 0.000000 | 0.000000 | 574290161
10-04-2025 0:06:30.000 | 50200105 |  | 50.2001 | -4504364 | 15611661 | 18642568 | 99599854 | 50136189 | 52977334 | 0.000000 | 0.000000 | 568089417
10-04-2025 0:06:25.000 | 51081883 |  | 51.0819 | -4836898 | 15608836 | 18981724 | 99554688 | 50123405 | 52273989 | 0.000000 | 0.000000 | 561653564
10-04-2025 0:06:20.000 | 50398715 |  | 50.3987 | -4751291 | 15608322 | 18727732 | 99558563 | 50138100 | 51564297 | 0.000000 | 0.000000 | 555042236
10-04-2025 0:06:15.000 | 48376500 |  | 48.3765 | -4812284 | 15611501 | 17982053 | 99508873 | 50179905 | 50875581 | 0.000000 | 0.000000 | 548394775
10-04-2025 0:06:10.000 | 47193945 |  | 47.1939 | -4700606 | 15613248 | 17541975 | 99507637 | 50190907 | 50209023 | 0.000000 | 0.000000 | 541771362
10-04-2025 0:06:05.000 | 46884906 |  | 46.8849 | -4675631 | 15614171 | 17425442 | 99506416 | 50182034 | 49557188 | 0.000000 | 0.000000 | 535144165
10-04-2025 0:06:00.000 | 46837227 |  | 46.8372 | -4955662 | 15617403 | 17415745 | 99444908 | 50174557 | 48908594 | 0.000000 | 0.000000 | 528367004
10-04-2025 0:05:55.000 | 48161125 |  | 48.1611 | -4547054 | 15615223 | 17890057 | 99557266 | 50145748 | 48250591 | 0.000000 | 0.000000 | 521650574
10-04-2025 0:05:50.000 | 48578164 |  | 48.5782 | -4291524 | 15610302 | 18039694 | 99612045 | 50138016 | 47580000 | 0.000000 | 0.000000 | 515485229
10-04-2025 0:05:45.000 | 48082469 |  | 48.0825 | -5037800 | 15607942 | 17886674 | 99455597 | 50139900 | 46908135 | 0.000000 | 0.000000 | 509411285
10-04-2025 0:05:40.000 | 47925309 |  | 47.9253 | -5068466 | 15611675 | 17825787 | 99445412 | 50140892 | 46238232 | 0.000000 | 0.000000 | 502284576
10-04-2025 0:05:35.000 | 47290906 |  | 47.2909 | -4974393 | 15613876 | 17586642 | 99451332 | 50145763 | 45579775 | 0.000000 | 0.000000 | 495277100
10-04-2025 0:05:30.000 | 47758004 |  | 47.758 | -5029554 | 15616312 | 17757366 | 99450027 | 50125164 | 44923281 | 0.000000 | 0.000000 | 488284485
10-04-2025 0:05:25.000 | 48928098 |  | 48.9281 | -5045693 | 15614881 | 18190171 | 99472466 | 50114594 | 44250698 | 0.000000 | 0.000000 | 481339752
10-04-2025 0:05:20.000 | 50212441 |  | 50.2124 | -5121333 | 15611916 | 18668379 | 99483894 | 50084503 | 43564404 | 0.000000 | 0.000000 | 474160248
10-04-2025 0:05:15.000 | 49540961 |  | 49.541 | -5044514 | 15612260 | 18418282 | 99485580 | 50105125 | 42866890 | 0.000000 | 0.000000 | 467218475
10-04-2025 0:05:10.000 | 49574527 |  | 49.5745 | -5361225 | 15614523 | 18440189 | 99420319 | 50114159 | 42180942 | 0.000000 | 0.000000 | 460074432
10-04-2025 0:05:05.000 | 50443141 |  | 50.4431 | -5402003 | 15614621 | 18761176 | 99431465 | 50107361 | 41484980 | 0.000000 | 0.000000 | 452551331
10-04-2025 0:05:00.000 | 50668941 |  | 50.6689 | -4943562 | 15609466 | 18832764 | 99527412 | 50110565 | 40781199 | 0.000000 | 0.000000 | 445383301
10-04-2025 0:04:55.000 | 49420020 |  | 49.42 | -4896405 | 15610846 | 18370044 | 99512772 | 50139683 | 40084023 | 0.000000 | 0.000000 | 438563904
10-04-2025 0:04:50.000 | 49537852 |  | 49.5379 | -5285543 | 15615143 | 18422838 | 99435600 | 50155186 | 39399138 | 0.000000 | 0.000000 | 431409943
10-04-2025 0:04:45.000 | 50180117 |  | 50.1801 | -5069458 | 15611686 | 18655565 | 99493568 | 50148621 | 38708225 | 0.000000 | 0.000000 | 424105255
10-04-2025 0:04:40.000 | 49909488 |  | 49.9095 | -5301505 | 15612789 | 18562788 | 99440567 | 50160202 | 38014417 | 0.000000 | 0.000000 | 416992157
10-04-2025 0:04:35.000 | 50407742 |  | 50.4077 | -5164776 | 15612604 | 18740963 | 99479195 | 50168961 | 37316633 | 0.000000 | 0.000000 | 409671600
10-04-2025 0:04:30.000 | 49692875 |  | 49.6929 | -5173021 | 15611082 | 18480292 | 99462524 | 50184795 | 36617271 | 0.000000 | 0.000000 | 402593750
10-04-2025 0:04:25.000 | 49411570 |  | 49.4116 | -5030406 | 15611804 | 18370513 | 99485771 | 50190357 | 35926150 | 0.000000 | 0.000000 | 395535095
10-04-2025 0:04:20.000 | 49745746 |  | 49.7457 | -5152272 | 15612643 | 18497341 | 99467918 | 50187340 | 35238579 | 0.000000 | 0.000000 | 388429047
10-04-2025 0:04:15.000 | 49489590 |  | 49.4896 | -4833918 | 15609114 | 18395635 | 99526360 | 50184498 | 34548396 | 0.000000 | 0.000000 | 381344971
10-04-2025 0:04:10.000 | 47753211 |  | 47.7532 | -4779998 | 15611237 | 17752899 | 99502754 | 50214420 | 33869724 | 0.000000 | 0.000000 | 374632355
10-04-2025 0:04:05.000 | 47251895 |  | 47.2519 | -4946414 | 15613426 | 17571216 | 99456551 | 50212017 | 33212637 | 0.000000 | 0.000000 | 367709778
10-04-2025 0:04:00.000 | 46876223 |  | 46.8762 | -4817844 | 15613452 | 17428442 | 99475983 | 50204338 | 32556841 | 0.000000 | 0.000000 | 360940033
10-04-2025 0:03:55.000 | 47688590 |  | 47.6886 | -5039455 | 15614337 | 17734231 | 99446281 | 50198620 | 31902122 | 0.000000 | 0.000000 | 354085968
10-04-2025 0:03:50.000 | 48232023 |  | 48.232 | -4928485 | 15613243 | 17932307 | 99481987 | 50177204 | 31237925 | 0.000000 | 0.000000 | 347147797
10-04-2025 0:03:45.000 | 48238230 |  | 48.2382 | -4859919 | 15612299 | 17932007 | 99496323 | 50180534 | 30565623 | 0.000000 | 0.000000 | 340397552
10-04-2025 0:03:40.000 | 49091867 |  | 49.0919 | -5077973 | 15613679 | 18252534 | 99469284 | 50174103 | 29893979 | 0.000000 | 0.000000 | 333473999
10-04-2025 0:03:35.000 | 49851875 |  | 49.8519 | -4970052 | 15610859 | 18531362 | 99506706 | 50152542 | 29209063 | 0.000000 | 0.000000 | 326472565
10-04-2025 0:03:30.000 | 49103063 |  | 49.1031 | -5018921 | 15610746 | 18257723 | 99481697 | 50168972 | 28515471 | 0.000000 | 0.000000 | 319662872
10-04-2025 0:03:25.000 | 49314266 |  | 49.3143 | -5113729 | 15611099 | 18338595 | 99466644 | 50171421 | 27832634 | 0.000000 | 0.000000 | 312636169
10-04-2025 0:03:20.000 | 49082121 |  | 49.0821 | -5004839 | 15612050 | 18248019 | 99484138 | 50165134 | 27146570 | 0.000000 | 0.000000 | 305523376
10-04-2025 0:03:15.000 | 48043969 |  | 48.044 | -4990631 | 15615675 | 17861648 | 99464813 | 50200794 | 26470989 | 0.000000 | 0.000000 | 298614044
10-04-2025 0:03:10.000 | 48815777 |  | 48.8158 | -5052671 | 15615023 | 18148579 | 99468605 | 50184891 | 25804907 | 0.000000 | 0.000000 | 291535889
10-04-2025 0:03:05.000 | 49444129 |  | 49.4441 | -5083022 | 15612020 | 18384495 | 99475723 | 50174183 | 25122834 | 0.000000 | 0.000000 | 284544861
10-04-2025 0:03:00.000 | 50472582 |  | 50.4726 | -5259699 | 15611641 | 18769934 | 99461403 | 50169102 | 24432429 | 0.000000 | 0.000000 | 277271423
10-04-2025 0:02:55.000 | 49779355 |  | 49.7794 | -5238071 | 15610075 | 18515792 | 99450935 | 50168037 | 23735320 | 0.000000 | 0.000000 | 270102264
10-04-2025 0:02:50.000 | 48769793 |  | 48.7698 | -5093371 | 15611307 | 18138606 | 99459068 | 50192154 | 23044895 | 0.000000 | 0.000000 | 263049591
10-04-2025 0:02:45.000 | 48792102 |  | 48.7921 | -5202560 | 15611796 | 18149454 | 99436333 | 50195305 | 22368071 | 0.000000 | 0.000000 | 255979706
10-04-2025 0:02:40.000 | 48766824 |  | 48.7668 | -5205768 | 15613762 | 18137813 | 99435066 | 50192413 | 21690046 | 0.000000 | 0.000000 | 248731155
10-04-2025 0:02:35.000 | 49409441 |  | 49.4094 | -5280785 | 15613656 | 18377230 | 99433701 | 50189583 | 21008250 | 0.000000 | 0.000000 | 241487473
10-04-2025 0:02:30.000 | 49592016 |  | 49.592 | -5255726 | 15612963 | 18444418 | 99443108 | 50192982 | 20318638 | 0.000000 | 0.000000 | 234185776
10-04-2025 0:02:25.000 | 49864313 |  | 49.8643 | -5551138 | 15613251 | 18555862 | 99386040 | 50212791 | 19626182 | 0.000000 | 0.000000 | 226796509
10-04-2025 0:02:20.000 | 51066168 |  | 51.0662 | -5658375 | 15610445 | 19005082 | 99391708 | 50194328 | 18926453 | 0.000000 | 0.000000 | 218949081
10-04-2025 0:02:15.000 | 50611891 |  | 50.6119 | -5624956 | 15610380 | 18836980 | 99388069 | 50217697 | 18216980 | 0.000000 | 0.000000 | 211146729
10-04-2025 0:02:10.000 | 49278523 |  | 49.2785 | -5707708 | 15610030 | 18351272 | 99335899 | 50246498 | 17522007 | 0.000000 | 0.000000 | 203425919
10-04-2025 0:02:05.000 | 49114215 |  | 49.1142 | -5687732 | 15612462 | 18287317 | 99336113 | 50247353 | 16839266 | 0.000000 | 0.000000 | 195429413
10-04-2025 0:02:00.000 | 49083855 |  | 49.0839 | -5635208 | 15612052 | 18273792 | 99347404 | 50247387 | 16157764 | 0.000000 | 0.000000 | 187524826
10-04-2025 0:01:55.000 | 48875730 |  | 48.8757 | -5725630 | 15614075 | 18199379 | 99320816 | 50250164 | 15476873 | 0.000000 | 0.000000 | 179708481
10-04-2025 0:01:50.000 | 49356918 |  | 49.3569 | -5798490 | 15613692 | 18379022 | 99316978 | 50259178 | 14792175 | 0.000000 | 0.000000 | 171778748
10-04-2025 0:01:45.000 | 50220055 |  | 50.2201 | -5854134 | 15611741 | 18701260 | 99327423 | 50252670 | 14102395 | 0.000000 | 0.000000 | 163623383
10-04-2025 0:01:40.000 | 49397082 |  | 49.3971 | -5803165 | 15610538 | 18397843 | 99316986 | 50259369 | 13407084 | 0.000000 | 0.000000 | 155543091
10-04-2025 0:01:35.000 | 48613984 |  | 48.614 | -5728875 | 15611356 | 18105912 | 99312790 | 50280655 | 12726064 | 0.000000 | 0.000000 | 147471130
10-04-2025 0:01:30.000 | 48195688 |  | 48.1957 | -5807850 | 15612713 | 17954680 | 99281731 | 50288120 | 12056934 | 0.000000 | 0.000000 | 139433533
10-04-2025 0:01:25.000 | 48009727 |  | 48.0097 | -5873354 | 15615467 | 17886169 | 99259979 | 50293312 | 11386754 | 0.000000 | 0.000000 | 131439224
10-04-2025 0:01:20.000 | 49523961 |  | 49.524 | -5603120 | 15612879 | 18433103 | 99366051 | 50268497 | 10710767 | 0.000000 | 0.000000 | 123352280
10-04-2025 0:01:15.000 | 49353426 |  | 49.3534 | -5582876 | 15612884 | 18369786 | 99366264 | 50266064 | 10024772 | 0.000000 | 0.000000 | 115570618
10-04-2025 0:01:10.000 | 49443180 |  | 49.4432 | -5647547 | 15612418 | 18406111 | 99353973 | 50265236 | 933644592 | 0.000000 | 0.000000 | 107789337
10-04-2025 0:01:05.000 | 49629895 |  | 49.6299 | -5816599 | 15612443 | 18481820 | 99320206 | 50268776 | 865046204 | 0.000000 | 0.000000 | 99919159
10-04-2025 0:01:00.000 | 49797688 |  | 49.7977 | -5638090 | 15609888 | 18539454 | 99365158 | 50255894 | 795830627 | 0.000000 | 0.000000 | 92015747
10-04-2025 0:00:55.000 | 49130066 |  | 49.1301 | -5674531 | 15608163 | 18297031 | 99339584 | 50265133 | 726905518 | 0.000000 | 0.000000 | 84160629
10-04-2025 0:00:50.000 | 47558891 |  | 47.5589 | -5599423 | 15612720 | 17712008 | 99314026 | 50289326 | 659643494 | 0.000000 | 0.000000 | 76297691
10-04-2025 0:00:45.000 | 46958238 |  | 46.9582 | -5675368 | 15610205 | 17497242 | 99277550 | 50283371 | 593803955 | 0.000000 | 0.000000 | 68591507
10-04-2025 0:00:40.000 | 46624305 |  | 46.6243 | -5786696 | 15613279 | 17376023 | 99238579 | 50275509 | 528883850 | 0.000000 | 0.000000 | 60477940
10-04-2025 0:00:35.000 | 46392996 |  | 46.393 | -5678666 | 15615430 | 17284094 | 99259186 | 50270809 | 464177734 | 0.000000 | 0.000000 | 52533512
10-04-2025 0:00:30.000 | 46944031 |  | 46.944 | -5785706 | 15615014 | 17491479 | 99249054 | 50249355 | 399367218 | 0.000000 | 0.000000 | 44626415
10-04-2025 0:00:25.000 | 47943441 |  | 47.9434 | -5398418 | 15613771 | 17843672 | 99372032 | 50229321 | 333371246 | 0.000000 | 0.000000 | 36761303
10-04-2025 0:00:20.000 | 47787355 |  | 47.7874 | -5415617 | 15614015 | 17786504 | 99363968 | 50236351 | 266755249 | 0.000000 | 0.000000 | 29349754
10-04-2025 0:00:15.000 | 48518039 |  | 48.518 | -5246251 | 15612221 | 18049772 | 99420471 | 50222050 | 199857147 | 0.000000 | 0.000000 | 21872038
10-04-2025 0:00:10.000 | 48497195 |  | 48.4972 | -5102097 | 15611535 | 18037194 | 99451157 | 50222179 | 132801758 | 0.000000 | 0.000000 | 14607929
10-04-2025 0:00:05.000 | 47464730 |  | 47.4647 | -5290089 | 15613199 | 17663667 | 99384636 | 50232182 | 66052666 | 0.000000 | 0.000000 | 7357205
10-04-2025 0:00:00.000 | 47842613 |  | 47.8426 | -5281729 | 15613089 | 17802271 | 99396126 | 50227108 | 12137878 | 0.000000 | 0.000000 | 17550957
09-04-2025 23:59:55.000 | 48133164 |  | 48.1332 | -5511759 | 15609603 | 17922552 | 99350746 | 50222164 | 12071489 | 0.000000 | 0.000000 | 17475961
09-04-2025 23:59:50.000 | 48123074 |  | 48.1231 | -7062937 | 15607061 | 18000502 | 98940048 | 50219101 | 12004307 | 0.000000 | 0.000000 | 17394922
09-04-2025 23:59:45.000 | 49157168 |  | 49.1572 | -7494151 | 15610527 | 18393760 | 98857780 | 50200890 | 11936759 | 0.000000 | 0.000000 | 17291487
09-04-2025 23:59:40.000 | 47966945 |  | 47.9669 | -7353814 | 15609633 | 17952755 | 98845123 | 50212997 | 11869064 | 0.000000 | 0.000000 | 17188630
09-04-2025 23:59:35.000 | 47807750 |  | 47.8077 | -7457091 | 15614323 | 17894716 | 98805260 | 50224564 | 11802408 | 0.000000 | 0.000000 | 17085154
09-04-2025 23:59:30.000 | 48425117 |  | 48.4251 | -7558865 | 15614920 | 18124844 | 98803558 | 50216225 | 11735897 | 0.000000 | 0.000000 | 16981285
09-04-2025 23:59:25.000 | 48162500 |  | 48.1625 | -7147698 | 15613109 | 18008662 | 98916618 | 50214767 | 11668673 | 0.000000 | 0.000000 | 16879382
09-04-2025 23:59:20.000 | 47786309 |  | 47.7863 | -7204431 | 15617159 | 17869102 | 98882530 | 50220802 | 11602260 | 0.000000 | 0.000000 | 16779589
09-04-2025 23:59:15.000 | 49221121 |  | 49.2211 | -7250477 | 15613971 | 18399719 | 98932419 | 50190998 | 11535504 | 0.000000 | 0.000000 | 16677960
09-04-2025 23:59:10.000 | 50068168 |  | 50.0682 | -6984664 | 15611719 | 18699647 | 99040924 | 50178406 | 11466558 | 0.000000 | 0.000000 | 16577612
09-04-2025 23:59:05.000 | 48914125 |  | 48.9141 | -7038800 | 15610954 | 18280343 | 98980431 | 50205173 | 11397816 | 0.000000 | 0.000000 | 16480686
09-04-2025 23:59:00.000 | 48747891 |  | 48.7479 | -7341471 | 15612111 | 18234393 | 98884903 | 50206703 | 11330237 | 0.000000 | 0.000000 | 16380806
09-04-2025 23:58:55.000 | 48661578 |  | 48.6616 | -7455729 | 15612140 | 18209583 | 98846512 | 50207069 | 11262363 | 0.000000 | 0.000000 | 16279105
09-04-2025 23:58:50.000 | 48672488 |  | 48.6725 | -7663328 | 15613602 | 18223156 | 98783104 | 50215603 | 11194985 | 0.000000 | 0.000000 | 16173877
09-04-2025 23:58:45.000 | 48954566 |  | 48.9546 | -7559473 | 15613397 | 18320668 | 98828659 | 50200306 | 11127217 | 0.000000 | 0.000000 | 16068405
09-04-2025 23:58:40.000 | 48807004 |  | 48.807 | -7399035 | 15611831 | 18259910 | 98870338 | 50202446 | 11059013 | 0.000000 | 0.000000 | 15964797
09-04-2025 23:58:35.000 | 48748371 |  | 48.7484 | -7546980 | 15614493 | 18243134 | 98822739 | 50205063 | 10991427 | 0.000000 | 0.000000 | 15860637
09-04-2025 23:58:30.000 | 48452754 |  | 48.4528 | -7487171 | 15613257 | 18132957 | 98827065 | 50207966 | 10923671 | 0.000000 | 0.000000 | 15757064
09-04-2025 23:58:25.000 | 48177891 |  | 48.1779 | -7386541 | 15612763 | 18027555 | 98845001 | 50218971 | 10856530 | 0.000000 | 0.000000 | 15653654
09-04-2025 23:58:20.000 | 48766754 |  | 48.7668 | -7221010 | 15611584 | 18235732 | 98921432 | 50208809 | 10789439 | 0.000000 | 0.000000 | 15551808
09-04-2025 23:58:15.000 | 49051367 |  | 49.0514 | -7491959 | 15614674 | 18350377 | 98853592 | 50206379 | 10721606 | 0.000000 | 0.000000 | 15449546
09-04-2025 23:58:10.000 | 50338160 |  | 50.3382 | -7416142 | 15612224 | 18819569 | 98932098 | 50185139 | 10652438 | 0.000000 | 0.000000 | 15345618
09-04-2025 23:58:05.000 | 49597781 |  | 49.5978 | -7593811 | 15610494 | 18560793 | 98848114 | 50191925 | 10582794 | 0.000000 | 0.000000 | 15242279
09-04-2025 23:58:00.000 | 49044082 |  | 49.0441 | -7338109 | 15612652 | 18341627 | 98899101 | 50207951 | 10513928 | 0.000000 | 0.000000 | 15138535
09-04-2025 23:57:55.000 | 48355629 |  | 48.3556 | -7625287 | 15612740 | 18106013 | 98779381 | 50219910 | 10446241 | 0.000000 | 0.000000 | 15035857
09-04-2025 23:57:50.000 | 48460301 |  | 48.4603 | -7725572 | 15614080 | 18149133 | 98752975 | 50221581 | 10378921 | 0.000000 | 0.000000 | 14928995
09-04-2025 23:57:45.000 | 49215121 |  | 49.2151 | -7643933 | 15613043 | 18421799 | 98815231 | 50205681 | 10310922 | 0.000000 | 0.000000 | 14822124
09-04-2025 23:57:40.000 | 49007961 |  | 49.008 | -7466209 | 15609815 | 18338907 | 98859337 | 50204357 | 10242378 | 0.000000 | 0.000000 | 14717799
09-04-2025 23:57:35.000 | 48675223 |  | 48.6752 | -7604548 | 15612868 | 18221165 | 98801498 | 50219059 | 10174455 | 0.000000 | 0.000000 | 14613474
09-04-2025 23:57:30.000 | 49209328 |  | 49.2093 | -7763492 | 15611736 | 18427031 | 98778275 | 50209011 | 10106498 | 0.000000 | 0.000000 | 14506146
09-04-2025 23:57:25.000 | 49097191 |  | 49.0972 | -7673790 | 15609996 | 18382848 | 98800484 | 50201332 | 10038020 | 0.000000 | 0.000000 | 14399321
09-04-2025 23:57:20.000 | 48248527 |  | 48.2485 | -7760007 | 15610626 | 18077017 | 98731186 | 50216660 | 99699619 | 0.000000 | 0.000000 | 14292776
09-04-2025 23:57:15.000 | 48549520 |  | 48.5495 | -8082681 | 15613244 | 18203040 | 98642326 | 50226952 | 99029150 | 0.000000 | 0.000000 | 14182684
09-04-2025 23:57:10.000 | 48610254 |  | 48.6103 | -8083128 | 15611837 | 18228043 | 98645500 | 50218651 | 98355908 | 0.000000 | 0.000000 | 14070396
09-04-2025 23:57:05.000 | 48519813 |  | 48.5198 | -7885060 | 15612203 | 18181887 | 98705086 | 50214874 | 97680088 | 0.000000 | 0.000000 | 13958494
09-04-2025 23:57:00.000 | 47251066 |  | 47.2511 | -7802840 | 15612190 | 17714301 | 98663780 | 50228947 | 97015293 | 0.000000 | 0.000000 | 13849049
09-04-2025 23:56:55.000 | 46960672 |  | 46.9607 | -7994973 | 15614036 | 17617607 | 98581535 | 50226563 | 96361504 | 0.000000 | 0.000000 | 13739446
09-04-2025 23:56:50.000 | 47512840 |  | 47.5128 | -7850274 | 15614418 | 17809550 | 98662369 | 50211411 | 95703135 | 0.000000 | 0.000000 | 13628716
09-04-2025 23:56:45.000 | 47450980 |  | 47.451 | -7864459 | 15610648 | 17792395 | 98654198 | 50215511 | 95042998 | 0.000000 | 0.000000 | 13519647
09-04-2025 23:56:40.000 | 47913891 |  | 47.9139 | -8112887 | 15612069 | 17974946 | 98596603 | 50207024 | 94380791 | 0.000000 | 0.000000 | 13408345
09-04-2025 23:56:35.000 | 47998836 |  | 47.9988 | -7961183 | 15613598 | 17995436 | 98652237 | 50197960 | 93710830 | 0.000000 | 0.000000 | 13296237
09-04-2025 23:56:30.000 | 47638402 |  | 47.6384 | -7910642 | 15613283 | 17860610 | 98649147 | 50218929 | 93045889 | 0.000000 | 0.000000 | 13187302
09-04-2025 23:56:25.000 | 48390004 |  | 48.39 | -7919462 | 15612840 | 18135688 | 98687103 | 50198307 | 92380059 | 0.000000 | 0.000000 | 13076868
09-04-2025 23:56:20.000 | 48751730 |  | 48.7517 | -7723984 | 15610426 | 18259193 | 98768059 | 50191570 | 91702539 | 0.000000 | 0.000000 | 12968521
09-04-2025 23:56:15.000 | 48133922 |  | 48.1339 | -7987301 | 15612578 | 18047025 | 98651009 | 50203503 | 91029434 | 0.000000 | 0.000000 | 12859303
09-04-2025 23:56:10.000 | 47970719 |  | 47.9707 | -7741357 | 15613896 | 17970763 | 98722771 | 50210106 | 90360645 | 0.000000 | 0.000000 | 12751488
09-04-2025 23:56:05.000 | 48615367 |  | 48.6154 | -7911414 | 15612727 | 18217743 | 98701599 | 50200279 | 89690703 | 0.000000 | 0.000000 | 12642644
09-04-2025 23:56:00.000 | 49364805 |  | 49.3648 | -7743830 | 15610789 | 18483927 | 98791855 | 50180843 | 89010469 | 0.000000 | 0.000000 | 12533768
09-04-2025 23:55:55.000 | 48441102 |  | 48.4411 | -7598428 | 15612184 | 18136406 | 98792007 | 50185802 | 88324941 | 0.000000 | 0.000000 | 12427386
09-04-2025 23:55:50.000 | 48270117 |  | 48.2701 | -7775980 | 15614018 | 18082466 | 98727173 | 50210579 | 87652539 | 0.000000 | 0.000000 | 12321498
09-04-2025 23:55:45.000 | 48937707 |  | 48.9377 | -7872236 | 15612179 | 18334083 | 98730743 | 50194504 | 86979307 | 0.000000 | 0.000000 | 12213097
09-04-2025 23:55:40.000 | 49181469 |  | 49.1815 | -7663093 | 15613355 | 18409572 | 98807785 | 50180862 | 86295293 | 0.000000 | 0.000000 | 12105955
09-04-2025 23:55:35.000 | 49034133 |  | 49.0341 | -7431373 | 15611072 | 18344993 | 98870964 | 50191898 | 85611865 | 0.000000 | 0.000000 | 12000814
09-04-2025 23:55:30.000 | 48928258 |  | 48.9283 | -7697741 | 15613944 | 18318931 | 98784920 | 50192249 | 84932783 | 0.000000 | 0.000000 | 11896152
09-04-2025 23:55:25.000 | 49057570 |  | 49.0576 | -7200688 | 15612691 | 18339865 | 98939873 | 50184952 | 84250518 | 0.000000 | 0.000000 | 11790862
09-04-2025 23:55:20.000 | 48625973 |  | 48.626 | -7636003 | 15611693 | 18206433 | 98789337 | 50203560 | 83572666 | 0.000000 | 0.000000 | 11689188
09-04-2025 23:55:15.000 | 49704207 |  | 49.7042 | -7744425 | 15612131 | 18605848 | 98807823 | 50173679 | 82890303 | 0.000000 | 0.000000 | 11581162
09-04-2025 23:55:10.000 | 49488727 |  | 49.4887 | -7554309 | 15610634 | 18518937 | 98854919 | 50175186 | 82197617 | 0.000000 | 0.000000 | 11474529
09-04-2025 23:55:05.000 | 48514176 |  | 48.5142 | -7663604 | 15612698 | 18166096 | 98775208 | 50197849 | 81516646 | 0.000000 | 0.000000 | 11369132
09-04-2025 23:55:00.000 | 48187957 |  | 48.188 | -7601082 | 15614569 | 18041451 | 98778679 | 50206196 | 80845830 | 0.000000 | 0.000000 | 11263015
09-04-2025 23:54:55.000 | 48725629 |  | 48.7256 | -7746686 | 15613616 | 18247792 | 98759644 | 50198174 | 80171865 | 0.000000 | 0.000000 | 11157343
09-04-2025 23:54:50.000 | 48810750 |  | 48.8107 | -7557048 | 15613630 | 18267227 | 98822609 | 50195702 | 79496309 | 0.000000 | 0.000000 | 11050448
09-04-2025 23:54:45.000 | 48625020 |  | 48.625 | -7560051 | 15613755 | 18200498 | 98812836 | 50204018 | 78819678 | 0.000000 | 0.000000 | 10946821
09-04-2025 23:54:40.000 | 49769930 |  | 49.7699 | -7619505 | 15612716 | 18622755 | 98848312 | 50180126 | 78138486 | 0.000000 | 0.000000 | 10840178
09-04-2025 23:54:35.000 | 49884262 |  | 49.8843 | -7555042 | 15610928 | 18662557 | 98872482 | 50175564 | 77447651 | 0.000000 | 0.000000 | 10734938
09-04-2025 23:54:30.000 | 49793813 |  | 49.7938 | -7818418 | 15610118 | 18645352 | 98789635 | 50178425 | 76755459 | 0.000000 | 0.000000 | 10628739
09-04-2025 23:54:25.000 | 49377082 |  | 49.3771 | -7640928 | 15610755 | 18482092 | 98823761 | 50177902 | 76067373 | 0.000000 | 0.000000 | 10520598
09-04-2025 23:54:20.000 | 48190676 |  | 48.1907 | -7746612 | 15611562 | 18054153 | 98732498 | 50203701 | 75387085 | 0.000000 | 0.000000 | 10414398
09-04-2025 23:54:15.000 | 48381445 |  | 48.3814 | -7871110 | 15612782 | 18129661 | 98702324 | 50198799 | 74715410 | 0.000000 | 0.000000 | 10305383
09-04-2025 23:54:10.000 | 48310383 |  | 48.3104 | -7693847 | 15612887 | 18092961 | 98755455 | 50203705 | 74043853 | 0.000000 | 0.000000 | 10197947
09-04-2025 23:54:05.000 | 47885566 |  | 47.8856 | -7802498 | 15612664 | 17944469 | 98698380 | 50211330 | 73376191 | 0.000000 | 0.000000 | 10090931
09-04-2025 23:54:00.000 | 48492641 |  | 48.4926 | -7737076 | 15613213 | 18161761 | 98750961 | 50203743 | 72708418 | 0.000000 | 0.000000 | 998341492
09-04-2025 23:53:55.000 | 48974262 |  | 48.9743 | -7729032 | 15611845 | 18338904 | 98777458 | 50198364 | 72035024 | 0.000000 | 0.000000 | 987596191
09-04-2025 23:53:50.000 | 48995832 |  | 48.9958 | -7694971 | 15611407 | 18345424 | 98789063 | 50184044 | 71354336 | 0.000000 | 0.000000 | 976835938
09-04-2025 23:53:45.000 | 48644496 |  | 48.6445 | -7856926 | 15611689 | 18226133 | 98720589 | 50199867 | 70674971 | 0.000000 | 0.000000 | 966146973
09-04-2025 23:53:40.000 | 48317715 |  | 48.3177 | -7771625 | 15611667 | 18102787 | 98731026 | 50200951 | 70001851 | 0.000000 | 0.000000 | 955267944
09-04-2025 23:53:35.000 | 48117809 |  | 48.1178 | -7942040 | 15610721 | 18039991 | 98665070 | 50201588 | 69330542 | 0.000000 | 0.000000 | 944360352
09-04-2025 23:53:30.000 | 47678027 |  | 47.678 | -7880592 | 15613904 | 17872301 | 98661369 | 50210274 | 68663364 | 0.000000 | 0.000000 | 933476563
09-04-2025 23:53:25.000 | 46933598 |  | 46.9336 | -7835213 | 15612535 | 17600354 | 98634979 | 50207577 | 68007422 | 0.000000 | 0.000000 | 922657776
09-04-2025 23:53:20.000 | 47536871 |  | 47.5369 | -7708774 | 15612611 | 17812024 | 98710518 | 50194988 | 67350669 | 0.000000 | 0.000000 | 911894653
09-04-2025 23:53:15.000 | 48008941 |  | 48.0089 | -7581127 | 15613023 | 17976757 | 98776054 | 50190468 | 66689707 | 0.000000 | 0.000000 | 901221436
09-04-2025 23:53:10.000 | 47852387 |  | 47.8524 | -7665253 | 15611491 | 17925747 | 98741203 | 50183475 | 66024663 | 0.000000 | 0.000000 | 890656555
09-04-2025 23:53:05.000 | 47671918 |  | 47.6719 | -7683430 | 15613010 | 17859351 | 98725929 | 50193344 | 65358110 | 0.000000 | 0.000000 | 880147095
09-04-2025 23:53:00.000 | 47901461 |  | 47.9015 | -7681842 | 15614556 | 17941599 | 98738396 | 50190052 | 64695405 | 0.000000 | 0.000000 | 869403625
09-04-2025 23:52:55.000 | 47951391 |  | 47.9514 | -7579136 | 15613921 | 17953973 | 98773796 | 50185043 | 64027974 | 0.000000 | 0.000000 | 858893982
09-04-2025 23:52:50.000 | 48197469 |  | 48.1975 | -7328875 | 15616531 | 18027424 | 98863571 | 50181740 | 63357114 | 0.000000 | 0.000000 | 848471619
09-04-2025 23:52:45.000 | 48610527 |  | 48.6105 | -7075609 | 15611893 | 18169423 | 98957199 | 50181446 | 62685498 | 0.000000 | 0.000000 | 838538208
09-04-2025 23:52:40.000 | 48295469 |  | 48.2955 | -7542839 | 15614394 | 18078057 | 98802238 | 50172787 | 62010688 | 0.000000 | 0.000000 | 828541016
09-04-2025 23:52:35.000 | 48680531 |  | 48.6805 | -7237336 | 15612157 | 18203597 | 98912849 | 50173820 | 61334478 | 0.000000 | 0.000000 | 818244873
09-04-2025 23:52:30.000 | 47841523 |  | 47.8415 | -7195875 | 15613830 | 17892483 | 98887672 | 50184986 | 60666582 | 0.000000 | 0.000000 | 808137878
09-04-2025 23:52:25.000 | 47338742 |  | 47.3387 | -7225578 | 15615169 | 17708864 | 98855087 | 50195480 | 60007788 | 0.000000 | 0.000000 | 798230835
09-04-2025 23:52:20.000 | 48747820 |  | 48.7478 | -7163538 | 15613096 | 18223406 | 98937447 | 50169125 | 59343657 | 0.000000 | 0.000000 | 788184875
09-04-2025 23:52:15.000 | 49437742 |  | 49.4377 | -7126565 | 15612473 | 18474197 | 98976921 | 50142887 | 58664775 | 0.000000 | 0.000000 | 778130981
09-04-2025 23:52:10.000 | 48447102 |  | 48.4471 | -7087715 | 15612250 | 18110166 | 98946724 | 50161816 | 57982476 | 0.000000 | 0.000000 | 768292419
09-04-2025 23:52:05.000 | 48390133 |  | 48.3901 | -7274884 | 15614037 | 18097267 | 98888725 | 50173943 | 57312158 | 0.000000 | 0.000000 | 758295410
09-04-2025 23:52:00.000 | 48843555 |  | 48.8436 | -7266238 | 15614997 | 18261609 | 98911476 | 50161922 | 56638784 | 0.000000 | 0.000000 | 748173523
09-04-2025 23:51:55.000 | 49528785 |  | 49.5288 | -7486490 | 15613215 | 18526438 | 98876831 | 50148869 | 55956714 | 0.000000 | 0.000000 | 738004883
09-04-2025 23:51:50.000 | 50066023 |  | 50.066 | -7402827 | 15610002 | 18722189 | 98924454 | 50139565 | 55266719 | 0.000000 | 0.000000 | 727672485
09-04-2025 23:51:45.000 | 49655539 |  | 49.6555 | -7439973 | 15609273 | 18574579 | 98896072 | 50145756 | 54574355 | 0.000000 | 0.000000 | 717354309
09-04-2025 23:51:40.000 | 49451340 |  | 49.4513 | -7353902 | 15611206 | 18493735 | 98912277 | 50150864 | 53888965 | 0.000000 | 0.000000 | 706876648
09-04-2025 23:51:35.000 | 48158633 |  | 48.1586 | -7258865 | 15611651 | 18014918 | 98883049 | 50164917 | 53214253 | 0.000000 | 0.000000 | 696662964
09-04-2025 23:51:30.000 | 47283871 |  | 47.2839 | -7365188 | 15614767 | 17697286 | 98808495 | 50185703 | 52548633 | 0.000000 | 0.000000 | 686582764
09-04-2025 23:51:25.000 | 48501617 |  | 48.5016 | -7103614 | 15612416 | 18131016 | 98944405 | 50167614 | 51884917 | 0.000000 | 0.000000 | 676335327
09-04-2025 23:51:20.000 | 48575996 |  | 48.576 | -7369684 | 15613271 | 18172175 | 98868629 | 50165787 | 51212603 | 0.000000 | 0.000000 | 666274353
09-04-2025 23:51:15.000 | 48646172 |  | 48.6462 | -7190810 | 15612615 | 18188280 | 98925064 | 50158028 | 50534111 | 0.000000 | 0.000000 | 656147095
09-04-2025 23:51:10.000 | 48850277 |  | 48.8503 | -7225590 | 15613402 | 18263622 | 98923714 | 50162853 | 49858179 | 0.000000 | 0.000000 | 646074768
09-04-2025 23:51:05.000 | 48786430 |  | 48.7864 | -7338290 | 15613737 | 18246195 | 98887581 | 50159843 | 49183149 | 0.000000 | 0.000000 | 635904724
09-04-2025 23:51:00.000 | 48168129 |  | 48.1681 | -6975119 | 15612092 | 18002327 | 98967743 | 50168129 | 48506230 | 0.000000 | 0.000000 | 625906677
09-04-2025 23:50:55.000 | 48169797 |  | 48.1698 | -7592037 | 15613511 | 18035834 | 98780624 | 50174934 | 47836479 | 0.000000 | 0.000000 | 615872375
09-04-2025 23:50:50.000 | 48633828 |  | 48.6338 | -7357724 | 15610422 | 18195435 | 98874870 | 50157398 | 47162319 | 0.000000 | 0.000000 | 605535461
09-04-2025 23:50:45.000 | 47508801 |  | 47.5088 | -7005783 | 15612671 | 17762153 | 98930153 | 50172058 | 46491445 | 0.000000 | 0.000000 | 595484192
09-04-2025 23:50:40.000 | 46520805 |  | 46.5208 | -6945351 | 15616711 | 17392721 | 98903831 | 50188053 | 45840635 | 0.000000 | 0.000000 | 585758240
09-04-2025 23:50:35.000 | 47221441 |  | 47.2214 | -7058316 | 15618406 | 17654175 | 98901276 | 50169922 | 45195693 | 0.000000 | 0.000000 | 576094177
09-04-2025 23:50:30.000 | 49436070 |  | 49.4361 | -6845006 | 15615089 | 18456882 | 99054985 | 50116512 | 44525718 | 0.000000 | 0.000000 | 566361877
09-04-2025 23:50:25.000 | 50286059 |  | 50.2861 | -6872788 | 15610469 | 18774224 | 99078896 | 50119911 | 43832871 | 0.000000 | 0.000000 | 556870117
09-04-2025 23:50:20.000 | 50265664 |  | 50.2657 | -6852205 | 15607275 | 18769708 | 99083595 | 50129841 | 43135527 | 0.000000 | 0.000000 | 547366882
09-04-2025 23:50:15.000 | 48667547 |  | 48.6675 | -7139277 | 15611873 | 18193776 | 98941093 | 50157967 | 42446865 | 0.000000 | 0.000000 | 537639160
09-04-2025 23:50:10.000 | 47333656 |  | 47.3337 | -7159188 | 15613217 | 17706228 | 98875443 | 50175167 | 41778159 | 0.000000 | 0.000000 | 527865845
09-04-2025 23:50:05.000 | 47838090 |  | 47.8381 | -7230922 | 15615786 | 17890867 | 98876831 | 50174004 | 41116646 | 0.000000 | 0.000000 | 517941467
09-04-2025 23:50:00.000 | 49368281 |  | 49.3683 | -7139435 | 15613811 | 18448085 | 98970436 | 50145222 | 40441914 | 0.000000 | 0.000000 | 507998444
09-04-2025 23:49:55.000 | 49311270 |  | 49.3113 | -6950500 | 15611970 | 18419371 | 99021194 | 50135578 | 39756431 | 0.000000 | 0.000000 | 498217377
09-04-2025 23:49:50.000 | 48694969 |  | 48.695 | -6992719 | 15614647 | 18192826 | 98984596 | 50150532 | 39072734 | 0.000000 | 0.000000 | 488550568
09-04-2025 23:49:45.000 | 49290121 |  | 49.2901 | -6631472 | 15612431 | 18395836 | 99107056 | 50149330 | 38392935 | 0.000000 | 0.000000 | 479134247
09-04-2025 23:49:40.000 | 49560078 |  | 49.5601 | -6566521 | 15610942 | 18493068 | 99133629 | 50139557 | 37707849 | 0.000000 | 0.000000 | 469861877
09-04-2025 23:49:35.000 | 49143219 |  | 49.1432 | -6747627 | 15609757 | 18350001 | 99070488 | 50142036 | 37022759 | 0.000000 | 0.000000 | 460574799
09-04-2025 23:49:30.000 | 47907109 |  | 47.9071 | -6678192 | 15611440 | 17891854 | 99042336 | 50156590 | 36345481 | 0.000000 | 0.000000 | 451294312
09-04-2025 23:49:25.000 | 46633254 |  | 46.6333 | -6751115 | 15613497 | 17427019 | 98968269 | 50165115 | 35683423 | 0.000000 | 0.000000 | 442113739
09-04-2025 23:49:20.000 | 46957242 |  | 46.9572 | -6530002 | 15614049 | 17533674 | 99046883 | 50150230 | 35033389 | 0.000000 | 0.000000 | 432746124
09-04-2025 23:49:15.000 | 46422340 |  | 46.4223 | -6481057 | 15613618 | 17336123 | 99039459 | 50152367 | 34387739 | 0.000000 | 0.000000 | 423702271
09-04-2025 23:49:10.000 | 46789000 |  | 46.789 | -6658687 | 15614523 | 17478169 | 99002480 | 50134205 | 33741724 | 0.000000 | 0.000000 | 414721527
09-04-2025 23:49:05.000 | 48954855 |  | 48.9549 | -6199855 | 15612938 | 18251581 | 99207581 | 50081310 | 33076157 | 0.000000 | 0.000000 | 405415497
09-04-2025 23:49:00.000 | 47551219 |  | 47.5512 | -5917585 | 15612081 | 17723969 | 99234535 | 50107090 | 32402856 | 0.000000 | 0.000000 | 397064453
09-04-2025 23:48:55.000 | 47471281 |  | 47.4713 | -6008456 | 15616096 | 17694690 | 99208496 | 50125164 | 31741506 | 0.000000 | 0.000000 | 388887207
09-04-2025 23:48:50.000 | 48702371 |  | 48.7024 | -6133254 | 15615649 | 18153024 | 99216347 | 50101517 | 31078557 | 0.000000 | 0.000000 | 380420197
09-04-2025 23:48:45.000 | 49154941 |  | 49.1549 | -5828349 | 15611763 | 18309401 | 99304375 | 50080959 | 30396138 | 0.000000 | 0.000000 | 372093872
09-04-2025 23:48:40.000 | 48398102 |  | 48.3981 | -5694896 | 15613616 | 18023081 | 99314819 | 50100864 | 29716089 | 0.000000 | 0.000000 | 364169800
09-04-2025 23:48:35.000 | 49225012 |  | 49.225 | -5982453 | 15614576 | 18337999 | 99269569 | 50089958 | 29039731 | 0.000000 | 0.000000 | 356035248
09-04-2025 23:48:30.000 | 49543543 |  | 49.5435 | -5883715 | 15612612 | 18453146 | 99302193 | 50072456 | 28350503 | 0.000000 | 0.000000 | 347786041
09-04-2025 23:48:25.000 | 49952582 |  | 49.9526 | -5883459 | 15611539 | 18604449 | 99313515 | 50078712 | 27658594 | 0.000000 | 0.000000 | 339546661
09-04-2025 23:48:20.000 | 49559367 |  | 49.5594 | -5975788 | 15612742 | 18463021 | 99280876 | 50079254 | 26970432 | 0.000000 | 0.000000 | 331184052
09-04-2025 23:48:15.000 | 48592500 |  | 48.5925 | -6127261 | 15611306 | 18117161 | 99214363 | 50092442 | 26285798 | 0.000000 | 0.000000 | 322941925
09-04-2025 23:48:10.000 | 47782469 |  | 47.7825 | -5926226 | 15612764 | 17808429 | 99239647 | 50107040 | 25611172 | 0.000000 | 0.000000 | 314574280
09-04-2025 23:48:05.000 | 48000250 |  | 48.0003 | -6148296 | 15614135 | 17896951 | 99189621 | 50104733 | 24952029 | 0.000000 | 0.000000 | 306226776
09-04-2025 23:48:00.000 | 48549832 |  | 48.5498 | -6062458 | 15614697 | 18094388 | 99229362 | 50087212 | 24280642 | 0.000000 | 0.000000 | 297848328
09-04-2025 23:47:55.000 | 49053168 |  | 49.0532 | -5775479 | 15614469 | 18267087 | 99313995 | 50075603 | 23601416 | 0.000000 | 0.000000 | 289621521
09-04-2025 23:47:50.000 | 49148301 |  | 49.1483 | -6008965 | 15613792 | 18312279 | 99260880 | 50083336 | 22921458 | 0.000000 | 0.000000 | 281509857
09-04-2025 23:47:45.000 | 50263164 |  | 50.2632 | -6065409 | 15613182 | 18724752 | 99279755 | 50066990 | 22232161 | 0.000000 | 0.000000 | 273066925
09-04-2025 23:47:40.000 | 49774652 |  | 49.7747 | -5865328 | 15608977 | 18541621 | 99312859 | 50080399 | 21534214 | 0.000000 | 0.000000 | 264818909
09-04-2025 23:47:35.000 | 48866453 |  | 48.8665 | -5899998 | 15611219 | 18206919 | 99278999 | 50107731 | 20849541 | 0.000000 | 0.000000 | 256554596
09-04-2025 23:47:30.000 | 48898164 |  | 48.8982 | -6130335 | 15610744 | 18230496 | 99223267 | 50103127 | 20174631 | 0.000000 | 0.000000 | 248124176
09-04-2025 23:47:25.000 | 48337293 |  | 48.3373 | -6045125 | 15612296 | 18018264 | 99227036 | 50104694 | 19496780 | 0.000000 | 0.000000 | 239765976
09-04-2025 23:47:20.000 | 48250992 |  | 48.251 | -5929435 | 15611105 | 17982933 | 99253380 | 50103065 | 18824642 | 0.000000 | 0.000000 | 231344757
09-04-2025 23:47:15.000 | 47865629 |  | 47.8656 | -6160544 | 15612638 | 17849753 | 99181900 | 50124077 | 18157292 | 0.000000 | 0.000000 | 223049713
09-04-2025 23:47:10.000 | 48148664 |  | 48.1487 | -5883105 | 15613590 | 17940276 | 99261780 | 50108715 | 17491868 | 0.000000 | 0.000000 | 214478043
09-04-2025 23:47:05.000 | 47195977 |  | 47.196 | -6263183 | 15615895 | 17605781 | 99130920 | 50133938 | 16827654 | 0.000000 | 0.000000 | 206380615
09-04-2025 23:47:00.000 | 49182988 |  | 49.183 | -5793783 | 15611260 | 18318705 | 99313293 | 50082836 | 16159264 | 0.000000 | 0.000000 | 197703293
09-04-2025 23:46:55.000 | 47885098 |  | 47.8851 | -6137438 | 15611952 | 17856567 | 99188606 | 50099762 | 15481608 | 0.000000 | 0.000000 | 189655167
09-04-2025 23:46:50.000 | 48074699 |  | 48.0747 | -5804450 | 15612103 | 17910963 | 99278992 | 50099117 | 14809974 | 0.000000 | 0.000000 | 181223572
09-04-2025 23:46:45.000 | 48317637 |  | 48.3176 | -6073323 | 15609940 | 18014756 | 99219269 | 50102295 | 14142693 | 0.000000 | 0.000000 | 173042679
09-04-2025 23:46:40.000 | 48530043 |  | 48.53 | -6023837 | 15611686 | 18088983 | 99238426 | 50090755 | 13467943 | 0.000000 | 0.000000 | 164505722
09-04-2025 23:46:35.000 | 47772035 |  | 47.772 | -6152256 | 15612426 | 17815861 | 99180916 | 50109543 | 12798436 | 0.000000 | 0.000000 | 156115356
09-04-2025 23:46:30.000 | 47722035 |  | 47.722 | -6203140 | 15611287 | 17800692 | 99165756 | 50113728 | 12136006 | 0.000000 | 0.000000 | 147664673
09-04-2025 23:46:25.000 | 47635102 |  | 47.6351 | -6182018 | 15613818 | 17765083 | 99168365 | 50110020 | 11474807 | 0.000000 | 0.000000 | 139028442
09-04-2025 23:46:20.000 | 47747855 |  | 47.7479 | -5847912 | 15612733 | 17793096 | 99258331 | 50117569 | 10810547 | 0.000000 | 0.000000 | 130720963
09-04-2025 23:46:15.000 | 48321551 |  | 48.3216 | -6002224 | 15612729 | 18010697 | 99237358 | 50107090 | 10149550 | 0.000000 | 0.000000 | 122318909
09-04-2025 23:46:10.000 | 48335148 |  | 48.3351 | -5908727 | 15612340 | 18012365 | 99261078 | 50094830 | 947657043 | 0.000000 | 0.000000 | 113989380
09-04-2025 23:46:05.000 | 48283469 |  | 48.2835 | -5702500 | 15613454 | 17982249 | 99309776 | 50099834 | 880443115 | 0.000000 | 0.000000 | 105988480
09-04-2025 23:46:00.000 | 47494066 |  | 47.4941 | -5736312 | 15614930 | 17691869 | 99278496 | 50101963 | 814051941 | 0.000000 | 0.000000 | 97970520
09-04-2025 23:45:55.000 | 47888781 |  | 47.8888 | -5673213 | 15614441 | 17835323 | 99305588 | 50095428 | 747908081 | 0.000000 | 0.000000 | 90069794
09-04-2025 23:45:50.000 | 49212094 |  | 49.2121 | -5853101 | 15616096 | 18326547 | 99300125 | 50079517 | 680606384 | 0.000000 | 0.000000 | 82076431
09-04-2025 23:45:45.000 | 49976926 |  | 49.9769 | -5801937 | 15612249 | 18609919 | 99332863 | 50060204 | 611659363 | 0.000000 | 0.000000 | 74090668
09-04-2025 23:45:40.000 | 50406789 |  | 50.4068 | -5683424 | 15610906 | 18763904 | 99370354 | 50068676 | 541540649 | 0.000000 | 0.000000 | 66144012
09-04-2025 23:45:35.000 | 49527402 |  | 49.5274 | -5579330 | 15611170 | 18436842 | 99371460 | 50086487 | 472369415 | 0.000000 | 0.000000 | 58183823
09-04-2025 23:45:30.000 | 48607035 |  | 48.607 | -6025892 | 15611382 | 18117253 | 99240295 | 50106010 | 404369202 | 0.000000 | 0.000000 | 50201550
09-04-2025 23:45:25.000 | 49693734 |  | 49.6937 | -6185910 | 15611537 | 18523325 | 99234116 | 50082306 | 336278015 | 0.000000 | 0.000000 | 41540249
09-04-2025 23:45:20.000 | 49076578 |  | 49.0766 | -5812151 | 15609115 | 18283003 | 99306007 | 50083744 | 267589081 | 0.000000 | 0.000000 | 33147541
09-04-2025 23:45:15.000 | 47335461 |  | 47.3355 | -5769455 | 15613345 | 17637253 | 99265381 | 50116741 | 200328766 | 0.000000 | 0.000000 | 25034992
09-04-2025 23:45:10.000 | 47761246 |  | 47.7612 | -6079446 | 15614330 | 17806338 | 99199600 | 50107235 | 134721176 | 0.000000 | 0.000000 | 16815950
09-04-2025 23:45:05.000 | 48679730 |  | 48.6797 | -6213262 | 15613475 | 18150497 | 99195274 | 50088886 | 67860565 | 0.000000 | 0.000000 | 8425528
09-04-2025 23:45:00.000 | 48559195 |  | 48.5592 | -5963254 | 15612029 | 18096946 | 99254387 | 50081676 | 12211368 | 0.000000 | 0.000000 | 13461184
09-04-2025 23:44:55.000 | 48275051 |  | 48.2751 | -5990365 | 15614087 | 17990337 | 99238884 | 50096748 | 12143943 | 0.000000 | 0.000000 | 13378362
09-04-2025 23:44:50.000 | 47806004 |  | 47.806 | -5869525 | 15613229 | 17815570 | 99254692 | 50090935 | 12077450 | 0.000000 | 0.000000 | 13296653
09-04-2025 23:44:45.000 | 48291641 |  | 48.2916 | -5608888 | 15615125 | 17979294 | 99332253 | 50087669 | 12010544 | 0.000000 | 0.000000 | 13216007
09-04-2025 23:44:40.000 | 48311105 |  | 48.3111 | -5657149 | 15614690 | 17988799 | 99321373 | 50085938 | 11943471 | 0.000000 | 0.000000 | 13137660
09-04-2025 23:44:35.000 | 48718418 |  | 48.7184 | -5772600 | 15612174 | 18147850 | 99305321 | 50086239 | 11876291 | 0.000000 | 0.000000 | 13059229
09-04-2025 23:44:30.000 | 49254016 |  | 49.254 | -5547503 | 15611876 | 18333654 | 99371689 | 50064083 | 11808193 | 0.000000 | 0.000000 | 12978892
09-04-2025 23:44:25.000 | 48978945 |  | 48.9789 | -5665411 | 15613309 | 18235975 | 99337654 | 50071167 | 11740005 | 0.000000 | 0.000000 | 12901687
09-04-2025 23:44:20.000 | 49295477 |  | 49.2955 | -5921841 | 15609948 | 18367554 | 99286163 | 50074745 | 11671879 | 0.000000 | 0.000000 | 12821934
09-04-2025 23:44:15.000 | 48813383 |  | 48.8134 | -5828490 | 15612497 | 18182678 | 99294670 | 50064423 | 11603412 | 0.000000 | 0.000000 | 12739828
09-04-2025 23:44:10.000 | 48468488 |  | 48.4685 | -5841050 | 15613099 | 18056318 | 99281654 | 50086548 | 11536044 | 0.000000 | 0.000000 | 12659679
09-04-2025 23:44:05.000 | 47560410 |  | 47.5604 | -5691240 | 15614757 | 17714698 | 99291634 | 50077209 | 11469320 | 0.000000 | 0.000000 | 12578706
09-04-2025 23:44:00.000 | 46994910 |  | 46.9949 | -5748899 | 15617684 | 17505823 | 99260063 | 50090816 | 11403498 | 0.000000 | 0.000000 | 12501577
09-04-2025 23:43:55.000 | 49099246 |  | 49.0992 | -5699584 | 15613621 | 18281566 | 99332970 | 50060287 | 11337215 | 0.000000 | 0.000000 | 12422399
09-04-2025 23:43:50.000 | 50224164 |  | 50.2242 | -5691183 | 15612289 | 18695160 | 99364098 | 50033028 | 11268230 | 0.000000 | 0.000000 | 12342651
09-04-2025 23:43:45.000 | 50500270 |  | 50.5003 | -5524042 | 15608761 | 18795114 | 99407043 | 50037735 | 11198256 | 0.000000 | 0.000000 | 12264551
09-04-2025 23:43:40.000 | 48645918 |  | 48.6459 | -5686500 | 15609266 | 18118784 | 99323692 | 50080250 | 11129067 | 0.000000 | 0.000000 | 12187363
09-04-2025 23:43:35.000 | 49440484 |  | 49.4405 | -5751663 | 15611365 | 18411283 | 99330101 | 50069946 | 11061141 | 0.000000 | 0.000000 | 12106019
09-04-2025 23:43:30.000 | 48068359 |  | 48.0684 | -5680282 | 15612968 | 17901938 | 99309013 | 50084595 | 10993154 | 0.000000 | 0.000000 | 12027258
09-04-2025 23:43:25.000 | 47302207 |  | 47.3022 | -5749888 | 15614542 | 17623169 | 99269287 | 50097565 | 10927211 | 0.000000 | 0.000000 | 11948038
09-04-2025 23:43:20.000 | 48133922 |  | 48.1339 | -5865411 | 15615254 | 17932327 | 99265724 | 50085018 | 10860785 | 0.000000 | 0.000000 | 11868110
09-04-2025 23:43:15.000 | 48597316 |  | 48.5973 | -5601539 | 15610969 | 18095878 | 99342255 | 50070351 | 10793724 | 0.000000 | 0.000000 | 11788466
09-04-2025 23:43:10.000 | 48748852 |  | 48.7489 | -5694493 | 15612840 | 18154565 | 99324638 | 50070900 | 10725966 | 0.000000 | 0.000000 | 11710693
09-04-2025 23:43:05.000 | 48732496 |  | 48.7325 | -5471188 | 15612490 | 18138461 | 99375671 | 50068157 | 10658158 | 0.000000 | 0.000000 | 11632158
09-04-2025 23:43:00.000 | 49027367 |  | 49.0274 | -5853302 | 15612564 | 18262671 | 99294846 | 50071632 | 10590738 | 0.000000 | 0.000000 | 11554180
09-04-2025 23:42:55.000 | 49608445 |  | 49.6084 | -5607905 | 15613252 | 18465851 | 99367119 | 50052685 | 10521979 | 0.000000 | 0.000000 | 11474841
09-04-2025 23:42:50.000 | 49143273 |  | 49.1433 | -5437275 | 15612551 | 18287211 | 99393486 | 50065094 | 10453355 | 0.000000 | 0.000000 | 11398094
09-04-2025 23:42:45.000 | 48853008 |  | 48.853 | -5537389 | 15613572 | 18183580 | 99363739 | 50069244 | 10385586 | 0.000000 | 0.000000 | 11322710
09-04-2025 23:42:40.000 | 49679785 |  | 49.6798 | -5420706 | 15612495 | 18484270 | 99409981 | 50058327 | 10317272 | 0.000000 | 0.000000 | 11245168
09-04-2025 23:42:35.000 | 49127559 |  | 49.1276 | -5306138 | 15612170 | 18277205 | 99421776 | 50061626 | 10248615 | 0.000000 | 0.000000 | 11170597
09-04-2025 23:42:30.000 | 48960965 |  | 48.961 | -5388005 | 15612735 | 18218569 | 99399925 | 50066467 | 10180644 | 0.000000 | 0.000000 | 11096471
09-04-2025 23:42:25.000 | 50064727 |  | 50.0647 | -5567068 | 15610334 | 18634713 | 99387428 | 50056778 | 10112195 | 0.000000 | 0.000000 | 11019183
09-04-2025 23:42:20.000 | 49861305 |  | 49.8613 | -5479172 | 15609854 | 18556079 | 99401642 | 50042473 | 10042605 | 0.000000 | 0.000000 | 10941674
09-04-2025 23:42:15.000 | 48631117 |  | 48.6311 | -5296743 | 15613897 | 18091466 | 99412079 | 50060719 | 99737559 | 0.000000 | 0.000000 | 10866714
09-04-2025 23:42:10.000 | 47575969 |  | 47.576 | -5744201 | 15616227 | 17722460 | 99278999 | 50095116 | 99070908 | 0.000000 | 0.000000 | 10792806
09-04-2025 23:42:05.000 | 48919281 |  | 48.9193 | -5932986 | 15614439 | 18225094 | 99272560 | 50063961 | 98401172 | 0.000000 | 0.000000 | 10713958
09-04-2025 23:42:00.000 | 50340898 |  | 50.3409 | -5543436 | 15610319 | 18734969 | 99399162 | 50037163 | 97707646 | 0.000000 | 0.000000 | 10634222
09-04-2025 23:41:55.000 | 49101613 |  | 49.1016 | -5409832 | 15609529 | 18274313 | 99398529 | 50058498 | 97015137 | 0.000000 | 0.000000 | 10558077
09-04-2025 23:41:50.000 | 48942367 |  | 48.9424 | -5596463 | 15613495 | 18219324 | 99352570 | 50073193 | 96337324 | 0.000000 | 0.000000 | 10480614
09-04-2025 23:41:45.000 | 49289711 |  | 49.2897 | -5529227 | 15612919 | 18345442 | 99376678 | 50058662 | 95655498 | 0.000000 | 0.000000 | 10402910
09-04-2025 23:41:40.000 | 49287617 |  | 49.2876 | -5687553 | 15612652 | 18351177 | 99340775 | 50065613 | 94972695 | 0.000000 | 0.000000 | 10326405
09-04-2025 23:41:35.000 | 49465211 |  | 49.4652 | -5918707 | 15612906 | 18425890 | 99291740 | 50065853 | 94287158 | 0.000000 | 0.000000 | 10246708
09-04-2025 23:41:30.000 | 49291129 |  | 49.2911 | -5544390 | 15611726 | 18347142 | 99373322 | 50060204 | 93598262 | 0.000000 | 0.000000 | 10167026
09-04-2025 23:41:25.000 | 49169527 |  | 49.1695 | -5816410 | 15612646 | 18313049 | 99307594 | 50072552 | 92918623 | 0.000000 | 0.000000 | 10088228
09-04-2025 23:41:20.000 | 50259871 |  | 50.2599 | -5794153 | 15608750 | 18718097 | 99342033 | 50059052 | 92230518 | 0.000000 | 0.000000 | 10006305
09-04-2025 23:41:15.000 | 49404164 |  | 49.4042 | -5809504 | 15610165 | 18402607 | 99315704 | 50065475 | 91537793 | 0.000000 | 0.000000 | 992510498
09-04-2025 23:41:10.000 | 48013207 |  | 48.0132 | -5690888 | 15610752 | 17885541 | 99304878 | 50089897 | 90856211 | 0.000000 | 0.000000 | 984660339
09-04-2025 23:41:05.000 | 47437484 |  | 47.4375 | -5729909 | 15614331 | 17671841 | 99278389 | 50090458 | 90192207 | 0.000000 | 0.000000 | 976682190
09-04-2025 23:41:00.000 | 47386094 |  | 47.3861 | -5635618 | 15614023 | 17648770 | 99300201 | 50089787 | 89536133 | 0.000000 | 0.000000 | 968772400
09-04-2025 23:40:55.000 | 48836969 |  | 48.837 | -5818340 | 15615362 | 18188093 | 99297775 | 50069035 | 88871025 | 0.000000 | 0.000000 | 960885925
09-04-2025 23:40:50.000 | 49457367 |  | 49.4574 | -5382981 | 15612414 | 18401042 | 99412895 | 50043114 | 88185801 | 0.000000 | 0.000000 | 953095825
09-04-2025 23:40:45.000 | 48692336 |  | 48.6923 | -5401136 | 15613256 | 18119578 | 99390419 | 50064327 | 87503613 | 0.000000 | 0.000000 | 945718994
09-04-2025 23:40:40.000 | 49192438 |  | 49.1924 | -5615831 | 15615200 | 18310045 | 99354668 | 50059765 | 86824268 | 0.000000 | 0.000000 | 938177612
09-04-2025 23:40:35.000 | 49966563 |  | 49.9666 | -5281494 | 15610366 | 18586498 | 99446007 | 50050472 | 86131494 | 0.000000 | 0.000000 | 930629028
09-04-2025 23:40:30.000 | 49701859 |  | 49.7019 | -5590651 | 15611954 | 18499540 | 99373314 | 50070862 | 85442510 | 0.000000 | 0.000000 | 923090332
09-04-2025 23:40:25.000 | 50126551 |  | 50.1266 | -5647499 | 15612772 | 18657319 | 99371307 | 50068031 | 84751211 | 0.000000 | 0.000000 | 915246155
09-04-2025 23:40:20.000 | 50157449 |  | 50.1574 | -5572956 | 15608084 | 18671040 | 99388397 | 50083290 | 84052627 | 0.000000 | 0.000000 | 907469482
09-04-2025 23:40:15.000 | 48860848 |  | 48.8608 | -5905584 | 15613724 | 18201786 | 99277481 | 50102932 | 83368936 | 0.000000 | 0.000000 | 899331970
09-04-2025 23:40:10.000 | 48894387 |  | 48.8944 | -6087607 | 15615372 | 18220729 | 99233818 | 50112087 | 82686377 | 0.000000 | 0.000000 | 891164307
09-04-2025 23:40:05.000 | 50188301 |  | 50.1883 | -6142920 | 15612538 | 18701498 | 99259254 | 50085751 | 81999150 | 0.000000 | 0.000000 | 882661682
09-04-2025 23:40:00.000 | 50114328 |  | 50.1143 | -5849199 | 15609444 | 18664818 | 99325737 | 50083679 | 81302988 | 0.000000 | 0.000000 | 874309265
09-04-2025 23:39:55.000 | 49535449 |  | 49.5354 | -6271085 | 15611510 | 18469005 | 99208153 | 50096836 | 80612012 | 0.000000 | 0.000000 | 865889526
09-04-2025 23:39:50.000 | 49902852 |  | 49.9029 | -6225388 | 15608336 | 18605374 | 99230835 | 50088287 | 79921978 | 0.000000 | 0.000000 | 857160889
09-04-2025 23:39:45.000 | 47785984 |  | 47.786 | -6146021 | 15611565 | 17821407 | 99183022 | 50115211 | 79235859 | 0.000000 | 0.000000 | 848689636
09-04-2025 23:39:40.000 | 46978090 |  | 46.9781 | -6170045 | 15614048 | 17523500 | 99148506 | 50135422 | 78576362 | 0.000000 | 0.000000 | 840227783
09-04-2025 23:39:35.000 | 46717133 |  | 46.7171 | -6048911 | 15613358 | 17422549 | 99172150 | 50115967 | 77928179 | 0.000000 | 0.000000 | 831749634
09-04-2025 23:39:30.000 | 46994328 |  | 46.9943 | -5805052 | 15616549 | 17510013 | 99245682 | 50100819 | 77275918 | 0.000000 | 0.000000 | 823429871
09-04-2025 23:39:25.000 | 47880281 |  | 47.8803 | -5695930 | 15616318 | 17830380 | 99299828 | 50095230 | 76620903 | 0.000000 | 0.000000 | 815493164
09-04-2025 23:39:20.000 | 49269520 |  | 49.2695 | -5735877 | 15614449 | 18344164 | 99329147 | 50052544 | 75950078 | 0.000000 | 0.000000 | 807387512
09-04-2025 23:39:15.000 | 49671469 |  | 49.6715 | -5334685 | 15611771 | 18478354 | 99428207 | 50049919 | 75260181 | 0.000000 | 0.000000 | 799828369
09-04-2025 23:39:10.000 | 49874703 |  | 49.8747 | -5305681 | 15611961 | 18552379 | 99438919 | 50045551 | 74570356 | 0.000000 | 0.000000 | 792406311
09-04-2025 23:39:05.000 | 49750164 |  | 49.7502 | -5342201 | 15611134 | 18508416 | 99428406 | 50043873 | 73878354 | 0.000000 | 0.000000 | 784990356
09-04-2025 23:39:00.000 | 49175980 |  | 49.176 | -5524808 | 15613995 | 18302161 | 99374809 | 50066875 | 73189170 | 0.000000 | 0.000000 | 777535095
09-04-2025 23:38:55.000 | 50104039 |  | 50.104 | -5240896 | 15611166 | 18634709 | 99457390 | 50051010 | 72501177 | 0.000000 | 0.000000 | 769953674
09-04-2025 23:38:50.000 | 49646055 |  | 49.6461 | -5325766 | 15610725 | 18470596 | 99429527 | 50058689 | 71808833 | 0.000000 | 0.000000 | 762651611
09-04-2025 23:38:45.000 | 49290547 |  | 49.2905 | -5416152 | 15612330 | 18342041 | 99401711 | 50066597 | 71119536 | 0.000000 | 0.000000 | 755305420
09-04-2025 23:38:40.000 | 47717313 |  | 47.7173 | -5334952 | 15613328 | 17758114 | 99380798 | 50096100 | 70442617 | 0.000000 | 0.000000 | 748042969
09-04-2025 23:38:35.000 | 48140273 |  | 48.1403 | -5597208 | 15613011 | 17926519 | 99330856 | 50085320 | 69784219 | 0.000000 | 0.000000 | 740330505
09-04-2025 23:38:30.000 | 49516016 |  | 49.516 | -5672432 | 15613481 | 18432998 | 99350220 | 50061913 | 69105161 | 0.000000 | 0.000000 | 732526367
09-04-2025 23:38:25.000 | 49793305 |  | 49.7933 | -5500869 | 15610647 | 18530902 | 99395302 | 50046986 | 68414888 | 0.000000 | 0.000000 | 724806396
09-04-2025 23:38:20.000 | 48784762 |  | 48.7848 | -5245791 | 15608018 | 18153084 | 99426842 | 50050522 | 67727583 | 0.000000 | 0.000000 | 717348450
09-04-2025 23:38:15.000 | 46725715 |  | 46.7257 | -5285742 | 15613921 | 17391737 | 99366241 | 50095989 | 67058901 | 0.000000 | 0.000000 | 710172241
09-04-2025 23:38:10.000 | 46673652 |  | 46.6737 | -5518506 | 15618385 | 17377948 | 99308258 | 50089405 | 66413379 | 0.000000 | 0.000000 | 702681580
09-04-2025 23:38:05.000 | 48295578 |  | 48.2956 | -5388723 | 15614720 | 17971703 | 99383270 | 50060604 | 65754619 | 0.000000 | 0.000000 | 695287720
09-04-2025 23:38:00.000 | 49810973 |  | 49.811 | -5292504 | 15610405 | 18529792 | 99440262 | 50041164 | 65073257 | 0.000000 | 0.000000 | 687854797
09-04-2025 23:37:55.000 | 50135805 |  | 50.1358 | -5289535 | 15609688 | 18649728 | 99448044 | 50036282 | 64378516 | 0.000000 | 0.000000 | 680490295
09-04-2025 23:37:50.000 | 49137883 |  | 49.1379 | -5228317 | 15611237 | 18278785 | 99438705 | 50048489 | 63687822 | 0.000000 | 0.000000 | 673259521
09-04-2025 23:37:45.000 | 48806434 |  | 48.8064 | -5366927 | 15612731 | 18160188 | 99400833 | 50063061 | 63006289 | 0.000000 | 0.000000 | 665936584
09-04-2025 23:37:40.000 | 48729129 |  | 48.7291 | -5472489 | 15614045 | 18135281 | 99375290 | 50066948 | 62330986 | 0.000000 | 0.000000 | 658471313
09-04-2025 23:37:35.000 | 48906695 |  | 48.9067 | -5202635 | 15613414 | 18190066 | 99438934 | 50059101 | 61652813 | 0.000000 | 0.000000 | 651013977
09-04-2025 23:37:30.000 | 49551539 |  | 49.5515 | -5202724 | 15613251 | 18427393 | 99453308 | 50050137 | 60971406 | 0.000000 | 0.000000 | 643704346
09-04-2025 23:37:25.000 | 49408199 |  | 49.4082 | -5409588 | 15611926 | 18384495 | 99405960 | 50058990 | 60285767 | 0.000000 | 0.000000 | 636402527
09-04-2025 23:37:20.000 | 49819570 |  | 49.8196 | -5367814 | 15612859 | 18533580 | 99424553 | 50046425 | 59598159 | 0.000000 | 0.000000 | 628852600
09-04-2025 23:37:15.000 | 49132172 |  | 49.1322 | -5357531 | 15614521 | 18278436 | 99410728 | 50051064 | 58908350 | 0.000000 | 0.000000 | 621419067
09-04-2025 23:37:10.000 | 49242465 |  | 49.2425 | -5261784 | 15612615 | 18317792 | 99433945 | 50056976 | 58227280 | 0.000000 | 0.000000 | 614127991
09-04-2025 23:37:05.000 | 49156230 |  | 49.1562 | -5531370 | 15614395 | 18294172 | 99372841 | 50057888 | 57542930 | 0.000000 | 0.000000 | 606726563
09-04-2025 23:37:00.000 | 49445559 |  | 49.4456 | -5371190 | 15612186 | 18396514 | 99415161 | 50048927 | 56858188 | 0.000000 | 0.000000 | 599146301
09-04-2025 23:36:55.000 | 49012223 |  | 49.0122 | -5357868 | 15613152 | 18235322 | 99407791 | 50059399 | 56177031 | 0.000000 | 0.000000 | 591795105
09-04-2025 23:36:50.000 | 49256332 |  | 49.2563 | -5570671 | 15609251 | 18338458 | 99366539 | 50057327 | 55496147 | 0.000000 | 0.000000 | 584227112
09-04-2025 23:36:45.000 | 49952316 |  | 49.9523 | -5496552 | 15612107 | 18588352 | 99400047 | 50045071 | 54808442 | 0.000000 | 0.000000 | 576463867
09-04-2025 23:36:40.000 | 49202266 |  | 49.2023 | -5561206 | 15609361 | 18317848 | 99367294 | 50048157 | 54118135 | 0.000000 | 0.000000 | 568791809
09-04-2025 23:36:35.000 | 47834258 |  | 47.8343 | -5661510 | 15613870 | 17815050 | 99306854 | 50069485 | 53440273 | 0.000000 | 0.000000 | 561121277
09-04-2025 23:36:30.000 | 47324395 |  | 47.3244 | -5522116 | 15616438 | 17618523 | 99326088 | 50080425 | 52779668 | 0.000000 | 0.000000 | 553398010
09-04-2025 23:36:25.000 | 47810066 |  | 47.8101 | -5481231 | 15615181 | 17796588 | 99349220 | 50066116 | 52121846 | 0.000000 | 0.000000 | 545765503
09-04-2025 23:36:20.000 | 48923520 |  | 48.9235 | -5327792 | 15611481 | 18204525 | 99412254 | 50044338 | 51451919 | 0.000000 | 0.000000 | 538241638
09-04-2025 23:36:15.000 | 49728871 |  | 49.7289 | -5095171 | 15609609 | 18493081 | 99479202 | 50027596 | 50768105 | 0.000000 | 0.000000 | 530784485
09-04-2025 23:36:10.000 | 48451176 |  | 48.4512 | -5407953 | 15611524 | 18033945 | 99382851 | 50048737 | 50086011 | 0.000000 | 0.000000 | 523545410
09-04-2025 23:36:05.000 | 48302480 |  | 48.3025 | -5578816 | 15611910 | 17985103 | 99339615 | 50048176 | 49411245 | 0.000000 | 0.000000 | 516006775
09-04-2025 23:36:00.000 | 48447141 |  | 48.4471 | -5230466 | 15611760 | 18023923 | 99422249 | 50045002 | 48737817 | 0.000000 | 0.000000 | 508410278
09-04-2025 23:35:55.000 | 47384000 |  | 47.384 | -5232718 | 15611641 | 17634136 | 99395760 | 50059200 | 48075483 | 0.000000 | 0.000000 | 501081116
09-04-2025 23:35:50.000 | 47630949 |  | 47.6309 | -5667758 | 15617683 | 17735631 | 99299461 | 50060410 | 47414131 | 0.000000 | 0.000000 | 493566650
09-04-2025 23:35:45.000 | 48977801 |  | 48.9778 | -5545273 | 15614242 | 18229235 | 99365158 | 50037422 | 46745181 | 0.000000 | 0.000000 | 485833832
09-04-2025 23:35:40.000 | 49056105 |  | 49.0561 | -5297881 | 15611490 | 18250918 | 99421890 | 50034534 | 46064819 | 0.000000 | 0.000000 | 478312927
09-04-2025 23:35:35.000 | 49744184 |  | 49.7442 | -5389052 | 15613639 | 18506042 | 99418289 | 50024662 | 45380674 | 0.000000 | 0.000000 | 470873810
09-04-2025 23:35:30.000 | 50893762 |  | 50.8938 | -5283740 | 15609145 | 18929675 | 99465401 | 50009285 | 44682461 | 0.000000 | 0.000000 | 463350220
09-04-2025 23:35:25.000 | 49628531 |  | 49.6285 | -5285669 | 15611474 | 18461329 | 99437614 | 50042667 | 43983823 | 0.000000 | 0.000000 | 455992432
09-04-2025 23:35:20.000 | 48771695 |  | 48.7717 | -5573757 | 15616148 | 18153811 | 99353302 | 50067039 | 43300850 | 0.000000 | 0.000000 | 448566925
09-04-2025 23:35:15.000 | 49826281 |  | 49.8263 | -5471554 | 15612583 | 18540458 | 99402458 | 50042873 | 42616646 | 0.000000 | 0.000000 | 440969482
09-04-2025 23:35:10.000 | 49733773 |  | 49.7338 | -5252477 | 15609240 | 18501078 | 99446930 | 50032692 | 41925503 | 0.000000 | 0.000000 | 433372528
09-04-2025 23:35:05.000 | 48832422 |  | 48.8324 | -5339176 | 15611935 | 18170204 | 99407578 | 50061474 | 41239541 | 0.000000 | 0.000000 | 425992218
09-04-2025 23:35:00.000 | 48223703 |  | 48.2237 | -5912237 | 15617228 | 17964442 | 99256828 | 50075245 | 40568735 | 0.000000 | 0.000000 | 418286713
09-04-2025 23:34:55.000 | 49158141 |  | 49.1581 | -5671130 | 15613143 | 18303065 | 99341118 | 50049911 | 39888188 | 0.000000 | 0.000000 | 410548859
09-04-2025 23:34:50.000 | 49407320 |  | 49.4073 | -5462548 | 15610561 | 18387798 | 99394356 | 50041508 | 39201201 | 0.000000 | 0.000000 | 402852814
09-04-2025 23:34:45.000 | 48209660 |  | 48.2097 | -5368995 | 15609511 | 17945070 | 99385574 | 50072147 | 38519685 | 0.000000 | 0.000000 | 395455444
09-04-2025 23:34:40.000 | 47175402 |  | 47.1754 | -5259420 | 15613902 | 17555138 | 99384270 | 50066246 | 37858425 | 0.000000 | 0.000000 | 387780731
09-04-2025 23:34:35.000 | 48097902 |  | 48.0979 | -5419252 | 15614463 | 17900475 | 99371239 | 50065140 | 37199827 | 0.000000 | 0.000000 | 380396301
09-04-2025 23:34:30.000 | 49311824 |  | 49.3118 | -5239157 | 15609250 | 18345485 | 99440331 | 50037292 | 36527000 | 0.000000 | 0.000000 | 372829651
09-04-2025 23:34:25.000 | 48150879 |  | 48.1509 | -5127708 | 15612757 | 17910026 | 99437744 | 50047924 | 35845845 | 0.000000 | 0.000000 | 365573120
09-04-2025 23:34:20.000 | 48402262 |  | 48.4023 | -5324240 | 15614351 | 18008342 | 99400436 | 50051434 | 35176624 | 0.000000 | 0.000000 | 358349121
09-04-2025 23:34:15.000 | 48861492 |  | 48.8615 | -5417807 | 15615560 | 18179431 | 99390884 | 50045246 | 34503931 | 0.000000 | 0.000000 | 350968781
09-04-2025 23:34:10.000 | 49692023 |  | 49.692 | -5145856 | 15611066 | 18479150 | 99468094 | 50041233 | 33820596 | 0.000000 | 0.000000 | 343658600
09-04-2025 23:34:05.000 | 50064082 |  | 50.0641 | -5255002 | 15612176 | 18619708 | 99453621 | 50037735 | 33127212 | 0.000000 | 0.000000 | 336274597
09-04-2025 23:34:00.000 | 49638652 |  | 49.6387 | -5238384 | 15611562 | 18462736 | 99447777 | 50048733 | 32435815 | 0.000000 | 0.000000 | 329069305
09-04-2025 23:33:55.000 | 49427309 |  | 49.4273 | -5163709 | 15611067 | 18382823 | 99458717 | 50050129 | 31747419 | 0.000000 | 0.000000 | 321908569
09-04-2025 23:33:50.000 | 49519824 |  | 49.5198 | -5232500 | 15610462 | 18419746 | 99446381 | 50044563 | 31060225 | 0.000000 | 0.000000 | 314665131
09-04-2025 23:33:45.000 | 48881000 |  | 48.881 | -5215375 | 15612965 | 18181663 | 99435616 | 50054874 | 30375847 | 0.000000 | 0.000000 | 307401245
09-04-2025 23:33:40.000 | 47530914 |  | 47.5309 | -5370827 | 15613922 | 17690677 | 99367638 | 50076706 | 29704663 | 0.000000 | 0.000000 | 300207947
09-04-2025 23:33:35.000 | 47889551 |  | 47.8896 | -5215946 | 15614108 | 17817427 | 99412086 | 50064934 | 29045774 | 0.000000 | 0.000000 | 292862213
09-04-2025 23:33:30.000 | 48224551 |  | 48.2246 | -4975635 | 15613861 | 17930404 | 99471947 | 50057072 | 28381057 | 0.000000 | 0.000000 | 285730499
09-04-2025 23:33:25.000 | 47613621 |  | 47.6136 | -4994024 | 15614728 | 17705420 | 99454437 | 50066223 | 27717888 | 0.000000 | 0.000000 | 278721466
09-04-2025 23:33:20.000 | 48512484 |  | 48.5125 | -5094601 | 15614425 | 18039645 | 99453102 | 50059143 | 27055471 | 0.000000 | 0.000000 | 271635406
09-04-2025 23:33:15.000 | 50249395 |  | 50.2494 | -4950347 | 15609608 | 18679565 | 99518242 | 50023006 | 26371250 | 0.000000 | 0.000000 | 264466705
09-04-2025 23:33:10.000 | 49259359 |  | 49.2594 | -4665304 | 15610775 | 18302899 | 99554504 | 50047161 | 25675908 | 0.000000 | 0.000000 | 257836761
09-04-2025 23:33:05.000 | 48790375 |  | 48.7904 | -5025350 | 15612488 | 18141448 | 99473747 | 50060589 | 24998086 | 0.000000 | 0.000000 | 251018341
09-04-2025 23:33:00.000 | 49010191 |  | 49.0102 | -4982554 | 15612707 | 18220537 | 99487198 | 50051567 | 24322026 | 0.000000 | 0.000000 | 244054001
09-04-2025 23:32:55.000 | 49249004 |  | 49.249 | -5067581 | 15612179 | 18311792 | 99474777 | 50045425 | 23638528 | 0.000000 | 0.000000 | 237226227
09-04-2025 23:32:50.000 | 48314543 |  | 48.3145 | -4746854 | 15613180 | 17955397 | 99520821 | 50062874 | 22955259 | 0.000000 | 0.000000 | 230491135
09-04-2025 23:32:45.000 | 47611262 |  | 47.6113 | -4923203 | 15613277 | 17704531 | 99469627 | 50081707 | 22289817 | 0.000000 | 0.000000 | 223926300
09-04-2025 23:32:40.000 | 49091664 |  | 49.0917 | -5194731 | 15614604 | 18257050 | 99444794 | 50052444 | 21622649 | 0.000000 | 0.000000 | 216864700
09-04-2025 23:32:35.000 | 49961137 |  | 49.9611 | -4625638 | 15609584 | 18562423 | 99574142 | 50042988 | 20929521 | 0.000000 | 0.000000 | 210055328
09-04-2025 23:32:30.000 | 49627281 |  | 49.6273 | -5043482 | 15611405 | 18451731 | 99487564 | 50053017 | 20239630 | 0.000000 | 0.000000 | 203330917
09-04-2025 23:32:25.000 | 49544109 |  | 49.5441 | -5029175 | 15614473 | 18417113 | 99488747 | 50041424 | 19547887 | 0.000000 | 0.000000 | 196316589
09-04-2025 23:32:20.000 | 49366672 |  | 49.3667 | -4901313 | 15611220 | 18351697 | 99510750 | 50048241 | 18858148 | 0.000000 | 0.000000 | 189603424
09-04-2025 23:32:15.000 | 48730176 |  | 48.7302 | -5030514 | 15612346 | 18119227 | 99471382 | 50073540 | 18174579 | 0.000000 | 0.000000 | 182926544
09-04-2025 23:32:10.000 | 48607633 |  | 48.6076 | -4649336 | 15613967 | 18059496 | 99545670 | 50063454 | 17499149 | 0.000000 | 0.000000 | 176025665
09-04-2025 23:32:05.000 | 48541480 |  | 48.5415 | -5159066 | 15612992 | 18055406 | 99439949 | 50074318 | 16827577 | 0.000000 | 0.000000 | 169383057
09-04-2025 23:32:00.000 | 49487641 |  | 49.4876 | -4683248 | 15610198 | 18388284 | 99555199 | 50044804 | 16144644 | 0.000000 | 0.000000 | 162432053
09-04-2025 23:31:55.000 | 47991121 |  | 47.9911 | -4577822 | 15611710 | 17832548 | 99548126 | 50078575 | 15465486 | 0.000000 | 0.000000 | 155975296
09-04-2025 23:31:50.000 | 47889203 |  | 47.8892 | -5308107 | 15616695 | 17817023 | 99391312 | 50079834 | 14807478 | 0.000000 | 0.000000 | 149130692
09-04-2025 23:31:45.000 | 49979785 |  | 49.9798 | -4947636 | 15611674 | 18577007 | 99513596 | 50042461 | 14128572 | 0.000000 | 0.000000 | 141972977
09-04-2025 23:31:40.000 | 49654953 |  | 49.655 | -4962401 | 15609391 | 18460858 | 99504333 | 50040222 | 13433832 | 0.000000 | 0.000000 | 135138260
09-04-2025 23:31:35.000 | 48546734 |  | 48.5467 | -5046894 | 15612781 | 18052544 | 99463959 | 50064114 | 12750953 | 0.000000 | 0.000000 | 128186661
09-04-2025 23:31:30.000 | 48166031 |  | 48.166 | -4721028 | 15608824 | 17905542 | 99523079 | 50062229 | 12079410 | 0.000000 | 0.000000 | 121222824
09-04-2025 23:31:25.000 | 46879617 |  | 46.8796 | -5055931 | 15614740 | 17437672 | 99423454 | 50089661 | 11415511 | 0.000000 | 0.000000 | 114631477
09-04-2025 23:31:20.000 | 47667348 |  | 47.6673 | -4989940 | 15613033 | 17727568 | 99456543 | 50068840 | 10759888 | 0.000000 | 0.000000 | 107734100
09-04-2025 23:31:15.000 | 48886285 |  | 48.8863 | -5123384 | 15612079 | 18181632 | 99455307 | 50054489 | 10090729 | 0.000000 | 0.000000 | 100725410
09-04-2025 23:31:10.000 | 48555453 |  | 48.5555 | -4826146 | 15611932 | 18048835 | 99509666 | 50045517 | 941078796 | 0.000000 | 0.000000 | 93770912
09-04-2025 23:31:05.000 | 47766801 |  | 47.7668 | -4829689 | 15611344 | 17759253 | 99492729 | 50066158 | 874307434 | 0.000000 | 0.000000 | 87042290
09-04-2025 23:31:00.000 | 47597898 |  | 47.5979 | -5097020 | 15613564 | 17704463 | 99431526 | 50069824 | 808270264 | 0.000000 | 0.000000 | 80162613
09-04-2025 23:30:55.000 | 48107145 |  | 48.1071 | -4893330 | 15614447 | 17883082 | 99486656 | 50058670 | 741278687 | 0.000000 | 0.000000 | 73223351
09-04-2025 23:30:50.000 | 48399406 |  | 48.3994 | -5009825 | 15614562 | 17995474 | 99468552 | 50067299 | 674567749 | 0.000000 | 0.000000 | 66502357
09-04-2025 23:30:45.000 | 49479469 |  | 49.4795 | -5026045 | 15612693 | 18395619 | 99488052 | 50033836 | 606848450 | 0.000000 | 0.000000 | 59546593
09-04-2025 23:30:40.000 | 49398309 |  | 49.3983 | -4736701 | 15610241 | 18357069 | 99543419 | 50029221 | 537621521 | 0.000000 | 0.000000 | 52818779
09-04-2025 23:30:35.000 | 48332859 |  | 48.3329 | -4721717 | 15612810 | 17961998 | 99526207 | 50063480 | 469425415 | 0.000000 | 0.000000 | 46386505
09-04-2025 23:30:30.000 | 47836633 |  | 47.8366 | -4935667 | 15615520 | 17785006 | 99471931 | 50063309 | 402927216 | 0.000000 | 0.000000 | 39717384
09-04-2025 23:30:25.000 | 47858320 |  | 47.8583 | -4777908 | 15612866 | 17789822 | 99505348 | 50064964 | 336428223 | 0.000000 | 0.000000 | 33101929
09-04-2025 23:30:20.000 | 48695379 |  | 48.6954 | -4648388 | 15613162 | 18093346 | 99547478 | 50059536 | 269647156 | 0.000000 | 0.000000 | 26465179
09-04-2025 23:30:15.000 | 48767598 |  | 48.7676 | -4815917 | 15611777 | 18126284 | 99515938 | 50052536 | 202160004 | 0.000000 | 0.000000 | 20007038
09-04-2025 23:30:10.000 | 49086684 |  | 49.0867 | -4675795 | 15609530 | 18241349 | 99549377 | 50034595 | 134064392 | 0.000000 | 0.000000 | 13496312
09-04-2025 23:30:05.000 | 48350426 |  | 48.3504 | -4923603 | 15613128 | 17975403 | 99485512 | 50052414 | 66342300 | 0.000000 | 0.000000 | 6913057
09-04-2025 23:30:00.000 | 47459930 |  | 47.4599 | -4912704 | 15614890 | 17645356 | 99468521 | 50061069 | 12165927 | 0.000000 | 0.000000 | 12790078
09-04-2025 23:29:55.000 | 47880570 |  | 47.8806 | -4774901 | 15615075 | 17794709 | 99506424 | 50054543 | 12100089 | 0.000000 | 0.000000 | 12723848
09-04-2025 23:29:50.000 | 49419039 |  | 49.419 | -4749353 | 15613750 | 18361599 | 99541382 | 50024532 | 12032611 | 0.000000 | 0.000000 | 12657423
09-04-2025 23:29:45.000 | 49497977 |  | 49.498 | -4405178 | 15613201 | 18379536 | 99606316 | 50017315 | 11964002 | 0.000000 | 0.000000 | 12593674
09-04-2025 23:29:40.000 | 48856688 |  | 48.8567 | -4640352 | 15616877 | 18147548 | 99551979 | 50029861 | 11895696 | 0.000000 | 0.000000 | 12531917
09-04-2025 23:29:35.000 | 50246750 |  | 50.2467 | -4535982 | 15612525 | 18660787 | 99595001 | 50023983 | 11826852 | 0.000000 | 0.000000 | 12468770
09-04-2025 23:29:30.000 | 51196953 |  | 51.197 | -4688654 | 15610641 | 19017191 | 99583267 | 50025688 | 11756573 | 0.000000 | 0.000000 | 12404911
09-04-2025 23:29:25.000 | 51401102 |  | 51.4011 | -4753943 | 15608283 | 19097815 | 99575027 | 50030483 | 11685431 | 0.000000 | 0.000000 | 12338021
09-04-2025 23:29:20.000 | 50475098 |  | 50.4751 | -4763267 | 15608538 | 18756785 | 99557678 | 50044113 | 11614646 | 0.000000 | 0.000000 | 12270566
09-04-2025 23:29:15.000 | 48548684 |  | 48.5487 | -5289291 | 15612153 | 18064552 | 99411743 | 50094707 | 11545548 | 0.000000 | 0.000000 | 12202589
09-04-2025 23:29:10.000 | 48703688 |  | 48.7037 | -5290827 | 15611208 | 18121633 | 99415115 | 50097092 | 11478226 | 0.000000 | 0.000000 | 12128237
09-04-2025 23:29:05.000 | 48865438 |  | 48.8654 | -5537375 | 15613213 | 18188359 | 99364059 | 50083900 | 11410556 | 0.000000 | 0.000000 | 12052584
09-04-2025 23:29:00.000 | 48662746 |  | 48.6627 | -5120242 | 15609859 | 18101149 | 99451004 | 50087013 | 11342292 | 0.000000 | 0.000000 | 11978184
09-04-2025 23:28:55.000 | 47003129 |  | 47.0031 | -5291235 | 15613358 | 17493925 | 99372337 | 50114201 | 11276069 | 0.000000 | 0.000000 | 11906317
09-04-2025 23:28:50.000 | 47493188 |  | 47.4932 | -5150075 | 15614767 | 17666791 | 99417191 | 50107224 | 11210545 | 0.000000 | 0.000000 | 11833053
09-04-2025 23:28:45.000 | 48211230 |  | 48.2112 | -5277246 | 15613726 | 17937329 | 99406242 | 50098209 | 11144063 | 0.000000 | 0.000000 | 11761438
09-04-2025 23:28:40.000 | 50222781 |  | 50.2228 | -5223430 | 15611302 | 18677292 | 99463493 | 50057610 | 11075998 | 0.000000 | 0.000000 | 11686206
09-04-2025 23:28:35.000 | 48979359 |  | 48.9794 | -4882016 | 15610040 | 18208464 | 99506920 | 50067009 | 11006697 | 0.000000 | 0.000000 | 11615856
09-04-2025 23:28:30.000 | 47471715 |  | 47.4717 | -5134114 | 15612038 | 17661594 | 99420250 | 50102772 | 10939481 | 0.000000 | 0.000000 | 11547333
09-04-2025 23:28:25.000 | 48485320 |  | 48.4853 | -5282041 | 15614207 | 18038046 | 99411819 | 50095737 | 10873175 | 0.000000 | 0.000000 | 11474364
09-04-2025 23:28:20.000 | 49355992 |  | 49.356 | -5264350 | 15611903 | 18359399 | 99435982 | 50067360 | 10805286 | 0.000000 | 0.000000 | 11400975
09-04-2025 23:28:15.000 | 49214836 |  | 49.2148 | -5125881 | 15611412 | 18302831 | 99461983 | 50073990 | 10736550 | 0.000000 | 0.000000 | 11328862
09-04-2025 23:28:10.000 | 48442094 |  | 48.4421 | -5250176 | 15613283 | 18021113 | 99417809 | 50087494 | 10668733 | 0.000000 | 0.000000 | 11257045
09-04-2025 23:28:05.000 | 48690137 |  | 48.6901 | -5494646 | 15613371 | 18122156 | 99369270 | 50085449 | 10601496 | 0.000000 | 0.000000 | 11183345
09-04-2025 23:28:00.000 | 49239223 |  | 49.2392 | -5146138 | 15612912 | 18310411 | 99458282 | 50069923 | 10533148 | 0.000000 | 0.000000 | 11108950
09-04-2025 23:27:55.000 | 49540727 |  | 49.5407 | -5038361 | 15611568 | 18419352 | 99486816 | 50077301 | 10464625 | 0.000000 | 0.000000 | 11038322
09-04-2025 23:27:50.000 | 50144660 |  | 50.1447 | -5232102 | 15608527 | 18652339 | 99460060 | 50084999 | 10395374 | 0.000000 | 0.000000 | 10968252
09-04-2025 23:27:45.000 | 49527641 |  | 49.5276 | -5118832 | 15609980 | 18419398 | 99470146 | 50081131 | 10325910 | 0.000000 | 0.000000 | 10894613
09-04-2025 23:27:40.000 | 48565969 |  | 48.566 | -5344005 | 15611042 | 18073665 | 99400047 | 50113251 | 10257924 | 0.000000 | 0.000000 | 10822550
09-04-2025 23:27:35.000 | 47209535 |  | 47.2095 | -5292446 | 15612964 | 17570234 | 99377480 | 50112778 | 10191253 | 0.000000 | 0.000000 | 10748473
09-04-2025 23:27:30.000 | 47427758 |  | 47.4278 | -5294609 | 15615007 | 17648445 | 99382645 | 50113960 | 10125309 | 0.000000 | 0.000000 | 10676475
09-04-2025 23:27:25.000 | 47453965 |  | 47.454 | -5080776 | 15614971 | 17649279 | 99431709 | 50089481 | 10059532 | 0.000000 | 0.000000 | 10603015
09-04-2025 23:27:20.000 | 47936086 |  | 47.9361 | -5060310 | 15613144 | 17827975 | 99447426 | 50086109 | 99935215 | 0.000000 | 0.000000 | 10532865
09-04-2025 23:27:15.000 | 48510379 |  | 48.5104 | -5080681 | 15613057 | 18039750 | 99456009 | 50073460 | 99265635 | 0.000000 | 0.000000 | 10463044
09-04-2025 23:27:10.000 | 48697934 |  | 48.6979 | -5149760 | 15611063 | 18113824 | 99445503 | 50059517 | 98591699 | 0.000000 | 0.000000 | 10391945
09-04-2025 23:27:05.000 | 47753484 |  | 47.7535 | -5374746 | 15610908 | 17776387 | 99372559 | 50077801 | 97919092 | 0.000000 | 0.000000 | 10320303
09-04-2025 23:27:00.000 | 47690813 |  | 47.6908 | -5373354 | 15615323 | 17747693 | 99371246 | 50080524 | 97253047 | 0.000000 | 0.000000 | 10246309
09-04-2025 23:26:55.000 | 48107715 |  | 48.1077 | -5094682 | 15613265 | 17892568 | 99443916 | 50076809 | 96587666 | 0.000000 | 0.000000 | 10173235
09-04-2025 23:26:50.000 | 48189480 |  | 48.1895 | -5389670 | 15613334 | 17933997 | 99380363 | 50084320 | 95921953 | 0.000000 | 0.000000 | 10100449
09-04-2025 23:26:45.000 | 48654461 |  | 48.6545 | -5219211 | 15612032 | 18099413 | 99429565 | 50057426 | 95249375 | 0.000000 | 0.000000 | 10025624
09-04-2025 23:26:40.000 | 48809820 |  | 48.8098 | -5056973 | 15610270 | 18152745 | 99467575 | 50067360 | 94571650 | 0.000000 | 0.000000 | 995391418
09-04-2025 23:26:35.000 | 47980668 |  | 47.9807 | -5167996 | 15612406 | 17850244 | 99424927 | 50077774 | 93902461 | 0.000000 | 0.000000 | 988252380
09-04-2025 23:26:30.000 | 47746266 |  | 47.7463 | -5409606 | 15613603 | 17771788 | 99364281 | 50083374 | 93236943 | 0.000000 | 0.000000 | 981052795
09-04-2025 23:26:25.000 | 48320219 |  | 48.3202 | -5095207 | 15611524 | 17972510 | 99448647 | 50079456 | 92570986 | 0.000000 | 0.000000 | 973727051
09-04-2025 23:26:20.000 | 47948375 |  | 47.9484 | -5176282 | 15612795 | 17837448 | 99422325 | 50076824 | 91906035 | 0.000000 | 0.000000 | 966568787
09-04-2025 23:26:15.000 | 47639121 |  | 47.6391 | -5301486 | 15612446 | 17729594 | 99386482 | 50088879 | 91242139 | 0.000000 | 0.000000 | 959418335
09-04-2025 23:26:10.000 | 48096539 |  | 48.0965 | -5250680 | 15613319 | 17895045 | 99409370 | 50079319 | 90578242 | 0.000000 | 0.000000 | 952029846
09-04-2025 23:26:05.000 | 48312117 |  | 48.3121 | -5137955 | 15612950 | 17969287 | 99439247 | 50068741 | 89910381 | 0.000000 | 0.000000 | 944846558
09-04-2025 23:26:00.000 | 47468078 |  | 47.4681 | -4993819 | 15613042 | 17653983 | 99451164 | 50080704 | 89242080 | 0.000000 | 0.000000 | 937830017
09-04-2025 23:25:55.000 | 47600922 |  | 47.6009 | -5112949 | 15613932 | 17705688 | 99428070 | 50080330 | 88581465 | 0.000000 | 0.000000 | 930846008
09-04-2025 23:25:50.000 | 48680754 |  | 48.6808 | -5129883 | 15612104 | 18105635 | 99449356 | 50065845 | 87915928 | 0.000000 | 0.000000 | 923639526
09-04-2025 23:25:45.000 | 48463457 |  | 48.4635 | -5165204 | 15612261 | 18027024 | 99436836 | 50066692 | 87240752 | 0.000000 | 0.000000 | 916579041
09-04-2025 23:25:40.000 | 48406277 |  | 48.4063 | -5072084 | 15613336 | 18001365 | 99455521 | 50059711 | 86565576 | 0.000000 | 0.000000 | 909476074
09-04-2025 23:25:35.000 | 48393723 |  | 48.3937 | -4971652 | 15611637 | 17994467 | 99476433 | 50068096 | 85895625 | 0.000000 | 0.000000 | 902456177
09-04-2025 23:25:30.000 | 48277836 |  | 48.2778 | -5203519 | 15613117 | 17959199 | 99424156 | 50069611 | 85224795 | 0.000000 | 0.000000 | 895397217
09-04-2025 23:25:25.000 | 48805469 |  | 48.8055 | -4716124 | 15612951 | 18135085 | 99536369 | 50050541 | 84548877 | 0.000000 | 0.000000 | 888343201
09-04-2025 23:25:20.000 | 48333941 |  | 48.3339 | -4817880 | 15612514 | 17965690 | 99506874 | 50073654 | 83875430 | 0.000000 | 0.000000 | 881832397
09-04-2025 23:25:15.000 | 49155734 |  | 49.1557 | -5022047 | 15614414 | 18273748 | 99482155 | 50057121 | 83200596 | 0.000000 | 0.000000 | 874930359
09-04-2025 23:25:10.000 | 49815285 |  | 49.8153 | -4747433 | 15612811 | 18508090 | 99548958 | 50032917 | 82511094 | 0.000000 | 0.000000 | 868058044
09-04-2025 23:25:05.000 | 49453656 |  | 49.4537 | -4991596 | 15612975 | 18383518 | 99494469 | 50050060 | 81822456 | 0.000000 | 0.000000 | 861361938
09-04-2025 23:25:00.000 | 49673977 |  | 49.674 | -5002166 | 15610524 | 18468285 | 99496803 | 50044834 | 81136533 | 0.000000 | 0.000000 | 854396362
09-04-2025 23:24:55.000 | 49767863 |  | 49.7679 | -4896972 | 15611297 | 18497834 | 99519394 | 50043697 | 80444990 | 0.000000 | 0.000000 | 847413879
09-04-2025 23:24:50.000 | 49453426 |  | 49.4534 | -4882654 | 15612622 | 18380165 | 99516129 | 50045071 | 79757295 | 0.000000 | 0.000000 | 840494812
09-04-2025 23:24:45.000 | 48529570 |  | 48.5296 | -5143666 | 15613604 | 18048739 | 99442993 | 50069038 | 79078169 | 0.000000 | 0.000000 | 833679382
09-04-2025 23:24:40.000 | 49371016 |  | 49.371 | -5405935 | 15612949 | 18369189 | 99405869 | 50056545 | 78400947 | 0.000000 | 0.000000 | 826453125
09-04-2025 23:24:35.000 | 50318605 |  | 50.3186 | -4972856 | 15609181 | 18705554 | 99515205 | 50044254 | 77706465 | 0.000000 | 0.000000 | 819159302
09-04-2025 23:24:30.000 | 48484570 |  | 48.4846 | -4998239 | 15610640 | 18029994 | 99472832 | 50075378 | 77020112 | 0.000000 | 0.000000 | 812338501
09-04-2025 23:24:25.000 | 48132805 |  | 48.1328 | -5341490 | 15612616 | 17912620 | 99389870 | 50084709 | 76350591 | 0.000000 | 0.000000 | 805160828
09-04-2025 23:24:20.000 | 48516000 |  | 48.516 | -5385912 | 15609169 | 18059108 | 99389442 | 50076141 | 75675283 | 0.000000 | 0.000000 | 797932495
09-04-2025 23:24:15.000 | 47920809 |  | 47.9208 | -5297788 | 15610392 | 17835146 | 99394447 | 50072063 | 75005010 | 0.000000 | 0.000000 | 790360291
09-04-2025 23:24:10.000 | 46631789 |  | 46.6318 | -4743750 | 15611971 | 17338601 | 99486557 | 50086605 | 74345771 | 0.000000 | 0.000000 | 783260315
09-04-2025 23:24:05.000 | 45115492 |  | 45.1155 | -4947648 | 15618841 | 16780922 | 99404037 | 50114841 | 73705439 | 0.000000 | 0.000000 | 776617004
09-04-2025 23:24:00.000 | 47432090 |  | 47.4321 | -4327798 | 15613137 | 17616926 | 99586327 | 50048077 | 73067783 | 0.000000 | 0.000000 | 769974487
09-04-2025 23:23:55.000 | 47192293 |  | 47.1923 | -4402710 | 15611297 | 17532421 | 99567642 | 50047344 | 72407837 | 0.000000 | 0.000000 | 764045044
09-04-2025 23:23:50.000 | 47800762 |  | 47.8008 | -4623516 | 15609379 | 17766315 | 99535477 | 50040638 | 71746851 | 0.000000 | 0.000000 | 757782593
09-04-2025 23:23:45.000 | 47901941 |  | 47.9019 | -4870840 | 15613707 | 17808168 | 99487000 | 50031872 | 71080947 | 0.000000 | 0.000000 | 751190918
09-04-2025 23:23:40.000 | 47167313 |  | 47.1673 | -4397931 | 15611146 | 17523369 | 99568123 | 50029190 | 70418467 | 0.000000 | 0.000000 | 744631470
09-04-2025 23:23:35.000 | 47220277 |  | 47.2203 | -4847082 | 15617618 | 17551646 | 99477295 | 50032711 | 69764463 | 0.000000 | 0.000000 | 738198242
09-04-2025 23:23:30.000 | 49396297 |  | 49.3963 | -4732132 | 15613191 | 18352820 | 99544258 | 49996407 | 69096724 | 0.000000 | 0.000000 | 731525818
09-04-2025 23:23:25.000 | 50121457 |  | 50.1215 | -4670809 | 15613135 | 18617727 | 99568588 | 49987328 | 68404116 | 0.000000 | 0.000000 | 724936035
09-04-2025 23:23:20.000 | 50438824 |  | 50.4388 | -4610849 | 15612695 | 18733236 | 99584770 | 50001461 | 67703115 | 0.000000 | 0.000000 | 718600098
09-04-2025 23:23:15.000 | 51002020 |  | 51.002 | -4588140 | 15610412 | 18942830 | 99597801 | 50009300 | 67002710 | 0.000000 | 0.000000 | 712162415
09-04-2025 23:23:10.000 | 50614949 |  | 50.6149 | -4741665 | 15608320 | 18807615 | 99564056 | 50025318 | 66298086 | 0.000000 | 0.000000 | 705719177
09-04-2025 23:23:05.000 | 49622094 |  | 49.6221 | -4773421 | 15608495 | 18443715 | 99540504 | 50049278 | 65597383 | 0.000000 | 0.000000 | 699177307
09-04-2025 23:23:00.000 | 48597262 |  | 48.5973 | -5019031 | 15609177 | 18074044 | 99470909 | 50063923 | 64917666 | 0.000000 | 0.000000 | 692197083
09-04-2025 23:22:55.000 | 47422922 |  | 47.4229 | -4986001 | 15613229 | 17636067 | 99451828 | 50070274 | 64251221 | 0.000000 | 0.000000 | 685214233
09-04-2025 23:22:50.000 | 46893488 |  | 46.8935 | -4822045 | 15613299 | 17435289 | 99475456 | 50070305 | 63592881 | 0.000000 | 0.000000 | 678461975
09-04-2025 23:22:45.000 | 45887777 |  | 45.8878 | -4903877 | 15616014 | 17066122 | 99433823 | 50081116 | 62950210 | 0.000000 | 0.000000 | 671809143
09-04-2025 23:22:40.000 | 46795660 |  | 46.7957 | -5030208 | 15615679 | 17405317 | 99427223 | 50054462 | 62308975 | 0.000000 | 0.000000 | 664977112
09-04-2025 23:22:35.000 | 48334844 |  | 48.3348 | -4765673 | 15611846 | 17965726 | 99517448 | 50019451 | 61645869 | 0.000000 | 0.000000 | 658193787
09-04-2025 23:22:30.000 | 47064586 |  | 47.0646 | -4673918 | 15614914 | 17490846 | 99510506 | 50031876 | 60980923 | 0.000000 | 0.000000 | 651765442
09-04-2025 23:22:25.000 | 46709711 |  | 46.7097 | -4698620 | 15618003 | 17357457 | 99497871 | 50026340 | 60330781 | 0.000000 | 0.000000 | 645248108
09-04-2025 23:22:20.000 | 47237375 |  | 47.2374 | -4277768 | 15615821 | 17539926 | 99592461 | 50015270 | 59678799 | 0.000000 | 0.000000 | 639082031
09-04-2025 23:22:15.000 | 48618133 |  | 48.6181 | -4770078 | 15620951 | 18058955 | 99522141 | 49997967 | 59017896 | 0.000000 | 0.000000 | 632824524
09-04-2025 23:22:10.000 | 51140273 |  | 51.1403 | -4326778 | 15614209 | 18980999 | 99643997 | 49957726 | 58326343 | 0.000000 | 0.000000 | 626499756
09-04-2025 23:22:05.000 | 52012445 |  | 52.0124 | -4561985 | 15612363 | 19311765 | 99617554 | 49958599 | 57610254 | 0.000000 | 0.000000 | 620289612
09-04-2025 23:22:00.000 | 52033922 |  | 52.0339 | -4584167 | 15611710 | 19320740 | 99614166 | 49967949 | 56885679 | 0.000000 | 0.000000 | 614022766
09-04-2025 23:21:55.000 | 52460016 |  | 52.46 | -4838912 | 15613011 | 19484606 | 99577286 | 49973091 | 56161094 | 0.000000 | 0.000000 | 607477112
09-04-2025 23:21:50.000 | 53019004 |  | 53.019 | -4905019 | 15606531 | 19701132 | 99574783 | 49961132 | 55426494 | 0.000000 | 0.000000 | 600784058
09-04-2025 23:21:45.000 | 52092563 |  | 52.0926 | -4551603 | 15603338 | 19351931 | 99620453 | 49985729 | 54690630 | 0.000000 | 0.000000 | 594102173
09-04-2025 23:21:40.000 | 48651719 |  | 48.6517 | -5237093 | 15609084 | 18103115 | 99425621 | 50069881 | 53987188 | 0.000000 | 0.000000 | 587566528
09-04-2025 23:21:35.000 | 48274277 |  | 48.2743 | -5410244 | 15612027 | 17967856 | 99377838 | 50073498 | 53314795 | 0.000000 | 0.000000 | 580104614
09-04-2025 23:21:30.000 | 47998297 |  | 47.9983 | -5460189 | 15611021 | 17871090 | 99359169 | 50076855 | 52643247 | 0.000000 | 0.000000 | 572594421
09-04-2025 23:21:25.000 | 47541551 |  | 47.5416 | -5326531 | 15614395 | 17692333 | 99378204 | 50083530 | 51981948 | 0.000000 | 0.000000 | 564860535
09-04-2025 23:21:20.000 | 47326383 |  | 47.3264 | -5299449 | 15613641 | 17614146 | 99378899 | 50080574 | 51327900 | 0.000000 | 0.000000 | 557511536
09-04-2025 23:21:15.000 | 48821066 |  | 48.8211 | -5277829 | 15613035 | 18162083 | 99420731 | 50041855 | 50664204 | 0.000000 | 0.000000 | 550074097
09-04-2025 23:21:10.000 | 49158637 |  | 49.1586 | -4854413 | 15610481 | 18273007 | 99515961 | 50030453 | 49980693 | 0.000000 | 0.000000 | 542935120
09-04-2025 23:21:05.000 | 48248906 |  | 48.2489 | -4936244 | 15611354 | 17941268 | 99480728 | 50054794 | 49307324 | 0.000000 | 0.000000 | 536098755
09-04-2025 23:21:00.000 | 47887598 |  | 47.8876 | -5223053 | 15614595 | 17815573 | 99410454 | 50066353 | 48640049 | 0.000000 | 0.000000 | 529064514
09-04-2025 23:20:55.000 | 48848441 |  | 48.8484 | -5136196 | 15614045 | 18165487 | 99451759 | 50038063 | 47967837 | 0.000000 | 0.000000 | 521788818
09-04-2025 23:20:50.000 | 49057527 |  | 49.0575 | -4962414 | 15613004 | 18236738 | 99492279 | 50038887 | 47290381 | 0.000000 | 0.000000 | 514681885
09-04-2025 23:20:45.000 | 48619742 |  | 48.6197 | -4994797 | 15612528 | 18077527 | 99476448 | 50048546 | 46613398 | 0.000000 | 0.000000 | 507862244
09-04-2025 23:20:40.000 | 49099223 |  | 49.0992 | -4900512 | 15612186 | 18251110 | 99505608 | 50038555 | 45933125 | 0.000000 | 0.000000 | 500914032
09-04-2025 23:20:35.000 | 49615180 |  | 49.6152 | -4952087 | 15609843 | 18445205 | 99505592 | 50030582 | 45248208 | 0.000000 | 0.000000 | 494024994
09-04-2025 23:20:30.000 | 48940824 |  | 48.9408 | -4830168 | 15608638 | 18193990 | 99516502 | 50030289 | 44562207 | 0.000000 | 0.000000 | 487199219
09-04-2025 23:20:25.000 | 47268465 |  | 47.2685 | -5056202 | 15613705 | 17581451 | 99432755 | 50052967 | 43889756 | 0.000000 | 0.000000 | 480259674
09-04-2025 23:20:20.000 | 47113047 |  | 47.113 | -5237933 | 15616085 | 17530287 | 99387642 | 50068192 | 43234771 | 0.000000 | 0.000000 | 473127258
09-04-2025 23:20:15.000 | 48340227 |  | 48.3402 | -5024104 | 15617346 | 17970034 | 99464241 | 50032707 | 42578423 | 0.000000 | 0.000000 | 465805328
09-04-2025 23:20:10.000 | 49917336 |  | 49.9173 | -5140094 | 15614211 | 18558335 | 99474014 | 50007687 | 41897578 | 0.000000 | 0.000000 | 458809296
09-04-2025 23:20:05.000 | 50921414 |  | 50.9214 | -5194639 | 15610715 | 18933816 | 99483696 | 50004364 | 41196001 | 0.000000 | 0.000000 | 451716827
09-04-2025 23:20:00.000 | 50679125 |  | 50.6791 | -4938634 | 15606610 | 18840382 | 99528542 | 50007771 | 40489387 | 0.000000 | 0.000000 | 444465973
09-04-2025 23:19:55.000 | 49543070 |  | 49.5431 | -5586024 | 15611630 | 18442026 | 99370361 | 50038589 | 39790742 | 0.000000 | 0.000000 | 437261719
09-04-2025 23:19:50.000 | 49570898 |  | 49.5709 | -5558397 | 15610969 | 18451663 | 99377205 | 50051575 | 39103345 | 0.000000 | 0.000000 | 429522095
09-04-2025 23:19:45.000 | 48951484 |  | 48.9515 | -5636822 | 15612198 | 18225864 | 99343529 | 50055019 | 38418982 | 0.000000 | 0.000000 | 421660431
09-04-2025 23:19:40.000 | 48072027 |  | 48.072 | -5339306 | 15610667 | 17892751 | 99388832 | 50064632 | 37738572 | 0.000000 | 0.000000 | 414108521
09-04-2025 23:19:35.000 | 47363355 |  | 47.3634 | -5712532 | 15613274 | 17644415 | 99280495 | 50087910 | 37076831 | 0.000000 | 0.000000 | 406429260
09-04-2025 23:19:30.000 | 47615578 |  | 47.6156 | -5812206 | 15613630 | 17741154 | 99263229 | 50085632 | 36418884 | 0.000000 | 0.000000 | 398502716
09-04-2025 23:19:25.000 | 47583645 |  | 47.5836 | -5658035 | 15613839 | 17722465 | 99300461 | 50077301 | 35756826 | 0.000000 | 0.000000 | 390542816
09-04-2025 23:19:20.000 | 48377609 |  | 48.3776 | -5569442 | 15614941 | 18008710 | 99343834 | 50072701 | 35090681 | 0.000000 | 0.000000 | 382734589
09-04-2025 23:19:15.000 | 48773363 |  | 48.7734 | -5404984 | 15612367 | 18150472 | 99391563 | 50063095 | 34417959 | 0.000000 | 0.000000 | 375022034
09-04-2025 23:19:10.000 | 48552809 |  | 48.5528 | -5501205 | 15612982 | 18072518 | 99364227 | 50062080 | 33742974 | 0.000000 | 0.000000 | 367501678
09-04-2025 23:19:05.000 | 48974359 |  | 48.9744 | -5391478 | 15612363 | 18223792 | 99399490 | 50061981 | 33065042 | 0.000000 | 0.000000 | 359994537
09-04-2025 23:19:00.000 | 49105336 |  | 49.1053 | -5552268 | 15612238 | 18278464 | 99366837 | 50055508 | 32384114 | 0.000000 | 0.000000 | 352495453
09-04-2025 23:18:55.000 | 48341969 |  | 48.342 | -5507786 | 15611437 | 17997058 | 99357208 | 50062038 | 31703831 | 0.000000 | 0.000000 | 344861816
09-04-2025 23:18:50.000 | 48149004 |  | 48.149 | -5460333 | 15610378 | 17925850 | 99363106 | 50069492 | 31031553 | 0.000000 | 0.000000 | 337254272
09-04-2025 23:18:45.000 | 47573875 |  | 47.5739 | -5496133 | 15609709 | 17716523 | 99339264 | 50071712 | 30362314 | 0.000000 | 0.000000 | 329632813
09-04-2025 23:18:40.000 | 46271484 |  | 46.2715 | -5309769 | 15612699 | 17226710 | 99348022 | 50075947 | 29709602 | 0.000000 | 0.000000 | 322118408
09-04-2025 23:18:35.000 | 45229691 |  | 45.2297 | -5470426 | 15611640 | 16852319 | 99276512 | 50094955 | 29073855 | 0.000000 | 0.000000 | 314816345
09-04-2025 23:18:30.000 | 45412590 |  | 45.4126 | -5363193 | 15614933 | 16911329 | 99309837 | 50071301 | 28445210 | 0.000000 | 0.000000 | 307176239
09-04-2025 23:18:25.000 | 45116035 |  | 45.116 | -5181295 | 15615515 | 16794235 | 99347000 | 50059052 | 27816008 | 0.000000 | 0.000000 | 299811218
09-04-2025 23:18:20.000 | 45272172 |  | 45.2722 | -5108612 | 15619287 | 16844476 | 99369347 | 50061775 | 27187302 | 0.000000 | 0.000000 | 292810822
09-04-2025 23:18:15.000 | 46535309 |  | 46.5353 | -4941131 | 15619563 | 17302261 | 99441010 | 50022720 | 26552517 | 0.000000 | 0.000000 | 285821442
09-04-2025 23:18:10.000 | 49306477 |  | 49.3065 | -4553412 | 15616205 | 18311002 | 99576286 | 49973675 | 25889128 | 0.000000 | 0.000000 | 279175171
09-04-2025 23:18:05.000 | 50174164 |  | 50.1742 | -4627034 | 15613465 | 18635503 | 99577469 | 49962776 | 25200059 | 0.000000 | 0.000000 | 272849823
09-04-2025 23:18:00.000 | 50275785 |  | 50.2758 | -4660389 | 15614420 | 18673555 | 99573120 | 49973877 | 24499463 | 0.000000 | 0.000000 | 266499786
09-04-2025 23:17:55.000 | 51007645 |  | 51.0076 | -4752452 | 15614043 | 18945668 | 99568764 | 49976372 | 23798232 | 0.000000 | 0.000000 | 260001617
09-04-2025 23:17:50.000 | 51548309 |  | 51.5483 | -4887904 | 15611287 | 19153174 | 99553452 | 49976845 | 23085420 | 0.000000 | 0.000000 | 253289413
09-04-2025 23:17:45.000 | 51926863 |  | 51.9269 | -5176168 | 15608971 | 19305881 | 99506851 | 49980701 | 22365198 | 0.000000 | 0.000000 | 246484177
09-04-2025 23:17:40.000 | 51239371 |  | 51.2394 | -4681134 | 15604859 | 19040924 | 99585281 | 50000366 | 21645796 | 0.000000 | 0.000000 | 239475433
09-04-2025 23:17:35.000 | 47796914 |  | 47.7969 | -5356525 | 15611844 | 17790195 | 99377884 | 50068619 | 20958084 | 0.000000 | 0.000000 | 232631714
09-04-2025 23:17:30.000 | 48434789 |  | 48.4348 | -5522708 | 15614970 | 18028204 | 99356201 | 50063469 | 20290126 | 0.000000 | 0.000000 | 225051590
09-04-2025 23:17:25.000 | 48928574 |  | 48.9286 | -5273527 | 15615125 | 18199923 | 99424187 | 50052216 | 19613754 | 0.000000 | 0.000000 | 217496704
09-04-2025 23:17:20.000 | 48458332 |  | 48.4583 | -5191775 | 15612474 | 18026204 | 99430954 | 50062141 | 18937776 | 0.000000 | 0.000000 | 210402527
09-04-2025 23:17:15.000 | 48864879 |  | 48.8649 | -5479814 | 15611660 | 18187919 | 99377075 | 50052296 | 18262776 | 0.000000 | 0.000000 | 203149216
09-04-2025 23:17:10.000 | 49302117 |  | 49.3021 | -5359423 | 15611313 | 18344280 | 99414337 | 50042496 | 17577749 | 0.000000 | 0.000000 | 195524841
09-04-2025 23:17:05.000 | 48840719 |  | 48.8407 | -5360059 | 15608717 | 18177825 | 99403183 | 50051132 | 16895804 | 0.000000 | 0.000000 | 188025681
09-04-2025 23:17:00.000 | 46671355 |  | 46.6714 | -5291425 | 15613748 | 17371899 | 99363419 | 50072624 | 16228820 | 0.000000 | 0.000000 | 180564102
09-04-2025 23:16:55.000 | 45912520 |  | 45.9125 | -5610996 | 15619158 | 17101636 | 99261490 | 50098412 | 15586658 | 0.000000 | 0.000000 | 173135483
09-04-2025 23:16:50.000 | 48586570 |  | 48.5866 | -5819751 | 15620953 | 18089490 | 99290253 | 50052837 | 14937833 | 0.000000 | 0.000000 | 165265900
09-04-2025 23:16:45.000 | 51857523 |  | 51.8575 | -4831331 | 15608982 | 19268540 | 99568817 | 49981983 | 14241085 | 0.000000 | 0.000000 | 157732697
09-04-2025 23:16:40.000 | 51403391 |  | 51.4034 | -5242708 | 15606841 | 19118193 | 99483910 | 50003899 | 13525137 | 0.000000 | 0.000000 | 150711029
09-04-2025 23:16:35.000 | 50911973 |  | 50.912 | -5263040 | 15609109 | 18935088 | 99469925 | 50020073 | 12812474 | 0.000000 | 0.000000 | 143286652
09-04-2025 23:16:30.000 | 49084125 |  | 49.0841 | -5135471 | 15609662 | 18257573 | 99457123 | 50061005 | 12113706 | 0.000000 | 0.000000 | 136112167
09-04-2025 23:16:25.000 | 48736383 |  | 48.7364 | -5858277 | 15610728 | 18157908 | 99285294 | 50079453 | 11437897 | 0.000000 | 0.000000 | 128615845
09-04-2025 23:16:20.000 | 48595824 |  | 48.5958 | -5688643 | 15610993 | 18099581 | 99321808 | 50068821 | 10761346 | 0.000000 | 0.000000 | 120491081
09-04-2025 23:16:15.000 | 47906020 |  | 47.906 | -5371850 | 15611144 | 17832386 | 99377174 | 50081181 | 10088044 | 0.000000 | 0.000000 | 112811646
09-04-2025 23:16:10.000 | 46980754 |  | 46.9808 | -5520223 | 15613689 | 17495248 | 99316757 | 50092339 | 943161865 | 0.000000 | 0.000000 | 105237404
09-04-2025 23:16:05.000 | 46481113 |  | 46.4811 | -5373760 | 15613248 | 17305793 | 99338326 | 50076683 | 878291626 | 0.000000 | 0.000000 | 97708466
09-04-2025 23:16:00.000 | 47398926 |  | 47.3989 | -5589211 | 15614635 | 17650607 | 99311928 | 50068718 | 813044678 | 0.000000 | 0.000000 | 90102303
09-04-2025 23:15:55.000 | 48578742 |  | 48.5787 | -5562667 | 15610719 | 18087384 | 99350769 | 50042591 | 746666260 | 0.000000 | 0.000000 | 82281754
09-04-2025 23:15:50.000 | 47730141 |  | 47.7301 | -5374213 | 15612153 | 17765919 | 99372070 | 50042816 | 679574341 | 0.000000 | 0.000000 | 74618179
09-04-2025 23:15:45.000 | 46774035 |  | 46.774 | -5278346 | 15614338 | 17408733 | 99369286 | 50053566 | 613944519 | 0.000000 | 0.000000 | 67159828
09-04-2025 23:15:40.000 | 46991500 |  | 46.9915 | -5471676 | 15616904 | 17494280 | 99328903 | 50043022 | 548701965 | 0.000000 | 0.000000 | 59767826
09-04-2025 23:15:35.000 | 48244438 |  | 48.2444 | -5436440 | 15615791 | 17953933 | 99371086 | 50022270 | 482941650 | 0.000000 | 0.000000 | 52245308
09-04-2025 23:15:30.000 | 49748941 |  | 49.7489 | -5315935 | 15612863 | 18504683 | 99433937 | 49993427 | 414988098 | 0.000000 | 0.000000 | 44796547
09-04-2025 23:15:25.000 | 49767809 |  | 49.7678 | -5093280 | 15612282 | 18503693 | 99480392 | 50003269 | 345553650 | 0.000000 | 0.000000 | 37502804
09-04-2025 23:15:20.000 | 50255441 |  | 50.2554 | -5392275 | 15611271 | 18695920 | 99429291 | 50015911 | 276122223 | 0.000000 | 0.000000 | 30278194
09-04-2025 23:15:15.000 | 50466961 |  | 50.467 | -5440678 | 15609193 | 18779539 | 99423904 | 50017166 | 206131088 | 0.000000 | 0.000000 | 22792694
09-04-2025 23:15:10.000 | 49281602 |  | 49.2816 | -5427005 | 15611604 | 18339091 | 99399117 | 50042797 | 136415070 | 0.000000 | 0.000000 | 15307862
09-04-2025 23:15:05.000 | 49072141 |  | 49.0721 | -5442108 | 15612474 | 18261578 | 99390671 | 50048611 | 68116943 | 0.000000 | 0.000000 | 7734013
09-04-2025 23:15:00.000 | 49314359 |  | 49.3144 | -5735731 | 15612443 | 18362764 | 99330391 | 50058277 | 16143089 | 0.000000 | 0.000000 | 11099596
09-04-2025 23:14:55.000 | 49437348 |  | 49.4373 | -5638901 | 15610448 | 18406625 | 99355774 | 50045956 | 16074586 | 0.000000 | 0.000000 | 11021490
09-04-2025 23:14:50.000 | 48825930 |  | 48.8259 | -5579614 | 15612084 | 18177346 | 99353378 | 50050442 | 16005970 | 0.000000 | 0.000000 | 10942053
09-04-2025 23:14:45.000 | 48230648 |  | 48.2306 | -5585509 | 15611585 | 17959937 | 99336090 | 50069260 | 15938833 | 0.000000 | 0.000000 | 10865726
09-04-2025 23:14:40.000 | 47578266 |  | 47.5783 | -5549372 | 15614802 | 17715322 | 99326660 | 50068794 | 15872476 | 0.000000 | 0.000000 | 10787435
09-04-2025 23:14:35.000 | 48109520 |  | 48.1095 | -5324673 | 15611776 | 17904036 | 99393089 | 50054699 | 15806092 | 0.000000 | 0.000000 | 10711136
09-04-2025 23:14:30.000 | 48566207 |  | 48.5662 | -5397796 | 15610851 | 18076119 | 99388023 | 50039024 | 15738894 | 0.000000 | 0.000000 | 10636046
09-04-2025 23:14:25.000 | 48115254 |  | 48.1153 | -5519824 | 15610180 | 17915702 | 99348381 | 50050072 | 15671549 | 0.000000 | 0.000000 | 10560457
09-04-2025 23:14:20.000 | 46764406 |  | 46.7644 | -5543328 | 15612291 | 17418206 | 99304764 | 50062286 | 15605580 | 0.000000 | 0.000000 | 10485128
09-04-2025 23:14:15.000 | 46970676 |  | 46.9707 | -5311952 | 15617364 | 17479177 | 99366592 | 50042931 | 15540541 | 0.000000 | 0.000000 | 10408689
09-04-2025 23:14:10.000 | 47578520 |  | 47.5785 | -5205337 | 15614740 | 17700411 | 99406845 | 50029236 | 15475030 | 0.000000 | 0.000000 | 10336259
09-04-2025 23:14:05.000 | 48468852 |  | 48.4689 | -5168243 | 15614055 | 18027428 | 99436302 | 50019558 | 15408821 | 0.000000 | 0.000000 | 10263779
09-04-2025 23:14:00.000 | 48854148 |  | 48.8541 | -5230471 | 15612837 | 18172566 | 99431755 | 50000904 | 15341340 | 0.000000 | 0.000000 | 10190705
09-04-2025 23:13:55.000 | 49038914 |  | 49.0389 | -5236586 | 15612571 | 18240955 | 99434685 | 49997631 | 15273089 | 0.000000 | 0.000000 | 10117737
09-04-2025 23:13:50.000 | 49194707 |  | 49.1947 | -5254308 | 15612112 | 18299402 | 99434456 | 49999279 | 15204981 | 0.000000 | 0.000000 | 10044980
09-04-2025 23:13:45.000 | 49582027 |  | 49.582 | -5268828 | 15610423 | 18444476 | 99440125 | 49997162 | 15136636 | 0.000000 | 0.000000 | 997151672
09-04-2025 23:13:40.000 | 50057359 |  | 50.0574 | -5538023 | 15611498 | 18628525 | 99393570 | 50001217 | 15067451 | 0.000000 | 0.000000 | 989637329
09-04-2025 23:13:35.000 | 50139406 |  | 50.1394 | -5191765 | 15610485 | 18647352 | 99468178 | 50012814 | 14997947 | 0.000000 | 0.000000 | 982031616
09-04-2025 23:13:30.000 | 49014223 |  | 49.0142 | -5681531 | 15613188 | 18249364 | 99334869 | 50049084 | 14929471 | 0.000000 | 0.000000 | 974743774
09-04-2025 23:13:25.000 | 49749359 |  | 49.7494 | -5734088 | 15614309 | 18520649 | 99342308 | 50029858 | 14860947 | 0.000000 | 0.000000 | 966856201
09-04-2025 23:13:20.000 | 49577363 |  | 49.5774 | -5418640 | 15612680 | 18446267 | 99408012 | 50045578 | 14791369 | 0.000000 | 0.000000 | 959195374
09-04-2025 23:13:15.000 | 49312215 |  | 49.3122 | -5596741 | 15615520 | 18353352 | 99362091 | 50049553 | 14722902 | 0.000000 | 0.000000 | 951576660
09-04-2025 23:13:10.000 | 50569070 |  | 50.5691 | -5339785 | 15611499 | 18809078 | 99447113 | 50044373 | 14653575 | 0.000000 | 0.000000 | 943924927
09-04-2025 23:13:05.000 | 50638637 |  | 50.6386 | -5194745 | 15614064 | 18826260 | 99477936 | 50056023 | 14583249 | 0.000000 | 0.000000 | 936553284
09-04-2025 23:13:00.000 | 50895031 |  | 50.895 | -5138052 | 15617086 | 18915210 | 99494278 | 50070660 | 14512764 | 0.000000 | 0.000000 | 929392822
09-04-2025 23:12:55.000 | 52246727 |  | 52.2467 | -5176890 | 15617746 | 19412140 | 99512688 | 50066483 | 14441409 | 0.000000 | 0.000000 | 922246643
09-04-2025 23:12:50.000 | 53889277 |  | 53.8893 | -4832996 | 15618325 | 20004413 | 99600250 | 50054325 | 14367867 | 0.000000 | 0.000000 | 915163635
09-04-2025 23:12:45.000 | 55304621 |  | 55.3046 | -4856727 | 15621282 | 20522017 | 99616615 | 50041153 | 14292357 | 0.000000 | 0.000000 | 908469604
09-04-2025 23:12:40.000 | 58131738 |  | 58.1317 | -4303786 | 15616112 | 21554319 | 99727058 | 50003510 | 14213938 | 0.000000 | 0.000000 | 901949524
09-04-2025 23:12:35.000 | 59206313 |  | 59.2063 | -4131418 | 15618761 | 21942310 | 99757423 | 50000591 | 14132886 | 0.000000 | 0.000000 | 896034607
09-04-2025 23:12:30.000 | 61165863 |  | 61.1659 | -4410998 | 15618239 | 22672581 | 99740982 | 49978622 | 14049706 | 0.000000 | 0.000000 | 890161133
09-04-2025 23:12:25.000 | 63907316 |  | 63.9073 | -3982528 | 15614436 | 23678547 | 99806389 | 49932178 | 13963110 | 0.000000 | 0.000000 | 884208984
09-04-2025 23:12:20.000 | 64177172 |  | 64.1772 | -3984481 | 15614391 | 23778501 | 99807823 | 49943588 | 13874064 | 0.000000 | 0.000000 | 878660583
09-04-2025 23:12:15.000 | 64377516 |  | 64.3775 | -3753724 | 15616915 | 23843428 | 99830444 | 49957596 | 13784897 | 0.000000 | 0.000000 | 873263367
09-04-2025 23:12:10.000 | 65284141 |  | 65.2841 | -3926383 | 15615393 | 24184265 | 99819633 | 49956360 | 13695263 | 0.000000 | 0.000000 | 867902649
09-04-2025 23:12:05.000 | 66527250 |  | 66.5272 | -4017476 | 15613561 | 24647266 | 99818161 | 49946461 | 13603879 | 0.000000 | 0.000000 | 862425781
09-04-2025 23:12:00.000 | 67411273 |  | 67.4113 | -4168323 | 15615287 | 24974717 | 99809372 | 49940491 | 13510751 | 0.000000 | 0.000000 | 856757141
09-04-2025 23:11:55.000 | 67738898 |  | 67.7389 | -3787341 | 15611512 | 25093389 | 99844063 | 49943649 | 13416697 | 0.000000 | 0.000000 | 851284729
09-04-2025 23:11:50.000 | 67421219 |  | 67.4212 | -4110299 | 15613804 | 24979734 | 99814682 | 49967869 | 13322932 | 0.000000 | 0.000000 | 845848022
09-04-2025 23:11:45.000 | 68004406 |  | 68.0044 | -3976650 | 15613522 | 25192280 | 99829460 | 49969284 | 13228738 | 0.000000 | 0.000000 | 840230896
09-04-2025 23:11:40.000 | 68666242 |  | 68.6662 | -4488100 | 15612358 | 25449688 | 99787079 | 49973663 | 13133920 | 0.000000 | 0.000000 | 834546631
09-04-2025 23:11:35.000 | 68483398 |  | 68.4834 | -4032335 | 15609511 | 25376868 | 99827103 | 49963535 | 13038173 | 0.000000 | 0.000000 | 828666992
09-04-2025 23:11:30.000 | 67624523 |  | 67.6245 | -4257719 | 15610699 | 25063362 | 99802383 | 49990078 | 12943492 | 0.000000 | 0.000000 | 823013977
09-04-2025 23:11:25.000 | 66564063 |  | 66.5641 | -4311461 | 15613539 | 24667625 | 99790886 | 49999184 | 12850120 | 0.000000 | 0.000000 | 817068054
09-04-2025 23:11:20.000 | 65830898 |  | 65.8309 | -4414612 | 15613910 | 24399263 | 99775902 | 50004551 | 12757819 | 0.000000 | 0.000000 | 811235046
09-04-2025 23:11:15.000 | 66871711 |  | 66.8717 | -4240565 | 15613541 | 24779702 | 99799538 | 49986435 | 12665540 | 0.000000 | 0.000000 | 805114319
09-04-2025 23:11:10.000 | 66383320 |  | 66.3833 | -4038752 | 15614861 | 24593469 | 99815437 | 49992599 | 12572839 | 0.000000 | 0.000000 | 799386963
09-04-2025 23:11:05.000 | 65937773 |  | 65.9378 | -4028200 | 15617454 | 24425090 | 99813919 | 49997440 | 12480772 | 0.000000 | 0.000000 | 793921448
09-04-2025 23:11:00.000 | 67412430 |  | 67.4124 | -3938035 | 15616253 | 24968586 | 99829811 | 49971436 | 12388362 | 0.000000 | 0.000000 | 788309082
09-04-2025 23:10:55.000 | 68514992 |  | 68.515 | -3806917 | 15612939 | 25377397 | 99845993 | 49955761 | 12294122 | 0.000000 | 0.000000 | 782917175
09-04-2025 23:10:50.000 | 69081570 |  | 69.0816 | -3831083 | 15613104 | 25587158 | 99846581 | 49965214 | 12198514 | 0.000000 | 0.000000 | 777668152
09-04-2025 23:10:45.000 | 69876156 |  | 69.8762 | -3872883 | 15611009 | 25885859 | 99846756 | 49960327 | 12102070 | 0.000000 | 0.000000 | 772305664
09-04-2025 23:10:40.000 | 69776055 |  | 69.7761 | -4043925 | 15610636 | 25852051 | 99832481 | 49966133 | 12005064 | 0.000000 | 0.000000 | 766805847
09-04-2025 23:10:35.000 | 69156461 |  | 69.1565 | -4015702 | 15609329 | 25624919 | 99831841 | 49991016 | 11908195 | 0.000000 | 0.000000 | 761365479
09-04-2025 23:10:30.000 | 68721000 |  | 68.721 | -4129535 | 15608889 | 25467556 | 99819939 | 50007217 | 11812374 | 0.000000 | 0.000000 | 755774353
09-04-2025 23:10:25.000 | 68900211 |  | 68.9002 | -4248052 | 15610090 | 25533979 | 99810471 | 49995972 | 11716997 | 0.000000 | 0.000000 | 749807739
09-04-2025 23:10:20.000 | 68240938 |  | 68.2409 | -4281648 | 15606664 | 25296807 | 99803741 | 50010120 | 11621375 | 0.000000 | 0.000000 | 743983154
09-04-2025 23:10:15.000 | 67041727 |  | 67.0417 | -4450546 | 15609184 | 24854023 | 99780380 | 50033154 | 11527481 | 0.000000 | 0.000000 | 737949219
09-04-2025 23:10:10.000 | 65943813 |  | 65.9438 | -4580626 | 15614835 | 24443198 | 99759621 | 50039696 | 11434973 | 0.000000 | 0.000000 | 731659180
09-04-2025 23:10:05.000 | 65701219 |  | 65.7012 | -4278915 | 15613652 | 24348584 | 99788597 | 50032810 | 11343375 | 0.000000 | 0.000000 | 725558838
09-04-2025 23:10:00.000 | 65694406 |  | 65.6944 | -4328951 | 15618271 | 24339717 | 99783592 | 50027313 | 11252141 | 0.000000 | 0.000000 | 719604004
09-04-2025 23:09:55.000 | 67173969 |  | 67.174 | -4044898 | 15614078 | 24886248 | 99819199 | 50003246 | 11159788 | 0.000000 | 0.000000 | 713810059
09-04-2025 23:09:50.000 | 68042313 |  | 68.0423 | -4099934 | 15614350 | 25207380 | 99818954 | 49984684 | 11066022 | 0.000000 | 0.000000 | 708087769
09-04-2025 23:09:45.000 | 68636367 |  | 68.6364 | -3871997 | 15610959 | 25427378 | 99841255 | 49966743 | 10970990 | 0.000000 | 0.000000 | 702566162
09-04-2025 23:09:40.000 | 68569547 |  | 68.5695 | -4183004 | 15609527 | 25411682 | 99814445 | 49974274 | 10875742 | 0.000000 | 0.000000 | 697067566
09-04-2025 23:09:35.000 | 68842266 |  | 68.8423 | -3938059 | 15607352 | 25510396 | 99836784 | 49962482 | 10780466 | 0.000000 | 0.000000 | 691281006
09-04-2025 23:09:30.000 | 67111406 |  | 67.1114 | -4203793 | 15610169 | 24872603 | 99804390 | 49992477 | 10685872 | 0.000000 | 0.000000 | 685723267
09-04-2025 23:09:25.000 | 66519930 |  | 66.5199 | -4110435 | 15612586 | 24648557 | 99809631 | 49999947 | 10592853 | 0.000000 | 0.000000 | 679890381
09-04-2025 23:09:20.000 | 66004516 |  | 66.0045 | -4247904 | 15616604 | 24455618 | 99793549 | 50003101 | 10500946 | 0.000000 | 0.000000 | 674105957
09-04-2025 23:09:15.000 | 66543320 |  | 66.5433 | -4216497 | 15614370 | 24657158 | 99799850 | 49981331 | 10408833 | 0.000000 | 0.000000 | 668326904
09-04-2025 23:09:10.000 | 67912516 |  | 67.9125 | -3916582 | 15611771 | 25159424 | 99834114 | 49950809 | 10315503 | 0.000000 | 0.000000 | 662607422
09-04-2025 23:09:05.000 | 67377648 |  | 67.3776 | -4036797 | 15611098 | 24965720 | 99821007 | 49962143 | 10221474 | 0.000000 | 0.000000 | 657183716
09-04-2025 23:09:00.000 | 67172859 |  | 67.1729 | -4046438 | 15613072 | 24887280 | 99819054 | 49964535 | 10127922 | 0.000000 | 0.000000 | 651514526
09-04-2025 23:08:55.000 | 67298336 |  | 67.2983 | -4017653 | 15612692 | 24933645 | 99822273 | 49972424 | 10034537 | 0.000000 | 0.000000 | 645928955
09-04-2025 23:08:50.000 | 67169672 |  | 67.1697 | -4274809 | 15613885 | 24890103 | 99798096 | 49975330 | 99411611 | 0.000000 | 0.000000 | 640245239
09-04-2025 23:08:45.000 | 67722117 |  | 67.7221 | -4167440 | 15614007 | 25091685 | 99811195 | 49958664 | 98475293 | 0.000000 | 0.000000 | 634392944
09-04-2025 23:08:40.000 | 67835258 |  | 67.8353 | -3937628 | 15611374 | 25132136 | 99831955 | 49946159 | 97532803 | 0.000000 | 0.000000 | 628685425
09-04-2025 23:08:35.000 | 67329508 |  | 67.3295 | -3952496 | 15613817 | 24942029 | 99828140 | 49969109 | 96592900 | 0.000000 | 0.000000 | 623253052
09-04-2025 23:08:30.000 | 68046367 |  | 68.0464 | -4186825 | 15613738 | 25212043 | 99811241 | 49958992 | 95654980 | 0.000000 | 0.000000 | 617661743
09-04-2025 23:08:25.000 | 68932930 |  | 68.9329 | -4025546 | 15610673 | 25540681 | 99829918 | 49941914 | 94703008 | 0.000000 | 0.000000 | 611830688
09-04-2025 23:08:20.000 | 67914570 |  | 67.9146 | -4137931 | 15610813 | 25166453 | 99814903 | 49958046 | 93753447 | 0.000000 | 0.000000 | 606228149
09-04-2025 23:08:15.000 | 67589133 |  | 67.5891 | -4405340 | 15613229 | 25049517 | 99788261 | 49958664 | 92810596 | 0.000000 | 0.000000 | 600275208
09-04-2025 23:08:10.000 | 68215789 |  | 68.2158 | -4431688 | 15611015 | 25284978 | 99789635 | 49956985 | 91866445 | 0.000000 | 0.000000 | 594227417
09-04-2025 23:08:05.000 | 67373984 |  | 67.374 | -4289742 | 15610518 | 24971653 | 99797920 | 49973747 | 90924277 | 0.000000 | 0.000000 | 588200317
09-04-2025 23:08:00.000 | 66654461 |  | 66.6545 | -4559717 | 15612279 | 24709143 | 99766830 | 49990532 | 89994883 | 0.000000 | 0.000000 | 582074585
09-04-2025 23:07:55.000 | 67007766 |  | 67.0078 | -4529620 | 15611897 | 24840457 | 99772301 | 49971916 | 89065869 | 0.000000 | 0.000000 | 575663757
09-04-2025 23:07:50.000 | 66389844 |  | 66.3898 | -4415499 | 15612946 | 24607148 | 99779564 | 49985714 | 88136709 | 0.000000 | 0.000000 | 569449585
09-04-2025 23:07:45.000 | 65899273 |  | 65.8993 | -4366878 | 15616795 | 24419395 | 99781158 | 49982731 | 87219346 | 0.000000 | 0.000000 | 563355530
09-04-2025 23:07:40.000 | 67254930 |  | 67.2549 | -4355923 | 15615922 | 24919788 | 99790916 | 49955284 | 86296934 | 0.000000 | 0.000000 | 557232544
09-04-2025 23:07:35.000 | 68268977 |  | 68.269 | -4391670 | 15614648 | 25298262 | 99793732 | 49937557 | 85355840 | 0.000000 | 0.000000 | 551213928
09-04-2025 23:07:30.000 | 69062406 |  | 69.0624 | -4271421 | 15610299 | 25594180 | 99809280 | 49929958 | 84400215 | 0.000000 | 0.000000 | 545234314
09-04-2025 23:07:25.000 | 68898859 |  | 68.8989 | -4080782 | 15611147 | 25528220 | 99825058 | 49923943 | 83443799 | 0.000000 | 0.000000 | 539303589
09-04-2025 23:07:20.000 | 68409492 |  | 68.4095 | -4371984 | 15611805 | 25352852 | 99796402 | 49955219 | 82491436 | 0.000000 | 0.000000 | 533578369
09-04-2025 23:07:15.000 | 69254516 |  | 69.2545 | -4716317 | 15611577 | 25673491 | 99768913 | 49953869 | 81537754 | 0.000000 | 0.000000 | 527320557
09-04-2025 23:07:10.000 | 69561695 |  | 69.5617 | -4526043 | 15606606 | 25790256 | 99788994 | 49942307 | 80572891 | 0.000000 | 0.000000 | 520873474
09-04-2025 23:07:05.000 | 67727250 |  | 67.7272 | -4662157 | 15606367 | 25118665 | 99763908 | 49979218 | 79612051 | 0.000000 | 0.000000 | 514540161
09-04-2025 23:07:00.000 | 65929883 |  | 65.9299 | -4615138 | 15610806 | 24446069 | 99755890 | 50015335 | 78682690 | 0.000000 | 0.000000 | 508019623
09-04-2025 23:06:55.000 | 64969609 |  | 64.9696 | -4884290 | 15612484 | 24096357 | 99718605 | 50023624 | 77774702 | 0.000000 | 0.000000 | 501433289
09-04-2025 23:06:50.000 | 66403797 |  | 66.4038 | -4591516 | 15612463 | 24617549 | 99761803 | 49977226 | 76866870 | 0.000000 | 0.000000 | 494490906
09-04-2025 23:06:45.000 | 65559891 |  | 65.5599 | -4569832 | 15614454 | 24302224 | 99757942 | 49986057 | 75951128 | 0.000000 | 0.000000 | 488209503
09-04-2025 23:06:40.000 | 65881523 |  | 65.8815 | -4475295 | 15614594 | 24418567 | 99770073 | 49963173 | 75040479 | 0.000000 | 0.000000 | 481831177
09-04-2025 23:06:35.000 | 65978047 |  | 65.978 | -4355215 | 15613035 | 24453728 | 99782845 | 49954937 | 74125249 | 0.000000 | 0.000000 | 475788300
09-04-2025 23:06:30.000 | 66706547 |  | 66.7065 | -4398174 | 15613463 | 24722549 | 99783348 | 49935429 | 73207329 | 0.000000 | 0.000000 | 469668396
09-04-2025 23:06:25.000 | 66797047 |  | 66.797 | -4126198 | 15613711 | 24749673 | 99809753 | 49921268 | 72278628 | 0.000000 | 0.000000 | 463706390
09-04-2025 23:06:20.000 | 66588344 |  | 66.5883 | -4227354 | 15613462 | 24674858 | 99799088 | 49933876 | 71351470 | 0.000000 | 0.000000 | 457973541
09-04-2025 23:06:15.000 | 67279430 |  | 67.2794 | -4286344 | 15613473 | 24931858 | 99797668 | 49922375 | 70421191 | 0.000000 | 0.000000 | 451956543
09-04-2025 23:06:10.000 | 66843273 |  | 66.8433 | -4048574 | 15610915 | 24769177 | 99817078 | 49921230 | 69488047 | 0.000000 | 0.000000 | 446206238
09-04-2025 23:06:05.000 | 66111164 |  | 66.1112 | -4034944 | 15613378 | 24494568 | 99814270 | 49930836 | 68562075 | 0.000000 | 0.000000 | 440690735
09-04-2025 23:06:00.000 | 66797563 |  | 66.7976 | -4034378 | 15612715 | 24748796 | 99818108 | 49915237 | 67640073 | 0.000000 | 0.000000 | 435040588
09-04-2025 23:05:55.000 | 67390078 |  | 67.3901 | -4325062 | 15611320 | 24976482 | 99794685 | 49910320 | 66710659 | 0.000000 | 0.000000 | 429283447
09-04-2025 23:05:50.000 | 67817320 |  | 67.8173 | -4124507 | 15612689 | 25127563 | 99815567 | 49894440 | 65770786 | 0.000000 | 0.000000 | 423236298
09-04-2025 23:05:45.000 | 67530156 |  | 67.5302 | -4437838 | 15611467 | 25030630 | 99784767 | 49905361 | 64831606 | 0.000000 | 0.000000 | 417384033
09-04-2025 23:05:40.000 | 67871273 |  | 67.8713 | -4344165 | 15610438 | 25156309 | 99795792 | 49899342 | 63890620 | 0.000000 | 0.000000 | 411194794
09-04-2025 23:05:35.000 | 67194508 |  | 67.1945 | -4421516 | 15612307 | 24905183 | 99784210 | 49900608 | 62953843 | 0.000000 | 0.000000 | 405016571
09-04-2025 23:05:30.000 | 66264422 |  | 66.2644 | -4498603 | 15612755 | 24563098 | 99770348 | 49926147 | 62022998 | 0.000000 | 0.000000 | 399012360
09-04-2025 23:05:25.000 | 66671055 |  | 66.6711 | -4839093 | 15613244 | 24721431 | 99737633 | 49914936 | 61103379 | 0.000000 | 0.000000 | 392601379
09-04-2025 23:05:20.000 | 67447539 |  | 67.4475 | -4491121 | 15610112 | 25003750 | 99779045 | 49895916 | 60170591 | 0.000000 | 0.000000 | 386018188
09-04-2025 23:05:15.000 | 66421406 |  | 66.4214 | -4644078 | 15611338 | 24626675 | 99756462 | 49916519 | 59239756 | 0.000000 | 0.000000 | 379760254
09-04-2025 23:05:10.000 | 67288609 |  | 67.2886 | -4616884 | 15612864 | 24943726 | 99765442 | 49887951 | 58317651 | 0.000000 | 0.000000 | 373080261
09-04-2025 23:05:05.000 | 67174992 |  | 67.175 | -4670274 | 15609950 | 24909019 | 99759193 | 49883900 | 57384707 | 0.000000 | 0.000000 | 366687622
09-04-2025 23:05:00.000 | 67008648 |  | 67.0086 | -4430626 | 15612502 | 24836624 | 99782120 | 49892513 | 56453433 | 0.000000 | 0.000000 | 360243988
09-04-2025 23:04:55.000 | 66316227 |  | 66.3162 | -4470657 | 15615340 | 24577661 | 99773537 | 49904499 | 55529990 | 0.000000 | 0.000000 | 354075104
09-04-2025 23:04:50.000 | 66524695 |  | 66.5247 | -4422775 | 15615892 | 24652668 | 99779732 | 49904678 | 54606914 | 0.000000 | 0.000000 | 347912079
09-04-2025 23:04:45.000 | 67064359 |  | 67.0644 | -4310451 | 15614271 | 24851323 | 99794083 | 49885952 | 53681479 | 0.000000 | 0.000000 | 341864502
09-04-2025 23:04:40.000 | 68020211 |  | 68.0202 | -4512002 | 15613694 | 25209739 | 99780716 | 49869854 | 52742441 | 0.000000 | 0.000000 | 335830536
09-04-2025 23:04:35.000 | 68947305 |  | 68.9473 | -4355880 | 15610320 | 25553289 | 99801025 | 49843788 | 51792285 | 0.000000 | 0.000000 | 329629578
09-04-2025 23:04:30.000 | 68464656 |  | 68.4647 | -4204078 | 15609620 | 25373062 | 99812004 | 49851109 | 50838071 | 0.000000 | 0.000000 | 323597015
09-04-2025 23:04:25.000 | 66933594 |  | 66.9336 | -4364116 | 15613282 | 24805928 | 99788116 | 49885281 | 49894019 | 0.000000 | 0.000000 | 317707458
09-04-2025 23:04:20.000 | 67147313 |  | 67.1473 | -4229902 | 15612517 | 24883394 | 99802177 | 49879684 | 48963716 | 0.000000 | 0.000000 | 311672668
09-04-2025 23:04:15.000 | 67303539 |  | 67.3035 | -4176610 | 15611715 | 24940667 | 99808006 | 49875301 | 48030908 | 0.000000 | 0.000000 | 305701630
09-04-2025 23:04:10.000 | 67578305 |  | 67.5783 | -4112400 | 15614534 | 25035908 | 99815353 | 49877148 | 47094673 | 0.000000 | 0.000000 | 299853119
09-04-2025 23:04:05.000 | 68165789 |  | 68.1658 | -4256173 | 15613264 | 25257800 | 99805641 | 49862926 | 46154888 | 0.000000 | 0.000000 | 294066101
09-04-2025 23:04:00.000 | 68247820 |  | 68.2478 | -3987200 | 15610975 | 25286104 | 99829781 | 49862484 | 45205591 | 0.000000 | 0.000000 | 288351318
09-04-2025 23:03:55.000 | 68294211 |  | 68.2942 | -4167313 | 15612856 | 25304299 | 99814346 | 49858696 | 44257427 | 0.000000 | 0.000000 | 282628723
09-04-2025 23:03:50.000 | 68516852 |  | 68.5169 | -4173772 | 15609218 | 25392476 | 99814980 | 49856716 | 43307593 | 0.000000 | 0.000000 | 276883484
09-04-2025 23:03:45.000 | 67377328 |  | 67.3773 | -4223006 | 15610447 | 24970713 | 99804153 | 49877380 | 42360288 | 0.000000 | 0.000000 | 271114807
09-04-2025 23:03:40.000 | 66259078 |  | 66.2591 | -4217331 | 15616348 | 24549111 | 99798050 | 49904762 | 41428843 | 0.000000 | 0.000000 | 265342712
09-04-2025 23:03:35.000 | 66560617 |  | 66.5606 | -4116906 | 15614408 | 24661421 | 99809265 | 49894394 | 40510010 | 0.000000 | 0.000000 | 259513397
09-04-2025 23:03:30.000 | 67965109 |  | 67.9651 | -4265263 | 15614489 | 25182100 | 99803658 | 49869896 | 39578696 | 0.000000 | 0.000000 | 253719055
09-04-2025 23:03:25.000 | 69255766 |  | 69.2558 | -4214114 | 15611633 | 25662024 | 99815384 | 49851307 | 38628579 | 0.000000 | 0.000000 | 247755219
09-04-2025 23:03:20.000 | 68446719 |  | 68.4467 | -4113628 | 15607420 | 25368081 | 99819885 | 49860828 | 37668677 | 0.000000 | 0.000000 | 242076553
09-04-2025 23:03:15.000 | 67305898 |  | 67.3059 | -4049155 | 15612846 | 24936650 | 99819527 | 49886917 | 36722190 | 0.000000 | 0.000000 | 236343063
09-04-2025 23:03:10.000 | 67109797 |  | 67.1098 | -4276074 | 15614059 | 24868186 | 99797623 | 49898712 | 35790374 | 0.000000 | 0.000000 | 230674316
09-04-2025 23:03:05.000 | 67618328 |  | 67.6183 | -3865517 | 15612889 | 25048464 | 99836998 | 49882568 | 34852668 | 0.000000 | 0.000000 | 225015823
09-04-2025 23:03:00.000 | 67936672 |  | 67.9367 | -4189679 | 15615063 | 25170181 | 99810379 | 49885174 | 33912295 | 0.000000 | 0.000000 | 219511093
09-04-2025 23:02:55.000 | 69097797 |  | 69.0978 | -4494240 | 15609664 | 25613447 | 99789146 | 49867443 | 32961074 | 0.000000 | 0.000000 | 213657455
09-04-2025 23:02:50.000 | 69627055 |  | 69.6271 | -4604494 | 15608182 | 25813577 | 99782051 | 49865593 | 31996108 | 0.000000 | 0.000000 | 207300262
09-04-2025 23:02:45.000 | 68354203 |  | 68.3542 | -4379298 | 15607237 | 25340439 | 99795395 | 49892986 | 31037744 | 0.000000 | 0.000000 | 201010696
09-04-2025 23:02:40.000 | 66949984 |  | 66.95 | -4637689 | 15611562 | 24821604 | 99760941 | 49917393 | 30097222 | 0.000000 | 0.000000 | 194667969
09-04-2025 23:02:35.000 | 65912156 |  | 65.9122 | -4587974 | 15613771 | 24433594 | 99758614 | 49925438 | 29174285 | 0.000000 | 0.000000 | 188343430
09-04-2025 23:02:30.000 | 66092383 |  | 66.0924 | -5120301 | 15613479 | 24515261 | 99701248 | 49924389 | 28260034 | 0.000000 | 0.000000 | 181799850
09-04-2025 23:02:25.000 | 66406008 |  | 66.406 | -4635440 | 15610505 | 24622546 | 99757256 | 49899006 | 27335498 | 0.000000 | 0.000000 | 175030655
09-04-2025 23:02:20.000 | 65317063 |  | 65.3171 | -4889009 | 15615116 | 24220300 | 99721039 | 49920914 | 26417786 | 0.000000 | 0.000000 | 168667526
09-04-2025 23:02:15.000 | 66242883 |  | 66.2429 | -4340756 | 15610568 | 24555400 | 99785995 | 49884701 | 25505300 | 0.000000 | 0.000000 | 161945938
09-04-2025 23:02:10.000 | 66899141 |  | 66.8991 | -4686841 | 15612509 | 24802466 | 99755493 | 49882759 | 24583872 | 0.000000 | 0.000000 | 155658127
09-04-2025 23:02:05.000 | 66997922 |  | 66.9979 | -4383561 | 15611165 | 24833689 | 99786644 | 49866482 | 23653787 | 0.000000 | 0.000000 | 149318375
09-04-2025 23:02:00.000 | 66099719 |  | 66.0997 | -4260809 | 15615315 | 24493193 | 99792885 | 49877438 | 22727881 | 0.000000 | 0.000000 | 143295380
09-04-2025 23:01:55.000 | 66278445 |  | 66.2784 | -4163729 | 15613638 | 24558984 | 99803253 | 49875187 | 21810300 | 0.000000 | 0.000000 | 137524292
09-04-2025 23:01:50.000 | 66900211 |  | 66.9002 | -4149356 | 15616679 | 24783806 | 99808212 | 49860676 | 20886294 | 0.000000 | 0.000000 | 131824753
09-04-2025 23:01:45.000 | 67829688 |  | 67.8297 | -4059425 | 15614781 | 25127568 | 99821396 | 49839500 | 19949088 | 0.000000 | 0.000000 | 126140114
09-04-2025 23:01:40.000 | 68983320 |  | 68.9833 | -4236178 | 15612170 | 25561746 | 99811981 | 49826466 | 19000343 | 0.000000 | 0.000000 | 120408401
09-04-2025 23:01:35.000 | 69624492 |  | 69.6245 | -4138125 | 15609727 | 25799626 | 99823845 | 49825500 | 18039342 | 0.000000 | 0.000000 | 114528885
09-04-2025 23:01:30.000 | 68981102 |  | 68.9811 | -4378934 | 15608447 | 25569763 | 99799118 | 49850510 | 17075867 | 0.000000 | 0.000000 | 108729118
09-04-2025 23:01:25.000 | 68101203 |  | 68.1012 | -4350010 | 15611637 | 25239099 | 99796616 | 49863010 | 16123763 | 0.000000 | 0.000000 | 102730347
09-04-2025 23:01:20.000 | 67850125 |  | 67.8501 | -4210891 | 15612096 | 25142568 | 99807976 | 49867130 | 15177997 | 0.000000 | 0.000000 | 96708313
09-04-2025 23:01:15.000 | 67459844 |  | 67.4598 | -4369892 | 15613644 | 25000027 | 99790848 | 49883472 | 14239475 | 0.000000 | 0.000000 | 90770805
09-04-2025 23:01:10.000 | 67836297 |  | 67.8363 | -4409144 | 15613868 | 25139121 | 99789436 | 49869724 | 13299882 | 0.000000 | 0.000000 | 84682838
09-04-2025 23:01:05.000 | 68457945 |  | 68.4579 | -4388810 | 15612688 | 25369985 | 99795128 | 49857338 | 12350021 | 0.000000 | 0.000000 | 78611351
09-04-2025 23:01:00.000 | 68577797 |  | 68.5778 | -4507101 | 15612087 | 25417854 | 99784721 | 49860111 | 11399114 | 0.000000 | 0.000000 | 72440659
09-04-2025 23:00:55.000 | 68066289 |  | 68.0663 | -4248400 | 15611242 | 25224541 | 99805779 | 49865753 | 10448340 | 0.000000 | 0.000000 | 66390068
09-04-2025 23:00:50.000 | 67594977 |  | 67.595 | -4265309 | 15613245 | 25047783 | 99801506 | 49875957 | 950717529 | 0.000000 | 0.000000 | 60418709
09-04-2025 23:00:45.000 | 67657688 |  | 67.6577 | -4291336 | 15615097 | 25069041 | 99799454 | 49877621 | 856860718 | 0.000000 | 0.000000 | 54449558
09-04-2025 23:00:40.000 | 67341578 |  | 67.3416 | -4174613 | 15614371 | 24950503 | 99808403 | 49881348 | 762680847 | 0.000000 | 0.000000 | 48633911
09-04-2025 23:00:35.000 | 68393016 |  | 68.393 | -4401450 | 15615969 | 25340974 | 99793564 | 49872925 | 668801025 | 0.000000 | 0.000000 | 42614571
09-04-2025 23:00:30.000 | 69418766 |  | 69.4188 | -4269071 | 15609243 | 25727295 | 99811440 | 49860882 | 572943848 | 0.000000 | 0.000000 | 36657364
09-04-2025 23:00:25.000 | 69425453 |  | 69.4255 | -4174422 | 15612032 | 25723611 | 99819717 | 49873863 | 476479370 | 0.000000 | 0.000000 | 30664751
09-04-2025 23:00:20.000 | 68718844 |  | 68.7188 | -4207768 | 15610327 | 25465913 | 99813057 | 49893028 | 380707428 | 0.000000 | 0.000000 | 24843946
09-04-2025 23:00:15.000 | 68370102 |  | 68.3701 | -4404575 | 15613424 | 25336824 | 99793129 | 49901680 | 285709595 | 0.000000 | 0.000000 | 18852743
09-04-2025 23:00:10.000 | 68907805 |  | 68.9078 | -4605961 | 15611279 | 25543787 | 99777351 | 49911625 | 190580963 | 0.000000 | 0.000000 | 12650860
09-04-2025 23:00:05.000 | 68478664 |  | 68.4787 | -4521799 | 15611202 | 25383928 | 99782700 | 49917614 | 94823189 | 0.000000 | 0.000000 | 6414055
09-04-2025 23:00:00.000 | 68188703 |  | 68.1887 | -4729831 | 15612982 | 25278479 | 99760300 | 49925865 | 16931924 | 0.000000 | 0.000000 | 12199154
09-04-2025 22:59:55.000 | 69149734 |  | 69.1497 | -4846156 | 15612069 | 25637258 | 99755325 | 49924675 | 16836760 | 0.000000 | 0.000000 | 12132074
09-04-2025 22:59:50.000 | 69092664 |  | 69.0927 | -4815212 | 15609045 | 25620669 | 99758034 | 49921627 | 16740678 | 0.000000 | 0.000000 | 12064468
09-04-2025 22:59:45.000 | 68332289 |  | 68.3323 | -4712573 | 15608834 | 25338459 | 99763031 | 49937817 | 16645254 | 0.000000 | 0.000000 | 11997319
09-04-2025 22:59:40.000 | 67569336 |  | 67.5693 | -5058475 | 15610961 | 25061895 | 99720947 | 49963696 | 16550930 | 0.000000 | 0.000000 | 11929635
09-04-2025 22:59:35.000 | 67175703 |  | 67.1757 | -5109954 | 15610232 | 24919485 | 99711929 | 49960049 | 16457311 | 0.000000 | 0.000000 | 11859137
09-04-2025 22:59:30.000 | 66420898 |  | 66.4209 | -4863101 | 15608777 | 24636760 | 99733040 | 49966194 | 16364311 | 0.000000 | 0.000000 | 11790210
09-04-2025 22:59:25.000 | 64967871 |  | 64.9679 | -4907771 | 15612648 | 24096016 | 99715889 | 49984138 | 16273174 | 0.000000 | 0.000000 | 11722352
09-04-2025 22:59:20.000 | 65372379 |  | 65.3724 | -4675471 | 15612589 | 24239033 | 99745216 | 49958954 | 16182722 | 0.000000 | 0.000000 | 11654172
09-04-2025 22:59:15.000 | 64651949 |  | 64.6519 | -4547858 | 15615008 | 23966011 | 99753502 | 49965885 | 16092228 | 0.000000 | 0.000000 | 11590143
09-04-2025 22:59:10.000 | 65009070 |  | 65.0091 | -4412459 | 15619681 | 24087212 | 99770447 | 49961231 | 16002361 | 0.000000 | 0.000000 | 11526969
09-04-2025 22:59:05.000 | 66578258 |  | 66.5783 | -4615317 | 15619498 | 24672036 | 99760590 | 49926804 | 15911452 | 0.000000 | 0.000000 | 11464734
09-04-2025 22:59:00.000 | 69883539 |  | 69.8835 | -3944040 | 15609051 | 25892334 | 99841118 | 49849575 | 15817383 | 0.000000 | 0.000000 | 11400901
09-04-2025 22:58:55.000 | 69251695 |  | 69.2517 | -4184629 | 15608241 | 25665649 | 99817932 | 49875198 | 15720537 | 0.000000 | 0.000000 | 11345487
09-04-2025 22:58:50.000 | 68675539 |  | 68.6755 | -4121685 | 15611173 | 25447021 | 99820381 | 49890934 | 15624839 | 0.000000 | 0.000000 | 11286523
09-04-2025 22:58:45.000 | 67979141 |  | 67.9791 | -4289993 | 15613715 | 25189395 | 99801468 | 49902744 | 15530162 | 0.000000 | 0.000000 | 11227614
09-04-2025 22:58:40.000 | 68351539 |  | 68.3515 | -4330394 | 15612197 | 25330964 | 99799911 | 49899811 | 15435529 | 0.000000 | 0.000000 | 11167588
09-04-2025 22:58:35.000 | 67937820 |  | 67.9378 | -4262116 | 15611246 | 25177644 | 99803795 | 49901081 | 15341003 | 0.000000 | 0.000000 | 11107136
09-04-2025 22:58:30.000 | 67719938 |  | 67.7199 | -4349962 | 15613237 | 25096104 | 99794334 | 49909077 | 15246646 | 0.000000 | 0.000000 | 11047388
09-04-2025 22:58:25.000 | 67720398 |  | 67.7204 | -4518356 | 15612882 | 25100725 | 99778160 | 49910786 | 15152526 | 0.000000 | 0.000000 | 10987037
09-04-2025 22:58:20.000 | 68767109 |  | 68.7671 | -4615439 | 15612782 | 25488943 | 99775520 | 49884914 | 15057893 | 0.000000 | 0.000000 | 10923391
09-04-2025 22:58:15.000 | 68253656 |  | 68.2537 | -4415867 | 15608016 | 25302827 | 99791367 | 49891102 | 14962349 | 0.000000 | 0.000000 | 10862423
09-04-2025 22:58:10.000 | 67230297 |  | 67.2303 | -4544419 | 15611024 | 24923130 | 99772324 | 49914185 | 14868181 | 0.000000 | 0.000000 | 10800380
09-04-2025 22:58:05.000 | 66094656 |  | 66.0947 | -4471688 | 15613035 | 24499177 | 99771919 | 49924904 | 14775442 | 0.000000 | 0.000000 | 10738988
09-04-2025 22:58:00.000 | 66742297 |  | 66.7423 | -4402789 | 15614146 | 24734739 | 99783127 | 49910038 | 14683387 | 0.000000 | 0.000000 | 10675959
09-04-2025 22:57:55.000 | 66155305 |  | 66.1553 | -4267732 | 15613549 | 24516460 | 99792564 | 49918865 | 14590798 | 0.000000 | 0.000000 | 10616964
09-04-2025 22:57:50.000 | 67395484 |  | 67.3955 | -4355082 | 15614946 | 24973831 | 99791862 | 49890903 | 14498692 | 0.000000 | 0.000000 | 10555837
09-04-2025 22:57:45.000 | 67904625 |  | 67.9046 | -4349403 | 15613045 | 25164236 | 99795502 | 49874683 | 14404688 | 0.000000 | 0.000000 | 10496362
09-04-2025 22:57:40.000 | 68502250 |  | 68.5023 | -4197341 | 15613951 | 25379639 | 99812805 | 49865433 | 14309880 | 0.000000 | 0.000000 | 10436718
09-04-2025 22:57:35.000 | 68501000 |  | 68.501 | -4036349 | 15613770 | 25376218 | 99826851 | 49873135 | 14214961 | 0.000000 | 0.000000 | 10379818
09-04-2025 22:57:30.000 | 68822578 |  | 68.8226 | -4135781 | 15613937 | 25497158 | 99819923 | 49873257 | 14119820 | 0.000000 | 0.000000 | 10322882
09-04-2025 22:57:25.000 | 69631406 |  | 69.6314 | -4078456 | 15613102 | 25795256 | 99828903 | 49873882 | 14023782 | 0.000000 | 0.000000 | 10265388
09-04-2025 22:57:20.000 | 70191688 |  | 70.1917 | -4333324 | 15609116 | 26014377 | 99809982 | 49876545 | 13926809 | 0.000000 | 0.000000 | 10208011
09-04-2025 22:57:15.000 | 70930500 |  | 70.9305 | -4599115 | 15609336 | 26293638 | 99790451 | 49870804 | 13828876 | 0.000000 | 0.000000 | 10145856
09-04-2025 22:57:10.000 | 71060656 |  | 71.0607 | -4520091 | 15603413 | 26349102 | 99798309 | 49873726 | 13730323 | 0.000000 | 0.000000 | 10081719
09-04-2025 22:57:05.000 | 68919203 |  | 68.9192 | -4678254 | 15602168 | 25564863 | 99770409 | 49919739 | 13632642 | 0.000000 | 0.000000 | 10017495
09-04-2025 22:57:00.000 | 66189297 |  | 66.1893 | -4681157 | 15608780 | 24546306 | 99750839 | 49968159 | 13538640 | 0.000000 | 0.000000 | 995173401
09-04-2025 22:56:55.000 | 65452238 |  | 65.4522 | -4872836 | 15615044 | 24269766 | 99724014 | 49973583 | 13447594 | 0.000000 | 0.000000 | 988394897
09-04-2025 22:56:50.000 | 65773078 |  | 65.7731 | -4651363 | 15614804 | 24383220 | 99750877 | 49956451 | 13356490 | 0.000000 | 0.000000 | 981666626
09-04-2025 22:56:45.000 | 66758008 |  | 66.758 | -4439383 | 15614733 | 24740681 | 99779617 | 49950470 | 13264479 | 0.000000 | 0.000000 | 975251343
09-04-2025 22:56:40.000 | 67355805 |  | 67.3558 | -4779439 | 15615381 | 24968982 | 99749191 | 49932945 | 13171479 | 0.000000 | 0.000000 | 968884094
09-04-2025 22:56:35.000 | 69339828 |  | 69.3398 | -4811516 | 15611515 | 25707261 | 99760117 | 49902863 | 13076712 | 0.000000 | 0.000000 | 962221985
09-04-2025 22:56:30.000 | 69417383 |  | 69.4174 | -4539703 | 15607525 | 25736345 | 99786842 | 49908813 | 12980039 | 0.000000 | 0.000000 | 955837463
09-04-2025 22:56:25.000 | 68850992 |  | 68.851 | -4666983 | 15607167 | 25530994 | 99771057 | 49924446 | 12884111 | 0.000000 | 0.000000 | 949239014
09-04-2025 22:56:20.000 | 68193336 |  | 68.1933 | -4734475 | 15608857 | 25286951 | 99759857 | 49935722 | 12788988 | 0.000000 | 0.000000 | 942599792
09-04-2025 22:56:15.000 | 66668719 |  | 66.6687 | -4826825 | 15613223 | 24721057 | 99738937 | 49957439 | 12694798 | 0.000000 | 0.000000 | 936030334
09-04-2025 22:56:10.000 | 66821680 |  | 66.8217 | -4772290 | 15614141 | 24773005 | 99745941 | 49965813 | 12601984 | 0.000000 | 0.000000 | 929414734
09-04-2025 22:56:05.000 | 67153031 |  | 67.153 | -4550253 | 15612849 | 24892161 | 99771217 | 49965740 | 12509040 | 0.000000 | 0.000000 | 923011719
09-04-2025 22:56:00.000 | 68340141 |  | 68.3401 | -4629750 | 15611865 | 25334053 | 99771317 | 49944412 | 12415718 | 0.000000 | 0.000000 | 916329712
09-04-2025 22:55:55.000 | 68388289 |  | 68.3883 | -4892124 | 15612763 | 25356401 | 99745117 | 49942432 | 12320521 | 0.000000 | 0.000000 | 909845276
09-04-2025 22:55:50.000 | 68903125 |  | 68.9031 | -4695892 | 15611524 | 25543689 | 99768570 | 49921509 | 12225224 | 0.000000 | 0.000000 | 903058411
09-04-2025 22:55:45.000 | 69047625 |  | 69.0476 | -4780402 | 15608942 | 25603137 | 99761192 | 49926125 | 12129491 | 0.000000 | 0.000000 | 896558289
09-04-2025 22:55:40.000 | 68416531 |  | 68.4165 | -4758735 | 15606873 | 25373530 | 99758980 | 49928303 | 12033996 | 0.000000 | 0.000000 | 889921631
09-04-2025 22:55:35.000 | 66976352 |  | 66.9764 | -4868551 | 15610411 | 24839399 | 99736847 | 49954685 | 11939956 | 0.000000 | 0.000000 | 883149841
09-04-2025 22:55:30.000 | 65979297 |  | 65.9793 | -4949431 | 15615238 | 24466099 | 99719818 | 49970474 | 11847668 | 0.000000 | 0.000000 | 876408081
09-04-2025 22:55:25.000 | 65733250 |  | 65.7332 | -4877855 | 15618891 | 24367485 | 99725800 | 49967415 | 11756173 | 0.000000 | 0.000000 | 869673340
09-04-2025 22:55:20.000 | 67573250 |  | 67.5733 | -4678707 | 15612972 | 25050894 | 99761154 | 49934086 | 11664127 | 0.000000 | 0.000000 | 863016174
09-04-2025 22:55:15.000 | 68456203 |  | 68.4562 | -4574242 | 15613638 | 25372163 | 99777496 | 49896988 | 11569869 | 0.000000 | 0.000000 | 856401001
09-04-2025 22:55:10.000 | 68572625 |  | 68.5726 | -4614724 | 15612898 | 25417463 | 99774323 | 49907822 | 11474564 | 0.000000 | 0.000000 | 850142212
09-04-2025 22:55:05.000 | 68608711 |  | 68.6087 | -4708626 | 15612430 | 25435044 | 99765327 | 49896790 | 11379560 | 0.000000 | 0.000000 | 843687134
09-04-2025 22:55:00.000 | 68743930 |  | 68.7439 | -4415459 | 15608849 | 25483020 | 99794357 | 49915497 | 11283960 | 0.000000 | 0.000000 | 837402710
09-04-2025 22:54:55.000 | 67866867 |  | 67.8669 | -4906628 | 15616452 | 25159138 | 99739670 | 49919216 | 11189355 | 0.000000 | 0.000000 | 830982910
09-04-2025 22:54:50.000 | 68925922 |  | 68.9259 | -4676625 | 15611070 | 25552712 | 99770607 | 49916016 | 11094148 | 0.000000 | 0.000000 | 824451111
09-04-2025 22:54:45.000 | 68297820 |  | 68.2978 | -4508128 | 15612517 | 25314031 | 99782867 | 49926598 | 10998583 | 0.000000 | 0.000000 | 818124451
09-04-2025 22:54:40.000 | 67714805 |  | 67.7148 | -4998004 | 15617643 | 25103369 | 99728714 | 49943119 | 10904140 | 0.000000 | 0.000000 | 811781799
09-04-2025 22:54:35.000 | 69109422 |  | 69.1094 | -4768307 | 15610519 | 25623093 | 99762817 | 49932381 | 10809012 | 0.000000 | 0.000000 | 805179199
09-04-2025 22:54:30.000 | 69422766 |  | 69.4228 | -4598143 | 15607552 | 25739336 | 99781372 | 49925541 | 10712745 | 0.000000 | 0.000000 | 798479187
09-04-2025 22:54:25.000 | 67798117 |  | 67.7981 | -4621448 | 15612988 | 25131550 | 99768486 | 49963776 | 10617171 | 0.000000 | 0.000000 | 792123352
09-04-2025 22:54:20.000 | 67806938 |  | 67.8069 | -4911651 | 15614623 | 25139570 | 99738678 | 49978474 | 10523010 | 0.000000 | 0.000000 | 785639465
09-04-2025 22:54:15.000 | 69373414 |  | 69.3734 | -5004346 | 15612815 | 25722717 | 99740829 | 49944408 | 10428140 | 0.000000 | 0.000000 | 778576904
09-04-2025 22:54:10.000 | 69649117 |  | 69.6491 | -5008640 | 15605436 | 25837144 | 99742432 | 49955486 | 10331248 | 0.000000 | 0.000000 | 771778625
09-04-2025 22:54:05.000 | 68178836 |  | 68.1788 | -5074088 | 15608243 | 25292517 | 99724205 | 49981277 | 10235145 | 0.000000 | 0.000000 | 764780518
09-04-2025 22:54:00.000 | 66993922 |  | 66.9939 | -5318940 | 15613492 | 24853672 | 99686310 | 50007282 | 10141167 | 0.000000 | 0.000000 | 757595215
09-04-2025 22:53:55.000 | 66197688 |  | 66.1977 | -5235131 | 15612833 | 24558567 | 99688751 | 50022942 | 10048529 | 0.000000 | 0.000000 | 750488159
09-04-2025 22:53:50.000 | 66431023 |  | 66.431 | -5080753 | 15614876 | 24637153 | 99708801 | 50014179 | 99566738 | 0.000000 | 0.000000 | 743180969
09-04-2025 22:53:45.000 | 66693070 |  | 66.6931 | -5146460 | 15614268 | 24736484 | 99703590 | 49997871 | 98645166 | 0.000000 | 0.000000 | 736034302
09-04-2025 22:53:40.000 | 67312922 |  | 67.3129 | -5258996 | 15613781 | 24968350 | 99696198 | 49983234 | 97714531 | 0.000000 | 0.000000 | 728912109
09-04-2025 22:53:35.000 | 67190633 |  | 67.1906 | -5006783 | 15613008 | 24917852 | 99723518 | 49972984 | 96777949 | 0.000000 | 0.000000 | 721752014
09-04-2025 22:53:30.000 | 67168633 |  | 67.1686 | -5068515 | 15614868 | 24908977 | 99716499 | 49972027 | 95843652 | 0.000000 | 0.000000 | 714738647
09-04-2025 22:53:25.000 | 66915031 |  | 66.915 | -4632438 | 15614077 | 24804656 | 99761230 | 49982006 | 94910020 | 0.000000 | 0.000000 | 707992004
09-04-2025 22:53:20.000 | 67080078 |  | 67.0801 | -5265396 | 15619670 | 24874458 | 99693352 | 49985588 | 93980146 | 0.000000 | 0.000000 | 701268188
09-04-2025 22:53:15.000 | 69006883 |  | 69.0069 | -5268207 | 15612431 | 25596204 | 99709854 | 49959679 | 93033564 | 0.000000 | 0.000000 | 694167480
09-04-2025 22:53:10.000 | 70403242 |  | 70.4032 | -5237787 | 15612225 | 26110640 | 99724396 | 49939709 | 92067070 | 0.000000 | 0.000000 | 686771606
09-04-2025 22:53:05.000 | 69789508 |  | 69.7895 | -5000358 | 15606983 | 25886648 | 99744301 | 49963638 | 91090352 | 0.000000 | 0.000000 | 679787048
09-04-2025 22:53:00.000 | 68326609 |  | 68.3266 | -5219175 | 15612706 | 25343264 | 99709534 | 49995861 | 90131201 | 0.000000 | 0.000000 | 672672668
09-04-2025 22:52:55.000 | 68107859 |  | 68.1079 | -5041423 | 15609371 | 25263672 | 99727165 | 49994656 | 89183271 | 0.000000 | 0.000000 | 665519653
09-04-2025 22:52:50.000 | 67461258 |  | 67.4613 | -5067268 | 15610463 | 25023298 | 99719086 | 50013008 | 88239619 | 0.000000 | 0.000000 | 658465332
09-04-2025 22:52:45.000 | 67116352 |  | 67.1164 | -5139147 | 15611313 | 24897610 | 99708130 | 50023022 | 87307275 | 0.000000 | 0.000000 | 651440002
09-04-2025 22:52:40.000 | 66330953 |  | 66.331 | -5427376 | 15615686 | 24609705 | 99666924 | 50032860 | 86381436 | 0.000000 | 0.000000 | 644211121
09-04-2025 22:52:35.000 | 66747633 |  | 66.7476 | -5181621 | 15613714 | 24758352 | 99700035 | 50015186 | 85456006 | 0.000000 | 0.000000 | 636831421
09-04-2025 22:52:30.000 | 66258492 |  | 66.2585 | -5224443 | 15613938 | 24579216 | 99690582 | 50017712 | 84530303 | 0.000000 | 0.000000 | 629690491
09-04-2025 22:52:25.000 | 66938680 |  | 66.9387 | -5118690 | 15612259 | 24829451 | 99708908 | 50013397 | 83606758 | 0.000000 | 0.000000 | 622374146
09-04-2025 22:52:20.000 | 67529680 |  | 67.5297 | -5335544 | 15613081 | 25052537 | 99689323 | 49994427 | 82673418 | 0.000000 | 0.000000 | 615158875
09-04-2025 22:52:15.000 | 67474211 |  | 67.4742 | -5110150 | 15611359 | 25027810 | 99714439 | 49991901 | 81733491 | 0.000000 | 0.000000 | 607907837
09-04-2025 22:52:10.000 | 67016164 |  | 67.0162 | -5247519 | 15614130 | 24859673 | 99694839 | 50003834 | 80798760 | 0.000000 | 0.000000 | 600773804
09-04-2025 22:52:05.000 | 66290578 |  | 66.2906 | -5123565 | 15616105 | 24584934 | 99702652 | 50010353 | 79872119 | 0.000000 | 0.000000 | 593700317
09-04-2025 22:52:00.000 | 67224359 |  | 67.2244 | -4767225 | 15614298 | 24923098 | 99749496 | 49996601 | 78943887 | 0.000000 | 0.000000 | 586725769
09-04-2025 22:51:55.000 | 68535195 |  | 68.5352 | -4992304 | 15613588 | 25413313 | 99735748 | 49978401 | 78005347 | 0.000000 | 0.000000 | 579887451
09-04-2025 22:51:50.000 | 69290547 |  | 69.2905 | -5087357 | 15612928 | 25695918 | 99731552 | 49969944 | 77049375 | 0.000000 | 0.000000 | 572853943
09-04-2025 22:51:45.000 | 69446164 |  | 69.4462 | -5230381 | 15612978 | 25755645 | 99717575 | 49982815 | 76083877 | 0.000000 | 0.000000 | 565845398
09-04-2025 22:51:40.000 | 70119391 |  | 70.1194 | -5206868 | 15611525 | 26006504 | 99725426 | 49985210 | 75115220 | 0.000000 | 0.000000 | 558739075
09-04-2025 22:51:35.000 | 70147234 |  | 70.1472 | -5247240 | 15610527 | 26018884 | 99721390 | 49993031 | 74139790 | 0.000000 | 0.000000 | 551489441
09-04-2025 22:51:30.000 | 69548984 |  | 69.549 | -5259654 | 15611824 | 25797351 | 99715263 | 50017662 | 73167612 | 0.000000 | 0.000000 | 544214417
09-04-2025 22:51:25.000 | 68607938 |  | 68.6079 | -5309437 | 15612418 | 25449785 | 99701889 | 50050026 | 72205049 | 0.000000 | 0.000000 | 537099854
09-04-2025 22:51:20.000 | 69123133 |  | 69.1231 | -5186507 | 15608438 | 25642666 | 99719688 | 50042301 | 71250098 | 0.000000 | 0.000000 | 529699402
09-04-2025 22:51:15.000 | 68361117 |  | 68.3611 | -5342301 | 15610104 | 25364097 | 99696037 | 50052063 | 70292495 | 0.000000 | 0.000000 | 522471497
09-04-2025 22:51:10.000 | 67311273 |  | 67.3113 | -5117381 | 15609858 | 24970967 | 99712250 | 50077023 | 69347852 | 0.000000 | 0.000000 | 515262634
09-04-2025 22:51:05.000 | 65883031 |  | 65.883 | -5245515 | 15616278 | 24437966 | 99684540 | 50101810 | 68422666 | 0.000000 | 0.000000 | 508149200
09-04-2025 22:51:00.000 | 66184320 |  | 66.1843 | -5284897 | 15617916 | 24547600 | 99682709 | 50085327 | 67507852 | 0.000000 | 0.000000 | 500901367
09-04-2025 22:50:55.000 | 67712609 |  | 67.7126 | -5135288 | 15617211 | 25107322 | 99713654 | 50056553 | 66577124 | 0.000000 | 0.000000 | 493721832
09-04-2025 22:50:50.000 | 68869703 |  | 68.8697 | -5033895 | 15612431 | 25538669 | 99733932 | 50041843 | 65629419 | 0.000000 | 0.000000 | 486718445
09-04-2025 22:50:45.000 | 69223953 |  | 69.224 | -5133870 | 15611113 | 25674094 | 99726120 | 50036766 | 64671860 | 0.000000 | 0.000000 | 479664001
09-04-2025 22:50:40.000 | 68481859 |  | 68.4819 | -5196411 | 15609882 | 25404438 | 99713348 | 50054333 | 63713164 | 0.000000 | 0.000000 | 472680695
09-04-2025 22:50:35.000 | 67776875 |  | 67.7769 | -5100606 | 15613595 | 25135447 | 99718025 | 50071072 | 62762222 | 0.000000 | 0.000000 | 465618500
09-04-2025 22:50:30.000 | 67162031 |  | 67.162 | -5028518 | 15615673 | 24904063 | 99720886 | 50081589 | 61823174 | 0.000000 | 0.000000 | 458681915
09-04-2025 22:50:25.000 | 67827813 |  | 67.8278 | -5076475 | 15613643 | 25154231 | 99721092 | 50081421 | 60888701 | 0.000000 | 0.000000 | 451704773
09-04-2025 22:50:20.000 | 69016156 |  | 69.0162 | -5183336 | 15611681 | 25598369 | 99719162 | 50057281 | 59942593 | 0.000000 | 0.000000 | 444483612
09-04-2025 22:50:15.000 | 68768680 |  | 68.7687 | -4949192 | 15608515 | 25505840 | 99742027 | 50059116 | 58982241 | 0.000000 | 0.000000 | 437471985
09-04-2025 22:50:10.000 | 68053703 |  | 68.0537 | -5041647 | 15608698 | 25244456 | 99726707 | 50083267 | 58032109 | 0.000000 | 0.000000 | 430452209
09-04-2025 22:50:05.000 | 67047719 |  | 67.0477 | -5048404 | 15610234 | 24870706 | 99717728 | 50097816 | 57093384 | 0.000000 | 0.000000 | 423382935
09-04-2025 22:50:00.000 | 66216820 |  | 66.2168 | -5114623 | 15611771 | 24563833 | 99703026 | 50107586 | 56170332 | 0.000000 | 0.000000 | 416298706
09-04-2025 22:49:55.000 | 65824266 |  | 65.8243 | -4928265 | 15613364 | 24411313 | 99720894 | 50099705 | 55254883 | 0.000000 | 0.000000 | 409312775
09-04-2025 22:49:50.000 | 65849430 |  | 65.8494 | -4978336 | 15615731 | 24418447 | 99715439 | 50091206 | 54342949 | 0.000000 | 0.000000 | 402492310
09-04-2025 22:49:45.000 | 66854367 |  | 66.8544 | -4997248 | 15614055 | 24793040 | 99721802 | 50057716 | 53423916 | 0.000000 | 0.000000 | 395505096
09-04-2025 22:49:40.000 | 66753234 |  | 66.7532 | -4704007 | 15611087 | 24751663 | 99752632 | 50055771 | 52490986 | 0.000000 | 0.000000 | 388821045
09-04-2025 22:49:35.000 | 66944695 |  | 66.9447 | -4816440 | 15608987 | 24828704 | 99742188 | 50059574 | 51563623 | 0.000000 | 0.000000 | 382200256
09-04-2025 22:49:30.000 | 66617484 |  | 66.6175 | -4864679 | 15611798 | 24704807 | 99734436 | 50060528 | 50634873 | 0.000000 | 0.000000 | 375510406
09-04-2025 22:49:25.000 | 65956867 |  | 65.9569 | -4492806 | 15612512 | 24450437 | 99768806 | 50057217 | 49711021 | 0.000000 | 0.000000 | 368938721
09-04-2025 22:49:20.000 | 65736609 |  | 65.7366 | -4920664 | 15616833 | 24373469 | 99721016 | 50064777 | 48800171 | 0.000000 | 0.000000 | 362468262
09-04-2025 22:49:15.000 | 66584664 |  | 66.5847 | -4966081 | 15616818 | 24687598 | 99723022 | 50040600 | 47884111 | 0.000000 | 0.000000 | 355561584
09-04-2025 22:49:10.000 | 67829422 |  | 67.8294 | -4844910 | 15617058 | 25142578 | 99745872 | 50015053 | 46948857 | 0.000000 | 0.000000 | 348753906
09-04-2025 22:49:05.000 | 68903000 |  | 68.903 | -4743041 | 15612684 | 25542991 | 99763916 | 50002892 | 45999365 | 0.000000 | 0.000000 | 342161865
09-04-2025 22:49:00.000 | 69066828 |  | 69.0668 | -4694513 | 15609348 | 25607522 | 99769798 | 50012505 | 45039644 | 0.000000 | 0.000000 | 335604065
09-04-2025 22:48:55.000 | 68641938 |  | 68.6419 | -4766996 | 15610784 | 25450557 | 99759720 | 50022816 | 44082793 | 0.000000 | 0.000000 | 329040771
09-04-2025 22:48:50.000 | 68120297 |  | 68.1203 | -4811957 | 15613650 | 25254370 | 99751434 | 50031425 | 43131748 | 0.000000 | 0.000000 | 322281036
09-04-2025 22:48:45.000 | 67950336 |  | 67.9503 | -4887188 | 15613253 | 25194214 | 99742355 | 50037830 | 42188477 | 0.000000 | 0.000000 | 315567413
09-04-2025 22:48:40.000 | 68167242 |  | 68.1672 | -5018849 | 15615458 | 25274087 | 99730064 | 50041859 | 41245205 | 0.000000 | 0.000000 | 308708221
09-04-2025 22:48:35.000 | 69227789 |  | 69.2278 | -5163321 | 15614917 | 25669998 | 99723015 | 50047588 | 40291948 | 0.000000 | 0.000000 | 301735138
09-04-2025 22:48:30.000 | 70012453 |  | 70.0125 | -5167497 | 15611060 | 25966021 | 99728722 | 50028095 | 39325234 | 0.000000 | 0.000000 | 294560974
09-04-2025 22:48:25.000 | 70115609 |  | 70.1156 | -5352911 | 15610123 | 26010994 | 99709846 | 50048508 | 38352607 | 0.000000 | 0.000000 | 287324738
09-04-2025 22:48:20.000 | 70414125 |  | 70.4141 | -5245013 | 15607089 | 26122756 | 99723724 | 50039585 | 37379741 | 0.000000 | 0.000000 | 279732239
09-04-2025 22:48:15.000 | 69121000 |  | 69.121 | -5303613 | 15605291 | 25650789 | 99706924 | 50086254 | 36408303 | 0.000000 | 0.000000 | 272372955
09-04-2025 22:48:10.000 | 67544320 |  | 67.5443 | -5588205 | 15607521 | 25074136 | 99659500 | 50120651 | 35458242 | 0.000000 | 0.000000 | 264928223
09-04-2025 22:48:05.000 | 67329906 |  | 67.3299 | -5805829 | 15609627 | 24998357 | 99630287 | 50121349 | 34522102 | 0.000000 | 0.000000 | 256910828
09-04-2025 22:48:00.000 | 66269094 |  | 66.2691 | -5542415 | 15610528 | 24597886 | 99652084 | 50124153 | 33593574 | 0.000000 | 0.000000 | 248923111
09-04-2025 22:47:55.000 | 65362254 |  | 65.3623 | -5451249 | 15617204 | 24250872 | 99654022 | 50139771 | 32677871 | 0.000000 | 0.000000 | 241357040
09-04-2025 22:47:50.000 | 66186852 |  | 66.1869 | -5553827 | 15616954 | 24557390 | 99649796 | 50124573 | 31768115 | 0.000000 | 0.000000 | 233687958
09-04-2025 22:47:45.000 | 67237516 |  | 67.2375 | -5524895 | 15614234 | 24948003 | 99664108 | 50103550 | 30843647 | 0.000000 | 0.000000 | 226120743
09-04-2025 22:47:40.000 | 69014266 |  | 69.0143 | -5417334 | 15608221 | 25609392 | 99693336 | 50067913 | 29899814 | 0.000000 | 0.000000 | 218427765
09-04-2025 22:47:35.000 | 67593133 |  | 67.5931 | -5309013 | 15608027 | 25082734 | 99692963 | 50086834 | 28947041 | 0.000000 | 0.000000 | 211040848
09-04-2025 22:47:30.000 | 66458086 |  | 66.4581 | -5456197 | 15612664 | 24661584 | 99664673 | 50111755 | 28015037 | 0.000000 | 0.000000 | 203605225
09-04-2025 22:47:25.000 | 65902984 |  | 65.903 | -5364895 | 15614952 | 24450317 | 99670288 | 50113991 | 27095078 | 0.000000 | 0.000000 | 196122299
09-04-2025 22:47:20.000 | 66512531 |  | 66.5125 | -5179950 | 15613940 | 24671343 | 99698112 | 50105839 | 26175181 | 0.000000 | 0.000000 | 188767136
09-04-2025 22:47:15.000 | 66718977 |  | 66.719 | -5114079 | 15613634 | 24745767 | 99707520 | 50098125 | 25248596 | 0.000000 | 0.000000 | 181664825
09-04-2025 22:47:10.000 | 67927555 |  | 67.9276 | -5342358 | 15615336 | 25194993 | 99692154 | 50088402 | 24316113 | 0.000000 | 0.000000 | 174491226
09-04-2025 22:47:05.000 | 68561086 |  | 68.5611 | -4971627 | 15610116 | 25426787 | 99738121 | 50065247 | 23368464 | 0.000000 | 0.000000 | 167386978
09-04-2025 22:47:00.000 | 68410977 |  | 68.411 | -5014489 | 15611544 | 25370769 | 99732437 | 50063572 | 22417898 | 0.000000 | 0.000000 | 160394775
09-04-2025 22:46:55.000 | 68415859 |  | 68.4159 | -4925554 | 15608645 | 25374321 | 99741844 | 50067902 | 21465918 | 0.000000 | 0.000000 | 153472610
09-04-2025 22:46:50.000 | 67601086 |  | 67.6011 | -5219847 | 15610642 | 25079053 | 99703217 | 50079964 | 20521917 | 0.000000 | 0.000000 | 146422974
09-04-2025 22:46:45.000 | 67565523 |  | 67.5655 | -5307422 | 15611260 | 25067051 | 99692902 | 50077957 | 19583898 | 0.000000 | 0.000000 | 139132294
09-04-2025 22:46:40.000 | 67095352 |  | 67.0954 | -5015299 | 15611245 | 24885674 | 99721794 | 50087349 | 18644280 | 0.000000 | 0.000000 | 132010559
09-04-2025 22:46:35.000 | 66303469 |  | 66.3035 | -5018012 | 15613481 | 24590251 | 99714836 | 50095272 | 17721603 | 0.000000 | 0.000000 | 124947075
09-04-2025 22:46:30.000 | 67031672 |  | 67.0317 | -5101292 | 15611505 | 24864128 | 99711670 | 50085136 | 16796254 | 0.000000 | 0.000000 | 117971138
09-04-2025 22:46:25.000 | 66737063 |  | 66.7371 | -4945846 | 15611831 | 24750623 | 99726517 | 50076973 | 15866304 | 0.000000 | 0.000000 | 110881065
09-04-2025 22:46:20.000 | 66801875 |  | 66.8019 | -4884585 | 15613735 | 24770610 | 99733734 | 50085640 | 14938849 | 0.000000 | 0.000000 | 104127480
09-04-2025 22:46:15.000 | 66149930 |  | 66.1499 | -4911516 | 15614294 | 24529209 | 99725494 | 50089912 | 14017783 | 0.000000 | 0.000000 | 97295052
09-04-2025 22:46:10.000 | 66570391 |  | 66.5704 | -4774421 | 15613242 | 24682361 | 99743797 | 50087421 | 13097363 | 0.000000 | 0.000000 | 90540543
09-04-2025 22:46:05.000 | 67074523 |  | 67.0745 | -4847012 | 15611160 | 24873491 | 99739922 | 50071835 | 12169698 | 0.000000 | 0.000000 | 83794243
09-04-2025 22:46:00.000 | 66701586 |  | 66.7016 | -4639750 | 15612516 | 24728699 | 99758949 | 50068916 | 11238131 | 0.000000 | 0.000000 | 77269875
09-04-2025 22:45:55.000 | 65979086 |  | 65.9791 | -4474496 | 15614606 | 24455466 | 99770836 | 50074551 | 10316891 | 0.000000 | 0.000000 | 70844452
09-04-2025 22:45:50.000 | 65139047 |  | 65.139 | -4436354 | 15616121 | 24141423 | 99768883 | 50079823 | 940739319 | 0.000000 | 0.000000 | 64650642
09-04-2025 22:45:45.000 | 66097859 |  | 66.0979 | -4405635 | 15616160 | 24495273 | 99778603 | 50050446 | 849841614 | 0.000000 | 0.000000 | 58521526
09-04-2025 22:45:40.000 | 67324977 |  | 67.325 | -4613065 | 15616641 | 24951606 | 99766075 | 50033653 | 757159729 | 0.000000 | 0.000000 | 52316002
09-04-2025 22:45:35.000 | 69415813 |  | 69.4158 | -4320083 | 15613143 | 25720940 | 99806900 | 50000584 | 662684692 | 0.000000 | 0.000000 | 45860191
09-04-2025 22:45:30.000 | 69628914 |  | 69.6289 | -4518023 | 15608229 | 25812517 | 99790146 | 50004650 | 565966553 | 0.000000 | 0.000000 | 39806980
09-04-2025 22:45:25.000 | 69477133 |  | 69.4771 | -4674098 | 15609549 | 25757949 | 99774467 | 50014069 | 469289612 | 0.000000 | 0.000000 | 33399590
09-04-2025 22:45:20.000 | 68601492 |  | 68.6015 | -4763573 | 15608375 | 25439375 | 99759781 | 50036938 | 373007874 | 0.000000 | 0.000000 | 26913218
09-04-2025 22:45:15.000 | 67618836 |  | 67.6188 | -5002877 | 15609275 | 25081914 | 99727417 | 50049656 | 278154541 | 0.000000 | 0.000000 | 20139675
09-04-2025 22:45:10.000 | 67296133 |  | 67.2961 | -4856423 | 15610692 | 24956209 | 99740623 | 50051865 | 184350693 | 0.000000 | 0.000000 | 13227076
09-04-2025 22:45:05.000 | 66212742 |  | 66.2127 | -4637982 | 15615399 | 24543657 | 99755569 | 50076511 | 91540237 | 0.000000 | 0.000000 | 6599284
09-04-2025 22:45:00.000 | 66446016 |  | 66.446 | -4524180 | 15618459 | 24622073 | 99769005 | 50088623 | 16940244 | 0.000000 | 0.000000 | 13930784
09-04-2025 22:44:55.000 | 66845164 |  | 66.8452 | -4234523 | 15615063 | 24766892 | 99799950 | 50055458 | 16847168 | 0.000000 | 0.000000 | 13871448
09-04-2025 22:44:50.000 | 68422750 |  | 68.4227 | -4158497 | 15609723 | 25356335 | 99815819 | 50032009 | 16753428 | 0.000000 | 0.000000 | 13813408
09-04-2025 22:44:45.000 | 68621188 |  | 68.6212 | -5570212 | 15610365 | 25466304 | 99672165 | 50028267 | 16658477 | 0.000000 | 0.000000 | 13747798
09-04-2025 22:44:40.000 | 68248391 |  | 68.2484 | -5782383 | 15611052 | 25333274 | 99642998 | 50025127 | 16563547 | 0.000000 | 0.000000 | 13668414
09-04-2025 22:44:35.000 | 67451219 |  | 67.4512 | -5547293 | 15613343 | 25028875 | 99663521 | 50045120 | 16468943 | 0.000000 | 0.000000 | 13590250
09-04-2025 22:44:30.000 | 66977828 |  | 66.9778 | -5766529 | 15616800 | 24855320 | 99631424 | 50052494 | 16375647 | 0.000000 | 0.000000 | 13512561
09-04-2025 22:44:25.000 | 67894609 |  | 67.8946 | -5356406 | 15615534 | 25183843 | 99690239 | 50036140 | 16281815 | 0.000000 | 0.000000 | 13435031
09-04-2025 22:44:20.000 | 68236141 |  | 68.2361 | -5217374 | 15614479 | 25306086 | 99708961 | 50044380 | 16187286 | 0.000000 | 0.000000 | 13361903
09-04-2025 22:44:15.000 | 69266820 |  | 69.2668 | -5165795 | 15610962 | 25691443 | 99723061 | 50023476 | 16091548 | 0.000000 | 0.000000 | 13290581
09-04-2025 22:44:10.000 | 69977680 |  | 69.9777 | -5202018 | 15603721 | 25966938 | 99724831 | 50025860 | 15994655 | 0.000000 | 0.000000 | 13219490
09-04-2025 22:44:05.000 | 69024336 |  | 69.0243 | -5989367 | 15610765 | 25626099 | 99625648 | 50056576 | 15897911 | 0.000000 | 0.000000 | 13140734
09-04-2025 22:44:00.000 | 69109586 |  | 69.1096 | -6104081 | 15607518 | 25666763 | 99612206 | 50066841 | 15801867 | 0.000000 | 0.000000 | 13056813
09-04-2025 22:43:55.000 | 67970102 |  | 67.9701 | -6075272 | 15607403 | 25246069 | 99602928 | 50084076 | 15706426 | 0.000000 | 0.000000 | 12971718
09-04-2025 22:43:50.000 | 66641430 |  | 66.6414 | -6019736 | 15610052 | 24750972 | 99594505 | 50106754 | 15612571 | 0.000000 | 0.000000 | 12887826
09-04-2025 22:43:45.000 | 65549852 |  | 65.5499 | -5843796 | 15613143 | 24337886 | 99604965 | 50126045 | 15520388 | 0.000000 | 0.000000 | 12805410
09-04-2025 22:43:40.000 | 65821508 |  | 65.8215 | -6054034 | 15615176 | 24442251 | 99579681 | 50110725 | 15429466 | 0.000000 | 0.000000 | 12722775
09-04-2025 22:43:35.000 | 67164188 |  | 67.1642 | -5646933 | 15607988 | 24934592 | 99648422 | 50071648 | 15337131 | 0.000000 | 0.000000 | 12640748
09-04-2025 22:43:30.000 | 66176594 |  | 66.1766 | -5885647 | 15612151 | 24571411 | 99606827 | 50080147 | 15244305 | 0.000000 | 0.000000 | 12561980
09-04-2025 22:43:25.000 | 66003344 |  | 66.0033 | -5955547 | 15615728 | 24504961 | 99595390 | 50074856 | 15152626 | 0.000000 | 0.000000 | 12479313
09-04-2025 22:43:20.000 | 66497234 |  | 66.4972 | -5573314 | 15615117 | 24675483 | 99650612 | 50059269 | 15060963 | 0.000000 | 0.000000 | 12397543
09-04-2025 22:43:15.000 | 67111156 |  | 67.1112 | -5685879 | 15616505 | 24902891 | 99643021 | 50040562 | 14968204 | 0.000000 | 0.000000 | 12318667
09-04-2025 22:43:10.000 | 68544453 |  | 68.5445 | -5465418 | 15613729 | 25428865 | 99683624 | 50015797 | 14873998 | 0.000000 | 0.000000 | 12240359
09-04-2025 22:43:05.000 | 68542547 |  | 68.5425 | -5515301 | 15613982 | 25429658 | 99677834 | 50017696 | 14778736 | 0.000000 | 0.000000 | 12164779
09-04-2025 22:43:00.000 | 68903711 |  | 68.9037 | -5781969 | 15612817 | 25571736 | 99649773 | 50026390 | 14683047 | 0.000000 | 0.000000 | 12088013
09-04-2025 22:42:55.000 | 69658664 |  | 69.6587 | -5709231 | 15609156 | 25854038 | 99665810 | 50023800 | 14586638 | 0.000000 | 0.000000 | 12008179
09-04-2025 22:42:50.000 | 68947430 |  | 68.9474 | -5831009 | 15608811 | 25596140 | 99644287 | 50044075 | 14490140 | 0.000000 | 0.000000 | 11928202
09-04-2025 22:42:45.000 | 67704234 |  | 67.7042 | -5895593 | 15610123 | 25137437 | 99623009 | 50072372 | 14395080 | 0.000000 | 0.000000 | 11847008
09-04-2025 22:42:40.000 | 67395508 |  | 67.3955 | -6003504 | 15612151 | 25024023 | 99605598 | 50082561 | 14301410 | 0.000000 | 0.000000 | 11764104
09-04-2025 22:42:35.000 | 66931477 |  | 66.9315 | -6172661 | 15613984 | 24855984 | 99577431 | 50088940 | 14208018 | 0.000000 | 0.000000 | 11680699
09-04-2025 22:42:30.000 | 67227523 |  | 67.2275 | -5895266 | 15611055 | 24961235 | 99617714 | 50083035 | 14114796 | 0.000000 | 0.000000 | 11597421
09-04-2025 22:42:25.000 | 66901883 |  | 66.9019 | -5873595 | 15612627 | 24837500 | 99616821 | 50092773 | 14021354 | 0.000000 | 0.000000 | 11515391
09-04-2025 22:42:20.000 | 67446344 |  | 67.4463 | -6076164 | 15613945 | 25043347 | 99596657 | 50081333 | 13928196 | 0.000000 | 0.000000 | 11432542
09-04-2025 22:42:15.000 | 68680867 |  | 68.6809 | -5835531 | 15610148 | 25496450 | 99640984 | 50058548 | 13833816 | 0.000000 | 0.000000 | 11349095
09-04-2025 22:42:10.000 | 67770641 |  | 67.7706 | -5495928 | 15612037 | 25147253 | 99672783 | 50069206 | 13739067 | 0.000000 | 0.000000 | 11268844
09-04-2025 22:42:05.000 | 67448742 |  | 67.4487 | -5410643 | 15612803 | 25024548 | 99679794 | 50091011 | 13645336 | 0.000000 | 0.000000 | 11193345
09-04-2025 22:42:00.000 | 67413688 |  | 67.4137 | -5304438 | 15614773 | 25005806 | 99691864 | 50090515 | 13552011 | 0.000000 | 0.000000 | 11118546
09-04-2025 22:41:55.000 | 67920883 |  | 67.9209 | -5639718 | 15617504 | 25198025 | 99657043 | 50077812 | 13458389 | 0.000000 | 0.000000 | 11043439
09-04-2025 22:41:50.000 | 68933234 |  | 68.9332 | -5366179 | 15612200 | 25571335 | 99698372 | 50060493 | 13363302 | 0.000000 | 0.000000 | 10967640
09-04-2025 22:41:45.000 | 68977781 |  | 68.9778 | -5381890 | 15611528 | 25589956 | 99696999 | 50057823 | 13267585 | 0.000000 | 0.000000 | 10893348
09-04-2025 22:41:40.000 | 68536508 |  | 68.5365 | -4939717 | 15610679 | 25415562 | 99741272 | 50067741 | 13171821 | 0.000000 | 0.000000 | 10821290
09-04-2025 22:41:35.000 | 68050148 |  | 68.0501 | -4970265 | 15612583 | 25234805 | 99734329 | 50087254 | 13076881 | 0.000000 | 0.000000 | 10752899
09-04-2025 22:41:30.000 | 67210531 |  | 67.2105 | -4850323 | 15614390 | 24918301 | 99740616 | 50102913 | 12982783 | 0.000000 | 0.000000 | 10684701
09-04-2025 22:41:25.000 | 68485141 |  | 68.4851 | -5184485 | 15615673 | 25395227 | 99714684 | 50081650 | 12889150 | 0.000000 | 0.000000 | 10614401
09-04-2025 22:41:20.000 | 68769469 |  | 68.7695 | -4912556 | 15609562 | 25502771 | 99745827 | 50070087 | 12793569 | 0.000000 | 0.000000 | 10545063
09-04-2025 22:41:15.000 | 68372992 |  | 68.373 | -5275843 | 15613285 | 25361248 | 99703621 | 50072472 | 12698339 | 0.000000 | 0.000000 | 10474254
09-04-2025 22:41:10.000 | 68965422 |  | 68.9654 | -5377676 | 15611439 | 25584453 | 99697365 | 50080654 | 12602991 | 0.000000 | 0.000000 | 10400938
09-04-2025 22:41:05.000 | 69034352 |  | 69.0344 | -5343075 | 15609752 | 25612209 | 99701820 | 50079872 | 12507227 | 0.000000 | 0.000000 | 10326267
09-04-2025 22:41:00.000 | 68474766 |  | 68.4748 | -5213723 | 15606973 | 25406423 | 99711380 | 50097935 | 12411975 | 0.000000 | 0.000000 | 10251981
09-04-2025 22:40:55.000 | 67744797 |  | 67.7448 | -5406938 | 15611427 | 25136331 | 99683006 | 50100349 | 12317746 | 0.000000 | 0.000000 | 10176434
09-04-2025 22:40:50.000 | 67843211 |  | 67.8432 | -5271953 | 15610306 | 25170466 | 99699432 | 50103882 | 12223611 | 0.000000 | 0.000000 | 10101547
09-04-2025 22:40:45.000 | 66231836 |  | 66.2318 | -5112989 | 15612502 | 24568049 | 99703346 | 50130219 | 12130062 | 0.000000 | 0.000000 | 10030234
09-04-2025 22:40:40.000 | 67031578 |  | 67.0316 | -5276997 | 15615318 | 24863745 | 99691559 | 50119644 | 12037871 | 0.000000 | 0.000000 | 995604980
09-04-2025 22:40:35.000 | 67679336 |  | 67.6793 | -5303396 | 15611650 | 25108091 | 99694389 | 50099163 | 11944443 | 0.000000 | 0.000000 | 988275452
09-04-2025 22:40:30.000 | 68160336 |  | 68.1603 | -5569953 | 15611104 | 25295078 | 99667770 | 50088963 | 11849863 | 0.000000 | 0.000000 | 980737610
09-04-2025 22:40:25.000 | 67844547 |  | 67.8445 | -5299064 | 15611578 | 25168977 | 99696358 | 50087769 | 11755008 | 0.000000 | 0.000000 | 973213989
09-04-2025 22:40:20.000 | 67477523 |  | 67.4775 | -5305124 | 15611004 | 25035234 | 99692368 | 50109097 | 11660979 | 0.000000 | 0.000000 | 965925537
09-04-2025 22:40:15.000 | 66921250 |  | 66.9213 | -5460378 | 15615958 | 24828342 | 99668770 | 50112125 | 11567812 | 0.000000 | 0.000000 | 958466492
09-04-2025 22:40:10.000 | 67249867 |  | 67.2499 | -5162299 | 15611192 | 24946594 | 99706665 | 50104843 | 11474478 | 0.000000 | 0.000000 | 951162170
09-04-2025 22:40:05.000 | 66655727 |  | 66.6557 | -5158115 | 15612078 | 24725994 | 99701920 | 50110661 | 11381376 | 0.000000 | 0.000000 | 944040222
09-04-2025 22:40:00.000 | 66338461 |  | 66.3385 | -4810616 | 15614149 | 24596379 | 99738106 | 50103382 | 11289062 | 0.000000 | 0.000000 | 936921143
09-04-2025 22:39:55.000 | 65899180 |  | 65.8992 | -5244700 | 15618632 | 24439929 | 99684792 | 50108044 | 11197438 | 0.000000 | 0.000000 | 930124207
09-04-2025 22:39:50.000 | 68441383 |  | 68.4414 | -4947722 | 15613622 | 25376536 | 99739716 | 50057446 | 11104057 | 0.000000 | 0.000000 | 923057312
09-04-2025 22:39:45.000 | 69050234 |  | 69.0502 | -5150613 | 15610111 | 25612000 | 99722954 | 50051575 | 11008369 | 0.000000 | 0.000000 | 916190002
09-04-2025 22:39:40.000 | 68426438 |  | 68.4264 | -5164953 | 15608414 | 25386731 | 99716339 | 50075012 | 10912420 | 0.000000 | 0.000000 | 909152161
09-04-2025 22:39:35.000 | 66715813 |  | 66.7158 | -5205858 | 15613099 | 24748357 | 99696945 | 50105442 | 10818064 | 0.000000 | 0.000000 | 902075623
09-04-2025 22:39:30.000 | 66564227 |  | 66.5642 | -5126721 | 15612287 | 24691177 | 99704712 | 50120152 | 10725416 | 0.000000 | 0.000000 | 894995300
09-04-2025 22:39:25.000 | 67098570 |  | 67.0986 | -5230191 | 15615313 | 24887395 | 99697586 | 50103088 | 10632542 | 0.000000 | 0.000000 | 887701294
09-04-2025 22:39:20.000 | 67854922 |  | 67.8549 | -5127963 | 15609733 | 25171743 | 99715660 | 50092384 | 10538758 | 0.000000 | 0.000000 | 880554260
09-04-2025 22:39:15.000 | 67829164 |  | 67.8292 | -5076407 | 15608403 | 25162576 | 99721115 | 50089642 | 10444308 | 0.000000 | 0.000000 | 873445740
09-04-2025 22:39:10.000 | 66804781 |  | 66.8048 | -5405251 | 15612110 | 24788508 | 99674271 | 50097942 | 10350613 | 0.000000 | 0.000000 | 866239990
09-04-2025 22:39:05.000 | 66842305 |  | 66.8423 | -5258337 | 15611607 | 24798418 | 99692001 | 50103500 | 10257207 | 0.000000 | 0.000000 | 858993530
09-04-2025 22:39:00.000 | 65926953 |  | 65.927 | -5235004 | 15613182 | 24458101 | 99686218 | 50109470 | 10164796 | 0.000000 | 0.000000 | 851744690
09-04-2025 22:38:55.000 | 65424582 |  | 65.4246 | -5142431 | 15615731 | 24265889 | 99692520 | 50109543 | 10073528 | 0.000000 | 0.000000 | 844553955
09-04-2025 22:38:50.000 | 66114086 |  | 66.1141 | -4869468 | 15614678 | 24514624 | 99729866 | 50092289 | 99823730 | 0.000000 | 0.000000 | 837577148
09-04-2025 22:38:45.000 | 67137727 |  | 67.1377 | -4829083 | 15613318 | 24892820 | 99742317 | 50061512 | 98900557 | 0.000000 | 0.000000 | 830733582
09-04-2025 22:38:40.000 | 68763172 |  | 68.7632 | -4770381 | 15610845 | 25494854 | 99760223 | 50027927 | 97958369 | 0.000000 | 0.000000 | 823981689
09-04-2025 22:38:35.000 | 67620477 |  | 67.6205 | -4506118 | 15609412 | 25069124 | 99778702 | 50042858 | 97006201 | 0.000000 | 0.000000 | 817530823
09-04-2025 22:38:30.000 | 66824148 |  | 66.8241 | -4741772 | 15611553 | 24777471 | 99749191 | 50071411 | 96071348 | 0.000000 | 0.000000 | 811185730
09-04-2025 22:38:25.000 | 66882328 |  | 66.8823 | -4754375 | 15613334 | 24796423 | 99748299 | 50069832 | 95141416 | 0.000000 | 0.000000 | 804596252
09-04-2025 22:38:20.000 | 67709406 |  | 67.7094 | -4705486 | 15613431 | 25099712 | 99759392 | 50056961 | 94207910 | 0.000000 | 0.000000 | 798011536
09-04-2025 22:38:15.000 | 68455172 |  | 68.4552 | -4698810 | 15613977 | 25374141 | 99765251 | 50029724 | 93262305 | 0.000000 | 0.000000 | 791460266
09-04-2025 22:38:10.000 | 68471914 |  | 68.4719 | -4792459 | 15611032 | 25387434 | 99755959 | 50042191 | 92310391 | 0.000000 | 0.000000 | 785057739
09-04-2025 22:38:05.000 | 68557633 |  | 68.5576 | -4749800 | 15608599 | 25421760 | 99760864 | 50051559 | 91357061 | 0.000000 | 0.000000 | 778390320
09-04-2025 22:38:00.000 | 67950008 |  | 67.95 | -5010996 | 15610988 | 25202305 | 99729187 | 50053822 | 90412480 | 0.000000 | 0.000000 | 771542908
09-04-2025 22:37:55.000 | 67328844 |  | 67.3288 | -5085248 | 15611284 | 24974058 | 99715988 | 50067181 | 89471973 | 0.000000 | 0.000000 | 764598083
09-04-2025 22:37:50.000 | 67268828 |  | 67.2688 | -5038304 | 15609835 | 24952610 | 99720688 | 50077042 | 88535488 | 0.000000 | 0.000000 | 757545532
09-04-2025 22:37:45.000 | 66356555 |  | 66.3566 | -5026471 | 15614655 | 24608564 | 99714333 | 50079395 | 87606387 | 0.000000 | 0.000000 | 750503967
09-04-2025 22:37:40.000 | 66821016 |  | 66.821 | -4979933 | 15614912 | 24777544 | 99723442 | 50071602 | 86685059 | 0.000000 | 0.000000 | 743589050
09-04-2025 22:37:35.000 | 66159609 |  | 66.1596 | -4868717 | 15616415 | 24528232 | 99730316 | 50077530 | 85759365 | 0.000000 | 0.000000 | 736840027
09-04-2025 22:37:30.000 | 67044211 |  | 67.0442 | -4948103 | 15615789 | 24857942 | 99728760 | 50053543 | 84835264 | 0.000000 | 0.000000 | 730022461
09-04-2025 22:37:25.000 | 68847156 |  | 68.8472 | -4917110 | 15611953 | 25529131 | 99745926 | 50023335 | 83893535 | 0.000000 | 0.000000 | 723109924
09-04-2025 22:37:20.000 | 69394828 |  | 69.3948 | -4760900 | 15607741 | 25732539 | 99765488 | 50025513 | 82934453 | 0.000000 | 0.000000 | 716288635
09-04-2025 22:37:15.000 | 68692031 |  | 68.692 | -4782310 | 15609572 | 25470950 | 99758530 | 50049370 | 81976797 | 0.000000 | 0.000000 | 709511414
09-04-2025 22:37:10.000 | 67716766 |  | 67.7168 | -5221168 | 15613429 | 25117922 | 99704079 | 50063381 | 81030879 | 0.000000 | 0.000000 | 702529968
09-04-2025 22:37:05.000 | 67908219 |  | 67.9082 | -5042804 | 15611025 | 25186401 | 99725418 | 50048237 | 80086787 | 0.000000 | 0.000000 | 695329590
09-04-2025 22:37:00.000 | 67446750 |  | 67.4467 | -5013242 | 15611528 | 25015608 | 99724899 | 50064598 | 79142769 | 0.000000 | 0.000000 | 688420227
09-04-2025 22:36:55.000 | 67363266 |  | 67.3633 | -5033348 | 15614357 | 24979800 | 99722015 | 50072464 | 78205913 | 0.000000 | 0.000000 | 681487061
09-04-2025 22:36:50.000 | 67513398 |  | 67.5134 | -5051333 | 15611592 | 25040203 | 99721268 | 50059467 | 77269780 | 0.000000 | 0.000000 | 674518677
09-04-2025 22:36:45.000 | 67650211 |  | 67.6502 | -5042521 | 15608924 | 25094353 | 99723358 | 50056965 | 76331719 | 0.000000 | 0.000000 | 667523743
09-04-2025 22:36:40.000 | 66623500 |  | 66.6235 | -5100956 | 15610767 | 24714902 | 99708183 | 50071278 | 75394556 | 0.000000 | 0.000000 | 660515503
09-04-2025 22:36:35.000 | 65903109 |  | 65.9031 | -5189805 | 15613570 | 24447278 | 99691368 | 50076416 | 74473481 | 0.000000 | 0.000000 | 653501160
09-04-2025 22:36:30.000 | 66071656 |  | 66.0717 | -5159803 | 15614962 | 24506125 | 99696457 | 50070129 | 73558179 | 0.000000 | 0.000000 | 646279297
09-04-2025 22:36:25.000 | 66291727 |  | 66.2917 | -5229569 | 15618836 | 24584395 | 99690285 | 50052410 | 72640894 | 0.000000 | 0.000000 | 639097412
09-04-2025 22:36:20.000 | 67873344 |  | 67.8733 | -4790486 | 15615536 | 25159238 | 99751854 | 50018166 | 71710078 | 0.000000 | 0.000000 | 631981445
09-04-2025 22:36:15.000 | 69120508 |  | 69.1205 | -4843825 | 15611514 | 25627361 | 99755356 | 50003422 | 70760610 | 0.000000 | 0.000000 | 625233337
09-04-2025 22:36:10.000 | 69761188 |  | 69.7612 | -4795105 | 15609453 | 25866011 | 99764603 | 50001411 | 69796855 | 0.000000 | 0.000000 | 618483093
09-04-2025 22:36:05.000 | 68434109 |  | 68.4341 | -4881891 | 15611331 | 25377349 | 99746521 | 50032948 | 68833320 | 0.000000 | 0.000000 | 611940247
09-04-2025 22:36:00.000 | 68090469 |  | 68.0905 | -4773193 | 15615452 | 25238977 | 99755196 | 50047642 | 67884063 | 0.000000 | 0.000000 | 605233643
09-04-2025 22:35:55.000 | 68409953 |  | 68.41 | -4884785 | 15614425 | 25362380 | 99746040 | 50058369 | 66936582 | 0.000000 | 0.000000 | 598603943
09-04-2025 22:35:50.000 | 69087578 |  | 69.0876 | -5131674 | 15616997 | 25614009 | 99725273 | 50041260 | 65984141 | 0.000000 | 0.000000 | 591596436
09-04-2025 22:35:45.000 | 70610430 |  | 70.6104 | -5013684 | 15612225 | 26180046 | 99748863 | 50021919 | 65014473 | 0.000000 | 0.000000 | 584600342
09-04-2025 22:35:40.000 | 71035711 |  | 71.0357 | -5153833 | 15608084 | 26348142 | 99737839 | 50025753 | 64030083 | 0.000000 | 0.000000 | 577589172
09-04-2025 22:35:35.000 | 70915070 |  | 70.9151 | -5580627 | 15608365 | 26314790 | 99691788 | 50036503 | 63044932 | 0.000000 | 0.000000 | 570105896
09-04-2025 22:35:30.000 | 70453117 |  | 70.4531 | -5484854 | 15604295 | 26148857 | 99698334 | 50066940 | 62063901 | 0.000000 | 0.000000 | 562313538
09-04-2025 22:35:25.000 | 68168508 |  | 68.1685 | -6101797 | 15611537 | 25313196 | 99601784 | 50114151 | 61099404 | 0.000000 | 0.000000 | 554360779
09-04-2025 22:35:20.000 | 67504266 |  | 67.5043 | -6039158 | 15611399 | 25068018 | 99602203 | 50123650 | 60153369 | 0.000000 | 0.000000 | 545938965
09-04-2025 22:35:15.000 | 67268273 |  | 67.2683 | -6161660 | 15613179 | 24981204 | 99583107 | 50135662 | 59215845 | 0.000000 | 0.000000 | 537529297
09-04-2025 22:35:10.000 | 67344680 |  | 67.3447 | -6233473 | 15614832 | 25008828 | 99574356 | 50133553 | 58280327 | 0.000000 | 0.000000 | 528976868
09-04-2025 22:35:05.000 | 67972211 |  | 67.9722 | -6096667 | 15612633 | 25238901 | 99600166 | 50123871 | 57339878 | 0.000000 | 0.000000 | 520445190
09-04-2025 22:35:00.000 | 67990813 |  | 67.9908 | -5997518 | 15614478 | 25239756 | 99613197 | 50126534 | 56395146 | 0.000000 | 0.000000 | 512088379
09-04-2025 22:34:55.000 | 68859047 |  | 68.859 | -6190962 | 15613961 | 25566658 | 99598267 | 50110649 | 55447695 | 0.000000 | 0.000000 | 503607635
09-04-2025 22:34:50.000 | 69492227 |  | 69.4922 | -6401473 | 15608083 | 25816755 | 99578400 | 50103050 | 54487070 | 0.000000 | 0.000000 | 494985199
09-04-2025 22:34:45.000 | 69198367 |  | 69.1984 | -6240930 | 15608955 | 25701289 | 99595764 | 50116306 | 53517959 | 0.000000 | 0.000000 | 486211060
09-04-2025 22:34:40.000 | 67219086 |  | 67.2191 | -6075871 | 15611786 | 24963821 | 99593979 | 50161240 | 52569785 | 0.000000 | 0.000000 | 477701630
09-04-2025 22:34:35.000 | 66605422 |  | 66.6054 | -6255732 | 15613810 | 24739355 | 99561829 | 50164635 | 51644385 | 0.000000 | 0.000000 | 469164429
09-04-2025 22:34:30.000 | 67060344 |  | 67.0603 | -5969762 | 15611525 | 24900603 | 99606102 | 50152187 | 50714160 | 0.000000 | 0.000000 | 460628418
09-04-2025 22:34:25.000 | 67115859 |  | 67.1159 | -6062489 | 15614314 | 24920142 | 99594513 | 50162800 | 49782754 | 0.000000 | 0.000000 | 452254364
09-04-2025 22:34:20.000 | 67339516 |  | 67.3395 | -6068587 | 15612646 | 25005205 | 99596382 | 50149147 | 48851641 | 0.000000 | 0.000000 | 443824310
09-04-2025 22:34:15.000 | 67329656 |  | 67.3297 | -6067869 | 15614929 | 24997678 | 99596359 | 50159382 | 47917192 | 0.000000 | 0.000000 | 435418884
09-04-2025 22:34:10.000 | 67322367 |  | 67.3224 | -6018394 | 15614425 | 24994070 | 99602791 | 50156002 | 46985850 | 0.000000 | 0.000000 | 427019592
09-04-2025 22:34:05.000 | 68366633 |  | 68.3666 | -6099906 | 15614429 | 25382041 | 99604317 | 50135021 | 46043706 | 0.000000 | 0.000000 | 418626648
09-04-2025 22:34:00.000 | 69386383 |  | 69.3864 | -5869625 | 15610839 | 25755481 | 99644104 | 50126690 | 45088491 | 0.000000 | 0.000000 | 410198456
09-04-2025 22:33:55.000 | 69258609 |  | 69.2586 | -5775642 | 15608894 | 25709319 | 99654091 | 50131435 | 44124810 | 0.000000 | 0.000000 | 402045898
09-04-2025 22:33:50.000 | 68601617 |  | 68.6016 | -5932564 | 15607811 | 25473357 | 99628159 | 50154423 | 43163994 | 0.000000 | 0.000000 | 393977936
09-04-2025 22:33:45.000 | 68160773 |  | 68.1608 | -6179942 | 15611646 | 25313315 | 99591492 | 50163651 | 42214111 | 0.000000 | 0.000000 | 385584839
09-04-2025 22:33:40.000 | 67532555 |  | 67.5326 | -6143386 | 15611726 | 25081558 | 99588783 | 50175495 | 41272207 | 0.000000 | 0.000000 | 377006897
09-04-2025 22:33:35.000 | 67201133 |  | 67.2011 | -6233064 | 15612842 | 24961121 | 99572609 | 50185616 | 40339006 | 0.000000 | 0.000000 | 368366608
09-04-2025 22:33:30.000 | 67084922 |  | 67.0849 | -6155833 | 15612044 | 24915166 | 99581627 | 50183472 | 39405813 | 0.000000 | 0.000000 | 359722961
09-04-2025 22:33:25.000 | 66888617 |  | 66.8886 | -6354950 | 15613993 | 24846533 | 99551704 | 50191101 | 38476313 | 0.000000 | 0.000000 | 351105988
09-04-2025 22:33:20.000 | 66983469 |  | 66.9835 | -6307780 | 15614634 | 24879082 | 99559532 | 50187027 | 37547024 | 0.000000 | 0.000000 | 342430725
09-04-2025 22:33:15.000 | 67784289 |  | 67.7843 | -6223537 | 15613175 | 25173040 | 99581154 | 50172016 | 36612300 | 0.000000 | 0.000000 | 333829163
09-04-2025 22:33:10.000 | 68088633 |  | 68.0886 | -6300022 | 15610259 | 25293308 | 99574669 | 50166004 | 35668972 | 0.000000 | 0.000000 | 325253479
09-04-2025 22:33:05.000 | 67840180 |  | 67.8402 | -6191524 | 15609396 | 25198899 | 99586105 | 50165123 | 34719971 | 0.000000 | 0.000000 | 316541412
09-04-2025 22:33:00.000 | 66972133 |  | 66.9721 | -6226911 | 15613301 | 24874336 | 99570541 | 50184731 | 33783928 | 0.000000 | 0.000000 | 307944275
09-04-2025 22:32:55.000 | 66564648 |  | 66.5646 | -6284177 | 15612938 | 24726458 | 99557320 | 50189114 | 32858987 | 0.000000 | 0.000000 | 299193939
09-04-2025 22:32:50.000 | 66449945 |  | 66.4499 | -6089459 | 15614349 | 24675784 | 99582733 | 50188126 | 31933794 | 0.000000 | 0.000000 | 290556946
09-04-2025 22:32:45.000 | 66374063 |  | 66.3741 | -6062601 | 15615196 | 24645574 | 99585442 | 50184082 | 31013296 | 0.000000 | 0.000000 | 282117279
09-04-2025 22:32:40.000 | 67503867 |  | 67.5039 | -6149658 | 15615369 | 25064199 | 99587601 | 50163559 | 30087043 | 0.000000 | 0.000000 | 273617645
09-04-2025 22:32:35.000 | 67859539 |  | 67.8595 | -5962762 | 15612765 | 25192793 | 99616173 | 50158119 | 29146174 | 0.000000 | 0.000000 | 265279388
09-04-2025 22:32:30.000 | 68744063 |  | 68.7441 | -6122263 | 15612831 | 25523752 | 99605774 | 50144283 | 28199910 | 0.000000 | 0.000000 | 256813721
09-04-2025 22:32:25.000 | 69396648 |  | 69.3966 | -6075905 | 15608632 | 25769822 | 99618912 | 50137512 | 27239917 | 0.000000 | 0.000000 | 248436920
09-04-2025 22:32:20.000 | 69206867 |  | 69.2069 | -6116485 | 15606052 | 25705154 | 99611725 | 50150993 | 26277134 | 0.000000 | 0.000000 | 239900986
09-04-2025 22:32:15.000 | 67416523 |  | 67.4165 | -6317363 | 15609383 | 25047483 | 99563828 | 50186119 | 25326155 | 0.000000 | 0.000000 | 231309280
09-04-2025 22:32:10.000 | 66430813 |  | 66.4308 | -6223163 | 15613672 | 24674216 | 99564079 | 50201347 | 24395310 | 0.000000 | 0.000000 | 222597778
09-04-2025 22:32:05.000 | 66009523 |  | 66.0095 | -6169984 | 15616758 | 24512649 | 99566002 | 50204384 | 23476140 | 0.000000 | 0.000000 | 214166031
09-04-2025 22:32:00.000 | 67753211 |  | 67.7532 | -5960969 | 15613982 | 25151748 | 99615204 | 50166386 | 22549526 | 0.000000 | 0.000000 | 205663925
09-04-2025 22:31:55.000 | 68802039 |  | 68.802 | -6243424 | 15611739 | 25551331 | 99590797 | 50152531 | 21601455 | 0.000000 | 0.000000 | 197233871
09-04-2025 22:31:50.000 | 69146734 |  | 69.1467 | -6318550 | 15608370 | 25686829 | 99585091 | 50157345 | 20640823 | 0.000000 | 0.000000 | 188583588
09-04-2025 22:31:45.000 | 68111031 |  | 68.111 | -6137120 | 15608298 | 25299224 | 99596512 | 50174080 | 19687037 | 0.000000 | 0.000000 | 179925308
09-04-2025 22:31:40.000 | 66216094 |  | 66.2161 | -6144373 | 15613621 | 24593367 | 99572235 | 50212608 | 18753942 | 0.000000 | 0.000000 | 171374481
09-04-2025 22:31:35.000 | 66742719 |  | 66.7427 | -6189904 | 15617521 | 24783528 | 99572693 | 50200897 | 17836974 | 0.000000 | 0.000000 | 162619400
09-04-2025 22:31:30.000 | 66971016 |  | 66.971 | -6016835 | 15613490 | 24866282 | 99598846 | 50183746 | 16913491 | 0.000000 | 0.000000 | 154142624
09-04-2025 22:31:25.000 | 67844758 |  | 67.8448 | -6150979 | 15614706 | 25190420 | 99591530 | 50168419 | 15981296 | 0.000000 | 0.000000 | 145669235
09-04-2025 22:31:20.000 | 68700523 |  | 68.7005 | -6241776 | 15609502 | 25517393 | 99589806 | 50147144 | 15035326 | 0.000000 | 0.000000 | 137095779
09-04-2025 22:31:15.000 | 68946000 |  | 68.946 | -6348463 | 15607031 | 25615078 | 99578751 | 50147984 | 14077789 | 0.000000 | 0.000000 | 128404907
09-04-2025 22:31:10.000 | 68221234 |  | 68.2212 | -6052504 | 15608337 | 25337815 | 99608757 | 50172150 | 13122655 | 0.000000 | 0.000000 | 119699249
09-04-2025 22:31:05.000 | 65864969 |  | 65.865 | -6255789 | 15614047 | 24466357 | 99551979 | 50212536 | 12189731 | 0.000000 | 0.000000 | 111175995
09-04-2025 22:31:00.000 | 66225844 |  | 66.2258 | -6281256 | 15615498 | 24597556 | 99553223 | 50208389 | 11273336 | 0.000000 | 0.000000 | 102465393
09-04-2025 22:30:55.000 | 67624117 |  | 67.6241 | -6031644 | 15615780 | 25104270 | 99604584 | 50178814 | 10345382 | 0.000000 | 0.000000 | 93801727
09-04-2025 22:30:50.000 | 68275742 |  | 68.2757 | -5882486 | 15612019 | 25344907 | 99630898 | 50173317 | 940194336 | 0.000000 | 0.000000 | 85543953
09-04-2025 22:30:45.000 | 69324617 |  | 69.3246 | -6118965 | 15611836 | 25739709 | 99612724 | 50160316 | 844899536 | 0.000000 | 0.000000 | 77120399
09-04-2025 22:30:40.000 | 68686414 |  | 68.6864 | -5983309 | 15609033 | 25504519 | 99622734 | 50170761 | 748889771 | 0.000000 | 0.000000 | 68839577
09-04-2025 22:30:35.000 | 67678555 |  | 67.6786 | -6151860 | 15611477 | 25134390 | 99589417 | 50194122 | 654129700 | 0.000000 | 0.000000 | 60509174
09-04-2025 22:30:30.000 | 67877258 |  | 67.8773 | -6140432 | 15612078 | 25206304 | 99593307 | 50185928 | 560014771 | 0.000000 | 0.000000 | 51980778
09-04-2025 22:30:25.000 | 67997203 |  | 67.9972 | -6254293 | 15609903 | 25257771 | 99579659 | 50183636 | 465476501 | 0.000000 | 0.000000 | 43450077
09-04-2025 22:30:20.000 | 67861398 |  | 67.8614 | -6302573 | 15609619 | 25210234 | 99571487 | 50179909 | 370895111 | 0.000000 | 0.000000 | 34744381
09-04-2025 22:30:15.000 | 66949250 |  | 66.9493 | -6214594 | 15610291 | 24870584 | 99571938 | 50197163 | 276847809 | 0.000000 | 0.000000 | 26035282
09-04-2025 22:30:10.000 | 65971836 |  | 65.9718 | -6364434 | 15613276 | 24511477 | 99537880 | 50216549 | 184314529 | 0.000000 | 0.000000 | 17347818
09-04-2025 22:30:05.000 | 66625922 |  | 66.6259 | -6183886 | 15613407 | 24745376 | 99572029 | 50193211 | 92226273 | 0.000000 | 0.000000 | 8537735
09-04-2025 22:30:00.000 | 65964023 |  | 65.964 | -6204633 | 15613897 | 24501287 | 99560539 | 50187210 | 16856150 | 0.000000 | 0.000000 | 13112751
09-04-2025 22:29:55.000 | 66604984 |  | 66.605 | -6110536 | 15614550 | 24732939 | 99581802 | 50177464 | 16763967 | 0.000000 | 0.000000 | 13027445
09-04-2025 22:29:50.000 | 67069961 |  | 67.07 | -5819845 | 15612254 | 24898621 | 99625641 | 50170055 | 16671174 | 0.000000 | 0.000000 | 12943588
09-04-2025 22:29:45.000 | 66561359 |  | 66.5614 | -5928613 | 15617413 | 24707102 | 99605675 | 50175121 | 16578672 | 0.000000 | 0.000000 | 12861667
09-04-2025 22:29:40.000 | 67463547 |  | 67.4635 | -5885785 | 15616161 | 25039961 | 99621582 | 50157101 | 16485896 | 0.000000 | 0.000000 | 12779362
09-04-2025 22:29:35.000 | 68402586 |  | 68.4026 | -6004864 | 15612207 | 25395193 | 99616882 | 50132984 | 16391629 | 0.000000 | 0.000000 | 12697537
09-04-2025 22:29:30.000 | 68775813 |  | 68.7758 | -5677733 | 15610861 | 25524521 | 99660973 | 50135380 | 16295862 | 0.000000 | 0.000000 | 12617036
09-04-2025 22:29:25.000 | 68260398 |  | 68.2604 | -5882552 | 15611945 | 25339080 | 99630722 | 50146927 | 16200997 | 0.000000 | 0.000000 | 12536357
09-04-2025 22:29:20.000 | 68360742 |  | 68.3607 | -6110898 | 15611847 | 25383586 | 99602837 | 50143219 | 16106397 | 0.000000 | 0.000000 | 12452803
09-04-2025 22:29:15.000 | 67956813 |  | 67.9568 | -6166870 | 15611433 | 25237593 | 99590775 | 50143490 | 16011509 | 0.000000 | 0.000000 | 12368191
09-04-2025 22:29:10.000 | 68088578 |  | 68.0886 | -6060859 | 15611883 | 25282341 | 99606163 | 50140877 | 15916732 | 0.000000 | 0.000000 | 12283784
09-04-2025 22:29:05.000 | 68267297 |  | 68.2673 | -5835546 | 15610687 | 25343003 | 99636642 | 50140873 | 15821847 | 0.000000 | 0.000000 | 12200117
09-04-2025 22:29:00.000 | 66743375 |  | 66.7434 | -6129481 | 15610479 | 24791479 | 99580948 | 50168839 | 15728036 | 0.000000 | 0.000000 | 12117797
09-04-2025 22:28:55.000 | 66330055 |  | 66.3301 | -6381275 | 15612391 | 24644453 | 99540421 | 50173779 | 15635642 | 0.000000 | 0.000000 | 12031890
09-04-2025 22:28:50.000 | 66796289 |  | 66.7963 | -6302024 | 15611881 | 24814307 | 99557884 | 50160534 | 15543090 | 0.000000 | 0.000000 | 11943219
09-04-2025 22:28:45.000 | 66165641 |  | 66.1656 | -6211327 | 15612843 | 24577834 | 99562263 | 50158264 | 15450692 | 0.000000 | 0.000000 | 11855393
09-04-2025 22:28:40.000 | 65783078 |  | 65.7831 | -6204946 | 15612878 | 24436401 | 99558090 | 50150997 | 15359095 | 0.000000 | 0.000000 | 11768928
09-04-2025 22:28:35.000 | 65254020 |  | 65.254 | -6010657 | 15614648 | 24231804 | 99578453 | 50147499 | 15267908 | 0.000000 | 0.000000 | 11684670
09-04-2025 22:28:30.000 | 65465297 |  | 65.4653 | -6009461 | 15618051 | 24304536 | 99581314 | 50140057 | 15177073 | 0.000000 | 0.000000 | 11602246
09-04-2025 22:28:25.000 | 67088320 |  | 67.0883 | -5784474 | 15613862 | 24901357 | 99630348 | 50105812 | 15085162 | 0.000000 | 0.000000 | 11519331
09-04-2025 22:28:20.000 | 67924547 |  | 67.9245 | -5785032 | 15613665 | 25209644 | 99639275 | 50083500 | 14991565 | 0.000000 | 0.000000 | 11439158
09-04-2025 22:28:15.000 | 69093703 |  | 69.0937 | -5835572 | 15608975 | 25650181 | 99645233 | 50073353 | 14896503 | 0.000000 | 0.000000 | 11359078
09-04-2025 22:28:10.000 | 68313352 |  | 68.3134 | -5909660 | 15609221 | 25364844 | 99627907 | 50087421 | 14800926 | 0.000000 | 0.000000 | 11278218
09-04-2025 22:28:05.000 | 67381922 |  | 67.3819 | -5742324 | 15611447 | 25012917 | 99638840 | 50110725 | 14706743 | 0.000000 | 0.000000 | 11196637
09-04-2025 22:28:00.000 | 66606328 |  | 66.6063 | -6104739 | 15616834 | 24729790 | 99582603 | 50132622 | 14613778 | 0.000000 | 0.000000 | 11115698
09-04-2025 22:27:55.000 | 67758070 |  | 67.7581 | -6082673 | 15615257 | 25155413 | 99599480 | 50111374 | 14520667 | 0.000000 | 0.000000 | 11031125
09-04-2025 22:27:50.000 | 67937023 |  | 67.937 | -5795102 | 15614802 | 25213149 | 99638161 | 50096180 | 14426244 | 0.000000 | 0.000000 | 10948113
09-04-2025 22:27:45.000 | 68533023 |  | 68.533 | -5621327 | 15609321 | 25435786 | 99665291 | 50092823 | 14331341 | 0.000000 | 0.000000 | 10869109
09-04-2025 22:27:40.000 | 68100461 |  | 68.1005 | -6066787 | 15610296 | 25288774 | 99605530 | 50090111 | 14236406 | 0.000000 | 0.000000 | 10787909
09-04-2025 22:27:35.000 | 68092984 |  | 68.093 | -5762388 | 15608448 | 25279893 | 99643837 | 50093826 | 14141662 | 0.000000 | 0.000000 | 10705208
09-04-2025 22:27:30.000 | 66230945 |  | 66.2309 | -5934961 | 15614094 | 24590203 | 99600906 | 50119724 | 14048125 | 0.000000 | 0.000000 | 10624663
09-04-2025 22:27:25.000 | 66023688 |  | 66.0237 | -5929967 | 15613501 | 24515295 | 99599083 | 50110931 | 13955921 | 0.000000 | 0.000000 | 10543145
09-04-2025 22:27:20.000 | 66105375 |  | 66.1054 | -5710669 | 15615208 | 24535090 | 99628937 | 50098167 | 13863909 | 0.000000 | 0.000000 | 10462629
09-04-2025 22:27:15.000 | 66649117 |  | 66.6491 | -5789165 | 15614025 | 24740112 | 99624886 | 50100204 | 13771636 | 0.000000 | 0.000000 | 10383192
09-04-2025 22:27:10.000 | 67360875 |  | 67.3609 | -5856775 | 15614043 | 25004080 | 99624146 | 50072193 | 13678794 | 0.000000 | 0.000000 | 10302047
09-04-2025 22:27:05.000 | 68132461 |  | 68.1325 | -5511561 | 15610102 | 25283906 | 99674400 | 50061481 | 13584457 | 0.000000 | 0.000000 | 10223270
09-04-2025 22:27:00.000 | 68011945 |  | 68.0119 | -5593315 | 15609203 | 25243081 | 99663536 | 50064770 | 13489960 | 0.000000 | 0.000000 | 10145385
09-04-2025 22:26:55.000 | 66911734 |  | 66.9117 | -5545548 | 15610068 | 24835381 | 99658318 | 50076481 | 13396116 | 0.000000 | 0.000000 | 10067404
09-04-2025 22:26:50.000 | 66672508 |  | 66.6725 | -5728354 | 15610453 | 24752158 | 99632935 | 50081028 | 13303778 | 0.000000 | 0.000000 | 998803772
09-04-2025 22:26:45.000 | 65578250 |  | 65.5782 | -5533216 | 15612899 | 24338496 | 99645927 | 50086079 | 13211585 | 0.000000 | 0.000000 | 990955688
09-04-2025 22:26:40.000 | 64850145 |  | 64.8501 | -5783906 | 15617007 | 24072063 | 99604622 | 50092228 | 13120823 | 0.000000 | 0.000000 | 983260315
09-04-2025 22:26:35.000 | 66210383 |  | 66.2104 | -5576286 | 15614222 | 24570764 | 99647217 | 50056911 | 13029864 | 0.000000 | 0.000000 | 975345581
09-04-2025 22:26:30.000 | 66683492 |  | 66.6835 | -5336719 | 15612897 | 24740303 | 99681282 | 50047707 | 12937580 | 0.000000 | 0.000000 | 967693481
09-04-2025 22:26:25.000 | 66668031 |  | 66.668 | -5142205 | 15613702 | 24727876 | 99703857 | 50047726 | 12845041 | 0.000000 | 0.000000 | 960349243
09-04-2025 22:26:20.000 | 67059727 |  | 67.0597 | -5234202 | 15613490 | 24875532 | 99696770 | 50042236 | 12752237 | 0.000000 | 0.000000 | 953167175
09-04-2025 22:26:15.000 | 67973734 |  | 67.9737 | -5008478 | 15609313 | 25212039 | 99729645 | 50024601 | 12658449 | 0.000000 | 0.000000 | 945959106
09-04-2025 22:26:10.000 | 67275414 |  | 67.2754 | -5239472 | 15612126 | 24956953 | 99698097 | 50037956 | 12564696 | 0.000000 | 0.000000 | 938694275
09-04-2025 22:26:05.000 | 66925172 |  | 66.9252 | -5103682 | 15614085 | 24820486 | 99710487 | 50040588 | 12471632 | 0.000000 | 0.000000 | 931330322
09-04-2025 22:26:00.000 | 66575914 |  | 66.5759 | -5055240 | 15615469 | 24688057 | 99712959 | 50056305 | 12378956 | 0.000000 | 0.000000 | 924362610
09-04-2025 22:25:55.000 | 67759820 |  | 67.7598 | -5364914 | 15613643 | 25136475 | 99688026 | 50037640 | 12286094 | 0.000000 | 0.000000 | 917200806
09-04-2025 22:25:50.000 | 69109203 |  | 69.1092 | -5269550 | 15609069 | 25638552 | 99710564 | 49998775 | 12191070 | 0.000000 | 0.000000 | 909688110
09-04-2025 22:25:45.000 | 67920156 |  | 67.9202 | -5208136 | 15608236 | 25200308 | 99707298 | 50021713 | 12095415 | 0.000000 | 0.000000 | 902458557
09-04-2025 22:25:40.000 | 66822867 |  | 66.8229 | -5398574 | 15611260 | 24796062 | 99675240 | 50045952 | 12001961 | 0.000000 | 0.000000 | 895097046
09-04-2025 22:25:35.000 | 66065984 |  | 66.066 | -5393705 | 15615362 | 24510188 | 99668396 | 50039024 | 11909656 | 0.000000 | 0.000000 | 887583740
09-04-2025 22:25:30.000 | 65699531 |  | 65.6995 | -5290384 | 15613884 | 24374231 | 99677361 | 50041035 | 11817927 | 0.000000 | 0.000000 | 880316833
09-04-2025 22:25:25.000 | 66115922 |  | 66.1159 | -5178107 | 15615603 | 24522334 | 99694710 | 50019028 | 11726426 | 0.000000 | 0.000000 | 873042175
09-04-2025 22:25:20.000 | 67322453 |  | 67.3225 | -5171442 | 15614408 | 24968669 | 99706261 | 50001228 | 11634106 | 0.000000 | 0.000000 | 865907532
09-04-2025 22:25:15.000 | 68087234 |  | 68.0872 | -5064823 | 15608697 | 25256863 | 99724472 | 49964596 | 11540266 | 0.000000 | 0.000000 | 858702271
09-04-2025 22:25:10.000 | 67522523 |  | 67.5225 | -5099879 | 15611021 | 25045542 | 99715988 | 49980682 | 11445583 | 0.000000 | 0.000000 | 851774658
09-04-2025 22:25:05.000 | 67516203 |  | 67.5162 | -4981474 | 15611142 | 25040278 | 99728920 | 49986713 | 11351913 | 0.000000 | 0.000000 | 844719604
09-04-2025 22:25:00.000 | 66751453 |  | 66.7515 | -4903265 | 15611479 | 24754912 | 99731300 | 49994057 | 11258507 | 0.000000 | 0.000000 | 837826782
09-04-2025 22:24:55.000 | 65443605 |  | 65.4436 | -4953959 | 15617760 | 24264153 | 99714714 | 50017227 | 11166722 | 0.000000 | 0.000000 | 831130127
09-04-2025 22:24:50.000 | 67117570 |  | 67.1176 | -4872309 | 15617565 | 24880862 | 99737549 | 49974701 | 11075471 | 0.000000 | 0.000000 | 824250793
09-04-2025 22:24:45.000 | 68416242 |  | 68.4162 | -4723699 | 15612271 | 25363364 | 99762497 | 49938095 | 10981450 | 0.000000 | 0.000000 | 817540527
09-04-2025 22:24:40.000 | 68570523 |  | 68.5705 | -4611029 | 15608281 | 25423762 | 99774666 | 49939224 | 10886153 | 0.000000 | 0.000000 | 811027039
09-04-2025 22:24:35.000 | 67381852 |  | 67.3819 | -4945285 | 15611274 | 24988831 | 99731766 | 49950909 | 10791635 | 0.000000 | 0.000000 | 804373413
09-04-2025 22:24:30.000 | 67282039 |  | 67.282 | -4805458 | 15609713 | 24950779 | 99745911 | 49964272 | 10698104 | 0.000000 | 0.000000 | 797553467
09-04-2025 22:24:25.000 | 66677656 |  | 66.6777 | -4982590 | 15613834 | 24726035 | 99721962 | 49978031 | 10605394 | 0.000000 | 0.000000 | 790731873
09-04-2025 22:24:20.000 | 67333281 |  | 67.3333 | -4979718 | 15613752 | 24968201 | 99727638 | 49964985 | 10512467 | 0.000000 | 0.000000 | 783747437
09-04-2025 22:24:15.000 | 67477328 |  | 67.4773 | -4884981 | 15611453 | 25022319 | 99738976 | 49965168 | 10418640 | 0.000000 | 0.000000 | 776934998
09-04-2025 22:24:10.000 | 67139828 |  | 67.1398 | -4907208 | 15611854 | 24897915 | 99733963 | 49967045 | 10325202 | 0.000000 | 0.000000 | 770196960
09-04-2025 22:24:05.000 | 67363266 |  | 67.3633 | -4878323 | 15613459 | 24977344 | 99738808 | 49955837 | 10231810 | 0.000000 | 0.000000 | 763326538
09-04-2025 22:24:00.000 | 67773727 |  | 67.7737 | -4910057 | 15611851 | 25132063 | 99738594 | 49949562 | 10137804 | 0.000000 | 0.000000 | 756528259
09-04-2025 22:23:55.000 | 67527711 |  | 67.5277 | -4773187 | 15611543 | 25038084 | 99751114 | 49955845 | 10043577 | 0.000000 | 0.000000 | 749845398
09-04-2025 22:23:50.000 | 67366133 |  | 67.3661 | -4735707 | 15612130 | 24976443 | 99753822 | 49969101 | 99499023 | 0.000000 | 0.000000 | 743202393
09-04-2025 22:23:45.000 | 67157633 |  | 67.1576 | -4955553 | 15614082 | 24902412 | 99728859 | 49967037 | 98566523 | 0.000000 | 0.000000 | 736500977
09-04-2025 22:23:40.000 | 67929484 |  | 67.9295 | -4913708 | 15610587 | 25191416 | 99739403 | 49941185 | 97628633 | 0.000000 | 0.000000 | 729547546
09-04-2025 22:23:35.000 | 67296875 |  | 67.2969 | -5064877 | 15610855 | 24961729 | 99717979 | 49957035 | 96687119 | 0.000000 | 0.000000 | 722695435
09-04-2025 22:23:30.000 | 67267344 |  | 67.2673 | -4888280 | 15612124 | 24943940 | 99737000 | 49964085 | 95752510 | 0.000000 | 0.000000 | 715674072
09-04-2025 22:23:25.000 | 67049023 |  | 67.049 | -5150194 | 15609866 | 24873987 | 99706291 | 49971977 | 94819717 | 0.000000 | 0.000000 | 708722351
09-04-2025 22:23:20.000 | 66741859 |  | 66.7419 | -5043260 | 15612484 | 24753801 | 99715721 | 49961933 | 93889082 | 0.000000 | 0.000000 | 701592224
09-04-2025 22:23:15.000 | 66209547 |  | 66.2095 | -5262754 | 15614447 | 24560647 | 99685585 | 49959587 | 92967666 | 0.000000 | 0.000000 | 694514038
09-04-2025 22:23:10.000 | 66844594 |  | 66.8446 | -5125376 | 15611458 | 24795605 | 99707329 | 49948887 | 92041455 | 0.000000 | 0.000000 | 687362671
09-04-2025 22:23:05.000 | 66432906 |  | 66.4329 | -5061877 | 15612195 | 24640774 | 99710968 | 49960587 | 91112979 | 0.000000 | 0.000000 | 680367126
09-04-2025 22:23:00.000 | 66811273 |  | 66.8113 | -5209418 | 15613863 | 24781807 | 99697395 | 49962704 | 90189189 | 0.000000 | 0.000000 | 673230225
09-04-2025 22:22:55.000 | 67210594 |  | 67.2106 | -5338656 | 15613862 | 24932656 | 99686012 | 49943119 | 89260518 | 0.000000 | 0.000000 | 665946899
09-04-2025 22:22:50.000 | 67464531 |  | 67.4645 | -5002483 | 15610907 | 25022124 | 99726219 | 49933483 | 88324170 | 0.000000 | 0.000000 | 658692322
09-04-2025 22:22:45.000 | 66246359 |  | 66.2464 | -4906400 | 15612491 | 24567668 | 99726860 | 49950863 | 87393467 | 0.000000 | 0.000000 | 651791443
09-04-2025 22:22:40.000 | 66131422 |  | 66.1314 | -5008212 | 15615367 | 24523035 | 99714470 | 49963100 | 86473047 | 0.000000 | 0.000000 | 644872131
09-04-2025 22:22:35.000 | 66946117 |  | 66.9461 | -4940880 | 15614793 | 24822412 | 99728760 | 49942375 | 85550498 | 0.000000 | 0.000000 | 637898560
09-04-2025 22:22:30.000 | 67432531 |  | 67.4325 | -4924070 | 15613115 | 25004102 | 99734451 | 49934380 | 84617471 | 0.000000 | 0.000000 | 631095215
09-04-2025 22:22:25.000 | 68418648 |  | 68.4186 | -5045091 | 15613684 | 25370159 | 99729233 | 49916080 | 83676113 | 0.000000 | 0.000000 | 624138000
09-04-2025 22:22:20.000 | 68130477 |  | 68.1305 | -4744022 | 15611430 | 25259978 | 99758453 | 49917839 | 82725547 | 0.000000 | 0.000000 | 617396179
09-04-2025 22:22:15.000 | 67879414 |  | 67.8794 | -4940156 | 15611154 | 25172607 | 99736214 | 49926613 | 81782432 | 0.000000 | 0.000000 | 610669678
09-04-2025 22:22:10.000 | 67671641 |  | 67.6716 | -4919789 | 15610819 | 25095967 | 99736771 | 49918259 | 80836895 | 0.000000 | 0.000000 | 603793213
09-04-2025 22:22:05.000 | 67052461 |  | 67.0525 | -5023925 | 15612150 | 24868428 | 99720490 | 49936890 | 79898818 | 0.000000 | 0.000000 | 597014954
09-04-2025 22:22:00.000 | 67061273 |  | 67.0613 | -4988419 | 15613754 | 24868472 | 99724480 | 49946358 | 78968813 | 0.000000 | 0.000000 | 590071777
09-04-2025 22:21:55.000 | 67184000 |  | 67.184 | -5157180 | 15612298 | 24920767 | 99706673 | 49938915 | 78036074 | 0.000000 | 0.000000 | 583046082
09-04-2025 22:21:50.000 | 68004633 |  | 68.0046 | -5171367 | 15610314 | 25226726 | 99712112 | 49914455 | 77100322 | 0.000000 | 0.000000 | 575777161
09-04-2025 22:21:45.000 | 67806813 |  | 67.8068 | -5204257 | 15610780 | 25153667 | 99706757 | 49925106 | 76156670 | 0.000000 | 0.000000 | 568560730
09-04-2025 22:21:40.000 | 65791305 |  | 65.7913 | -5145561 | 15614660 | 24403374 | 99695557 | 49953114 | 75225732 | 0.000000 | 0.000000 | 561492798
09-04-2025 22:21:35.000 | 66076734 |  | 66.0767 | -5202689 | 15614342 | 24510205 | 99691460 | 49936367 | 74314209 | 0.000000 | 0.000000 | 554192078
09-04-2025 22:21:30.000 | 67093047 |  | 67.093 | -5341364 | 15611313 | 24893706 | 99684601 | 49911549 | 73391040 | 0.000000 | 0.000000 | 546839294
09-04-2025 22:21:25.000 | 67536930 |  | 67.5369 | -5181042 | 15610402 | 25054045 | 99707039 | 49902668 | 72454380 | 0.000000 | 0.000000 | 539540161
09-04-2025 22:21:20.000 | 66373383 |  | 66.3734 | -4850871 | 15612913 | 24612119 | 99733994 | 49920841 | 71524126 | 0.000000 | 0.000000 | 532519775
09-04-2025 22:21:15.000 | 65814492 |  | 65.8145 | -4838260 | 15616561 | 24399976 | 99730881 | 49915527 | 70607363 | 0.000000 | 0.000000 | 525674927
09-04-2025 22:21:10.000 | 66417133 |  | 66.4171 | -5021983 | 15614221 | 24630720 | 99715355 | 49904694 | 69689248 | 0.000000 | 0.000000 | 518912476
09-04-2025 22:21:05.000 | 67538852 |  | 67.5389 | -4712355 | 15610901 | 25042036 | 99757477 | 49876640 | 68758359 | 0.000000 | 0.000000 | 512009705
09-04-2025 22:21:00.000 | 67176531 |  | 67.1765 | -4816467 | 15611918 | 24908611 | 99743950 | 49888844 | 67822446 | 0.000000 | 0.000000 | 505380280
09-04-2025 22:20:55.000 | 66933805 |  | 66.9338 | -4857346 | 15613081 | 24818491 | 99737717 | 49890083 | 66890781 | 0.000000 | 0.000000 | 498651520
09-04-2025 22:20:50.000 | 67118406 |  | 67.1184 | -4885674 | 15611133 | 24890786 | 99736115 | 49889359 | 65960073 | 0.000000 | 0.000000 | 491975433
09-04-2025 22:20:45.000 | 67175391 |  | 67.1754 | -4778128 | 15612950 | 24905786 | 99747986 | 49885464 | 65026567 | 0.000000 | 0.000000 | 485181549
09-04-2025 22:20:40.000 | 67398477 |  | 67.3985 | -4915883 | 15614518 | 24989277 | 99735062 | 49897099 | 64093374 | 0.000000 | 0.000000 | 478504761
09-04-2025 22:20:35.000 | 68070734 |  | 68.0707 | -4938334 | 15611142 | 25243062 | 99737877 | 49871155 | 63155000 | 0.000000 | 0.000000 | 471659790
09-04-2025 22:20:30.000 | 68413148 |  | 68.4131 | -4975942 | 15610355 | 25371917 | 99736534 | 49860275 | 62205830 | 0.000000 | 0.000000 | 464748749
09-04-2025 22:20:25.000 | 67949742 |  | 67.9497 | -4986749 | 15608743 | 25203494 | 99731789 | 49871273 | 61259702 | 0.000000 | 0.000000 | 457832489
09-04-2025 22:20:20.000 | 66774484 |  | 66.7745 | -5223734 | 15610505 | 24773889 | 99695404 | 49891617 | 60322559 | 0.000000 | 0.000000 | 450825592
09-04-2025 22:20:15.000 | 66873156 |  | 66.8732 | -5309189 | 15610491 | 24813047 | 99686325 | 49892944 | 59394766 | 0.000000 | 0.000000 | 443580017
09-04-2025 22:20:10.000 | 66315453 |  | 66.3155 | -5120820 | 15614331 | 24595854 | 99703186 | 49892452 | 58468638 | 0.000000 | 0.000000 | 436396484
09-04-2025 22:20:05.000 | 66521484 |  | 66.5215 | -5044662 | 15614487 | 24669390 | 99713684 | 49882187 | 57546904 | 0.000000 | 0.000000 | 429239777
09-04-2025 22:20:00.000 | 66830703 |  | 66.8307 | -5022328 | 15614188 | 24783137 | 99718811 | 49869183 | 56622446 | 0.000000 | 0.000000 | 422227722
09-04-2025 22:19:55.000 | 67149094 |  | 67.1491 | -4757836 | 15615082 | 24892793 | 99749924 | 49856472 | 55690410 | 0.000000 | 0.000000 | 415366150
09-04-2025 22:19:50.000 | 67056547 |  | 67.0565 | -4645600 | 15614721 | 24855459 | 99760880 | 49873768 | 54756865 | 0.000000 | 0.000000 | 408893982
09-04-2025 22:19:45.000 | 67735117 |  | 67.7351 | -4951818 | 15614694 | 25113945 | 99733841 | 49861275 | 53824839 | 0.000000 | 0.000000 | 402274261
09-04-2025 22:19:40.000 | 69795203 |  | 69.7952 | -4657799 | 15610780 | 25872878 | 99778061 | 49816509 | 52871133 | 0.000000 | 0.000000 | 395541046
09-04-2025 22:19:35.000 | 69734719 |  | 69.7347 | -4679810 | 15606736 | 25857617 | 99775581 | 49824928 | 51899629 | 0.000000 | 0.000000 | 389077637
09-04-2025 22:19:30.000 | 68395734 |  | 68.3957 | -4849021 | 15612702 | 25358079 | 99749626 | 49868500 | 50938535 | 0.000000 | 0.000000 | 382559631
09-04-2025 22:19:25.000 | 68352172 |  | 68.3522 | -5010729 | 15612170 | 25347378 | 99732376 | 49863266 | 49990908 | 0.000000 | 0.000000 | 375689484
09-04-2025 22:19:20.000 | 68414531 |  | 68.4145 | -4794333 | 15612087 | 25365149 | 99755356 | 49861927 | 49040625 | 0.000000 | 0.000000 | 368885925
09-04-2025 22:19:15.000 | 68342766 |  | 68.3428 | -4908006 | 15613438 | 25339895 | 99743126 | 49867996 | 48088604 | 0.000000 | 0.000000 | 362195099
09-04-2025 22:19:10.000 | 68842133 |  | 68.8421 | -5125807 | 15609733 | 25534841 | 99723953 | 49862183 | 47136675 | 0.000000 | 0.000000 | 355246338
09-04-2025 22:19:05.000 | 68289805 |  | 68.2898 | -5092877 | 15611431 | 25328413 | 99723068 | 49876709 | 46181504 | 0.000000 | 0.000000 | 348185211
09-04-2025 22:19:00.000 | 67703578 |  | 67.7036 | -5056460 | 15610280 | 25112881 | 99722267 | 49893002 | 45234346 | 0.000000 | 0.000000 | 341114594
09-04-2025 22:18:55.000 | 66891195 |  | 66.8912 | -5032753 | 15612516 | 24809053 | 99718163 | 49907879 | 44300112 | 0.000000 | 0.000000 | 334052979
09-04-2025 22:18:50.000 | 66548859 |  | 66.5489 | -4998692 | 15614337 | 24678511 | 99719086 | 49908428 | 43373760 | 0.000000 | 0.000000 | 327026093
09-04-2025 22:18:45.000 | 66206664 |  | 66.2067 | -5115921 | 15615532 | 24553709 | 99702782 | 49904255 | 42453579 | 0.000000 | 0.000000 | 320044891
09-04-2025 22:18:40.000 | 67425141 |  | 67.4251 | -4911174 | 15614562 | 24999114 | 99735779 | 49885403 | 41526167 | 0.000000 | 0.000000 | 313036926
09-04-2025 22:18:35.000 | 68110922 |  | 68.1109 | -5022887 | 15614102 | 25255952 | 99729179 | 49873367 | 40587764 | 0.000000 | 0.000000 | 306182251
09-04-2025 22:18:30.000 | 68584367 |  | 68.5844 | -5009931 | 15613575 | 25430747 | 99734268 | 49859680 | 39637551 | 0.000000 | 0.000000 | 299284912
09-04-2025 22:18:25.000 | 69488156 |  | 69.4882 | -4805849 | 15611996 | 25761375 | 99761696 | 49849525 | 38680630 | 0.000000 | 0.000000 | 292205017
09-04-2025 22:18:20.000 | 68814031 |  | 68.814 | -4912065 | 15609890 | 25518552 | 99746201 | 49862274 | 37721509 | 0.000000 | 0.000000 | 285513153
09-04-2025 22:18:15.000 | 67178148 |  | 67.1781 | -4831157 | 15614637 | 24905366 | 99742409 | 49889259 | 36774690 | 0.000000 | 0.000000 | 278713531
09-04-2025 22:18:10.000 | 67790992 |  | 67.791 | -4920327 | 15615450 | 25133162 | 99737640 | 49889088 | 35838318 | 0.000000 | 0.000000 | 271989288
09-04-2025 22:18:05.000 | 68419281 |  | 68.4193 | -4619368 | 15611438 | 25363174 | 99772858 | 49865120 | 34892805 | 0.000000 | 0.000000 | 265392700
09-04-2025 22:18:00.000 | 68461508 |  | 68.4615 | -4669154 | 15611572 | 25379595 | 99768242 | 49873993 | 33939692 | 0.000000 | 0.000000 | 259055908
09-04-2025 22:17:55.000 | 68755594 |  | 68.7556 | -4672626 | 15612012 | 25487400 | 99769867 | 49862667 | 32988569 | 0.000000 | 0.000000 | 252525513
09-04-2025 22:17:50.000 | 68589234 |  | 68.5892 | -4562861 | 15612929 | 25422009 | 99779457 | 49870785 | 32033147 | 0.000000 | 0.000000 | 246153168
09-04-2025 22:17:45.000 | 68663156 |  | 68.6632 | -4730171 | 15614216 | 25451030 | 99763550 | 49875610 | 31080146 | 0.000000 | 0.000000 | 239665787
09-04-2025 22:17:40.000 | 69416977 |  | 69.417 | -4784115 | 15609251 | 25738979 | 99763351 | 49877911 | 30120527 | 0.000000 | 0.000000 | 233109177
09-04-2025 22:17:35.000 | 68808234 |  | 68.8082 | -4856243 | 15609829 | 25514998 | 99751877 | 49893623 | 29156719 | 0.000000 | 0.000000 | 226416412
09-04-2025 22:17:30.000 | 68566305 |  | 68.5663 | -5045879 | 15610651 | 25429658 | 99730309 | 49898991 | 28202532 | 0.000000 | 0.000000 | 219553894
09-04-2025 22:17:25.000 | 68596602 |  | 68.5966 | -4943298 | 15609320 | 25439978 | 99741348 | 49892586 | 27249136 | 0.000000 | 0.000000 | 212502441
09-04-2025 22:17:20.000 | 68055773 |  | 68.0558 | -5123676 | 15609347 | 25245623 | 99717796 | 49911327 | 26298892 | 0.000000 | 0.000000 | 205527954
09-04-2025 22:17:15.000 | 66903945 |  | 66.9039 | -5129346 | 15613106 | 24815256 | 99707397 | 49928074 | 25362131 | 0.000000 | 0.000000 | 198423965
09-04-2025 22:17:10.000 | 66315078 |  | 66.3151 | -5244609 | 15613932 | 24600088 | 99688728 | 49927032 | 24437119 | 0.000000 | 0.000000 | 191283264
09-04-2025 22:17:05.000 | 67273828 |  | 67.2738 | -5057126 | 15613205 | 24948923 | 99718651 | 49909416 | 23510417 | 0.000000 | 0.000000 | 184070404
09-04-2025 22:17:00.000 | 66724117 |  | 66.7241 | -4971147 | 15613104 | 24744028 | 99723618 | 49915596 | 22580139 | 0.000000 | 0.000000 | 177063568
09-04-2025 22:16:55.000 | 67252023 |  | 67.252 | -5334970 | 15612678 | 24950637 | 99686829 | 49910023 | 21651768 | 0.000000 | 0.000000 | 169988312
09-04-2025 22:16:50.000 | 68048641 |  | 68.0486 | -5081597 | 15609053 | 25242305 | 99722336 | 49885044 | 20711694 | 0.000000 | 0.000000 | 162703476
09-04-2025 22:16:45.000 | 67462625 |  | 67.4626 | -5040030 | 15610545 | 25022739 | 99722092 | 49900951 | 19768896 | 0.000000 | 0.000000 | 155621613
09-04-2025 22:16:40.000 | 67022508 |  | 67.0225 | -5083214 | 15613820 | 24857036 | 99713623 | 49913898 | 18836354 | 0.000000 | 0.000000 | 148608704
09-04-2025 22:16:35.000 | 67399727 |  | 67.3997 | -5092645 | 15615673 | 24993486 | 99715759 | 49912125 | 17906091 | 0.000000 | 0.000000 | 141455826
09-04-2025 22:16:30.000 | 67102539 |  | 67.1025 | -5057422 | 15616642 | 24880793 | 99717186 | 49919579 | 16971453 | 0.000000 | 0.000000 | 134500198
09-04-2025 22:16:25.000 | 68653500 |  | 68.6535 | -5170796 | 15613339 | 25460659 | 99717567 | 49887260 | 16033804 | 0.000000 | 0.000000 | 127323212
09-04-2025 22:16:20.000 | 69668594 |  | 69.6686 | -5233750 | 15609563 | 25842869 | 99719009 | 49866871 | 15071741 | 0.000000 | 0.000000 | 120167595
09-04-2025 22:16:15.000 | 68767961 |  | 68.768 | -5243559 | 15607744 | 25514536 | 99710556 | 49899128 | 14104670 | 0.000000 | 0.000000 | 113045006
09-04-2025 22:16:10.000 | 67074648 |  | 67.0746 | -5198128 | 15611859 | 24882200 | 99701050 | 49933449 | 13157778 | 0.000000 | 0.000000 | 105826408
09-04-2025 22:16:05.000 | 67117102 |  | 67.1171 | -5379945 | 15614002 | 24899231 | 99680275 | 49944382 | 12226639 | 0.000000 | 0.000000 | 98550674
09-04-2025 22:16:00.000 | 68146063 |  | 68.1461 | -5395448 | 15614284 | 25278772 | 99688034 | 49922909 | 11289502 | 0.000000 | 0.000000 | 91042793
09-04-2025 22:15:55.000 | 68378266 |  | 68.3783 | -5425426 | 15612767 | 25367424 | 99686699 | 49912861 | 10340381 | 0.000000 | 0.000000 | 83593941
09-04-2025 22:15:50.000 | 68549375 |  | 68.5494 | -5675087 | 15609780 | 25442998 | 99659058 | 49910076 | 938805664 | 0.000000 | 0.000000 | 75948090
09-04-2025 22:15:45.000 | 68410492 |  | 68.4105 | -5541816 | 15609595 | 25388552 | 99673492 | 49919704 | 843373352 | 0.000000 | 0.000000 | 68227089
09-04-2025 22:15:40.000 | 68070938 |  | 68.0709 | -5605560 | 15611141 | 25262129 | 99662651 | 49925365 | 748812927 | 0.000000 | 0.000000 | 60425251
09-04-2025 22:15:35.000 | 67566852 |  | 67.5669 | -5531358 | 15610641 | 25075276 | 99666580 | 49929428 | 654351074 | 0.000000 | 0.000000 | 52687111
09-04-2025 22:15:30.000 | 66720070 |  | 66.7201 | -5479062 | 15612846 | 24757891 | 99664513 | 49945869 | 561108704 | 0.000000 | 0.000000 | 45071655
09-04-2025 22:15:25.000 | 66364414 |  | 66.3644 | -5440326 | 15615229 | 24622175 | 99665680 | 49949570 | 468938080 | 0.000000 | 0.000000 | 37532459
09-04-2025 22:15:20.000 | 67129281 |  | 67.1293 | -5440587 | 15612978 | 24907378 | 99673180 | 49933746 | 376390778 | 0.000000 | 0.000000 | 29874277
09-04-2025 22:15:15.000 | 66973711 |  | 66.9737 | -5350391 | 15614096 | 24845352 | 99682419 | 49933937 | 282953247 | 0.000000 | 0.000000 | 22371170
09-04-2025 22:15:10.000 | 67336602 |  | 67.3366 | -5391037 | 15617147 | 24975625 | 99681046 | 49932735 | 189848984 | 0.000000 | 0.000000 | 14911353
09-04-2025 22:15:05.000 | 68730008 |  | 68.73 | -5385507 | 15613707 | 25494429 | 99694412 | 49908108 | 95698822 | 0.000000 | 0.000000 | 7371476
09-04-2025 22:15:00.000 | 69182383 |  | 69.1824 | -5328170 | 15609982 | 25665591 | 99704735 | 49907318 | 16996998 | 0.000000 | 0.000000 | 14238475
09-04-2025 22:14:55.000 | 68649086 |  | 68.6491 | -5555506 | 15610016 | 25476448 | 99674149 | 49929775 | 16901064 | 0.000000 | 0.000000 | 14164033
09-04-2025 22:14:50.000 | 69074500 |  | 69.0745 | -5627001 | 15609962 | 25634500 | 99669830 | 49929192 | 16805371 | 0.000000 | 0.000000 | 14085870
09-04-2025 22:14:45.000 | 68362445 |  | 68.3624 | -5618333 | 15608059 | 25374944 | 99663986 | 49946617 | 16709533 | 0.000000 | 0.000000 | 14008134
09-04-2025 22:14:40.000 | 67251609 |  | 67.2516 | -5751641 | 15611080 | 24965256 | 99636276 | 49965065 | 16614914 | 0.000000 | 0.000000 | 13928519
09-04-2025 22:14:35.000 | 66445672 |  | 66.4457 | -5780329 | 15613423 | 24665068 | 99623741 | 49982365 | 16521816 | 0.000000 | 0.000000 | 13848792
09-04-2025 22:14:30.000 | 66557656 |  | 66.5577 | -5686207 | 15613497 | 24703274 | 99637047 | 49971848 | 16429674 | 0.000000 | 0.000000 | 13769541
09-04-2025 22:14:25.000 | 66540195 |  | 66.5402 | -5449325 | 15615148 | 24687256 | 99666336 | 49956856 | 16337162 | 0.000000 | 0.000000 | 13691492
09-04-2025 22:14:20.000 | 66870539 |  | 66.8705 | -5419951 | 15615165 | 24809287 | 99673141 | 49947239 | 16244846 | 0.000000 | 0.000000 | 13616136
09-04-2025 22:14:15.000 | 68087320 |  | 68.0873 | -5413008 | 15612411 | 25260532 | 99685471 | 49918098 | 16151696 | 0.000000 | 0.000000 | 13539899
09-04-2025 22:14:10.000 | 67968266 |  | 67.9683 | -5386448 | 15610441 | 25219429 | 99687447 | 49916595 | 16056885 | 0.000000 | 0.000000 | 13464755
09-04-2025 22:14:05.000 | 67330039 |  | 67.33 | -5366254 | 15612755 | 24979419 | 99683891 | 49928890 | 15962840 | 0.000000 | 0.000000 | 13390398
09-04-2025 22:14:00.000 | 67658070 |  | 67.6581 | -5200079 | 15614471 | 25093806 | 99705940 | 49931969 | 15869248 | 0.000000 | 0.000000 | 13315006
09-04-2025 22:13:55.000 | 67638727 |  | 67.6387 | -5356308 | 15616993 | 25086494 | 99687912 | 49932594 | 15775337 | 0.000000 | 0.000000 | 13242013
09-04-2025 22:13:50.000 | 68786594 |  | 68.7866 | -5410027 | 15613987 | 25515811 | 99692139 | 49914055 | 15680702 | 0.000000 | 0.000000 | 13167732
09-04-2025 22:13:45.000 | 70067094 |  | 70.0671 | -5440610 | 15610772 | 25994104 | 99699890 | 49895851 | 15584318 | 0.000000 | 0.000000 | 13092062
09-04-2025 22:13:40.000 | 69675094 |  | 69.6751 | -5379403 | 15604660 | 25858743 | 99703278 | 49908569 | 15486916 | 0.000000 | 0.000000 | 13017157
09-04-2025 22:13:35.000 | 68240195 |  | 68.2402 | -5605019 | 15611301 | 25325464 | 99664375 | 49957436 | 15390883 | 0.000000 | 0.000000 | 12940957
09-04-2025 22:13:30.000 | 67810703 |  | 67.8107 | -5539295 | 15614931 | 25158076 | 99668015 | 49969975 | 15296680 | 0.000000 | 0.000000 | 12862609
09-04-2025 22:13:25.000 | 67976820 |  | 67.9768 | -5370265 | 15613256 | 25216899 | 99689392 | 49962189 | 15202365 | 0.000000 | 0.000000 | 12787124
09-04-2025 22:13:20.000 | 68208523 |  | 68.2085 | -5436632 | 15611484 | 25307693 | 99683853 | 49954182 | 15108060 | 0.000000 | 0.000000 | 12711357
09-04-2025 22:13:15.000 | 68442609 |  | 68.4426 | -5700598 | 15611631 | 25401189 | 99654930 | 49944862 | 15013285 | 0.000000 | 0.000000 | 12634167
09-04-2025 22:13:10.000 | 68070969 |  | 68.071 | -5471480 | 15610571 | 25259187 | 99678520 | 49952572 | 14918199 | 0.000000 | 0.000000 | 12557169
09-04-2025 22:13:05.000 | 67532828 |  | 67.5328 | -5324118 | 15613057 | 25053401 | 99690674 | 49977749 | 14823835 | 0.000000 | 0.000000 | 12482555
09-04-2025 22:13:00.000 | 67213352 |  | 67.2134 | -5611532 | 15615796 | 24939109 | 99653297 | 49972534 | 14730536 | 0.000000 | 0.000000 | 12406384
09-04-2025 22:12:55.000 | 67991266 |  | 67.9913 | -5541410 | 15614349 | 25225698 | 99669518 | 49956463 | 14636651 | 0.000000 | 0.000000 | 12329153
09-04-2025 22:12:50.000 | 68365984 |  | 68.366 | -5357272 | 15615320 | 25356853 | 99694382 | 49951866 | 14541854 | 0.000000 | 0.000000 | 12252511
09-04-2025 22:12:45.000 | 68352172 |  | 68.3522 | -5560245 | 15615486 | 25357280 | 99670769 | 49963936 | 14446897 | 0.000000 | 0.000000 | 12178805
09-04-2025 22:12:40.000 | 70081016 |  | 70.081 | -5442793 | 15608849 | 26002012 | 99699768 | 49939014 | 14351026 | 0.000000 | 0.000000 | 12102136
09-04-2025 22:12:35.000 | 69911453 |  | 69.9115 | -5429791 | 15604266 | 25946978 | 99699753 | 49942791 | 14253808 | 0.000000 | 0.000000 | 12025969
09-04-2025 22:12:30.000 | 67605945 |  | 67.6059 | -5572271 | 15607798 | 25095115 | 99662048 | 49987217 | 14157922 | 0.000000 | 0.000000 | 11949319
09-04-2025 22:12:25.000 | 66030086 |  | 66.0301 | -5508517 | 15612798 | 24504783 | 99653824 | 50011047 | 14064937 | 0.000000 | 0.000000 | 11871818
09-04-2025 22:12:20.000 | 65233184 |  | 65.2332 | -5579581 | 15615557 | 24208652 | 99636200 | 50018272 | 13973929 | 0.000000 | 0.000000 | 11795579
09-04-2025 22:12:15.000 | 65924391 |  | 65.9244 | -6037642 | 15616946 | 24476123 | 99583237 | 49998821 | 13883063 | 0.000000 | 0.000000 | 11715654
09-04-2025 22:12:10.000 | 67962820 |  | 67.9628 | -6319263 | 15619295 | 25232148 | 99570511 | 49959354 | 13790521 | 0.000000 | 0.000000 | 11629653
09-04-2025 22:12:05.000 | 68804445 |  | 68.8044 | -5442317 | 15610514 | 25528516 | 99688629 | 49944271 | 13695763 | 0.000000 | 0.000000 | 11548682
09-04-2025 22:12:00.000 | 68945938 |  | 68.9459 | -5612152 | 15611227 | 25584766 | 99670341 | 49950050 | 13599965 | 0.000000 | 0.000000 | 11471749
09-04-2025 22:11:55.000 | 68893141 |  | 68.8931 | -5421449 | 15610507 | 25560989 | 99691795 | 49947384 | 13504231 | 0.000000 | 0.000000 | 11394714
09-04-2025 22:11:50.000 | 68249484 |  | 68.2495 | -5553699 | 15611744 | 25325540 | 99670555 | 49955574 | 13409054 | 0.000000 | 0.000000 | 11318126
09-04-2025 22:11:45.000 | 68136414 |  | 68.1364 | -5520726 | 15611896 | 25282847 | 99673355 | 49965160 | 13314291 | 0.000000 | 0.000000 | 11241235
09-04-2025 22:11:40.000 | 67601461 |  | 67.6015 | -5514320 | 15611319 | 25086472 | 99668961 | 49971046 | 13219909 | 0.000000 | 0.000000 | 11165173
09-04-2025 22:11:35.000 | 68285328 |  | 68.2853 | -5774201 | 15612254 | 25344392 | 99644386 | 49962936 | 13125396 | 0.000000 | 0.000000 | 11086467
09-04-2025 22:11:30.000 | 68545242 |  | 68.5452 | -5936245 | 15610762 | 25447908 | 99627090 | 49953762 | 13030449 | 0.000000 | 0.000000 | 11005459
09-04-2025 22:11:25.000 | 68340359 |  | 68.3404 | -5925419 | 15612811 | 25368723 | 99626221 | 49960068 | 12935160 | 0.000000 | 0.000000 | 10923932
09-04-2025 22:11:20.000 | 68274422 |  | 68.2744 | -5790265 | 15611021 | 25343755 | 99642303 | 49962353 | 12840229 | 0.000000 | 0.000000 | 10842148
09-04-2025 22:11:15.000 | 67678461 |  | 67.6785 | -5645591 | 15613816 | 25114470 | 99653877 | 49979958 | 12745674 | 0.000000 | 0.000000 | 10762389
09-04-2025 22:11:10.000 | 67022938 |  | 67.0229 | -5813641 | 15617228 | 24872573 | 99625908 | 50010181 | 12652192 | 0.000000 | 0.000000 | 10683738
09-04-2025 22:11:05.000 | 68424492 |  | 68.4245 | -5840675 | 15617867 | 25388777 | 99637665 | 49976967 | 12558631 | 0.000000 | 0.000000 | 10602023
09-04-2025 22:11:00.000 | 70107203 |  | 70.1072 | -5705081 | 15612177 | 26014023 | 99670532 | 49956776 | 12462396 | 0.000000 | 0.000000 | 10521954
09-04-2025 22:10:55.000 | 70429188 |  | 70.4292 | -5702601 | 15610069 | 26136011 | 99673805 | 49949337 | 12364819 | 0.000000 | 0.000000 | 10442242
09-04-2025 22:10:50.000 | 70489086 |  | 70.4891 | -5776522 | 15610241 | 26161401 | 99665901 | 49970886 | 12266801 | 0.000000 | 0.000000 | 10362968
09-04-2025 22:10:45.000 | 70043344 |  | 70.0433 | -6103755 | 15608944 | 26008262 | 99622459 | 49984589 | 12169307 | 0.000000 | 0.000000 | 10279917
09-04-2025 22:10:40.000 | 69155711 |  | 69.1557 | -6076617 | 15608582 | 25681843 | 99616173 | 50016846 | 12072297 | 0.000000 | 0.000000 | 10195952
09-04-2025 22:10:35.000 | 68120023 |  | 68.12 | -6269282 | 15614073 | 25296724 | 99579170 | 50039368 | 11976969 | 0.000000 | 0.000000 | 10110742
09-04-2025 22:10:30.000 | 67899828 |  | 67.8998 | -6126606 | 15613639 | 25211409 | 99595398 | 50043491 | 11882326 | 0.000000 | 0.000000 | 10025117
09-04-2025 22:10:25.000 | 68030023 |  | 68.03 | -6290231 | 15613104 | 25266907 | 99575256 | 50046860 | 11787706 | 0.000000 | 0.000000 | 993982971
09-04-2025 22:10:20.000 | 68839070 |  | 68.8391 | -6125371 | 15612528 | 25559111 | 99606453 | 50032619 | 11692738 | 0.000000 | 0.000000 | 985276489
09-04-2025 22:10:15.000 | 68547930 |  | 68.5479 | -6115441 | 15614209 | 25448975 | 99604401 | 50037510 | 11597377 | 0.000000 | 0.000000 | 976761169
09-04-2025 22:10:10.000 | 68982188 |  | 68.9822 | -6258338 | 15612424 | 25616646 | 99590981 | 50028610 | 11502232 | 0.000000 | 0.000000 | 968227356
09-04-2025 22:10:05.000 | 69422469 |  | 69.4225 | -6363704 | 15608650 | 25788650 | 99582497 | 50029972 | 11405919 | 0.000000 | 0.000000 | 959524658
09-04-2025 22:10:00.000 | 69239102 |  | 69.2391 | -6447121 | 15608595 | 25724143 | 99569290 | 50055363 | 11309648 | 0.000000 | 0.000000 | 950628540
09-04-2025 22:09:55.000 | 67527156 |  | 67.5272 | -6634917 | 15611895 | 25095063 | 99520760 | 50084606 | 11214412 | 0.000000 | 0.000000 | 941621887
09-04-2025 22:09:50.000 | 67474078 |  | 67.4741 | -6513482 | 15612762 | 25070852 | 99537300 | 50086205 | 11120853 | 0.000000 | 0.000000 | 932414978
09-04-2025 22:09:45.000 | 67665391 |  | 67.6654 | -6541926 | 15611555 | 25142961 | 99535896 | 50083603 | 11027088 | 0.000000 | 0.000000 | 923358582
09-04-2025 22:09:40.000 | 67345672 |  | 67.3457 | -6132854 | 15611587 | 25011047 | 99587914 | 50079819 | 10933170 | 0.000000 | 0.000000 | 914487671
09-04-2025 22:09:35.000 | 66448938 |  | 66.4489 | -6276926 | 15613624 | 24682446 | 99556808 | 50114418 | 10839992 | 0.000000 | 0.000000 | 906026367
09-04-2025 22:09:30.000 | 67016875 |  | 67.0169 | -6072813 | 15613345 | 24885295 | 99591949 | 50095673 | 10747767 | 0.000000 | 0.000000 | 897362732
09-04-2025 22:09:25.000 | 67441195 |  | 67.4412 | -5946933 | 15613357 | 25038389 | 99613472 | 50096863 | 10654728 | 0.000000 | 0.000000 | 888907104
09-04-2025 22:09:20.000 | 67145602 |  | 67.1456 | -6073771 | 15615963 | 24928674 | 99593376 | 50091877 | 10561408 | 0.000000 | 0.000000 | 880477295
09-04-2025 22:09:15.000 | 68289492 |  | 68.2895 | -5993542 | 15613158 | 25351692 | 99617058 | 50081890 | 10467472 | 0.000000 | 0.000000 | 872075195
09-04-2025 22:09:10.000 | 69073242 |  | 69.0732 | -5940707 | 15611210 | 25642126 | 99632187 | 50071869 | 10372375 | 0.000000 | 0.000000 | 863760498
09-04-2025 22:09:05.000 | 68378469 |  | 68.3785 | -6039154 | 15610692 | 25389680 | 99612251 | 50087048 | 10276790 | 0.000000 | 0.000000 | 855489868
09-04-2025 22:09:00.000 | 68456578 |  | 68.4566 | -5984408 | 15612738 | 25413772 | 99620071 | 50086880 | 10181696 | 0.000000 | 0.000000 | 847180664
09-04-2025 22:08:55.000 | 68349016 |  | 68.349 | -6140626 | 15612928 | 25378547 | 99598846 | 50081722 | 10086562 | 0.000000 | 0.000000 | 838817322
09-04-2025 22:08:50.000 | 68761156 |  | 68.7612 | -5732096 | 15612227 | 25518579 | 99654335 | 50081688 | 99910869 | 0.000000 | 0.000000 | 830588684
09-04-2025 22:08:45.000 | 68148250 |  | 68.1483 | -5840967 | 15614406 | 25292781 | 99634705 | 50093044 | 98960840 | 0.000000 | 0.000000 | 822541931
09-04-2025 22:08:40.000 | 68706875 |  | 68.7069 | -5774607 | 15611439 | 25501323 | 99648666 | 50084023 | 98012520 | 0.000000 | 0.000000 | 814459778
09-04-2025 22:08:35.000 | 68718227 |  | 68.7182 | -5759739 | 15612422 | 25503269 | 99650574 | 50081451 | 97059092 | 0.000000 | 0.000000 | 806416443
09-04-2025 22:08:30.000 | 68352531 |  | 68.3525 | -5805454 | 15610593 | 25373894 | 99641251 | 50080864 | 96105801 | 0.000000 | 0.000000 | 798306274
09-04-2025 22:08:25.000 | 67914328 |  | 67.9143 | -5750083 | 15615143 | 25202351 | 99643494 | 50097469 | 95154609 | 0.000000 | 0.000000 | 790406311
09-04-2025 22:08:20.000 | 68893242 |  | 68.8932 | -5923180 | 15613567 | 25570964 | 99632439 | 50084888 | 94206816 | 0.000000 | 0.000000 | 782314941
09-04-2025 22:08:15.000 | 69352406 |  | 69.3524 | -5861716 | 15609533 | 25744731 | 99644714 | 50084923 | 93245693 | 0.000000 | 0.000000 | 774122742
09-04-2025 22:08:10.000 | 68709672 |  | 68.7097 | -6083040 | 15610160 | 25514241 | 99610390 | 50106812 | 92283203 | 0.000000 | 0.000000 | 765982117
09-04-2025 22:08:05.000 | 68436977 |  | 68.437 | -5955947 | 15609188 | 25411594 | 99623444 | 50112820 | 91328398 | 0.000000 | 0.000000 | 757624878
09-04-2025 22:08:00.000 | 67238883 |  | 67.2389 | -6071389 | 15611194 | 24970288 | 99594810 | 50136013 | 90384805 | 0.000000 | 0.000000 | 749363770
09-04-2025 22:07:55.000 | 66035867 |  | 66.0359 | -6124579 | 15615132 | 24522988 | 99572662 | 50151321 | 89456523 | 0.000000 | 0.000000 | 741013489
09-04-2025 22:07:50.000 | 66731883 |  | 66.7319 | -5970001 | 15615401 | 24773564 | 99602211 | 50140503 | 88532861 | 0.000000 | 0.000000 | 732595520
09-04-2025 22:07:45.000 | 68145156 |  | 68.1452 | -5881521 | 15613924 | 25293601 | 99629608 | 50117310 | 87599209 | 0.000000 | 0.000000 | 724291809
09-04-2025 22:07:40.000 | 68195984 |  | 68.196 | -5990652 | 15615097 | 25314226 | 99616386 | 50115402 | 86653857 | 0.000000 | 0.000000 | 716140137
09-04-2025 22:07:35.000 | 69204852 |  | 69.2049 | -6045568 | 15610585 | 25695017 | 99620605 | 50099880 | 85700723 | 0.000000 | 0.000000 | 707740051
09-04-2025 22:07:30.000 | 69163469 |  | 69.1635 | -5957986 | 15609327 | 25679058 | 99631020 | 50111248 | 84737813 | 0.000000 | 0.000000 | 699392517
09-04-2025 22:07:25.000 | 68227000 |  | 68.227 | -5787371 | 15609533 | 25327751 | 99642166 | 50140572 | 83781758 | 0.000000 | 0.000000 | 691129883
09-04-2025 22:07:20.000 | 67598656 |  | 67.5987 | -6118264 | 15612425 | 25102427 | 99592911 | 50150837 | 82841455 | 0.000000 | 0.000000 | 682750671
09-04-2025 22:07:15.000 | 68118258 |  | 68.1183 | -6082955 | 15612853 | 25292117 | 99603645 | 50139603 | 81899214 | 0.000000 | 0.000000 | 674193542
09-04-2025 22:07:10.000 | 68109156 |  | 68.1092 | -5994858 | 15612636 | 25286685 | 99614876 | 50143486 | 80951230 | 0.000000 | 0.000000 | 665797668
09-04-2025 22:07:05.000 | 68579414 |  | 68.5794 | -6215629 | 15612877 | 25466194 | 99591789 | 50137222 | 80005781 | 0.000000 | 0.000000 | 657269226
09-04-2025 22:07:00.000 | 68910828 |  | 68.9108 | -5935949 | 15610289 | 25583496 | 99631050 | 50121235 | 79053242 | 0.000000 | 0.000000 | 648764587
09-04-2025 22:06:55.000 | 67741828 |  | 67.7418 | -6068303 | 15613989 | 25151106 | 99601173 | 50148972 | 78101738 | 0.000000 | 0.000000 | 640526245
09-04-2025 22:06:50.000 | 68449070 |  | 68.4491 | -5941640 | 15612658 | 25409334 | 99625374 | 50139668 | 77158828 | 0.000000 | 0.000000 | 632142517
09-04-2025 22:06:45.000 | 68552523 |  | 68.5525 | -5945651 | 15613423 | 25448101 | 99625992 | 50136814 | 76209502 | 0.000000 | 0.000000 | 623891785
09-04-2025 22:06:40.000 | 69186797 |  | 69.1868 | -5973758 | 15611262 | 25685315 | 99629318 | 50130428 | 75253413 | 0.000000 | 0.000000 | 615569153
09-04-2025 22:06:35.000 | 68853750 |  | 68.8538 | -5981813 | 15611045 | 25563105 | 99624741 | 50158791 | 74293398 | 0.000000 | 0.000000 | 607283691
09-04-2025 22:06:30.000 | 69259789 |  | 69.2598 | -6169998 | 15610572 | 25718777 | 99605537 | 50148167 | 73339995 | 0.000000 | 0.000000 | 598697083
09-04-2025 22:06:25.000 | 68751898 |  | 68.7519 | -5983453 | 15609191 | 25528096 | 99623428 | 50153809 | 72381392 | 0.000000 | 0.000000 | 590191284
09-04-2025 22:06:20.000 | 67953141 |  | 67.9531 | -6182111 | 15612500 | 25234868 | 99588722 | 50167282 | 71431362 | 0.000000 | 0.000000 | 581710632
09-04-2025 22:06:15.000 | 67775180 |  | 67.7752 | -5978447 | 15614248 | 25159705 | 99613205 | 50179432 | 70487192 | 0.000000 | 0.000000 | 573311279
09-04-2025 22:06:10.000 | 68043625 |  | 68.0436 | -6014594 | 15612450 | 25264041 | 99611610 | 50165211 | 69544336 | 0.000000 | 0.000000 | 564929138
09-04-2025 22:06:05.000 | 68155625 |  | 68.1556 | -5726683 | 15611485 | 25296948 | 99648857 | 50169579 | 68597119 | 0.000000 | 0.000000 | 556713989
09-04-2025 22:06:00.000 | 67614102 |  | 67.6141 | -5959285 | 15614676 | 25098999 | 99613846 | 50184387 | 67656318 | 0.000000 | 0.000000 | 548647888
09-04-2025 22:05:55.000 | 68486328 |  | 68.4863 | -6142113 | 15611784 | 25431580 | 99600250 | 50162376 | 66713789 | 0.000000 | 0.000000 | 540267700
09-04-2025 22:05:50.000 | 68834766 |  | 68.8348 | -6124867 | 15607379 | 25566243 | 99606468 | 50148445 | 65759937 | 0.000000 | 0.000000 | 531760559
09-04-2025 22:05:45.000 | 67982047 |  | 67.982 | -6102216 | 15609872 | 25247839 | 99599556 | 50160984 | 64805698 | 0.000000 | 0.000000 | 523160706
09-04-2025 22:05:40.000 | 66699938 |  | 66.6999 | -5979304 | 15611433 | 24768882 | 99600594 | 50192215 | 63866890 | 0.000000 | 0.000000 | 514861450
09-04-2025 22:05:35.000 | 66143141 |  | 66.1431 | -6068802 | 15615896 | 24560288 | 99581711 | 50195190 | 62948428 | 0.000000 | 0.000000 | 506419708
09-04-2025 22:05:30.000 | 67320219 |  | 67.3202 | -5833998 | 15614415 | 24987405 | 99626602 | 50172478 | 62024565 | 0.000000 | 0.000000 | 498016418
09-04-2025 22:05:25.000 | 67164047 |  | 67.164 | -5670733 | 15614741 | 24923928 | 99645462 | 50172634 | 61092710 | 0.000000 | 0.000000 | 490012482
09-04-2025 22:05:20.000 | 66928531 |  | 66.9285 | -5705438 | 15613424 | 24840959 | 99638618 | 50178841 | 60161631 | 0.000000 | 0.000000 | 482123383
09-04-2025 22:05:15.000 | 67034977 |  | 67.035 | -5778173 | 15613228 | 24882666 | 99630569 | 50172756 | 59232373 | 0.000000 | 0.000000 | 474153503
09-04-2025 22:05:10.000 | 67127031 |  | 67.127 | -5857100 | 15614540 | 24916543 | 99621498 | 50175182 | 58301211 | 0.000000 | 0.000000 | 466089355
09-04-2025 22:05:05.000 | 67288523 |  | 67.2885 | -5755744 | 15612698 | 24976130 | 99636154 | 50171482 | 57366245 | 0.000000 | 0.000000 | 458035187
09-04-2025 22:05:00.000 | 67901367 |  | 67.9014 | -5850212 | 15612387 | 25205007 | 99630898 | 50162273 | 56428472 | 0.000000 | 0.000000 | 449973480
09-04-2025 22:04:55.000 | 68808000 |  | 68.808 | -5776940 | 15611394 | 25539067 | 99649406 | 50140926 | 55481079 | 0.000000 | 0.000000 | 441766998
09-04-2025 22:04:50.000 | 68582844 |  | 68.5828 | -5601924 | 15609737 | 25452800 | 99668068 | 50144321 | 54526714 | 0.000000 | 0.000000 | 433890137
09-04-2025 22:04:45.000 | 67530398 |  | 67.5304 | -5748892 | 15613804 | 25063137 | 99639595 | 50162193 | 53579507 | 0.000000 | 0.000000 | 426016632
09-04-2025 22:04:40.000 | 68369594 |  | 68.3696 | -5900964 | 15613997 | 25377021 | 99629601 | 50156403 | 52637168 | 0.000000 | 0.000000 | 417917603
09-04-2025 22:04:35.000 | 68765852 |  | 68.7659 | -6031504 | 15610994 | 25532102 | 99617546 | 50141525 | 51686030 | 0.000000 | 0.000000 | 409593933
09-04-2025 22:04:30.000 | 68551180 |  | 68.5512 | -5877895 | 15608817 | 25451199 | 99634407 | 50147133 | 50731567 | 0.000000 | 0.000000 | 401317078
09-04-2025 22:04:25.000 | 67105914 |  | 67.1059 | -5915886 | 15611724 | 24915530 | 99613663 | 50172035 | 49788564 | 0.000000 | 0.000000 | 393144989
09-04-2025 22:04:20.000 | 66721820 |  | 66.7218 | -5850930 | 15613132 | 24771687 | 99617714 | 50181080 | 48857119 | 0.000000 | 0.000000 | 384924957
09-04-2025 22:04:15.000 | 66864539 |  | 66.8645 | -5852729 | 15612931 | 24823215 | 99619102 | 50176033 | 47930591 | 0.000000 | 0.000000 | 376733826
09-04-2025 22:04:10.000 | 66715625 |  | 66.7156 | -5589198 | 15610694 | 24762952 | 99650909 | 50166744 | 47000864 | 0.000000 | 0.000000 | 368710358
09-04-2025 22:04:05.000 | 66102984 |  | 66.103 | -5926220 | 15610664 | 24547886 | 99600540 | 50170746 | 46077534 | 0.000000 | 0.000000 | 360747345
09-04-2025 22:04:00.000 | 65803273 |  | 65.8033 | -5946720 | 15615966 | 24429807 | 99594139 | 50170349 | 45162446 | 0.000000 | 0.000000 | 352391602
09-04-2025 22:03:55.000 | 66538039 |  | 66.538 | -5618453 | 15616874 | 24688423 | 99645393 | 50150463 | 44248755 | 0.000000 | 0.000000 | 344164154
09-04-2025 22:03:50.000 | 67639008 |  | 67.639 | -5584301 | 15614676 | 25096619 | 99660919 | 50122330 | 43318306 | 0.000000 | 0.000000 | 336352448
09-04-2025 22:03:45.000 | 68121570 |  | 68.1216 | -5485956 | 15612392 | 25275220 | 99677299 | 50114014 | 42373584 | 0.000000 | 0.000000 | 328702087
09-04-2025 22:03:40.000 | 67591797 |  | 67.5918 | -5320766 | 15611812 | 25076072 | 99691597 | 50118942 | 41428696 | 0.000000 | 0.000000 | 321244629
09-04-2025 22:03:35.000 | 67741266 |  | 67.7413 | -5625739 | 15613356 | 25138328 | 99656929 | 50120892 | 40488611 | 0.000000 | 0.000000 | 313640991
09-04-2025 22:03:30.000 | 67911711 |  | 67.9117 | -5459282 | 15613276 | 25195864 | 99678444 | 50117908 | 39546477 | 0.000000 | 0.000000 | 305942047
09-04-2025 22:03:25.000 | 67885930 |  | 67.8859 | -5559545 | 15614543 | 25186938 | 99666336 | 50119892 | 38602429 | 0.000000 | 0.000000 | 298441254
09-04-2025 22:03:20.000 | 69084523 |  | 69.0845 | -5427090 | 15610875 | 25631162 | 99692856 | 50113743 | 37653062 | 0.000000 | 0.000000 | 290795227
09-04-2025 22:03:15.000 | 68688711 |  | 68.6887 | -5384666 | 15611860 | 25482942 | 99694138 | 50109970 | 36696733 | 0.000000 | 0.000000 | 283186066
09-04-2025 22:03:10.000 | 68607391 |  | 68.6074 | -5252256 | 15612104 | 25448074 | 99708244 | 50124271 | 35744221 | 0.000000 | 0.000000 | 275768555
09-04-2025 22:03:05.000 | 68806344 |  | 68.8063 | -5494155 | 15610462 | 25531089 | 99682716 | 50111698 | 34793711 | 0.000000 | 0.000000 | 268242188
09-04-2025 22:03:00.000 | 68509102 |  | 68.5091 | -5345612 | 15608993 | 25420452 | 99696968 | 50113865 | 33836584 | 0.000000 | 0.000000 | 260663910
09-04-2025 22:02:55.000 | 68395719 |  | 68.3957 | -5520934 | 15610379 | 25381023 | 99675797 | 50129646 | 32889512 | 0.000000 | 0.000000 | 253157623
09-04-2025 22:02:50.000 | 67363250 |  | 67.3632 | -5569559 | 15609810 | 25002390 | 99659950 | 50133369 | 31947007 | 0.000000 | 0.000000 | 245492462
09-04-2025 22:02:45.000 | 67359383 |  | 67.3594 | -5418954 | 15611987 | 24993145 | 99677963 | 50141640 | 31009307 | 0.000000 | 0.000000 | 237800461
09-04-2025 22:02:40.000 | 66823234 |  | 66.8232 | -5546600 | 15613482 | 24797273 | 99657288 | 50153561 | 30079900 | 0.000000 | 0.000000 | 230187057
09-04-2025 22:02:35.000 | 66966016 |  | 66.966 | -5582755 | 15616269 | 24845818 | 99654297 | 50143723 | 29151868 | 0.000000 | 0.000000 | 222442368
09-04-2025 22:02:30.000 | 67588578 |  | 67.5886 | -5135846 | 15613522 | 25066824 | 99712547 | 50137634 | 28216423 | 0.000000 | 0.000000 | 214985153
09-04-2025 22:02:25.000 | 67520578 |  | 67.5206 | -5374419 | 15615254 | 25045537 | 99684715 | 50146950 | 27280112 | 0.000000 | 0.000000 | 207659210
09-04-2025 22:02:20.000 | 68702109 |  | 68.7021 | -5290732 | 15612939 | 25483052 | 99704788 | 50117546 | 26337871 | 0.000000 | 0.000000 | 200093826
09-04-2025 22:02:15.000 | 68638336 |  | 68.6383 | -5272781 | 15613778 | 25457678 | 99706238 | 50119656 | 25385129 | 0.000000 | 0.000000 | 192721573
09-04-2025 22:02:10.000 | 69013375 |  | 69.0134 | -5203674 | 15613726 | 25594077 | 99716942 | 50118160 | 24433279 | 0.000000 | 0.000000 | 185338882
09-04-2025 22:02:05.000 | 68909297 |  | 68.9093 | -5310006 | 15609565 | 25564873 | 99704422 | 50129471 | 23474648 | 0.000000 | 0.000000 | 178145676
09-04-2025 22:02:00.000 | 68774414 |  | 68.7744 | -5363638 | 15608241 | 25519243 | 99697266 | 50141891 | 22516980 | 0.000000 | 0.000000 | 170731384
09-04-2025 22:01:55.000 | 67695523 |  | 67.6955 | -5402584 | 15609584 | 25120115 | 99683052 | 50154095 | 21570044 | 0.000000 | 0.000000 | 163151810
09-04-2025 22:01:50.000 | 66938734 |  | 66.9387 | -5417798 | 15612227 | 24837878 | 99674065 | 50175919 | 20635686 | 0.000000 | 0.000000 | 155707321
09-04-2025 22:01:45.000 | 66392609 |  | 66.3926 | -5728469 | 15612972 | 24644485 | 99629837 | 50184296 | 19712039 | 0.000000 | 0.000000 | 148064926
09-04-2025 22:01:40.000 | 67537586 |  | 67.5376 | -5998188 | 15614374 | 25072581 | 99607933 | 50152672 | 18785166 | 0.000000 | 0.000000 | 139845703
09-04-2025 22:01:35.000 | 67519563 |  | 67.5196 | -5476711 | 15610436 | 25056343 | 99672646 | 50153030 | 17842301 | 0.000000 | 0.000000 | 131991135
09-04-2025 22:01:30.000 | 67352820 |  | 67.3528 | -5465403 | 15612833 | 24990789 | 99672386 | 50157669 | 16906121 | 0.000000 | 0.000000 | 124317780
09-04-2025 22:01:25.000 | 67122445 |  | 67.1224 | -5474953 | 15613075 | 24905708 | 99668991 | 50167583 | 15972443 | 0.000000 | 0.000000 | 116738274
09-04-2025 22:01:20.000 | 67324047 |  | 67.324 | -5476250 | 15612854 | 24980151 | 99670807 | 50166676 | 15043330 | 0.000000 | 0.000000 | 109155884
09-04-2025 22:01:15.000 | 67280719 |  | 67.2807 | -5482427 | 15611126 | 24967063 | 99669647 | 50156460 | 14108579 | 0.000000 | 0.000000 | 101560898
09-04-2025 22:01:10.000 | 67232047 |  | 67.232 | -5372937 | 15610794 | 24946384 | 99682190 | 50151794 | 13171112 | 0.000000 | 0.000000 | 93994125
09-04-2025 22:01:05.000 | 66336711 |  | 66.3367 | -5189259 | 15614151 | 24606455 | 99695435 | 50171268 | 12239152 | 0.000000 | 0.000000 | 86613693
09-04-2025 22:01:00.000 | 65686742 |  | 65.6867 | -5245755 | 15618743 | 24360706 | 99682632 | 50177094 | 11322606 | 0.000000 | 0.000000 | 79345901
09-04-2025 22:00:55.000 | 67404953 |  | 67.405 | -5049482 | 15612785 | 24998088 | 99720581 | 50133778 | 10401788 | 0.000000 | 0.000000 | 72099556
09-04-2025 22:00:50.000 | 67389797 |  | 67.3898 | -4745670 | 15611385 | 24986934 | 99752960 | 50124382 | 946207092 | 0.000000 | 0.000000 | 65328293
09-04-2025 22:00:45.000 | 66459039 |  | 66.459 | -4691889 | 15612436 | 24639963 | 99751724 | 50147495 | 852714478 | 0.000000 | 0.000000 | 58861713
09-04-2025 22:00:40.000 | 66330031 |  | 66.33 | -4970644 | 15614237 | 24597124 | 99720390 | 50147789 | 760866394 | 0.000000 | 0.000000 | 52234303
09-04-2025 22:00:35.000 | 66978992 |  | 66.979 | -4509732 | 15612006 | 24828652 | 99774101 | 50135452 | 668563782 | 0.000000 | 0.000000 | 45587940
09-04-2025 22:00:30.000 | 66929250 |  | 66.9292 | -4788610 | 15616825 | 24809087 | 99745026 | 50133480 | 575529785 | 0.000000 | 0.000000 | 39158554
09-04-2025 22:00:25.000 | 68244391 |  | 68.2444 | -4561553 | 15615636 | 25290022 | 99777359 | 50117283 | 481738831 | 0.000000 | 0.000000 | 32605503
09-04-2025 22:00:20.000 | 68623359 |  | 68.6234 | -4579886 | 15615479 | 25430857 | 99778030 | 50111610 | 387119781 | 0.000000 | 0.000000 | 26308678
09-04-2025 22:00:15.000 | 69888641 |  | 69.8886 | -4625372 | 15611229 | 25905886 | 99781715 | 50099884 | 291108795 | 0.000000 | 0.000000 | 19934946
09-04-2025 22:00:10.000 | 70513016 |  | 70.513 | -4686754 | 15609197 | 26140898 | 99779839 | 50092350 | 193883423 | 0.000000 | 0.000000 | 13382008
09-04-2025 22:00:05.000 | 69777258 |  | 69.7773 | -4800762 | 15610727 | 25870549 | 99764160 | 50128979 | 96283875 | 0.000000 | 0.000000 | 6870286
09-04-2025 22:00:00.000 | 69278063 |  | 69.2781 | -5102779 | 15608278 | 25697249 | 99729836 | 50143665 | 18982775 | 0.000000 | 0.000000 | 748206055
09-04-2025 21:59:55.000 | 68700148 |  | 68.7001 | -4813187 | 15609141 | 25475012 | 99755478 | 50157898 | 18886537 | 0.000000 | 0.000000 | 741286133
09-04-2025 21:59:50.000 | 67480922 |  | 67.4809 | -4747405 | 15612110 | 25018940 | 99753448 | 50192200 | 18792033 | 0.000000 | 0.000000 | 734641663
09-04-2025 21:59:45.000 | 67149359 |  | 67.1494 | -4657427 | 15616093 | 24888015 | 99760330 | 50190723 | 18698738 | 0.000000 | 0.000000 | 727976257
09-04-2025 21:59:40.000 | 68271008 |  | 68.271 | -4559526 | 15614550 | 25301602 | 99777725 | 50174755 | 18604773 | 0.000000 | 0.000000 | 721481812
09-04-2025 21:59:35.000 | 68989367 |  | 68.9894 | -4398054 | 15611788 | 25567473 | 99797417 | 50155140 | 18509418 | 0.000000 | 0.000000 | 715183167
09-04-2025 21:59:30.000 | 68963992 |  | 68.964 | -4330883 | 15611100 | 25557471 | 99803398 | 50160717 | 18413689 | 0.000000 | 0.000000 | 709054688
09-04-2025 21:59:25.000 | 68498938 |  | 68.4989 | -4474385 | 15607896 | 25394805 | 99787338 | 50164722 | 18318236 | 0.000000 | 0.000000 | 703041382
09-04-2025 21:59:20.000 | 68389711 |  | 68.3897 | -4429410 | 15609828 | 25350181 | 99790916 | 50163277 | 18223027 | 0.000000 | 0.000000 | 696760498
09-04-2025 21:59:15.000 | 67662523 |  | 67.6625 | -4327902 | 15611452 | 25077488 | 99796059 | 50182167 | 18128227 | 0.000000 | 0.000000 | 690624084
09-04-2025 21:59:10.000 | 67572445 |  | 67.5724 | -4523743 | 15614124 | 25044060 | 99776657 | 50184540 | 18034471 | 0.000000 | 0.000000 | 684470703
09-04-2025 21:59:05.000 | 68016398 |  | 68.0164 | -4552427 | 15612939 | 25210857 | 99776756 | 50174015 | 17940105 | 0.000000 | 0.000000 | 678195313
09-04-2025 21:59:00.000 | 68239000 |  | 68.239 | -4655519 | 15610895 | 25298320 | 99768082 | 50171913 | 17845521 | 0.000000 | 0.000000 | 671869263
09-04-2025 21:58:55.000 | 68602523 |  | 68.6025 | -4556907 | 15607718 | 25434858 | 99780113 | 50163860 | 17750707 | 0.000000 | 0.000000 | 665467896
09-04-2025 21:58:50.000 | 66931844 |  | 66.9318 | -4603329 | 15611424 | 24814006 | 99764328 | 50192200 | 17656238 | 0.000000 | 0.000000 | 659205994
09-04-2025 21:58:45.000 | 66391000 |  | 66.391 | -4612444 | 15614941 | 24608782 | 99759537 | 50194782 | 17563813 | 0.000000 | 0.000000 | 652806824
09-04-2025 21:58:40.000 | 66901867 |  | 66.9019 | -4540850 | 15612277 | 24799873 | 99770454 | 50179737 | 17471438 | 0.000000 | 0.000000 | 646453247
09-04-2025 21:58:35.000 | 66957727 |  | 66.9577 | -4561106 | 15611114 | 24822720 | 99768791 | 50173237 | 17378492 | 0.000000 | 0.000000 | 640104492
09-04-2025 21:58:30.000 | 67142828 |  | 67.1428 | -4582181 | 15612412 | 24889277 | 99767937 | 50167408 | 17285357 | 0.000000 | 0.000000 | 633738037
09-04-2025 21:58:25.000 | 66287289 |  | 66.2873 | -4199941 | 15616826 | 24557424 | 99799881 | 50182026 | 17192453 | 0.000000 | 0.000000 | 627627319
09-04-2025 21:58:20.000 | 66455828 |  | 66.4558 | -4397558 | 15618574 | 24621528 | 99781776 | 50178661 | 17100443 | 0.000000 | 0.000000 | 621629028
09-04-2025 21:58:15.000 | 68336633 |  | 68.3366 | -4180618 | 15614624 | 25316802 | 99813393 | 50141781 | 17007027 | 0.000000 | 0.000000 | 615589050
09-04-2025 21:58:10.000 | 69436141 |  | 69.4361 | -4358377 | 15608801 | 25736094 | 99803589 | 50126438 | 16911719 | 0.000000 | 0.000000 | 609688965
09-04-2025 21:58:05.000 | 68826953 |  | 68.827 | -4381918 | 15608866 | 25511685 | 99797951 | 50133316 | 16815607 | 0.000000 | 0.000000 | 603580139
09-04-2025 21:58:00.000 | 67377055 |  | 67.3771 | -4398069 | 15610867 | 24974287 | 99787636 | 50164944 | 16720660 | 0.000000 | 0.000000 | 597512756
09-04-2025 21:57:55.000 | 66327273 |  | 66.3273 | -4321700 | 15614323 | 24579343 | 99788399 | 50185875 | 16627732 | 0.000000 | 0.000000 | 591544922
09-04-2025 21:57:50.000 | 66765945 |  | 66.7659 | -4353307 | 15616533 | 24738228 | 99788109 | 50180157 | 16535506 | 0.000000 | 0.000000 | 585534851
09-04-2025 21:57:45.000 | 67986242 |  | 67.9862 | -4467695 | 15614907 | 25193767 | 99784775 | 50153133 | 16442270 | 0.000000 | 0.000000 | 579468262
09-04-2025 21:57:40.000 | 69003875 |  | 69.0039 | -4303421 | 15614832 | 25565374 | 99806099 | 50142605 | 16347140 | 0.000000 | 0.000000 | 573312683
09-04-2025 21:57:35.000 | 69493672 |  | 69.4937 | -4211214 | 15608783 | 25754990 | 99816895 | 50138451 | 16250841 | 0.000000 | 0.000000 | 567456543
09-04-2025 21:57:30.000 | 68762766 |  | 68.7628 | -4306646 | 15606101 | 25491216 | 99804443 | 50170330 | 16154641 | 0.000000 | 0.000000 | 561647888
09-04-2025 21:57:25.000 | 67315195 |  | 67.3152 | -4499667 | 15610897 | 24954495 | 99777336 | 50201725 | 16060299 | 0.000000 | 0.000000 | 555436829
09-04-2025 21:57:20.000 | 66722758 |  | 66.7228 | -4575800 | 15614652 | 24733914 | 99765671 | 50209599 | 15967553 | 0.000000 | 0.000000 | 549028809
09-04-2025 21:57:15.000 | 66855836 |  | 66.8558 | -4489846 | 15614923 | 24777927 | 99775253 | 50203762 | 15875144 | 0.000000 | 0.000000 | 542783325
09-04-2025 21:57:10.000 | 67250820 |  | 67.2508 | -4457562 | 15613445 | 24924590 | 99781052 | 50191017 | 15782275 | 0.000000 | 0.000000 | 536532898
09-04-2025 21:57:05.000 | 67233633 |  | 67.2336 | -4493461 | 15611158 | 24923232 | 99777412 | 50188446 | 15689003 | 0.000000 | 0.000000 | 530404480
09-04-2025 21:57:00.000 | 67580625 |  | 67.5806 | -4614919 | 15613285 | 25050281 | 99767654 | 50179703 | 15595524 | 0.000000 | 0.000000 | 524092468
09-04-2025 21:56:55.000 | 67288914 |  | 67.2889 | -4352271 | 15609673 | 24941946 | 99791473 | 50187603 | 15501740 | 0.000000 | 0.000000 | 517947449
09-04-2025 21:56:50.000 | 66382664 |  | 66.3827 | -4365603 | 15614287 | 24600959 | 99784454 | 50191319 | 15408960 | 0.000000 | 0.000000 | 511804657
09-04-2025 21:56:45.000 | 65891406 |  | 65.8914 | -4220747 | 15615312 | 24414492 | 99795471 | 50188728 | 15316887 | 0.000000 | 0.000000 | 505836761
09-04-2025 21:56:40.000 | 66504984 |  | 66.505 | -4128801 | 15614735 | 24639353 | 99807846 | 50176533 | 15224796 | 0.000000 | 0.000000 | 500019928
09-04-2025 21:56:35.000 | 67376977 |  | 67.377 | -3959474 | 15615479 | 24956284 | 99827774 | 50158306 | 15131780 | 0.000000 | 0.000000 | 494379730
09-04-2025 21:56:30.000 | 67901484 |  | 67.9015 | -4238643 | 15615136 | 25156536 | 99805733 | 50156403 | 15037813 | 0.000000 | 0.000000 | 488760071
09-04-2025 21:56:25.000 | 69606734 |  | 69.6067 | -4137448 | 15611186 | 25790571 | 99823807 | 50122654 | 14942716 | 0.000000 | 0.000000 | 482839386
09-04-2025 21:56:20.000 | 69601320 |  | 69.6013 | -4120186 | 15606619 | 25795518 | 99825249 | 50129948 | 14845720 | 0.000000 | 0.000000 | 477090515
09-04-2025 21:56:15.000 | 68690781 |  | 68.6908 | -4582692 | 15607103 | 25469226 | 99778198 | 50154793 | 14749321 | 0.000000 | 0.000000 | 471152130
09-04-2025 21:56:10.000 | 67865750 |  | 67.8658 | -4574007 | 15609254 | 25160979 | 99773643 | 50172157 | 14654221 | 0.000000 | 0.000000 | 464828125
09-04-2025 21:56:05.000 | 66853875 |  | 66.8539 | -4456876 | 15611787 | 24781963 | 99778519 | 50198711 | 14560658 | 0.000000 | 0.000000 | 458522125
09-04-2025 21:56:00.000 | 66101789 |  | 66.1018 | -4739726 | 15614425 | 24506348 | 99743919 | 50200058 | 14468638 | 0.000000 | 0.000000 | 452221863
09-04-2025 21:55:55.000 | 66975430 |  | 66.9754 | -4524606 | 15611251 | 24827866 | 99772583 | 50186150 | 14376512 | 0.000000 | 0.000000 | 445704712
09-04-2025 21:55:50.000 | 66703805 |  | 66.7038 | -4524109 | 15612803 | 24726450 | 99770790 | 50185467 | 14283972 | 0.000000 | 0.000000 | 439334167
09-04-2025 21:55:45.000 | 66387883 |  | 66.3879 | -4518074 | 15615303 | 24604697 | 99769226 | 50188923 | 14191817 | 0.000000 | 0.000000 | 433011993
09-04-2025 21:55:40.000 | 66737586 |  | 66.7376 | -4253212 | 15611874 | 24732610 | 99797539 | 50179260 | 14099380 | 0.000000 | 0.000000 | 426975647
09-04-2025 21:55:35.000 | 66865148 |  | 66.8651 | -4155278 | 15610411 | 24779805 | 99807465 | 50183807 | 14006669 | 0.000000 | 0.000000 | 421237183
09-04-2025 21:55:30.000 | 66831977 |  | 66.832 | -4135616 | 15611191 | 24766282 | 99809090 | 50178570 | 13913359 | 0.000000 | 0.000000 | 415498749
09-04-2025 21:55:25.000 | 66499125 |  | 66.4991 | -3908035 | 15610836 | 24638511 | 99827759 | 50176003 | 13820472 | 0.000000 | 0.000000 | 409865967
09-04-2025 21:55:20.000 | 66346930 |  | 66.3469 | -3989819 | 15613457 | 24580198 | 99819672 | 50174683 | 13728355 | 0.000000 | 0.000000 | 404415100
09-04-2025 21:55:15.000 | 66987492 |  | 66.9875 | -3913403 | 15614366 | 24813462 | 99829788 | 50166218 | 13635803 | 0.000000 | 0.000000 | 398889038
09-04-2025 21:55:10.000 | 67877570 |  | 67.8776 | -3836344 | 15613149 | 25142769 | 99840668 | 50151268 | 13542515 | 0.000000 | 0.000000 | 393499664
09-04-2025 21:55:05.000 | 67622586 |  | 67.6226 | -3710008 | 15611392 | 25048330 | 99849838 | 50149109 | 13448329 | 0.000000 | 0.000000 | 388256805
09-04-2025 21:55:00.000 | 67588570 |  | 67.5886 | -3877471 | 15611505 | 25039314 | 99835846 | 50151016 | 13354228 | 0.000000 | 0.000000 | 383109589
09-04-2025 21:54:55.000 | 68442383 |  | 68.4424 | -3965769 | 15611065 | 25357395 | 99832550 | 50129097 | 13259718 | 0.000000 | 0.000000 | 377590759
09-04-2025 21:54:50.000 | 68047758 |  | 68.0478 | -3856482 | 15609927 | 25210718 | 99839790 | 50136219 | 13164607 | 0.000000 | 0.000000 | 372113861
09-04-2025 21:54:45.000 | 67401266 |  | 67.4013 | -3904413 | 15610068 | 24973313 | 99832642 | 50143009 | 13070169 | 0.000000 | 0.000000 | 366755035
09-04-2025 21:54:40.000 | 66667438 |  | 66.6674 | -3688337 | 15611408 | 24694980 | 99847313 | 50165310 | 12976831 | 0.000000 | 0.000000 | 361420685
09-04-2025 21:54:35.000 | 66586891 |  | 66.5869 | -3782183 | 15614940 | 24662004 | 99839073 | 50167450 | 12884384 | 0.000000 | 0.000000 | 356058594
09-04-2025 21:54:30.000 | 66602859 |  | 66.6029 | -3741508 | 15616374 | 24664561 | 99842583 | 50172699 | 12792025 | 0.000000 | 0.000000 | 350956421
09-04-2025 21:54:25.000 | 67697039 |  | 67.697 | -3670908 | 15614768 | 25070332 | 99853302 | 50154678 | 12699088 | 0.000000 | 0.000000 | 345813293
09-04-2025 21:54:20.000 | 68277797 |  | 68.2778 | -3585481 | 15611738 | 25287847 | 99862404 | 50135342 | 12604684 | 0.000000 | 0.000000 | 340776733
09-04-2025 21:54:15.000 | 68390188 |  | 68.3902 | -3749611 | 15610854 | 25333796 | 99850037 | 50127876 | 12509632 | 0.000000 | 0.000000 | 335711060
09-04-2025 21:54:10.000 | 68212773 |  | 68.2128 | -3730847 | 15609346 | 25270251 | 99850761 | 50133728 | 12414634 | 0.000000 | 0.000000 | 330566925
09-04-2025 21:54:05.000 | 67115875 |  | 67.1159 | -3721010 | 15610671 | 24862878 | 99846664 | 50149715 | 12320381 | 0.000000 | 0.000000 | 325423218
09-04-2025 21:54:00.000 | 66795578 |  | 66.7956 | -3530732 | 15613246 | 24737129 | 99860588 | 50161556 | 12227306 | 0.000000 | 0.000000 | 320326355
09-04-2025 21:53:55.000 | 65696430 |  | 65.6964 | -3553052 | 15618670 | 24323040 | 99854073 | 50178822 | 12135459 | 0.000000 | 0.000000 | 315319824
09-04-2025 21:53:50.000 | 66865078 |  | 66.8651 | -3551463 | 15616146 | 24758015 | 99859245 | 50142971 | 12043797 | 0.000000 | 0.000000 | 310357513
09-04-2025 21:53:45.000 | 67859586 |  | 67.8596 | -3398451 | 15613725 | 25126038 | 99874832 | 50122158 | 11950103 | 0.000000 | 0.000000 | 305582275
09-04-2025 21:53:40.000 | 67876242 |  | 67.8762 | -3283272 | 15612145 | 25132615 | 99883217 | 50123737 | 11855747 | 0.000000 | 0.000000 | 300975128
09-04-2025 21:53:35.000 | 68605805 |  | 68.6058 | -3364652 | 15610965 | 25405925 | 99879951 | 50117157 | 11761545 | 0.000000 | 0.000000 | 296244171
09-04-2025 21:53:30.000 | 68268102 |  | 68.2681 | -3392043 | 15610354 | 25282549 | 99876785 | 50121288 | 11666242 | 0.000000 | 0.000000 | 291545135
09-04-2025 21:53:25.000 | 67933055 |  | 67.9331 | -3409577 | 15613697 | 25153503 | 99874283 | 50137592 | 11571414 | 0.000000 | 0.000000 | 286840424
09-04-2025 21:53:20.000 | 68260578 |  | 68.2606 | -3562769 | 15612069 | 25280813 | 99864067 | 50125877 | 11476855 | 0.000000 | 0.000000 | 281999786
09-04-2025 21:53:15.000 | 68655500 |  | 68.6555 | -3523353 | 15612105 | 25425925 | 99868576 | 50120743 | 11381573 | 0.000000 | 0.000000 | 277108978
09-04-2025 21:53:10.000 | 68359805 |  | 68.3598 | -3449402 | 15609263 | 25318958 | 99872932 | 50128674 | 11286384 | 0.000000 | 0.000000 | 272327972
09-04-2025 21:53:05.000 | 67573008 |  | 67.573 | -3459691 | 15610548 | 25026758 | 99869186 | 50135635 | 11192024 | 0.000000 | 0.000000 | 267458832
09-04-2025 21:53:00.000 | 67184906 |  | 67.1849 | -3651423 | 15610347 | 24887759 | 99852638 | 50141148 | 11098079 | 0.000000 | 0.000000 | 262586121
09-04-2025 21:52:55.000 | 67354000 |  | 67.354 | -3569430 | 15609693 | 24949150 | 99859871 | 50140041 | 11004472 | 0.000000 | 0.000000 | 257509857
09-04-2025 21:52:50.000 | 67041469 |  | 67.0415 | -3717456 | 15610612 | 24835144 | 99846619 | 50155159 | 10911515 | 0.000000 | 0.000000 | 252371033
09-04-2025 21:52:45.000 | 66143383 |  | 66.1434 | -3568230 | 15612786 | 24497207 | 99854805 | 50163055 | 10818604 | 0.000000 | 0.000000 | 247324417
09-04-2025 21:52:40.000 | 66845898 |  | 66.8459 | -3499148 | 15613319 | 24754470 | 99863274 | 50157574 | 10726160 | 0.000000 | 0.000000 | 242432922
09-04-2025 21:52:35.000 | 67756031 |  | 67.756 | -3491683 | 15611424 | 25093330 | 99867477 | 50134476 | 10632846 | 0.000000 | 0.000000 | 237465820
09-04-2025 21:52:30.000 | 67656859 |  | 67.6569 | -3125013 | 15611497 | 25050244 | 99893501 | 50142448 | 10538901 | 0.000000 | 0.000000 | 232761475
09-04-2025 21:52:25.000 | 67000203 |  | 67.0002 | -3300811 | 15615772 | 24804788 | 99878868 | 50160587 | 10445529 | 0.000000 | 0.000000 | 228329575
09-04-2025 21:52:20.000 | 67692742 |  | 67.6927 | -3019167 | 15616894 | 25052744 | 99900688 | 50149414 | 10352449 | 0.000000 | 0.000000 | 223884186
09-04-2025 21:52:15.000 | 68990633 |  | 68.9906 | -3058737 | 15618762 | 25529900 | 99901863 | 50133080 | 10258034 | 0.000000 | 0.000000 | 219607193
09-04-2025 21:52:10.000 | 70730219 |  | 70.7302 | -2931931 | 15616054 | 26174739 | 99914192 | 50108868 | 10161284 | 0.000000 | 0.000000 | 215479492
09-04-2025 21:52:05.000 | 72338469 |  | 72.3385 | -2743192 | 15609330 | 26777822 | 99928177 | 50080364 | 10061747 | 0.000000 | 0.000000 | 211349503
09-04-2025 21:52:00.000 | 71344883 |  | 71.3449 | -2943462 | 15611987 | 26408643 | 99915001 | 50124943 | 99615586 | 0.000000 | 0.000000 | 207519272
09-04-2025 21:51:55.000 | 70834094 |  | 70.8341 | -3055670 | 15616504 | 26215129 | 99907082 | 50146999 | 98628555 | 0.000000 | 0.000000 | 203372330
09-04-2025 21:51:50.000 | 71932031 |  | 71.932 | -2801785 | 15616618 | 26615947 | 99924232 | 50143284 | 97638184 | 0.000000 | 0.000000 | 199168640
09-04-2025 21:51:45.000 | 73288070 |  | 73.2881 | -2863910 | 15615726 | 27119097 | 99923737 | 50142353 | 96630166 | 0.000000 | 0.000000 | 195228287
09-04-2025 21:51:40.000 | 74312703 |  | 74.3127 | -2843363 | 15613988 | 27500522 | 99926880 | 50124134 | 95611104 | 0.000000 | 0.000000 | 191247711
09-04-2025 21:51:35.000 | 74871586 |  | 74.8716 | -2802312 | 15612789 | 27708787 | 99930031 | 50125069 | 94573965 | 0.000000 | 0.000000 | 187318741
09-04-2025 21:51:30.000 | 75187219 |  | 75.1872 | -2731892 | 15611563 | 27826174 | 99934059 | 50150639 | 93533574 | 0.000000 | 0.000000 | 183476349
09-04-2025 21:51:25.000 | 74313313 |  | 74.3133 | -2920235 | 15615560 | 27498743 | 99922882 | 50171974 | 92501113 | 0.000000 | 0.000000 | 179655273
09-04-2025 21:51:20.000 | 75631359 |  | 75.6314 | -2861859 | 15615394 | 27985776 | 99928482 | 50163914 | 91457715 | 0.000000 | 0.000000 | 175661331
09-04-2025 21:51:15.000 | 76832922 |  | 76.8329 | -2785903 | 15617181 | 28424807 | 99934326 | 50154758 | 90398740 | 0.000000 | 0.000000 | 171708298
09-04-2025 21:51:10.000 | 77722656 |  | 77.7227 | -2500434 | 15614741 | 28754270 | 99948288 | 50149200 | 89325400 | 0.000000 | 0.000000 | 167995636
09-04-2025 21:51:05.000 | 78281563 |  | 78.2816 | -2344089 | 15616100 | 28956902 | 99955200 | 50160725 | 88244658 | 0.000000 | 0.000000 | 164548935
09-04-2025 21:51:00.000 | 78931125 |  | 78.9311 | -2250399 | 15619354 | 29189570 | 99959381 | 50176102 | 87154980 | 0.000000 | 0.000000 | 161448929
09-04-2025 21:50:55.000 | 80750406 |  | 80.7504 | -1964801 | 15619602 | 29858384 | 99970413 | 50151428 | 86048213 | 0.000000 | 0.000000 | 158397018
09-04-2025 21:50:50.000 | 83270008 |  | 83.27 | -1882024 | 15616104 | 30795698 | 99974472 | 50115799 | 84911055 | 0.000000 | 0.000000 | 155696198
09-04-2025 21:50:45.000 | 84662656 |  | 84.6627 | -1892744 | 15614435 | 31314207 | 99975021 | 50103039 | 83745410 | 0.000000 | 0.000000 | 153187622
09-04-2025 21:50:40.000 | 85602734 |  | 85.6027 | -1495970 | 15615350 | 31656665 | 99984734 | 50097054 | 82563389 | 0.000000 | 0.000000 | 150683533
09-04-2025 21:50:35.000 | 85755828 |  | 85.7558 | -1728701 | 15612877 | 31720869 | 99979691 | 50114262 | 81373677 | 0.000000 | 0.000000 | 148572189
09-04-2025 21:50:30.000 | 86728758 |  | 86.7288 | -1575220 | 15612626 | 32079050 | 99983513 | 50100742 | 80177300 | 0.000000 | 0.000000 | 146222885
09-04-2025 21:50:25.000 | 87046461 |  | 87.0465 | -1685248 | 15613765 | 32194983 | 99981262 | 50111557 | 78971748 | 0.000000 | 0.000000 | 144062424
09-04-2025 21:50:20.000 | 87115172 |  | 87.1152 | -1523611 | 15616577 | 32213694 | 99984711 | 50128048 | 77761577 | 0.000000 | 0.000000 | 141804291
09-04-2025 21:50:15.000 | 87546188 |  | 87.5462 | -1497705 | 15613953 | 32378228 | 99985367 | 50141491 | 76550464 | 0.000000 | 0.000000 | 139705276
09-04-2025 21:50:10.000 | 88807117 |  | 88.8071 | -1711816 | 15610968 | 32852009 | 99981430 | 50124161 | 75329102 | 0.000000 | 0.000000 | 137519012
09-04-2025 21:50:05.000 | 89283008 |  | 89.283 | -1810421 | 15608885 | 33032927 | 99979446 | 50119595 | 74091748 | 0.000000 | 0.000000 | 135170761
09-04-2025 21:50:00.000 | 88705453 |  | 88.7055 | -1869717 | 15607706 | 32822566 | 99977791 | 50146473 | 72855107 | 0.000000 | 0.000000 | 132535522
09-04-2025 21:49:55.000 | 87564852 |  | 87.5649 | -2162742 | 15610130 | 32398291 | 99969513 | 50166809 | 71633579 | 0.000000 | 0.000000 | 129710602
09-04-2025 21:49:50.000 | 87189789 |  | 87.1898 | -2226372 | 15612334 | 32255212 | 99967415 | 50169796 | 70420645 | 0.000000 | 0.000000 | 126701866
09-04-2025 21:49:45.000 | 86888906 |  | 86.8889 | -1991897 | 15610912 | 32145071 | 99973732 | 50179382 | 69211055 | 0.000000 | 0.000000 | 123779922
09-04-2025 21:49:40.000 | 86445961 |  | 86.446 | -2199455 | 15613855 | 31977234 | 99967651 | 50173630 | 68007988 | 0.000000 | 0.000000 | 120838829
09-04-2025 21:49:35.000 | 87032961 |  | 87.033 | -1822986 | 15611911 | 32194941 | 99978073 | 50154461 | 66800269 | 0.000000 | 0.000000 | 117953331
09-04-2025 21:49:30.000 | 86261938 |  | 86.2619 | -1706806 | 15613788 | 31904888 | 99980431 | 50165092 | 65595015 | 0.000000 | 0.000000 | 115426559
09-04-2025 21:49:25.000 | 86250328 |  | 86.2503 | -1670361 | 15618582 | 31890735 | 99981255 | 50170197 | 64398799 | 0.000000 | 0.000000 | 113175148
09-04-2025 21:49:20.000 | 87696320 |  | 87.6963 | -1838342 | 15617550 | 32428364 | 99978035 | 50128498 | 63193706 | 0.000000 | 0.000000 | 110730278
09-04-2025 21:49:15.000 | 89173781 |  | 89.1738 | -1631345 | 15608750 | 32991834 | 99983269 | 50108559 | 61961763 | 0.000000 | 0.000000 | 108417114
09-04-2025 21:49:10.000 | 88771750 |  | 88.7717 | -1685632 | 15607623 | 32845500 | 99981979 | 50121433 | 60726455 | 0.000000 | 0.000000 | 106122810
09-04-2025 21:49:05.000 | 87797852 |  | 87.7979 | -1658438 | 15607699 | 32486082 | 99982162 | 50137890 | 59498877 | 0.000000 | 0.000000 | 103872025
09-04-2025 21:49:00.000 | 87237000 |  | 87.237 | -1854541 | 15609584 | 32275232 | 99977409 | 50145031 | 58283828 | 0.000000 | 0.000000 | 101315170
09-04-2025 21:48:55.000 | 86195047 |  | 86.195 | -1766709 | 15613719 | 31880994 | 99979004 | 50155422 | 57080063 | 0.000000 | 0.000000 | 98764809
09-04-2025 21:48:50.000 | 86020727 |  | 86.0207 | -1633271 | 15615603 | 31811692 | 99981979 | 50151695 | 55887671 | 0.000000 | 0.000000 | 96385765
09-04-2025 21:48:45.000 | 86237898 |  | 86.2379 | -1465617 | 15618300 | 31885095 | 99985565 | 50151436 | 54692373 | 0.000000 | 0.000000 | 94211052
09-04-2025 21:48:40.000 | 87751656 |  | 87.7517 | -1374149 | 15615926 | 32449785 | 99987740 | 50122589 | 53487305 | 0.000000 | 0.000000 | 92240822
09-04-2025 21:48:35.000 | 88751656 |  | 88.7517 | -1390667 | 15613704 | 32824307 | 99987724 | 50095421 | 52263774 | 0.000000 | 0.000000 | 90357124
09-04-2025 21:48:30.000 | 89218805 |  | 89.2188 | -1465071 | 15607031 | 33012512 | 99986519 | 50085026 | 51024414 | 0.000000 | 0.000000 | 88455452
09-04-2025 21:48:25.000 | 88368219 |  | 88.3682 | -1601809 | 15609056 | 32692749 | 99983574 | 50115376 | 49785371 | 0.000000 | 0.000000 | 86429916
09-04-2025 21:48:20.000 | 88063781 |  | 88.0638 | -1675959 | 15609783 | 32579243 | 99981895 | 50122486 | 48560337 | 0.000000 | 0.000000 | 84183372
09-04-2025 21:48:15.000 | 87499055 |  | 87.4991 | -1792094 | 15609676 | 32372056 | 99979034 | 50129215 | 47341338 | 0.000000 | 0.000000 | 81797844
09-04-2025 21:48:10.000 | 86920617 |  | 86.9206 | -1621161 | 15611659 | 32152813 | 99982613 | 50145615 | 46128403 | 0.000000 | 0.000000 | 79577309
09-04-2025 21:48:05.000 | 86429117 |  | 86.4291 | -1580842 | 15615824 | 31961641 | 99983276 | 50157516 | 44924189 | 0.000000 | 0.000000 | 77366333
09-04-2025 21:48:00.000 | 87502789 |  | 87.5028 | -1423360 | 15613401 | 32362568 | 99986771 | 50130810 | 43721494 | 0.000000 | 0.000000 | 75179199
09-04-2025 21:47:55.000 | 87489148 |  | 87.4891 | -1430255 | 15612839 | 32359048 | 99986641 | 50120022 | 42504473 | 0.000000 | 0.000000 | 73210823
09-04-2025 21:47:50.000 | 87885250 |  | 87.8852 | -1509861 | 15611094 | 32510601 | 99985245 | 50112705 | 41283535 | 0.000000 | 0.000000 | 71256073
09-04-2025 21:47:45.000 | 88151578 |  | 88.1516 | -1663448 | 15610869 | 32609690 | 99982201 | 50106827 | 40062104 | 0.000000 | 0.000000 | 69085297
09-04-2025 21:47:40.000 | 87699250 |  | 87.6993 | -1484336 | 15609729 | 32443340 | 99985680 | 50116325 | 38839084 | 0.000000 | 0.000000 | 66916313
09-04-2025 21:47:35.000 | 86965820 |  | 86.9658 | -1560707 | 15611099 | 32170449 | 99983902 | 50129726 | 37627957 | 0.000000 | 0.000000 | 64697624
09-04-2025 21:47:30.000 | 86450617 |  | 86.4506 | -1599754 | 15612285 | 31976992 | 99982880 | 50135628 | 36422061 | 0.000000 | 0.000000 | 62545910
09-04-2025 21:47:25.000 | 86491906 |  | 86.4919 | -1725122 | 15614896 | 31988101 | 99980118 | 50132133 | 35220408 | 0.000000 | 0.000000 | 60201660
09-04-2025 21:47:20.000 | 87013477 |  | 87.0135 | -1623182 | 15614161 | 32181448 | 99982605 | 50115124 | 34015593 | 0.000000 | 0.000000 | 57813335
09-04-2025 21:47:15.000 | 86817180 |  | 86.8172 | -1538539 | 15611692 | 32113413 | 99984299 | 50113205 | 32805645 | 0.000000 | 0.000000 | 55679710
09-04-2025 21:47:10.000 | 86818633 |  | 86.8186 | -1665450 | 15612535 | 32112947 | 99981606 | 50124329 | 31598230 | 0.000000 | 0.000000 | 53530926
09-04-2025 21:47:05.000 | 87051953 |  | 87.052 | -1603778 | 15611519 | 32200979 | 99983032 | 50117958 | 30393547 | 0.000000 | 0.000000 | 51294209
09-04-2025 21:47:00.000 | 87074672 |  | 87.0747 | -1427827 | 15614197 | 32202935 | 99986557 | 50114204 | 29183306 | 0.000000 | 0.000000 | 49099682
09-04-2025 21:46:55.000 | 87233211 |  | 87.2332 | -1385623 | 15615097 | 32259314 | 99987389 | 50122837 | 27974316 | 0.000000 | 0.000000 | 47126938
09-04-2025 21:46:50.000 | 87527336 |  | 87.5273 | -1585989 | 15615875 | 32367520 | 99983589 | 50113792 | 26762356 | 0.000000 | 0.000000 | 45206635
09-04-2025 21:46:45.000 | 88699867 |  | 88.6999 | -1472195 | 15607654 | 32817637 | 99986229 | 50080219 | 25538625 | 0.000000 | 0.000000 | 43034363
09-04-2025 21:46:40.000 | 87884000 |  | 87.884 | -1373075 | 15609474 | 32511360 | 99987801 | 50090740 | 24309998 | 0.000000 | 0.000000 | 40989899
09-04-2025 21:46:35.000 | 86910398 |  | 86.9104 | -1277931 | 15611275 | 32147041 | 99989189 | 50119911 | 23096802 | 0.000000 | 0.000000 | 39081230
09-04-2025 21:46:30.000 | 86068805 |  | 86.0688 | -1422263 | 15618363 | 31822358 | 99986351 | 50125454 | 21897224 | 0.000000 | 0.000000 | 37163246
09-04-2025 21:46:25.000 | 87921203 |  | 87.9212 | -1278505 | 15620161 | 32502729 | 99989426 | 50096348 | 20689731 | 0.000000 | 0.000000 | 35254406
09-04-2025 21:46:20.000 | 89144250 |  | 89.1442 | -1097049 | 15611951 | 32971196 | 99992432 | 50065342 | 19460626 | 0.000000 | 0.000000 | 33684238
09-04-2025 21:46:15.000 | 89724063 |  | 89.7241 | -1361112 | 15607156 | 33196780 | 99988495 | 50074226 | 18216451 | 0.000000 | 0.000000 | 32077171
09-04-2025 21:46:10.000 | 89742023 |  | 89.742 | -1494746 | 15605614 | 33207534 | 99986130 | 50078644 | 16969818 | 0.000000 | 0.000000 | 30041515
09-04-2025 21:46:05.000 | 87752234 |  | 87.7522 | -1700271 | 15608529 | 32466885 | 99981232 | 50113941 | 15735863 | 0.000000 | 0.000000 | 27789772
09-04-2025 21:46:00.000 | 86729719 |  | 86.7297 | -1694592 | 15611773 | 32083486 | 99980919 | 50134186 | 14522239 | 0.000000 | 0.000000 | 25359791
09-04-2025 21:45:55.000 | 85901188 |  | 85.9012 | -1856590 | 15614973 | 31770762 | 99976654 | 50149029 | 13323750 | 0.000000 | 0.000000 | 22932882
09-04-2025 21:45:50.000 | 86079313 |  | 86.0793 | -1776898 | 15618103 | 31829663 | 99978699 | 50140408 | 12132526 | 0.000000 | 0.000000 | 20434776
09-04-2025 21:45:45.000 | 87369180 |  | 87.3692 | -1706022 | 15617284 | 32307151 | 99980942 | 50108875 | 10927914 | 0.000000 | 0.000000 | 18083591
09-04-2025 21:45:40.000 | 88642875 |  | 88.6429 | -1606514 | 15609329 | 32793682 | 99983582 | 50073658 | 970652893 | 0.000000 | 0.000000 | 15750249
09-04-2025 21:45:35.000 | 87850570 |  | 87.8506 | -1399036 | 15609995 | 32499348 | 99987320 | 50092751 | 847830261 | 0.000000 | 0.000000 | 13724521
09-04-2025 21:45:30.000 | 86874813 |  | 86.8748 | -1439152 | 15611950 | 32133662 | 99986282 | 50115311 | 726747925 | 0.000000 | 0.000000 | 11807529
09-04-2025 21:45:25.000 | 86712656 |  | 86.7127 | -1584614 | 15614282 | 32070132 | 99983307 | 50115028 | 606203674 | 0.000000 | 0.000000 | 9694328
09-04-2025 21:45:20.000 | 87373664 |  | 87.3737 | -1295987 | 15611796 | 32317471 | 99988998 | 50108795 | 485513397 | 0.000000 | 0.000000 | 7617723
09-04-2025 21:45:15.000 | 86656969 |  | 86.657 | -1509818 | 15614876 | 32047468 | 99984825 | 50120033 | 364593903 | 0.000000 | 0.000000 | 5731447
09-04-2025 21:45:10.000 | 87551430 |  | 87.5514 | -1443489 | 15615160 | 32376970 | 99986412 | 50104301 | 243615204 | 0.000000 | 0.000000 | 3647205
09-04-2025 21:45:05.000 | 87430258 |  | 87.4303 | -1304288 | 15612604 | 32336763 | 99988876 | 50098614 | 121886620 | 0.000000 | 0.000000 | 1766117
09-04-2025 21:45:00.000 | 87819398 |  | 87.8194 | -1169269 | 15613651 | 32478555 | 99991135 | 50098122 | 21894750 | 34748161 | 0.000000 | 92423813
09-04-2025 21:44:55.000 | 87972758 |  | 87.9728 | -1114586 | 15612911 | 32535935 | 99991974 | 50088203 | 21772455 | 34748161 | 0.000000 | 90839798
09-04-2025 21:44:50.000 | 88607273 |  | 88.6073 | -9694560 | 15612071 | 32771782 | 99994019 | 50089787 | 21650008 | 34748161 | 0.000000 | 89363052
09-04-2025 21:44:45.000 | 87726359 |  | 87.7264 | -1057006 | 15613821 | 32443364 | 99992744 | 50094231 | 21527588 | 34748161 | 0.000000 | 87980728
09-04-2025 21:44:40.000 | 88280047 |  | 88.28 | -9208183 | 15610928 | 32653320 | 99994560 | 50091377 | 21405479 | 34748161 | 0.000000 | 86641068
09-04-2025 21:44:35.000 | 87840672 |  | 87.8407 | -1114940 | 15610640 | 32492654 | 99991943 | 50099510 | 21283291 | 34748161 | 0.000000 | 85208237
09-04-2025 21:44:30.000 | 87784570 |  | 87.7846 | -1293148 | 15611677 | 32469607 | 99989151 | 50097458 | 21161635 | 34748161 | 0.000000 | 83507576
09-04-2025 21:44:25.000 | 87847945 |  | 87.8479 | -9963283 | 15609684 | 32495879 | 99993568 | 50099594 | 21039676 | 34748161 | 0.000000 | 81917480
09-04-2025 21:44:20.000 | 87383625 |  | 87.3836 | -1383684 | 15613057 | 32318916 | 99987465 | 50104107 | 20918268 | 34748161 | 0.000000 | 80329994
09-04-2025 21:44:15.000 | 88151844 |  | 88.1518 | -1168202 | 15610634 | 32607637 | 99991219 | 50087425 | 20796328 | 34748161 | 0.000000 | 78470001
09-04-2025 21:44:10.000 | 87332352 |  | 87.3324 | -1153601 | 15608758 | 32307627 | 99991280 | 50100166 | 20674572 | 34748161 | 0.000000 | 76893997
09-04-2025 21:44:05.000 | 86937563 |  | 86.9376 | -1321347 | 15613629 | 32152625 | 99988449 | 50110405 | 20553631 | 34748161 | 0.000000 | 75117935
09-04-2025 21:44:00.000 | 87189422 |  | 87.1894 | -1039816 | 15611459 | 32248845 | 99992889 | 50112141 | 20432873 | 34748161 | 0.000000 | 73392761
09-04-2025 21:43:55.000 | 86479773 |  | 86.4798 | -1252130 | 15615855 | 31978462 | 99989517 | 50126675 | 20312168 | 34748161 | 0.000000 | 71911354
09-04-2025 21:43:50.000 | 87729398 |  | 87.7294 | -1030569 | 15612630 | 32445918 | 99993103 | 50098808 | 20191336 | 34748161 | 0.000000 | 70154846
09-04-2025 21:43:45.000 | 87522383 |  | 87.5224 | -9634229 | 15614494 | 32365391 | 99993942 | 50099094 | 20069363 | 34748161 | 0.000000 | 68807037
09-04-2025 21:43:40.000 | 87880391 |  | 87.8804 | -8408448 | 15612403 | 32501597 | 99995422 | 50101261 | 19947521 | 34748161 | 0.000000 | 67578064
09-04-2025 21:43:35.000 | 87939969 |  | 87.94 | -8847072 | 15614931 | 32518411 | 99994942 | 50094257 | 19825422 | 34748161 | 0.000000 | 66394135
09-04-2025 21:43:30.000 | 88880367 |  | 88.8804 | -9609158 | 15611672 | 32873137 | 99994156 | 50084217 | 19702766 | 34748161 | 0.000000 | 65160141
09-04-2025 21:43:25.000 | 88748328 |  | 88.7483 | -7721666 | 15607378 | 32832815 | 99996216 | 50088425 | 19579348 | 34748161 | 0.000000 | 63922661
09-04-2025 21:43:20.000 | 87642828 |  | 87.6428 | -1022891 | 15609743 | 32420100 | 99993187 | 50112247 | 19457197 | 34748161 | 0.000000 | 62680630
09-04-2025 21:43:15.000 | 86941742 |  | 86.9417 | -1275931 | 15611520 | 32158218 | 99989235 | 50123028 | 19335854 | 34748161 | 0.000000 | 61167496
09-04-2025 21:43:10.000 | 87287461 |  | 87.2875 | -1187350 | 15609391 | 32290115 | 99990753 | 50114521 | 19214693 | 34748161 | 0.000000 | 59382236
09-04-2025 21:43:05.000 | 86213586 |  | 86.2136 | -1110483 | 15612631 | 31885891 | 99991707 | 50130409 | 19094146 | 34748161 | 0.000000 | 57744308
09-04-2025 21:43:00.000 | 86365602 |  | 86.3656 | -8709051 | 15616539 | 31933689 | 99994919 | 50125610 | 18974373 | 34748161 | 0.000000 | 56335381
09-04-2025 21:42:55.000 | 87356531 |  | 87.3565 | -8583147 | 15616400 | 32300203 | 99995171 | 50111507 | 18854010 | 34748161 | 0.000000 | 55099094
09-04-2025 21:42:50.000 | 88496320 |  | 88.4963 | -6100933 | 15612459 | 32729194 | 99997627 | 50080017 | 18732293 | 34748161 | 0.000000 | 53964901
09-04-2025 21:42:45.000 | 88407328 |  | 88.4073 | -6342562 | 15606824 | 32708013 | 99997429 | 50074661 | 18609617 | 34748161 | 0.000000 | 53085709
09-04-2025 21:42:40.000 | 87451133 |  | 87.4511 | -7887526 | 15611220 | 32345300 | 99995934 | 50097057 | 18487129 | 34748161 | 0.000000 | 52071484
09-04-2025 21:42:35.000 | 86990219 |  | 86.9902 | -9015355 | 15612290 | 32172832 | 99994629 | 50104828 | 18366055 | 34748161 | 0.000000 | 51019943
09-04-2025 21:42:30.000 | 87301203 |  | 87.3012 | -7101278 | 15610697 | 32290366 | 99996689 | 50098579 | 18244898 | 34748161 | 0.000000 | 49757404
09-04-2025 21:42:25.000 | 86630438 |  | 86.6304 | -9853141 | 15611776 | 32041133 | 99993530 | 50109268 | 18124076 | 34748161 | 0.000000 | 48628197
09-04-2025 21:42:20.000 | 86417578 |  | 86.4176 | -8283105 | 15614604 | 31956133 | 99995407 | 50097897 | 18003684 | 34748161 | 0.000000 | 47426067
09-04-2025 21:42:15.000 | 86542352 |  | 86.5424 | -7505724 | 15613702 | 32003962 | 99996239 | 50093197 | 17883629 | 34748161 | 0.000000 | 46372181
09-04-2025 21:42:10.000 | 86887969 |  | 86.888 | -6230729 | 15617371 | 32123618 | 99997429 | 50095371 | 17763215 | 34748161 | 0.000000 | 45416000
09-04-2025 21:42:05.000 | 86971031 |  | 86.971 | -5640580 | 15613824 | 32161606 | 99997894 | 50087429 | 17642379 | 34748161 | 0.000000 | 44738022
09-04-2025 21:42:00.000 | 87872039 |  | 87.872 | -6614771 | 15615073 | 32492407 | 99997169 | 50077526 | 17520848 | 34748161 | 0.000000 | 44011150
09-04-2025 21:41:55.000 | 88728078 |  | 88.7281 | -4537669 | 15613694 | 32811489 | 99998695 | 50067440 | 17398275 | 34748161 | 0.000000 | 43237606
09-04-2025 21:41:50.000 | 88856500 |  | 88.8565 | -5778933 | 15609701 | 32867451 | 99997887 | 50072960 | 17275035 | 34748161 | 0.000000 | 42570301
09-04-2025 21:41:45.000 | 89346805 |  | 89.3468 | -7403062 | 15606850 | 33055942 | 99996567 | 50079361 | 17151262 | 34748161 | 0.000000 | 41629940
09-04-2025 21:41:40.000 | 88228055 |  | 88.2281 | -1102690 | 15607352 | 32642051 | 99992188 | 50095654 | 17027828 | 34748161 | 0.000000 | 40351696
09-04-2025 21:41:35.000 | 87430820 |  | 87.4308 | -9455150 | 15610401 | 32339622 | 99994156 | 50119038 | 16905539 | 34748161 | 0.000000 | 38816021
09-04-2025 21:41:30.000 | 86901625 |  | 86.9016 | -9917103 | 15610841 | 32143948 | 99993492 | 50132656 | 16784721 | 34748161 | 0.000000 | 37443108
09-04-2025 21:41:25.000 | 86989453 |  | 86.9895 | -9939771 | 15610108 | 32177468 | 99993469 | 50124912 | 16663893 | 34748161 | 0.000000 | 36067219
09-04-2025 21:41:20.000 | 86409406 |  | 86.4094 | -1103361 | 15614030 | 31955291 | 99991852 | 50126827 | 16543449 | 34748161 | 0.000000 | 34553684
09-04-2025 21:41:15.000 | 86414617 |  | 86.4146 | -6966179 | 15612467 | 31959275 | 99996750 | 50121712 | 16423359 | 34748161 | 0.000000 | 33286705
09-04-2025 21:41:10.000 | 86279609 |  | 86.2796 | -7023328 | 15616117 | 31902043 | 99996689 | 50122715 | 16303280 | 34748161 | 0.000000 | 32316936
09-04-2025 21:41:05.000 | 87342844 |  | 87.3428 | -6119208 | 15614399 | 32298672 | 99997543 | 50109619 | 16182999 | 34748161 | 0.000000 | 31398800
09-04-2025 21:41:00.000 | 87744133 |  | 87.7441 | -4506474 | 15612975 | 32449104 | 99998680 | 50091537 | 16061475 | 34748161 | 0.000000 | 30648079
09-04-2025 21:40:55.000 | 88201859 |  | 88.2019 | -6368099 | 15610957 | 32623530 | 99997391 | 50083992 | 15939407 | 34748161 | 0.000000 | 29885187
09-04-2025 21:40:50.000 | 88030492 |  | 88.0305 | -6876212 | 15609687 | 32562148 | 99996948 | 50080059 | 15816653 | 34748161 | 0.000000 | 28985321
09-04-2025 21:40:45.000 | 87612445 |  | 87.6124 | -6482393 | 15607876 | 32412588 | 99997261 | 50093361 | 15694644 | 34748161 | 0.000000 | 28108425
09-04-2025 21:40:40.000 | 87496938 |  | 87.4969 | -8690564 | 15613068 | 32358716 | 99995071 | 50094067 | 15572984 | 34748161 | 0.000000 | 27023775
09-04-2025 21:40:35.000 | 86992961 |  | 86.993 | -6571727 | 15611268 | 32175413 | 99997147 | 50106236 | 15451660 | 34748161 | 0.000000 | 26020565
09-04-2025 21:40:30.000 | 87168414 |  | 87.1684 | -6011250 | 15614443 | 32233125 | 99997620 | 50101425 | 15330755 | 34748161 | 0.000000 | 25017038
09-04-2025 21:40:25.000 | 86934016 |  | 86.934 | -4291277 | 15615016 | 32145259 | 99998779 | 50116871 | 15209854 | 34748161 | 0.000000 | 24383787
09-04-2025 21:40:20.000 | 87961242 |  | 87.9612 | -5558997 | 15619347 | 32516157 | 99998001 | 50094692 | 15088549 | 34748161 | 0.000000 | 23737625
09-04-2025 21:40:15.000 | 89572172 |  | 89.5722 | -2464686 | 15609695 | 33132131 | 99999619 | 50064037 | 14965517 | 34748161 | 0.000000 | 23268379
09-04-2025 21:40:10.000 | 88717125 |  | 88.7171 | -5047712 | 15612251 | 32810420 | 99998383 | 50092575 | 14841467 | 34748161 | 0.000000 | 22770624
09-04-2025 21:40:05.000 | 88526531 |  | 88.5265 | -5657520 | 15610242 | 32744814 | 99997955 | 50099461 | 14718095 | 34748161 | 0.000000 | 22096647
09-04-2025 21:40:00.000 | 88515250 |  | 88.5152 | -7021836 | 15611705 | 32737971 | 99996857 | 50105709 | 14595216 | 34748161 | 0.000000 | 21139297
09-04-2025 21:39:55.000 | 87801602 |  | 87.8016 | -7467507 | 15610396 | 32476418 | 99996384 | 50116852 | 14472820 | 34748161 | 0.000000 | 20154541
09-04-2025 21:39:50.000 | 87731141 |  | 87.7311 | -4212778 | 15609575 | 32450979 | 99998848 | 50119846 | 14350947 | 34748161 | 0.000000 | 19228014
09-04-2025 21:39:45.000 | 87054914 |  | 87.0549 | -6740748 | 15611957 | 32197078 | 99997002 | 50133724 | 14229778 | 34748161 | 0.000000 | 18474802
09-04-2025 21:39:40.000 | 87199328 |  | 87.1993 | -4967735 | 15612352 | 32248789 | 99998375 | 50125294 | 14108744 | 34748161 | 0.000000 | 17607918
09-04-2025 21:39:35.000 | 87213961 |  | 87.214 | -6280157 | 15611930 | 32255400 | 99997406 | 50126232 | 13987401 | 34748161 | 0.000000 | 16889103
09-04-2025 21:39:30.000 | 86821352 |  | 86.8214 | -6623873 | 15611738 | 32110671 | 99997093 | 50134922 | 13866351 | 34748161 | 0.000000 | 16154375
09-04-2025 21:39:25.000 | 86328211 |  | 86.3282 | -6063542 | 15617079 | 31917717 | 99997536 | 50140633 | 13745921 | 34748161 | 0.000000 | 15376987
09-04-2025 21:39:20.000 | 87387555 |  | 87.3876 | -4789042 | 15614808 | 32313728 | 99998497 | 50124538 | 13625283 | 34748161 | 0.000000 | 14713941
09-04-2025 21:39:15.000 | 87845398 |  | 87.8454 | -4666263 | 15611814 | 32489214 | 99998589 | 50116180 | 13503670 | 34748161 | 0.000000 | 14152284
09-04-2025 21:39:10.000 | 88364016 |  | 88.364 | -4581987 | 15612915 | 32678657 | 99998657 | 50105965 | 13381432 | 34748161 | 0.000000 | 13501616
09-04-2025 21:39:05.000 | 88841930 |  | 88.8419 | -2759232 | 15612143 | 32858740 | 99999519 | 50101501 | 13258845 | 34748161 | 0.000000 | 12964866
09-04-2025 21:39:00.000 | 88235906 |  | 88.2359 | -2353205 | 15612828 | 32630752 | 99999641 | 50104172 | 13135819 | 34748161 | 0.000000 | 12631159
09-04-2025 21:38:55.000 | 88014898 |  | 88.0149 | -3632779 | 15608848 | 32557581 | 99999146 | 50109699 | 13013352 | 34748161 | 0.000000 | 12273323
09-04-2025 21:38:50.000 | 88221477 |  | 88.2215 | -2752610 | 15609661 | 32632329 | 99999512 | 50102299 | 12890883 | 34748161 | 0.000000 | 11761164
09-04-2025 21:38:45.000 | 87765250 |  | 87.7652 | -5876561 | 15610506 | 32462229 | 99997757 | 50114353 | 12768883 | 34748161 | 0.000000 | 11232023
09-04-2025 21:38:40.000 | 86954516 |  | 86.9545 | -3596127 | 15610355 | 32162527 | 99999146 | 50119102 | 12647177 | 34748161 | 0.000000 | 10573092
09-04-2025 21:38:35.000 | 86161258 |  | 86.1613 | -3034942 | 15618164 | 31853225 | 99999382 | 50148479 | 12526619 | 34748161 | 0.000000 | 10121624
09-04-2025 21:38:30.000 | 87017031 |  | 87.017 | -3592802 | 15616268 | 32173027 | 99999146 | 50129978 | 12406882 | 34748161 | 0.000000 | 9735018
09-04-2025 21:38:25.000 | 88024805 |  | 88.0248 | -3138682 | 15617598 | 32543889 | 99999367 | 50103493 | 12285225 | 34748161 | 0.000000 | 9392629
09-04-2025 21:38:20.000 | 89546172 |  | 89.5462 | -77949356 | 15611226 | 33118774 | 100000000 | 50079704 | 12162262 | 34748161 | 0.000000 | 9118868
09-04-2025 21:38:15.000 | 88928922 |  | 88.9289 | -36710304 | 15612783 | 32887581 | 100000000 | 50107693 | 12038132 | 34675518 | 0.000000 | 9097216
09-04-2025 21:38:10.000 | 89121195 |  | 89.1212 | -1056265 | 15610050 | 32964248 | 99999931 | 50111145 | 11914893 | 34675518 | 0.000000 | 8945031
09-04-2025 21:38:05.000 | 88670273 |  | 88.6703 | -3139798 | 15609423 | 32800349 | 99999374 | 50114754 | 11791492 | 34675518 | 0.000000 | 8667072
09-04-2025 21:38:00.000 | 87660773 |  | 87.6608 | -2140919 | 15607692 | 32429243 | 99999702 | 50133446 | 11668502 | 34675518 | 0.000000 | 8272764
09-04-2025 21:37:55.000 | 86360422 |  | 86.3604 | -4044812 | 15612865 | 31938120 | 99998901 | 50159523 | 11547380 | 34675518 | 0.000000 | 7935400
09-04-2025 21:37:50.000 | 85953039 |  | 85.953 | -4067340 | 15616575 | 31780417 | 99998878 | 50161068 | 11427486 | 34675518 | 0.000000 | 7497155
09-04-2025 21:37:45.000 | 87035938 |  | 87.0359 | -1057452 | 15614854 | 32183569 | 99999924 | 50148903 | 11307143 | 34675518 | 0.000000 | 7196746
09-04-2025 21:37:40.000 | 87584766 |  | 87.5848 | 32972683 | 15614967 | 32386323 | 100000000 | 50136250 | 11186205 | 34672913 | 0.000000 | 7054528
09-04-2025 21:37:35.000 | 88086531 |  | 88.0865 | -2434082 | 15614362 | 32572634 | 99999619 | 50129478 | 11064389 | 34646652 | 0.000000 | 6942839
09-04-2025 21:37:30.000 | 88939359 |  | 88.9394 | -1766314 | 15612438 | 32892915 | 99999802 | 50104301 | 10941629 | 34646652 | 0.000000 | 6620275
09-04-2025 21:37:25.000 | 88579305 |  | 88.5793 | -3493615 | 15606590 | 32772629 | 99999222 | 50119381 | 10818309 | 34646652 | 0.000000 | 6276393
09-04-2025 21:37:20.000 | 87135320 |  | 87.1353 | -4308371 | 15608557 | 32234260 | 99998779 | 50134228 | 10696074 | 34646652 | 0.000000 | 5749438
09-04-2025 21:37:15.000 | 86127844 |  | 86.1278 | -1256051 | 15609129 | 31859619 | 99999893 | 50160282 | 10575217 | 34646652 | 0.000000 | 5339836
09-04-2025 21:37:10.000 | 85139117 |  | 85.1391 | -3988045 | 15613271 | 31485422 | 99998901 | 50174538 | 10456540 | 34646652 | 0.000000 | 4955703
09-04-2025 21:37:05.000 | 85441516 |  | 85.4415 | -2611353 | 15615531 | 31594041 | 99999535 | 50155567 | 10338331 | 34646652 | 0.000000 | 4521643
09-04-2025 21:37:00.000 | 85682406 |  | 85.6824 | -98961624 | 15617524 | 31678557 | 99999931 | 50141022 | 10219688 | 34638767 | 0.000000 | 4366242
09-04-2025 21:36:55.000 | 86528867 |  | 86.5289 | 324770447 | 15614663 | 31996873 | -99999298 | 50105965 | 10100178 | 34457703 | 0.000000 | 4338753
09-04-2025 21:36:50.000 | 87189617 |  | 87.1896 | 508728088 | 15615313 | 32239626 | -99998299 | 50103676 | 99795039 | 33886864 | 0.000000 | 4338753
09-04-2025 21:36:45.000 | 87897820 |  | 87.8978 | 665454651 | 15617197 | 32497891 | -99997131 | 50086655 | 98579941 | 33139351 | 0.000000 | 4338753
09-04-2025 21:36:40.000 | 88736570 |  | 88.7366 | 614629822 | 15615161 | 32811760 | -99997604 | 50074051 | 97353516 | 32239025 | 0.000000 | 4338753
09-04-2025 21:36:35.000 | 89647250 |  | 89.6472 | 534965576 | 15610987 | 33156907 | -99998222 | 50077042 | 96114580 | 31417492 | 0.000000 | 4338753
09-04-2025 21:36:30.000 | 89723211 |  | 89.7232 | 223053909 | 15610502 | 33186243 | -99999687 | 50081879 | 94868447 | 30857784 | 0.000000 | 4338753
09-04-2025 21:36:25.000 | 90396063 |  | 90.3961 | 79235062 | 15605953 | 33444102 | 100000000 | 50078327 | 93619297 | 30724388 | 0.000000 | 4318359
09-04-2025 21:36:20.000 | 89126695 |  | 89.1267 | 60019485 | 15610704 | 32964558 | 100000000 | 50118481 | 92371357 | 30682358 | 0.000000 | 4291270
09-04-2025 21:36:15.000 | 88266047 |  | 88.266 | -35561718 | 15614142 | 32639265 | 100000000 | 50140900 | 91139951 | 30631769 | 0.000000 | 4291270
09-04-2025 21:36:10.000 | 88418719 |  | 88.4187 | 96855911 | 15609985 | 32704460 | -99999939 | 50127834 | 89914463 | 30585005 | 0.000000 | 4281392
09-04-2025 21:36:05.000 | 87869125 |  | 87.8691 | 81850540 | 15611142 | 32498760 | 100000000 | 50139137 | 88688848 | 30468348 | 0.000000 | 4281392
09-04-2025 21:36:00.000 | 87313430 |  | 87.3134 | 168184845 | 15611834 | 32292397 | -99999817 | 50152473 | 87471338 | 30360775 | 0.000000 | 4281392
09-04-2025 21:35:55.000 | 87377695 |  | 87.3777 | -72320869 | 15614556 | 32309729 | 100000000 | 50159210 | 86259531 | 30273926 | 0.000000 | 4254257
09-04-2025 21:35:50.000 | 87987078 |  | 87.9871 | -1290908 | 15612942 | 32538655 | 99999893 | 50143467 | 85042471 | 30255404 | 0.000000 | 4153560
09-04-2025 21:35:45.000 | 88964961 |  | 88.965 | -93115158 | 15609499 | 32907178 | 99999947 | 50133293 | 83815039 | 30255404 | 0.000000 | 3914140
09-04-2025 21:35:40.000 | 88750344 |  | 88.7503 | -2814593 | 15607127 | 32833975 | 99999496 | 50129051 | 82580010 | 30255404 | 0.000000 | 3653879
09-04-2025 21:35:35.000 | 87875547 |  | 87.8755 | -1835070 | 15608346 | 32506909 | 99999779 | 50145863 | 81350728 | 30255404 | 0.000000 | 3247358
09-04-2025 21:35:30.000 | 85707383 |  | 85.7074 | -3080046 | 15613622 | 31694346 | 99999352 | 50185680 | 80140366 | 30255404 | 0.000000 | 3027959
09-04-2025 21:35:25.000 | 86076516 |  | 86.0765 | -1231932 | 15613639 | 31830432 | 99999901 | 50176590 | 78947109 | 30255404 | 0.000000 | 2748069
09-04-2025 21:35:20.000 | 86214781 |  | 86.2148 | 25994074 | 15614329 | 31880007 | 100000000 | 50173222 | 77749556 | 30220160 | 0.000000 | 2674107
09-04-2025 21:35:15.000 | 86888891 |  | 86.8889 | 87548592 | 15614875 | 32128252 | -99999947 | 50164913 | 76547871 | 30070927 | 0.000000 | 2674107
09-04-2025 21:35:10.000 | 87415711 |  | 87.4157 | 280843140 | 15614195 | 32324578 | -99999481 | 50152588 | 75338911 | 29856976 | 0.000000 | 2674107
09-04-2025 21:35:05.000 | 87533586 |  | 87.5336 | 492293488 | 15611719 | 32373628 | -99998421 | 50147537 | 74123398 | 29362486 | 0.000000 | 2674107
09-04-2025 21:35:00.000 | 87190836 |  | 87.1908 | 225382126 | 15616354 | 32236870 | -99999664 | 50166260 | 72909312 | 28823830 | 0.000000 | 2674107
09-04-2025 21:34:55.000 | 88504844 |  | 88.5048 | 277160522 | 15614907 | 32726343 | -99999512 | 50137943 | 71693154 | 28445459 | 0.000000 | 2674107
09-04-2025 21:34:50.000 | 89795313 |  | 89.7953 | 241592896 | 15609548 | 33214277 | -99999641 | 50118942 | 70455864 | 28063803 | 0.000000 | 2674107
09-04-2025 21:34:45.000 | 88895508 |  | 88.8955 | 307606537 | 15608928 | 32882991 | -99999405 | 50143219 | 69211592 | 27585386 | 0.000000 | 2674107
09-04-2025 21:34:40.000 | 88278367 |  | 88.2784 | 0.469530 | 15611491 | 32649170 | 100000000 | 50163898 | 67981323 | 27346062 | 0.000000 | 2674107
09-04-2025 21:34:35.000 | 88434898 |  | 88.4349 | 39191402 | 15613516 | 32702893 | 100000000 | 50159496 | 66756187 | 27299480 | 0.000000 | 2674107
09-04-2025 21:34:30.000 | 89401773 |  | 89.4018 | -94733063 | 15607999 | 33072173 | 99999947 | 50149658 | 65523008 | 27266657 | 0.000000 | 2635598
09-04-2025 21:34:25.000 | 88666305 |  | 88.6663 | -1608444 | 15605933 | 32804192 | 99999832 | 50162445 | 64283691 | 27266657 | 0.000000 | 2488127
09-04-2025 21:34:20.000 | 87123961 |  | 87.124 | -4072218 | 15609315 | 32227805 | 99998909 | 50196972 | 63060435 | 27266657 | 0.000000 | 2224206
09-04-2025 21:34:15.000 | 87248156 |  | 87.2482 | -4543753 | 15610831 | 32269971 | 99998642 | 50193829 | 61848486 | 27266657 | 0.000000 | 1668890
09-04-2025 21:34:10.000 | 86576141 |  | 86.5761 | -3446817 | 15612018 | 32018806 | 99999207 | 50201752 | 60636450 | 27266657 | 0.000000 | 1165672
09-04-2025 21:34:05.000 | 85679148 |  | 85.6791 | -3995510 | 15618252 | 31675107 | 99998909 | 50221024 | 59437666 | 27266657 | 0.000000 | 0.896868
09-04-2025 21:34:00.000 | 86534836 |  | 86.5348 | -2710403 | 15617785 | 31991492 | 99999512 | 50192352 | 58243706 | 27266657 | 0.000000 | 0.501910
09-04-2025 21:33:55.000 | 87695977 |  | 87.696 | 127952614 | 15611993 | 32432622 | -99999893 | 50169201 | 57032568 | 27257193 | 0.000000 | 0.391987
09-04-2025 21:33:50.000 | 87867188 |  | 87.8672 | -53297134 | 15614476 | 32490784 | 100000000 | 50169544 | 55814531 | 27199278 | 0.000000 | 0.388032
09-04-2025 21:33:45.000 | 89271109 |  | 89.2711 | 40938805 | 15608669 | 33022854 | 100000000 | 50145905 | 54585967 | 27172182 | 0.000000 | 0.315388
09-04-2025 21:33:40.000 | 88990039 |  | 88.99 | 170974396 | 15607694 | 32920767 | -99999817 | 50169018 | 53348989 | 27032423 | 0.000000 | 0.315388
09-04-2025 21:33:35.000 | 87756273 |  | 87.7563 | -1630479 | 15612086 | 32454668 | 99999825 | 50194706 | 52123379 | 26917551 | 0.000000 | 0.293604
09-04-2025 21:33:30.000 | 87945383 |  | 87.9454 | -1009303 | 15610604 | 32527913 | 99999931 | 50185719 | 50903540 | 26917551 | 0.000000 | 0.139219
09-04-2025 21:33:25.000 | 87280289 |  | 87.2803 | 96248924 | 15614644 | 32273428 | -99999939 | 50169624 | 49684692 | 26899780 | 0.000000 | 0.089444
09-04-2025 21:33:20.000 | 86800602 |  | 86.8006 | 184609650 | 15611559 | 32102576 | -99999771 | 50191284 | 48475303 | 26661324 | 0.000000 | 0.089444
09-04-2025 21:33:15.000 | 86213313 |  | 86.2133 | -1420194 | 15615872 | 31876780 | 99999863 | 50205379 | 47274526 | 26456484 | 0.000000 | 0.089444
09-04-2025 21:33:10.000 | 87480008 |  | 87.48 | 256719208 | 15613030 | 32350894 | -99999573 | 50171658 | 46067905 | 26383436 | 0.000000 | 0.003056
09-04-2025 21:33:05.000 | 87642422 |  | 87.6424 | -10217535 | 15612975 | 32411021 | 100000000 | 50169178 | 44850293 | 26101261 | 0.000000 | 0.003056
09-04-2025 21:33:00.000 | 88072891 |  | 88.0729 | 51317596 | 15610775 | 32574802 | 100000000 | 50153751 | 43626494 | 26037558 | 0.000000 | 0.000000
09-04-2025 21:32:55.000 | 87412797 |  | 87.4128 | 199918747 | 15611733 | 32328508 | -99999741 | 50169151 | 42406631 | 25771866 | 0.000000 | 0.000000
09-04-2025 21:32:50.000 | 87134867 |  | 87.1349 | 178838577 | 15613189 | 32222861 | -99999786 | 50178394 | 41194800 | 25554892 | 0.000000 | 0.000000
09-04-2025 21:32:45.000 | 87238938 |  | 87.2389 | 74138489 | 15611728 | 32264309 | 100000000 | 50173878 | 39984126 | 25330156 | 0.000000 | 0.000000
09-04-2025 21:32:40.000 | 86845898 |  | 86.8459 | 283428467 | 15612399 | 32117559 | -99999466 | 50185192 | 38775039 | 25046000 | 0.000000 | 0.000000
09-04-2025 21:32:35.000 | 87066063 |  | 87.0661 | 187360291 | 15612684 | 32198433 | -99999771 | 50180634 | 37568938 | 24680946 | 0.000000 | 0.000000
09-04-2025 21:32:30.000 | 87335734 |  | 87.3357 | 28580797 | 15612926 | 32297478 | 100000000 | 50169945 | 36356851 | 24480593 | 0.000000 | 0.000000
09-04-2025 21:32:25.000 | 87296578 |  | 87.2966 | 164799103 | 15610518 | 32288137 | -99999825 | 50173832 | 35143831 | 24301086 | 0.000000 | 0.000000
09-04-2025 21:32:20.000 | 86988047 |  | 86.988 | 270181702 | 15610600 | 32173774 | -99999519 | 50175655 | 33931880 | 23999918 | 0.000000 | 0.000000
09-04-2025 21:32:15.000 | 86984398 |  | 86.9844 | 82951942 | 15613271 | 32166912 | 100000000 | 50174400 | 32727502 | 23832476 | 0.000000 | 0.000000
09-04-2025 21:32:10.000 | 87705375 |  | 87.7054 | 344916351 | 15610079 | 32440315 | -99999229 | 50155514 | 31514045 | 23586102 | 0.000000 | 0.000000
09-04-2025 21:32:05.000 | 87536250 |  | 87.5362 | 286532684 | 15609514 | 32378835 | -99999466 | 50160175 | 30298438 | 23267809 | 0.000000 | 0.000000
09-04-2025 21:32:00.000 | 87077180 |  | 87.0772 | 368307129 | 15610177 | 32207825 | -99999107 | 50159210 | 29084092 | 22828365 | 0.000000 | 0.000000
09-04-2025 21:31:55.000 | 86905063 |  | 86.9051 | 504720032 | 15611391 | 32141895 | -99998314 | 50164440 | 27874763 | 22329971 | 0.000000 | 0.000000
09-04-2025 21:31:50.000 | 86278625 |  | 86.2786 | 445954010 | 15612606 | 31907644 | -99998665 | 50186504 | 26671443 | 21665565 | 0.000000 | 0.000000
09-04-2025 21:31:45.000 | 86432117 |  | 86.4321 | 321720520 | 15614059 | 31961270 | -99999306 | 50175011 | 25473850 | 21164694 | 0.000000 | 0.000000
09-04-2025 21:31:40.000 | 86278781 |  | 86.2788 | 504612640 | 15612289 | 31909016 | -99998291 | 50182655 | 24271272 | 20485453 | 0.000000 | 0.000000
09-04-2025 21:31:35.000 | 86628883 |  | 86.6289 | 586140930 | 15613631 | 32035537 | -99997711 | 50167770 | 23073608 | 19835827 | 0.000000 | 0.000000
09-04-2025 21:31:30.000 | 86642641 |  | 86.6426 | 648072144 | 15612586 | 32043027 | -99997200 | 50169506 | 21870764 | 18991627 | 0.000000 | 0.000000
09-04-2025 21:31:25.000 | 86478375 |  | 86.4784 | 540453674 | 15611730 | 31983660 | -99998047 | 50170364 | 20668452 | 18134975 | 0.000000 | 0.000000
09-04-2025 21:31:20.000 | 86721586 |  | 86.7216 | 564146484 | 15611030 | 32075334 | -99997887 | 50163303 | 19465621 | 17315498 | 0.000000 | 0.000000
09-04-2025 21:31:15.000 | 86344773 |  | 86.3448 | 893250977 | 15610390 | 31937910 | -99994652 | 50162518 | 18260317 | 16400299 | 0.000000 | 0.000000
09-04-2025 21:31:10.000 | 86258008 |  | 86.258 | 689458374 | 15616854 | 31891921 | -99996803 | 50168320 | 17065096 | 15344483 | 0.000000 | 0.000000
09-04-2025 21:31:05.000 | 87057188 |  | 87.0572 | 785177002 | 15614531 | 32192644 | -99995934 | 50156239 | 15864592 | 14344497 | 0.000000 | 0.000000
09-04-2025 21:31:00.000 | 87686875 |  | 87.6869 | 940080383 | 15613668 | 32427705 | -99994255 | 50139923 | 14652968 | 13236061 | 0.000000 | 0.000000
09-04-2025 21:30:55.000 | 88437992 |  | 88.438 | 842467834 | 15612743 | 32706941 | -99995461 | 50135357 | 13431163 | 11974126 | 0.000000 | 0.000000
09-04-2025 21:30:50.000 | 89416453 |  | 89.4165 | 877278198 | 15609670 | 33075220 | -99995186 | 50128632 | 12197372 | 10820211 | 0.000000 | 0.000000
09-04-2025 21:30:45.000 | 88646602 |  | 88.6466 | 812882629 | 15611356 | 32786848 | -99995796 | 50135075 | 10959167 | 9697289 | 0.000000 | 0.000000
09-04-2025 21:30:40.000 | 88271539 |  | 88.2715 | 689846130 | 15611614 | 32647283 | -99996948 | 50156372 | 972982788 | 8608883 | 0.000000 | 0.000000
09-04-2025 21:30:35.000 | 88202008 |  | 88.202 | 786842102 | 15613097 | 32618709 | -99996017 | 50149803 | 850405762 | 7677274 | 0.000000 | 0.000000
09-04-2025 21:30:30.000 | 88257945 |  | 88.2579 | 582589966 | 15611752 | 32641709 | -99997818 | 50157906 | 728063965 | 6717577 | 0.000000 | 0.000000
09-04-2025 21:30:25.000 | 88553805 |  | 88.5538 | 597491028 | 15607351 | 32760371 | -99997726 | 50138733 | 605338684 | 5945820 | 0.000000 | 0.000000
09-04-2025 21:30:20.000 | 88124625 |  | 88.1246 | 679601868 | 15609483 | 32597295 | -99997025 | 50143269 | 482447418 | 5121928 | 0.000000 | 0.000000
09-04-2025 21:30:15.000 | 86802133 |  | 86.8021 | 793992310 | 15611306 | 32105027 | -99995819 | 50175468 | 360813782 | 4055405 | 0.000000 | 0.000000
09-04-2025 21:30:10.000 | 86794125 |  | 86.7941 | 829786560 | 15613510 | 32097717 | -99995430 | 50171783 | 240290878 | 3030733 | 0.000000 | 0.000000
09-04-2025 21:30:05.000 | 86697305 |  | 86.6973 | 12849995 | 15610436 | 32070066 | -99989021 | 50166222 | 119742142 | 1677366 | 0.000000 | 0.000000
09-04-2025 21:30:00.000 | 86201227 |  | 86.2012 | 12131843 | 15612935 | 31881118 | -99990097 | 50176083 | 21898160 | 663869446 | 0.000000 | 0.000000
09-04-2025 21:29:55.000 | 86535242 |  | 86.5352 | 10223379 | 15615503 | 31998611 | -99993019 | 50168884 | 21778211 | 662245117 | 0.000000 | 0.000000
09-04-2025 21:29:50.000 | 87498633 |  | 87.4986 | 11668693 | 15614247 | 32358062 | -99991112 | 50147846 | 21657152 | 660708374 | 0.000000 | 0.000000
09-04-2025 21:29:45.000 | 87623203 |  | 87.6232 | 11771302 | 15610697 | 32412214 | -99990974 | 50138054 | 21535281 | 659101318 | 0.000000 | 0.000000
09-04-2025 21:29:40.000 | 87754266 |  | 87.7543 | 795263000 | 15610033 | 32459941 | -99995895 | 50141823 | 21413445 | 657684814 | 0.000000 | 0.000000
09-04-2025 21:29:35.000 | 87209164 |  | 87.2092 | 817377991 | 15608870 | 32260630 | -99995605 | 50138348 | 21291732 | 656513855 | 0.000000 | 0.000000
09-04-2025 21:29:30.000 | 86303086 |  | 86.3031 | 10981689 | 15612478 | 31919175 | -99991905 | 50159969 | 21170932 | 655222412 | 0.000000 | 0.000000
09-04-2025 21:29:25.000 | 85979063 |  | 85.9791 | 12063197 | 15618233 | 31788135 | -99990158 | 50167339 | 21051600 | 653787231 | 0.000000 | 0.000000
09-04-2025 21:29:20.000 | 87521273 |  | 87.5213 | 13087229 | 15615055 | 32365322 | -99988823 | 50140106 | 20931549 | 651984131 | 0.000000 | 0.000000
09-04-2025 21:29:15.000 | 88757977 |  | 88.758 | 12682203 | 15613544 | 32825459 | -99989792 | 50109901 | 20809359 | 650305176 | 0.000000 | 0.000000
09-04-2025 21:29:10.000 | 88973180 |  | 88.9732 | 14978000 | 15609366 | 32915190 | -99985832 | 50114643 | 20685613 | 648432922 | 0.000000 | 0.000000
09-04-2025 21:29:05.000 | 88462266 |  | 88.4623 | 14040579 | 15610449 | 32723567 | -99987404 | 50135124 | 20562629 | 646482849 | 0.000000 | 0.000000
09-04-2025 21:29:00.000 | 88989891 |  | 88.9899 | 13766483 | 15609561 | 32920518 | -99988037 | 50135944 | 20439342 | 644619202 | 0.000000 | 0.000000
09-04-2025 21:28:55.000 | 88889703 |  | 88.8897 | 12452997 | 15610924 | 32879612 | -99990189 | 50143387 | 20315666 | 642772034 | 0.000000 | 0.000000
09-04-2025 21:28:50.000 | 88333906 |  | 88.3339 | 13500852 | 15611285 | 32673943 | -99988319 | 50152885 | 20192621 | 640944763 | 0.000000 | 0.000000
09-04-2025 21:28:45.000 | 87680508 |  | 87.6805 | 13887849 | 15612632 | 32429871 | -99987457 | 50166271 | 20070252 | 638946228 | 0.000000 | 0.000000
09-04-2025 21:28:40.000 | 87480688 |  | 87.4807 | 16492012 | 15612611 | 32357588 | -99982231 | 50165016 | 19948434 | 636758728 | 0.000000 | 0.000000
09-04-2025 21:28:35.000 | 87392508 |  | 87.3925 | 18276565 | 15612172 | 32327278 | -99978142 | 50166813 | 19826631 | 634392517 | 0.000000 | 0.000000
09-04-2025 21:28:30.000 | 87102539 |  | 87.1025 | 18121038 | 15616997 | 32210344 | -99978363 | 50187534 | 19705520 | 631857422 | 0.000000 | 0.000000
09-04-2025 21:28:25.000 | 88327320 |  | 88.3273 | 18649611 | 15614268 | 32669146 | -99977715 | 50164864 | 19584016 | 629389954 | 0.000000 | 0.000000
09-04-2025 21:28:20.000 | 89297711 |  | 89.2977 | 20535791 | 15610307 | 33037385 | -99973564 | 50150059 | 19460889 | 626701538 | 0.000000 | 0.000000
09-04-2025 21:28:15.000 | 88875297 |  | 88.8753 | 17702129 | 15606889 | 32886272 | -99980171 | 50159798 | 19336928 | 623893250 | 0.000000 | 0.000000
09-04-2025 21:28:10.000 | 88226383 |  | 88.2264 | 15855326 | 15609370 | 32639600 | -99983856 | 50162998 | 19213725 | 621584900 | 0.000000 | 0.000000
09-04-2025 21:28:05.000 | 86850703 |  | 86.8507 | 15504497 | 15609120 | 32131145 | -99984070 | 50189617 | 19091576 | 619306641 | 0.000000 | 0.000000
09-04-2025 21:28:00.000 | 85983969 |  | 85.984 | 15697789 | 15613343 | 31802461 | -99983337 | 50201870 | 18971436 | 617139099 | 0.000000 | 0.000000
09-04-2025 21:27:55.000 | 86048281 |  | 86.0483 | 16120771 | 15616308 | 31820344 | -99982452 | 50194870 | 18852051 | 614975891 | 0.000000 | 0.000000
09-04-2025 21:27:50.000 | 87325320 |  | 87.3253 | 17461733 | 15614421 | 32297524 | -99980011 | 50163277 | 18731861 | 612757813 | 0.000000 | 0.000000
09-04-2025 21:27:45.000 | 87346117 |  | 87.3461 | 21529639 | 15612709 | 32311660 | -99969635 | 50163895 | 18610648 | 610108643 | 0.000000 | 0.000000
09-04-2025 21:27:40.000 | 87202961 |  | 87.203 | 20627202 | 15613377 | 32256658 | -99972038 | 50174381 | 18489643 | 607167053 | 0.000000 | 0.000000
09-04-2025 21:27:35.000 | 87693328 |  | 87.6933 | 21022251 | 15611281 | 32442524 | -99971275 | 50155113 | 18368191 | 604257446 | 0.000000 | 0.000000
09-04-2025 21:27:30.000 | 87920672 |  | 87.9207 | 21895820 | 15612204 | 32525486 | -99969002 | 50152042 | 18246141 | 601332581 | 0.000000 | 0.000000
09-04-2025 21:27:25.000 | 88157961 |  | 88.158 | 21566262 | 15611997 | 32613413 | -99970093 | 50146881 | 18123936 | 598446960 | 0.000000 | 0.000000
09-04-2025 21:27:20.000 | 88038461 |  | 88.0385 | 19911653 | 15611803 | 32568303 | -99974434 | 50148483 | 18001668 | 595541870 | 0.000000 | 0.000000
09-04-2025 21:27:15.000 | 87467359 |  | 87.4674 | 22137346 | 15611246 | 32360664 | -99967987 | 50156578 | 17879758 | 592660950 | 0.000000 | 0.000000
09-04-2025 21:27:10.000 | 87280023 |  | 87.28 | 21454319 | 15614305 | 32284434 | -99969803 | 50169662 | 17758268 | 589677124 | 0.000000 | 0.000000
09-04-2025 21:27:05.000 | 88500039 |  | 88.5 | 21905962 | 15613401 | 32737180 | -99969383 | 50141083 | 17636395 | 586802490 | 0.000000 | 0.000000
09-04-2025 21:27:00.000 | 88468836 |  | 88.4688 | 23032800 | 15609481 | 32735303 | -99966125 | 50136387 | 17513504 | 583688293 | 0.000000 | 0.000000
09-04-2025 21:26:55.000 | 87686406 |  | 87.6864 | 20019730 | 15610625 | 32440615 | -99973946 | 50161129 | 17391289 | 580467346 | 0.000000 | 0.000000
09-04-2025 21:26:50.000 | 87644172 |  | 87.6442 | 20010948 | 15608534 | 32429197 | -99973946 | 50149361 | 17269361 | 577662842 | 0.000000 | 0.000000
09-04-2025 21:26:45.000 | 87376594 |  | 87.3766 | 18817073 | 15612704 | 32320618 | -99976822 | 50154324 | 17147684 | 574976318 | 0.000000 | 0.000000
09-04-2025 21:26:40.000 | 86764094 |  | 86.7641 | 18786957 | 15611400 | 32097805 | -99976563 | 50170765 | 17026504 | 572351990 | 0.000000 | 0.000000
09-04-2025 21:26:35.000 | 87039141 |  | 87.0391 | 19575322 | 15613710 | 32194548 | -99974716 | 50168037 | 16905859 | 569698853 | 0.000000 | 0.000000
09-04-2025 21:26:30.000 | 86894070 |  | 86.8941 | 20095814 | 15614529 | 32139797 | -99973267 | 50175922 | 16785086 | 566888123 | 0.000000 | 0.000000
09-04-2025 21:26:25.000 | 87805734 |  | 87.8057 | 20254519 | 15610620 | 32484888 | -99973404 | 50153473 | 16663816 | 564087769 | 0.000000 | 0.000000
09-04-2025 21:26:20.000 | 87777828 |  | 87.7778 | 20097950 | 15611055 | 32474021 | -99973801 | 50145416 | 16541660 | 561290405 | 0.000000 | 0.000000
09-04-2025 21:26:15.000 | 87410070 |  | 87.4101 | 19484464 | 15609355 | 32340872 | -99975166 | 50157440 | 16420045 | 558502258 | 0.000000 | 0.000000
09-04-2025 21:26:10.000 | 86193070 |  | 86.1931 | 18188540 | 15615313 | 31877585 | -99977745 | 50177593 | 16299562 | 555823059 | 0.000000 | 0.000000
09-04-2025 21:26:05.000 | 86835875 |  | 86.8359 | 21074758 | 15614440 | 32119517 | -99970566 | 50167007 | 16179714 | 553122070 | 0.000000 | 0.000000
09-04-2025 21:26:00.000 | 87661563 |  | 87.6616 | 21691162 | 15615104 | 32423474 | -99969398 | 50146851 | 16058688 | 550169128 | 0.000000 | 0.000000
09-04-2025 21:25:55.000 | 88413898 |  | 88.4139 | 23265850 | 15611816 | 32710024 | -99965393 | 50134365 | 15936267 | 547079956 | 0.000000 | 0.000000
09-04-2025 21:25:50.000 | 88926391 |  | 88.9264 | 20366404 | 15613625 | 32892915 | -99973785 | 50125008 | 15813280 | 544109619 | 0.000000 | 0.000000
09-04-2025 21:25:45.000 | 88538125 |  | 88.5381 | 24491592 | 15610967 | 32759102 | -99961761 | 50123062 | 15689807 | 540800293 | 0.000000 | 0.000000
09-04-2025 21:25:40.000 | 88625664 |  | 88.6257 | 23848828 | 15611323 | 32790151 | -99963814 | 50130848 | 15566753 | 537402527 | 0.000000 | 0.000000
09-04-2025 21:25:35.000 | 88719781 |  | 88.7198 | 21941213 | 15609714 | 32826592 | -99969437 | 50119469 | 15443619 | 534219666 | 0.000000 | 0.000000
09-04-2025 21:25:30.000 | 88226016 |  | 88.226 | 21814343 | 15609397 | 32644250 | -99969444 | 50125946 | 15320587 | 531167908 | 0.000000 | 0.000000
09-04-2025 21:25:25.000 | 87279914 |  | 87.2799 | 20865891 | 15611058 | 32290251 | -99971436 | 50141998 | 15198369 | 528169861 | 0.000000 | 0.000000
09-04-2025 21:25:20.000 | 86825023 |  | 86.825 | 20269189 | 15614516 | 32114202 | -99972763 | 50165466 | 15077422 | 525223389 | 0.000000 | 0.000000
09-04-2025 21:25:15.000 | 86961914 |  | 86.9619 | 21350291 | 15612349 | 32170654 | -99969872 | 50157005 | 14956780 | 522373474 | 0.000000 | 0.000000
09-04-2025 21:25:10.000 | 87406094 |  | 87.4061 | 19839142 | 15615377 | 32326875 | -99974251 | 50150093 | 14835683 | 519506042 | 0.000000 | 0.000000
09-04-2025 21:25:05.000 | 88246328 |  | 88.2463 | 21663669 | 15613131 | 32643684 | -99969879 | 50137577 | 14713572 | 516560791 | 0.000000 | 0.000000
09-04-2025 21:25:00.000 | 88623016 |  | 88.623 | 22969033 | 15613688 | 32783084 | -99966431 | 50134613 | 14591012 | 513460754 | 0.000000 | 0.000000
09-04-2025 21:24:55.000 | 88438352 |  | 88.4384 | 23000313 | 15611919 | 32718853 | -99966202 | 50135487 | 14468192 | 510184662 | 0.000000 | 0.000000
09-04-2025 21:24:50.000 | 89164070 |  | 89.1641 | 22328237 | 15609663 | 32991011 | -99968658 | 50125000 | 14344781 | 507120697 | 0.000000 | 0.000000
09-04-2025 21:24:45.000 | 89063891 |  | 89.0639 | 20456627 | 15608299 | 32955103 | -99973633 | 50126339 | 14221124 | 504188812 | 0.000000 | 0.000000
09-04-2025 21:24:40.000 | 88510477 |  | 88.5105 | 19636028 | 15608078 | 32750249 | -99975403 | 50132816 | 14097746 | 501430908 | 0.000000 | 0.000000
09-04-2025 21:24:35.000 | 87456234 |  | 87.4562 | 18018690 | 15612006 | 32350886 | -99978783 | 50150471 | 13975520 | 498852966 | 0.000000 | 0.000000
09-04-2025 21:24:30.000 | 86711602 |  | 86.7116 | 22435095 | 15614213 | 32074868 | -99966545 | 50172665 | 13854440 | 496147583 | 0.000000 | 0.000000
09-04-2025 21:24:25.000 | 86620883 |  | 86.6209 | 21834705 | 15617423 | 32034287 | -99968246 | 50187786 | 13734285 | 492947388 | 0.000000 | 0.000000
09-04-2025 21:24:20.000 | 87846203 |  | 87.8462 | 21721738 | 15612965 | 32497432 | -99969444 | 50154003 | 13613348 | 489867188 | 0.000000 | 0.000000
09-04-2025 21:24:15.000 | 88268922 |  | 88.2689 | 23855010 | 15609247 | 32662461 | -99963501 | 50133213 | 13490926 | 486781586 | 0.000000 | 0.000000
09-04-2025 21:24:10.000 | 87102859 |  | 87.1029 | 23627285 | 15609429 | 32230708 | -99963226 | 50159348 | 13368807 | 483439911 | 0.000000 | 0.000000
09-04-2025 21:24:05.000 | 86423234 |  | 86.4232 | 23945630 | 15611750 | 31975781 | -99961639 | 50162022 | 13248311 | 480149872 | 0.000000 | 0.000000
09-04-2025 21:24:00.000 | 85922656 |  | 85.9227 | 24700613 | 15612835 | 31788484 | -99958702 | 50149250 | 13128447 | 476777557 | 0.000000 | 0.000000
09-04-2025 21:23:55.000 | 85333367 |  | 85.3334 | 23806455 | 15617853 | 31559529 | -99961105 | 50161953 | 13009171 | 473178009 | 0.000000 | 0.000000
09-04-2025 21:23:50.000 | 86614992 |  | 86.615 | 25292485 | 15614573 | 32041392 | -99957390 | 50134060 | 12889909 | 469669281 | 0.000000 | 0.000000
09-04-2025 21:23:45.000 | 87951391 |  | 87.9514 | 27030234 | 15609521 | 32548196 | -99952805 | 50094673 | 12768803 | 466063416 | 0.000000 | 0.000000
09-04-2025 21:23:40.000 | 87387102 |  | 87.3871 | 27543354 | 15606586 | 32345908 | -99950363 | 50098545 | 12646761 | 462239197 | 0.000000 | 0.000000
09-04-2025 21:23:35.000 | 85644492 |  | 85.6445 | 27274326 | 15612379 | 31689656 | -99949333 | 50134186 | 12526702 | 458402893 | 0.000000 | 0.000000
09-04-2025 21:23:30.000 | 84937906 |  | 84.9379 | 27755774 | 15617084 | 31419373 | -99946648 | 50137291 | 12408415 | 454570526 | 0.000000 | 0.000000
09-04-2025 21:23:25.000 | 86215422 |  | 86.2154 | 30259924 | 15617137 | 31894468 | -99938461 | 50106651 | 12289904 | 450607666 | 0.000000 | 0.000000
09-04-2025 21:23:20.000 | 87346836 |  | 87.3468 | 31370251 | 15616703 | 32314773 | -99935570 | 50083649 | 12169516 | 446347473 | 0.000000 | 0.000000
09-04-2025 21:23:15.000 | 88977961 |  | 88.978 | 32553989 | 15612200 | 32928647 | -99933136 | 50059250 | 12047392 | 441912292 | 0.000000 | 0.000000
09-04-2025 21:23:10.000 | 88994805 |  | 88.9948 | 33107993 | 15607044 | 32947014 | -99930870 | 50067394 | 11923782 | 437392059 | 0.000000 | 0.000000
09-04-2025 21:23:05.000 | 88224352 |  | 88.2244 | 30273923 | 15610047 | 32651523 | -99941177 | 50071873 | 11800787 | 432979004 | 0.000000 | 0.000000
09-04-2025 21:23:00.000 | 87687164 |  | 87.6872 | 31060708 | 15612543 | 32449363 | -99937325 | 50089767 | 11678416 | 428628845 | 0.000000 | 0.000000
09-04-2025 21:22:55.000 | 87150031 |  | 87.15 | 30420671 | 15614591 | 32245173 | -99939133 | 50107243 | 11556901 | 424222321 | 0.000000 | 0.000000
09-04-2025 21:22:50.000 | 88500266 |  | 88.5003 | 29289631 | 15612626 | 32746836 | -99945282 | 50090725 | 11435328 | 420161285 | 0.000000 | 0.000000
09-04-2025 21:22:45.000 | 89294828 |  | 89.2948 | 28336135 | 15608542 | 33048386 | -99949692 | 50071133 | 11311944 | 416151886 | 0.000000 | 0.000000
09-04-2025 21:22:40.000 | 88505594 |  | 88.5056 | 27064334 | 15610146 | 32754446 | -99953278 | 50088196 | 11188356 | 412244659 | 0.000000 | 0.000000
09-04-2025 21:22:35.000 | 87107586 |  | 87.1076 | 27888162 | 15611517 | 32233005 | -99948792 | 50120098 | 11065864 | 408374756 | 0.000000 | 0.000000
09-04-2025 21:22:30.000 | 86822352 |  | 86.8224 | 26015740 | 15613199 | 32121812 | -99955139 | 50130501 | 10945279 | 404616211 | 0.000000 | 0.000000
09-04-2025 21:22:25.000 | 87173977 |  | 87.174 | 25170396 | 15611821 | 32253621 | -99958344 | 50120461 | 10824580 | 400980591 | 0.000000 | 0.000000
09-04-2025 21:22:20.000 | 87178758 |  | 87.1788 | 28466909 | 15612331 | 32258081 | -99946732 | 50117516 | 10703224 | 397371094 | 0.000000 | 0.000000
09-04-2025 21:22:15.000 | 86974289 |  | 86.9743 | 25295798 | 15611979 | 32179661 | -99957733 | 50130791 | 10582488 | 393541565 | 0.000000 | 0.000000
09-04-2025 21:22:10.000 | 87219414 |  | 87.2194 | 26038198 | 15609947 | 32275464 | -99955467 | 50110027 | 10461417 | 390078949 | 0.000000 | 0.000000
09-04-2025 21:22:05.000 | 87128961 |  | 87.129 | 24405896 | 15611011 | 32237778 | -99960793 | 50111835 | 10340146 | 386652802 | 0.000000 | 0.000000
09-04-2025 21:22:00.000 | 85599609 |  | 85.5996 | 25545317 | 15612099 | 31671423 | -99955498 | 50129597 | 10219812 | 383143921 | 0.000000 | 0.000000
09-04-2025 21:21:55.000 | 85550594 |  | 85.5506 | 26715752 | 15617438 | 31643804 | -99951279 | 50135593 | 10100945 | 379532928 | 0.000000 | 0.000000
09-04-2025 21:21:50.000 | 86832672 |  | 86.8327 | 29371033 | 15614916 | 32126782 | -99942841 | 50102268 | 99815820 | 375734192 | 0.000000 | 0.000000
09-04-2025 21:21:45.000 | 88041047 |  | 88.041 | 30150584 | 15612447 | 32578633 | -99941414 | 50068924 | 98599912 | 371654419 | 0.000000 | 0.000000
09-04-2025 21:21:40.000 | 87797414 |  | 87.7974 | 32351843 | 15612584 | 32491497 | -99932182 | 50065575 | 97377061 | 367406830 | 0.000000 | 0.000000
09-04-2025 21:21:35.000 | 87920328 |  | 87.9203 | 30655996 | 15614264 | 32531304 | -99939270 | 50081482 | 96157354 | 363020020 | 0.000000 | 0.000000
09-04-2025 21:21:30.000 | 88370727 |  | 88.3707 | 34210342 | 15614074 | 32703403 | -99925156 | 50070866 | 94935957 | 358631805 | 0.000000 | 0.000000
09-04-2025 21:21:25.000 | 88367414 |  | 88.3674 | 32965256 | 15613068 | 32701631 | -99930489 | 50071095 | 93711855 | 353981659 | 0.000000 | 0.000000
09-04-2025 21:21:20.000 | 89333758 |  | 89.3338 | 32519866 | 15609860 | 33064985 | -99933807 | 50064087 | 92479619 | 349471008 | 0.000000 | 0.000000
09-04-2025 21:21:15.000 | 89545969 |  | 89.546 | 31493242 | 15607979 | 33145991 | -99938210 | 50063053 | 91237881 | 345053436 | 0.000000 | 0.000000
09-04-2025 21:21:10.000 | 88528930 |  | 88.5289 | 28383435 | 15605924 | 32770791 | -99948647 | 50074467 | 89999229 | 340838623 | 0.000000 | 0.000000
09-04-2025 21:21:05.000 | 87136703 |  | 87.1367 | 27301572 | 15611445 | 32243176 | -99950951 | 50101746 | 88775664 | 337066925 | 0.000000 | 0.000000
09-04-2025 21:21:00.000 | 85970688 |  | 85.9707 | 28292305 | 15614183 | 31807593 | -99945892 | 50129124 | 87572734 | 333103882 | 0.000000 | 0.000000
09-04-2025 21:20:55.000 | 86568359 |  | 86.5684 | 30067002 | 15616938 | 32025029 | -99939735 | 50112644 | 86378584 | 329226837 | 0.000000 | 0.000000
09-04-2025 21:20:50.000 | 87527867 |  | 87.5279 | 30761929 | 15616399 | 32381743 | -99938301 | 50094208 | 85172012 | 325051880 | 0.000000 | 0.000000
09-04-2025 21:20:45.000 | 88366898 |  | 88.3669 | 31445291 | 15613323 | 32698757 | -99936745 | 50078903 | 83948721 | 320543915 | 0.000000 | 0.000000
09-04-2025 21:20:40.000 | 88668859 |  | 88.6689 | 31249143 | 15610772 | 32815693 | -99937958 | 50060745 | 82718857 | 316154083 | 0.000000 | 0.000000
09-04-2025 21:20:35.000 | 88955227 |  | 88.9552 | 29240278 | 15607751 | 32925347 | -99946022 | 50062813 | 81485449 | 311979340 | 0.000000 | 0.000000
09-04-2025 21:20:30.000 | 88215039 |  | 88.215 | 29399526 | 15607167 | 32652981 | -99944511 | 50063965 | 80255239 | 307938538 | 0.000000 | 0.000000
09-04-2025 21:20:25.000 | 86341945 |  | 86.3419 | 28761387 | 15612134 | 31949590 | -99944565 | 50091747 | 79040327 | 303857544 | 0.000000 | 0.000000
09-04-2025 21:20:20.000 | 85818922 |  | 85.8189 | 30488914 | 15615436 | 31751790 | -99936951 | 50107838 | 77844468 | 299786407 | 0.000000 | 0.000000
09-04-2025 21:20:15.000 | 86075023 |  | 86.075 | 31302527 | 15618192 | 31841890 | -99933937 | 50082695 | 76654404 | 295541504 | 0.000000 | 0.000000
09-04-2025 21:20:10.000 | 87226844 |  | 87.2268 | 34079189 | 15613212 | 32281628 | -99923767 | 50063763 | 75450669 | 291065308 | 0.000000 | 0.000000
09-04-2025 21:20:05.000 | 87255836 |  | 87.2558 | 35780557 | 15614913 | 32291321 | -99916031 | 50062199 | 74240869 | 286307800 | 0.000000 | 0.000000
09-04-2025 21:20:00.000 | 87210922 |  | 87.2109 | 36727896 | 15617829 | 32270093 | -99911438 | 50059029 | 73029639 | 281395020 | 0.000000 | 0.000000
09-04-2025 21:19:55.000 | 88268242 |  | 88.2682 | 36825732 | 15616027 | 32664705 | -99913086 | 50057663 | 71812871 | 276313599 | 0.000000 | 0.000000
09-04-2025 21:19:50.000 | 89537602 |  | 89.5376 | 34460989 | 15611511 | 33139460 | -99926018 | 50032261 | 70581333 | 271304626 | 0.000000 | 0.000000
09-04-2025 21:19:45.000 | 90081648 |  | 90.0816 | 33622642 | 15607225 | 33348496 | -99930420 | 50023815 | 69333306 | 266603455 | 0.000000 | 0.000000
09-04-2025 21:19:40.000 | 89319734 |  | 89.3197 | 31381025 | 15608314 | 33061516 | -99938339 | 50051239 | 68086294 | 262096741 | 0.000000 | 0.000000
09-04-2025 21:19:35.000 | 88126867 |  | 88.1269 | 32036582 | 15611602 | 32615271 | -99933990 | 50076530 | 66855176 | 257788025 | 0.000000 | 0.000000
09-04-2025 21:19:30.000 | 87831242 |  | 87.8312 | 30031809 | 15614974 | 32495659 | -99941597 | 50088966 | 65633154 | 253449310 | 0.000000 | 0.000000
09-04-2025 21:19:25.000 | 88165305 |  | 88.1653 | 30615073 | 15612424 | 32625063 | -99939766 | 50079079 | 64411704 | 249268326 | 0.000000 | 0.000000
09-04-2025 21:19:20.000 | 88448016 |  | 88.448 | 29480596 | 15611843 | 32729785 | -99944496 | 50070724 | 63184492 | 245141083 | 0.000000 | 0.000000
09-04-2025 21:19:15.000 | 88025688 |  | 88.0257 | 30780342 | 15609892 | 32579573 | -99938919 | 50075829 | 61956831 | 240893509 | 0.000000 | 0.000000
09-04-2025 21:19:10.000 | 87779648 |  | 87.7796 | 27720159 | 15610536 | 32482966 | -99950172 | 50089371 | 60737246 | 236765717 | 0.000000 | 0.000000
09-04-2025 21:19:05.000 | 87651180 |  | 87.6512 | 29226731 | 15610369 | 32437715 | -99944450 | 50081352 | 59518149 | 232842712 | 0.000000 | 0.000000
09-04-2025 21:19:00.000 | 86924672 |  | 86.9247 | 29963960 | 15610784 | 32169456 | -99940643 | 50089901 | 58303398 | 228817123 | 0.000000 | 0.000000
09-04-2025 21:18:55.000 | 86234336 |  | 86.2343 | 27202258 | 15611779 | 31908801 | -99950287 | 50102329 | 57099756 | 224874496 | 0.000000 | 0.000000
09-04-2025 21:18:50.000 | 86690875 |  | 86.6909 | 29761079 | 15611845 | 32080671 | -99941124 | 50068027 | 55897954 | 221061325 | 0.000000 | 0.000000
09-04-2025 21:18:45.000 | 86109516 |  | 86.1095 | 33633560 | 15616688 | 31861006 | -99923805 | 50089836 | 54696611 | 216648422 | 0.000000 | 0.000000
09-04-2025 21:18:40.000 | 86559117 |  | 86.5591 | 32924092 | 15619923 | 32019497 | -99927742 | 50083488 | 53500337 | 212025238 | 0.000000 | 0.000000
09-04-2025 21:18:35.000 | 88056453 |  | 88.0565 | 37481885 | 15613801 | 32591799 | -99909531 | 50047150 | 52290430 | 207241577 | 0.000000 | 0.000000
09-04-2025 21:18:30.000 | 89189133 |  | 89.1891 | 35151021 | 15609873 | 33015073 | -99922424 | 50044197 | 51059702 | 202149338 | 0.000000 | 0.000000
09-04-2025 21:18:25.000 | 88857789 |  | 88.8578 | 35382598 | 15608391 | 32896443 | -99920815 | 50050220 | 49820400 | 197238937 | 0.000000 | 0.000000
09-04-2025 21:18:20.000 | 88305648 |  | 88.3056 | 32741826 | 15610660 | 32683579 | -99931335 | 50057983 | 48588770 | 192502396 | 0.000000 | 0.000000
09-04-2025 21:18:15.000 | 88107570 |  | 88.1076 | 30864673 | 15610002 | 32609385 | -99938698 | 50067146 | 47364111 | 187963821 | 0.000000 | 0.000000
09-04-2025 21:18:10.000 | 87903617 |  | 87.9036 | 31192710 | 15609998 | 32534458 | -99937103 | 50065937 | 46138999 | 183663300 | 0.000000 | 0.000000
09-04-2025 21:18:05.000 | 87125133 |  | 87.1251 | 33209810 | 15610492 | 32248232 | -99927429 | 50079781 | 44922056 | 179224701 | 0.000000 | 0.000000
09-04-2025 21:18:00.000 | 86406984 |  | 86.407 | 32196682 | 15613016 | 31976487 | -99930649 | 50099586 | 43717520 | 174697968 | 0.000000 | 0.000000
09-04-2025 21:17:55.000 | 86559992 |  | 86.56 | 30361350 | 15614104 | 32028357 | -99938545 | 50092979 | 42517632 | 170420212 | 0.000000 | 0.000000
09-04-2025 21:17:50.000 | 87050242 |  | 87.0502 | 29903557 | 15611378 | 32214351 | -99941048 | 50083649 | 41312124 | 166213058 | 0.000000 | 0.000000
09-04-2025 21:17:45.000 | 86271633 |  | 86.2716 | 33015059 | 15611466 | 31932029 | -99926857 | 50091217 | 40105085 | 161941025 | 0.000000 | 0.000000
09-04-2025 21:17:40.000 | 85909922 |  | 85.9099 | 31434060 | 15615938 | 31786082 | -99933128 | 50097527 | 38911235 | 157531006 | 0.000000 | 0.000000
09-04-2025 21:17:35.000 | 86266898 |  | 86.2669 | 32017151 | 15616479 | 31917581 | -99931198 | 50078976 | 37715515 | 153014160 | 0.000000 | 0.000000
09-04-2025 21:17:30.000 | 87000766 |  | 87.0008 | 34060942 | 15614786 | 32194673 | -99923454 | 50058910 | 36511982 | 148480728 | 0.000000 | 0.000000
09-04-2025 21:17:25.000 | 87439813 |  | 87.4398 | 33175945 | 15612547 | 32360457 | -99928101 | 50060650 | 35302251 | 143708755 | 0.000000 | 0.000000
09-04-2025 21:17:20.000 | 88071367 |  | 88.0714 | 35268215 | 15610896 | 32600259 | -99919914 | 50042187 | 34083743 | 139022614 | 0.000000 | 0.000000
09-04-2025 21:17:15.000 | 87781328 |  | 87.7813 | 34369309 | 15610458 | 32492642 | -99923439 | 50037403 | 32862375 | 134173462 | 0.000000 | 0.000000
09-04-2025 21:17:10.000 | 86965836 |  | 86.9658 | 35256113 | 15609764 | 32193818 | -99917923 | 50048786 | 31645554 | 129442337 | 0.000000 | 0.000000
09-04-2025 21:17:05.000 | 86370102 |  | 86.3701 | 31593079 | 15613109 | 31961541 | -99933167 | 50078888 | 30443157 | 124626762 | 0.000000 | 0.000000
09-04-2025 21:17:00.000 | 86909180 |  | 86.9092 | 35613110 | 15611912 | 32169114 | -99916145 | 50063293 | 29240537 | 120035126 | 0.000000 | 0.000000
09-04-2025 21:16:55.000 | 86658063 |  | 86.6581 | 34089673 | 15612529 | 32072722 | -99922714 | 50069893 | 28035388 | 115144333 | 0.000000 | 0.000000
09-04-2025 21:16:50.000 | 87225539 |  | 87.2255 | 33326689 | 15610466 | 32286150 | -99927086 | 50053097 | 26829043 | 110562103 | 0.000000 | 0.000000
09-04-2025 21:16:45.000 | 86605594 |  | 86.6056 | 33181260 | 15613605 | 32050059 | -99926689 | 50060745 | 25617815 | 105858665 | 0.000000 | 0.000000
09-04-2025 21:16:40.000 | 86112250 |  | 86.1123 | 34674956 | 15614757 | 31867390 | -99919029 | 50067436 | 24417480 | 101095955 | 0.000000 | 0.000000
09-04-2025 21:16:35.000 | 86828156 |  | 86.8282 | 36133804 | 15615095 | 32133384 | -99913521 | 50039211 | 23219570 | 96314713 | 0.000000 | 0.000000
09-04-2025 21:16:30.000 | 87314430 |  | 87.3144 | 37947991 | 15608761 | 32328960 | -99905693 | 50024021 | 22010190 | 91181732 | 0.000000 | 0.000000
09-04-2025 21:16:25.000 | 86819477 |  | 86.8195 | 37437695 | 15612097 | 32138757 | -99907158 | 50041321 | 20799700 | 85945656 | 0.000000 | 0.000000
09-04-2025 21:16:20.000 | 86962875 |  | 86.9629 | 37477715 | 15612447 | 32190891 | -99907265 | 50040142 | 19594962 | 80805618 | 0.000000 | 0.000000
09-04-2025 21:16:15.000 | 86745219 |  | 86.7452 | 38591345 | 15612999 | 32110945 | -99901184 | 50036316 | 18386796 | 75490608 | 0.000000 | 0.000000
09-04-2025 21:16:10.000 | 86738625 |  | 86.7386 | 39008438 | 15618911 | 32097324 | -99899025 | 50047215 | 17181560 | 70118965 | 0.000000 | 0.000000
09-04-2025 21:16:05.000 | 88192617 |  | 88.1926 | 40162588 | 15620748 | 32632114 | -99896469 | 50037594 | 15971700 | 64632782 | 0.000000 | 0.000000
09-04-2025 21:16:00.000 | 91079938 |  | 91.0799 | 42017739 | 15613353 | 33717024 | -99893761 | 49993443 | 14730712 | 58939590 | 0.000000 | 0.000000
09-04-2025 21:15:55.000 | 92356781 |  | 92.3568 | 44652314 | 15603920 | 34213911 | -99883331 | 49951691 | 13457772 | 53093349 | 0.000000 | 0.000000
09-04-2025 21:15:50.000 | 90620672 |  | 90.6207 | 40942463 | 15604086 | 33565696 | -99898094 | 50003071 | 12183773 | 47036770 | 0.000000 | 0.000000
09-04-2025 21:15:45.000 | 89351422 |  | 89.3514 | 35441848 | 15605561 | 33084634 | -99921425 | 50040035 | 10934630 | 41769405 | 0.000000 | 0.000000
09-04-2025 21:15:40.000 | 88546727 |  | 88.5467 | 36882476 | 15604294 | 32792119 | -99913361 | 50050816 | 969784302 | 36889561 | 0.000000 | 0.000000
09-04-2025 21:15:35.000 | 86140539 |  | 86.1405 | 32969959 | 15610538 | 31883916 | -99926834 | 50091496 | 848282227 | 31866659 | 0.000000 | 0.000000
09-04-2025 21:15:30.000 | 86188547 |  | 86.1885 | 31172910 | 15615621 | 31889089 | -99934654 | 50085434 | 728870483 | 27456028 | 0.000000 | 0.000000
09-04-2025 21:15:25.000 | 86081305 |  | 86.0813 | 30121792 | 15617077 | 31844768 | -99938835 | 50082794 | 609254395 | 23048967 | 0.000000 | 0.000000
09-04-2025 21:15:20.000 | 87278844 |  | 87.2788 | 33281414 | 15614318 | 32297234 | -99927376 | 50057976 | 489068329 | 18664553 | 0.000000 | 0.000000
09-04-2025 21:15:15.000 | 88816992 |  | 88.817 | 33015593 | 15609441 | 32875444 | -99930984 | 50021519 | 366781769 | 14051481 | 0.000000 | 0.000000
09-04-2025 21:15:10.000 | 88713180 |  | 88.7132 | 35368579 | 15606524 | 32846499 | -99920616 | 50018944 | 243428223 | 9358027 | 0.000000 | 0.000000
09-04-2025 21:15:05.000 | 87445852 |  | 87.4459 | 33434819 | 15611812 | 32364407 | -99926987 | 50046852 | 120926720 | 4603139 | 0.000000 | 0.000000
09-04-2025 21:15:00.000 | 86823031 |  | 86.823 | 33315037 | 15614902 | 32128652 | -99926460 | 50070198 | 21897063 | 944505249 | 0.000000 | 0.000000
09-04-2025 21:14:55.000 | 87423758 |  | 87.4238 | 33736145 | 15614156 | 32351855 | -99925629 | 50050632 | 21776520 | 940016052 | 0.000000 | 0.000000
09-04-2025 21:14:50.000 | 88195680 |  | 88.1957 | 32577459 | 15612011 | 32639902 | -99931847 | 50038448 | 21654707 | 935410217 | 0.000000 | 0.000000
09-04-2025 21:14:45.000 | 88249688 |  | 88.2497 | 35449070 | 15613303 | 32661218 | -99919418 | 50032154 | 21532047 | 930716492 | 0.000000 | 0.000000
09-04-2025 21:14:40.000 | 87944859 |  | 87.9449 | 36926753 | 15613535 | 32550291 | -99911964 | 50049309 | 21409799 | 925691101 | 0.000000 | 0.000000
09-04-2025 21:14:35.000 | 88187227 |  | 88.1872 | 35854458 | 15615706 | 32633962 | -99917450 | 50043247 | 21287811 | 920650452 | 0.000000 | 0.000000
09-04-2025 21:14:30.000 | 89739695 |  | 89.7397 | 34521433 | 15609435 | 33218879 | -99926094 | 50016430 | 21164281 | 915752747 | 0.000000 | 0.000000
09-04-2025 21:14:25.000 | 89599367 |  | 89.5994 | 34380151 | 15608902 | 33167588 | -99926468 | 50017315 | 21039629 | 911068176 | 0.000000 | 0.000000
09-04-2025 21:14:20.000 | 87992094 |  | 87.9921 | 33751865 | 15609014 | 32572485 | -99926514 | 50062954 | 20916047 | 906223816 | 0.000000 | 0.000000
09-04-2025 21:14:15.000 | 86412016 |  | 86.412 | 34141511 | 15616345 | 31974026 | -99922035 | 50090744 | 20794830 | 901506714 | 0.000000 | 0.000000
09-04-2025 21:14:10.000 | 86455289 |  | 86.4553 | 34360762 | 15617300 | 31988960 | -99921112 | 50087612 | 20675055 | 896677307 | 0.000000 | 0.000000
09-04-2025 21:14:05.000 | 88535359 |  | 88.5354 | 34927930 | 15615934 | 32760532 | -99922272 | 50044945 | 20553676 | 891966858 | 0.000000 | 0.000000
09-04-2025 21:14:00.000 | 89225914 |  | 89.2259 | 35301919 | 15611602 | 33025522 | -99921822 | 50049503 | 20430100 | 886909363 | 0.000000 | 0.000000
09-04-2025 21:13:55.000 | 89902039 |  | 89.902 | 37026809 | 15609076 | 33284407 | -99915291 | 50036789 | 20305641 | 881973694 | 0.000000 | 0.000000
09-04-2025 21:13:50.000 | 89489211 |  | 89.4892 | 36502913 | 15602998 | 33142705 | -99916908 | 50052887 | 20180863 | 876851501 | 0.000000 | 0.000000
09-04-2025 21:13:45.000 | 87754742 |  | 87.7547 | 30572004 | 15609475 | 32480107 | -99939369 | 50092884 | 20057496 | 872132446 | 0.000000 | 0.000000
09-04-2025 21:13:40.000 | 86898984 |  | 86.899 | 28773464 | 15611148 | 32157510 | -99945229 | 50109455 | 19936252 | 867962769 | 0.000000 | 0.000000
09-04-2025 21:13:35.000 | 86607547 |  | 86.6075 | 30040466 | 15611084 | 32051897 | -99939896 | 50109871 | 19815549 | 863906921 | 0.000000 | 0.000000
09-04-2025 21:13:30.000 | 86271539 |  | 86.2715 | 30117627 | 15611950 | 31925630 | -99939117 | 50101677 | 19695621 | 859749939 | 0.000000 | 0.000000
09-04-2025 21:13:25.000 | 85966227 |  | 85.9662 | 30547559 | 15608954 | 31819866 | -99936928 | 50095749 | 19575916 | 855565125 | 0.000000 | 0.000000
09-04-2025 21:13:20.000 | 85594336 |  | 85.5943 | 32622310 | 15613110 | 31676687 | -99927452 | 50090538 | 19456873 | 851297791 | 0.000000 | 0.000000
09-04-2025 21:13:15.000 | 85473797 |  | 85.4738 | 34199585 | 15617512 | 31625227 | -99920052 | 50080799 | 19337973 | 846725586 | 0.000000 | 0.000000
09-04-2025 21:13:10.000 | 86090828 |  | 86.0908 | 35932830 | 15617017 | 31856821 | -99913010 | 50066753 | 19218938 | 841786804 | 0.000000 | 0.000000
09-04-2025 21:13:05.000 | 87717336 |  | 87.7173 | 37170330 | 15615250 | 32463179 | -99910339 | 50023830 | 19098566 | 836756409 | 0.000000 | 0.000000
09-04-2025 21:13:00.000 | 87889445 |  | 87.8894 | 39634182 | 15608438 | 32544858 | -99898476 | 50013252 | 18976408 | 831419189 | 0.000000 | 0.000000
09-04-2025 21:12:55.000 | 87580703 |  | 87.5807 | 38596597 | 15611572 | 32422439 | -99903030 | 50032883 | 18854514 | 825942261 | 0.000000 | 0.000000
09-04-2025 21:12:50.000 | 87140633 |  | 87.1406 | 38615432 | 15614556 | 32253713 | -99901955 | 50042397 | 18733111 | 820571960 | 0.000000 | 0.000000
09-04-2025 21:12:45.000 | 87466266 |  | 87.4663 | 39131956 | 15618737 | 32366965 | -99900070 | 50041859 | 18612010 | 815192993 | 0.000000 | 0.000000
09-04-2025 21:12:40.000 | 89187797 |  | 89.1878 | 39399233 | 15614310 | 33011743 | -99902565 | 50012585 | 18489617 | 809718201 | 0.000000 | 0.000000
09-04-2025 21:12:35.000 | 89552164 |  | 89.5522 | 41001997 | 15609936 | 33158494 | -99895348 | 50011333 | 18365324 | 804140564 | 0.000000 | 0.000000
09-04-2025 21:12:30.000 | 89388391 |  | 89.3884 | 40684990 | 15608195 | 33101094 | -99896584 | 50022114 | 18241012 | 798492859 | 0.000000 | 0.000000
09-04-2025 21:12:25.000 | 88590930 |  | 88.5909 | 36262834 | 15609901 | 32795693 | -99916328 | 50045322 | 18117350 | 793001465 | 0.000000 | 0.000000
09-04-2025 21:12:20.000 | 88581977 |  | 88.582 | 35063530 | 15609431 | 32791650 | -99921753 | 50047985 | 17994139 | 788053955 | 0.000000 | 0.000000
09-04-2025 21:12:15.000 | 87759781 |  | 87.7598 | 35099241 | 15610088 | 32486460 | -99920120 | 50046783 | 17871361 | 783184204 | 0.000000 | 0.000000
09-04-2025 21:12:10.000 | 86934727 |  | 86.9347 | 35991475 | 15610622 | 32182493 | -99914406 | 50072037 | 17749738 | 778134033 | 0.000000 | 0.000000
09-04-2025 21:12:05.000 | 86283313 |  | 86.2833 | 34318848 | 15617004 | 31925474 | -99920990 | 50091171 | 17629686 | 773230591 | 0.000000 | 0.000000
09-04-2025 21:12:00.000 | 86966617 |  | 86.9666 | 35963115 | 15615911 | 32182505 | -99914604 | 50080593 | 17509486 | 768360107 | 0.000000 | 0.000000
09-04-2025 21:11:55.000 | 87762625 |  | 87.7626 | 35446987 | 15611685 | 32484641 | -99918533 | 50063709 | 17388393 | 763298279 | 0.000000 | 0.000000
09-04-2025 21:11:50.000 | 88240602 |  | 88.2406 | 34733569 | 15608427 | 32667026 | -99922623 | 50044178 | 17266076 | 758494812 | 0.000000 | 0.000000
09-04-2025 21:11:45.000 | 87601391 |  | 87.6014 | 38705046 | 15608188 | 32437478 | -99902534 | 50051537 | 17143740 | 753482056 | 0.000000 | 0.000000
09-04-2025 21:11:40.000 | 85931992 |  | 85.932 | 35854185 | 15618130 | 31795913 | -99913071 | 50086304 | 17023250 | 748273560 | 0.000000 | 0.000000
09-04-2025 21:11:35.000 | 87296953 |  | 87.297 | 38377556 | 15616743 | 32306714 | -99903503 | 50070389 | 16903361 | 743129761 | 0.000000 | 0.000000
09-04-2025 21:11:30.000 | 88668125 |  | 88.6681 | 41569458 | 15611979 | 32828496 | -99890282 | 50028656 | 16781188 | 737669800 | 0.000000 | 0.000000
09-04-2025 21:11:25.000 | 88842992 |  | 88.843 | 39856375 | 15610749 | 32893467 | -99899521 | 50025352 | 16657934 | 731982544 | 0.000000 | 0.000000
09-04-2025 21:11:20.000 | 88060078 |  | 88.0601 | 40450532 | 15610873 | 32604583 | -99894661 | 50038353 | 16534998 | 726294434 | 0.000000 | 0.000000
09-04-2025 21:11:15.000 | 87997383 |  | 87.9974 | 38916152 | 15611579 | 32577031 | -99902351 | 50036366 | 16412725 | 720817505 | 0.000000 | 0.000000
09-04-2025 21:11:10.000 | 88046469 |  | 88.0465 | 37537822 | 15608923 | 32599094 | -99909241 | 50031891 | 16290207 | 715423157 | 0.000000 | 0.000000
09-04-2025 21:11:05.000 | 87203117 |  | 87.2031 | 36803494 | 15611311 | 32280955 | -99911057 | 50049969 | 16167961 | 710174377 | 0.000000 | 0.000000
09-04-2025 21:11:00.000 | 86490148 |  | 86.4901 | 36582246 | 15612821 | 32013875 | -99910667 | 50065845 | 16047216 | 704948792 | 0.000000 | 0.000000
09-04-2025 21:10:55.000 | 86610266 |  | 86.6103 | 36338447 | 15613329 | 32056787 | -99912102 | 50066986 | 15927001 | 699920593 | 0.000000 | 0.000000
09-04-2025 21:10:50.000 | 87000000 |  | 87 | 37175056 | 15612191 | 32204705 | -99908829 | 50068649 | 15806500 | 694961182 | 0.000000 | 0.000000
09-04-2025 21:10:45.000 | 86896813 |  | 86.8968 | 35447688 | 15613937 | 32160146 | -99916901 | 50056305 | 15685635 | 689987671 | 0.000000 | 0.000000
09-04-2025 21:10:40.000 | 86627680 |  | 86.6277 | 39707979 | 15611432 | 32072742 | -99895111 | 50058926 | 15564990 | 684833191 | 0.000000 | 0.000000
09-04-2025 21:10:35.000 | 86629047 |  | 86.629 | 36678301 | 15614402 | 32062083 | -99910492 | 50068504 | 15444657 | 679584229 | 0.000000 | 0.000000
09-04-2025 21:10:30.000 | 87125461 |  | 87.1255 | 38633149 | 15612775 | 32251995 | -99901833 | 50059620 | 15324091 | 674447693 | 0.000000 | 0.000000
09-04-2025 21:10:25.000 | 87357164 |  | 87.3572 | 38843628 | 15612188 | 32339106 | -99901291 | 50057003 | 15202958 | 669062439 | 0.000000 | 0.000000
09-04-2025 21:10:20.000 | 87838641 |  | 87.8386 | 37900474 | 15612643 | 32514619 | -99907043 | 50038155 | 15081373 | 663835083 | 0.000000 | 0.000000
09-04-2025 21:10:15.000 | 87546078 |  | 87.5461 | 39467964 | 15613356 | 32407488 | -99898537 | 50051853 | 14959209 | 658458557 | 0.000000 | 0.000000
09-04-2025 21:10:10.000 | 87385070 |  | 87.3851 | 40047183 | 15615939 | 32343660 | -99895149 | 50061306 | 14837830 | 652905884 | 0.000000 | 0.000000
09-04-2025 21:10:05.000 | 87799906 |  | 87.7999 | 39195134 | 15614590 | 32498198 | -99900505 | 50050846 | 14716310 | 647379028 | 0.000000 | 0.000000
09-04-2025 21:10:00.000 | 88997773 |  | 88.9978 | 38564697 | 15611408 | 32946650 | -99906250 | 50036743 | 14593823 | 642026123 | 0.000000 | 0.000000
09-04-2025 21:09:55.000 | 89428461 |  | 89.4285 | 37591584 | 15609797 | 33107354 | -99911766 | 50032772 | 14469935 | 636705078 | 0.000000 | 0.000000
09-04-2025 21:09:50.000 | 88478813 |  | 88.4788 | 37953247 | 15608828 | 32759133 | -99908127 | 50041424 | 14346095 | 631482300 | 0.000000 | 0.000000
09-04-2025 21:09:45.000 | 88067039 |  | 88.067 | 35376465 | 15610491 | 32599485 | -99919418 | 50059105 | 14223480 | 626308228 | 0.000000 | 0.000000
09-04-2025 21:09:40.000 | 87862656 |  | 87.8627 | 35251399 | 15609515 | 32526003 | -99919609 | 50046665 | 14101293 | 621479553 | 0.000000 | 0.000000
09-04-2025 21:09:35.000 | 87157258 |  | 87.1573 | 37733091 | 15609234 | 32269834 | -99906418 | 50069283 | 13979502 | 616427551 | 0.000000 | 0.000000
09-04-2025 21:09:30.000 | 86237328 |  | 86.2373 | 38141436 | 15614787 | 31919102 | -99902336 | 50079063 | 13859233 | 611256775 | 0.000000 | 0.000000
09-04-2025 21:09:25.000 | 86798914 |  | 86.7989 | 36338733 | 15614007 | 32125522 | -99912476 | 50057800 | 13739522 | 605984985 | 0.000000 | 0.000000
09-04-2025 21:09:20.000 | 87243547 |  | 87.2435 | 37001719 | 15611431 | 32295974 | -99910179 | 50043324 | 13618658 | 600916321 | 0.000000 | 0.000000
09-04-2025 21:09:15.000 | 86414883 |  | 86.4149 | 38042996 | 15613525 | 31987012 | -99903236 | 50068813 | 13497773 | 595606201 | 0.000000 | 0.000000
09-04-2025 21:09:10.000 | 86632516 |  | 86.6325 | 38255266 | 15614800 | 32065056 | -99902649 | 50058693 | 13377736 | 590408325 | 0.000000 | 0.000000
09-04-2025 21:09:05.000 | 87541375 |  | 87.5414 | 38166938 | 15612779 | 32404841 | -99905090 | 50051441 | 13256694 | 584981384 | 0.000000 | 0.000000
09-04-2025 21:09:00.000 | 88461805 |  | 88.4618 | 37455178 | 15609709 | 32750339 | -99910484 | 50028099 | 13134518 | 579717407 | 0.000000 | 0.000000
09-04-2025 21:08:55.000 | 88053938 |  | 88.0539 | 36687129 | 15612196 | 32593059 | -99913315 | 50031464 | 13011692 | 574531311 | 0.000000 | 0.000000
09-04-2025 21:08:50.000 | 87741430 |  | 87.7414 | 34094331 | 15613203 | 32471714 | -99924591 | 50043236 | 12889709 | 569462524 | 0.000000 | 0.000000
09-04-2025 21:08:45.000 | 88088977 |  | 88.089 | 35499470 | 15617432 | 32593298 | -99918900 | 50030285 | 12767476 | 564622131 | 0.000000 | 0.000000
09-04-2025 21:08:40.000 | 88401617 |  | 88.4016 | 39441719 | 15612280 | 32726050 | -99900620 | 50029060 | 12644970 | 559330444 | 0.000000 | 0.000000
09-04-2025 21:08:35.000 | 88815781 |  | 88.8158 | 35432190 | 15613031 | 32870872 | -99920517 | 50032955 | 12522307 | 554138306 | 0.000000 | 0.000000
09-04-2025 21:08:30.000 | 89913180 |  | 89.9132 | 34555449 | 15605187 | 33291946 | -99926231 | 50010948 | 12398056 | 549290894 | 0.000000 | 0.000000
09-04-2025 21:08:25.000 | 88496719 |  | 88.4967 | 34427009 | 15605120 | 32768193 | -99924416 | 50038239 | 12273607 | 544411804 | 0.000000 | 0.000000
09-04-2025 21:08:20.000 | 86134805 |  | 86.1348 | 33870127 | 15610367 | 31883442 | -99922775 | 50083195 | 12152022 | 539621521 | 0.000000 | 0.000000
09-04-2025 21:08:15.000 | 85383547 |  | 85.3835 | 34193633 | 15612371 | 31602275 | -99919907 | 50086468 | 12033031 | 534963379 | 0.000000 | 0.000000
09-04-2025 21:08:10.000 | 85283352 |  | 85.2834 | 36112754 | 15616540 | 31559980 | -99910469 | 50086262 | 11914704 | 530199341 | 0.000000 | 0.000000
09-04-2025 21:08:05.000 | 86032836 |  | 86.0328 | 37157070 | 15618624 | 31833894 | -99906860 | 50068325 | 11796154 | 525169250 | 0.000000 | 0.000000
09-04-2025 21:08:00.000 | 88247266 |  | 88.2473 | 38995569 | 15612589 | 32667305 | -99902512 | 50018177 | 11675490 | 519957031 | 0.000000 | 0.000000
09-04-2025 21:07:55.000 | 89384445 |  | 89.3844 | 37707852 | 15608171 | 33094839 | -99911133 | 50007854 | 11552088 | 514596069 | 0.000000 | 0.000000
09-04-2025 21:07:50.000 | 88513164 |  | 88.5132 | 37016567 | 15608240 | 32772031 | -99912666 | 50029022 | 11428551 | 509309113 | 0.000000 | 0.000000
09-04-2025 21:07:45.000 | 87774961 |  | 87.775 | 34881230 | 15612374 | 32486963 | -99921135 | 50036877 | 11306246 | 504331635 | 0.000000 | 0.000000
09-04-2025 21:07:40.000 | 87734984 |  | 87.735 | 34547737 | 15612559 | 32471389 | -99922562 | 50042191 | 11184293 | 499389984 | 0.000000 | 0.000000
09-04-2025 21:07:35.000 | 88303867 |  | 88.3039 | 36163079 | 15612406 | 32684334 | -99916245 | 50029072 | 11062117 | 494569061 | 0.000000 | 0.000000
09-04-2025 21:07:30.000 | 87979320 |  | 87.9793 | 37356309 | 15610568 | 32569983 | -99909981 | 50025723 | 10939611 | 489454041 | 0.000000 | 0.000000
09-04-2025 21:07:25.000 | 87896336 |  | 87.8963 | 35455017 | 15611560 | 32534260 | -99918747 | 50040569 | 10817508 | 484288361 | 0.000000 | 0.000000
09-04-2025 21:07:20.000 | 87783602 |  | 87.7836 | 36036255 | 15610420 | 32495793 | -99915848 | 50036728 | 10695376 | 479330902 | 0.000000 | 0.000000
09-04-2025 21:07:15.000 | 87547266 |  | 87.5473 | 34434434 | 15612362 | 32402102 | -99922737 | 50039116 | 10573564 | 474477997 | 0.000000 | 0.000000
09-04-2025 21:07:10.000 | 87324891 |  | 87.3249 | 35907493 | 15611346 | 32324270 | -99915565 | 50043407 | 10452001 | 469512787 | 0.000000 | 0.000000
09-04-2025 21:07:05.000 | 86911508 |  | 86.9115 | 34586465 | 15610742 | 32170708 | -99920914 | 50052776 | 10331282 | 464559631 | 0.000000 | 0.000000
09-04-2025 21:07:00.000 | 87102328 |  | 87.1023 | 33320791 | 15610893 | 32239180 | -99926910 | 50049900 | 10210532 | 459924347 | 0.000000 | 0.000000
09-04-2025 21:06:55.000 | 86650406 |  | 86.6504 | 32807651 | 15615549 | 32062532 | -99928398 | 50055698 | 10089729 | 455316620 | 0.000000 | 0.000000
09-04-2025 21:06:50.000 | 86691352 |  | 86.6914 | 33019604 | 15617234 | 32073835 | -99927544 | 50060539 | 99692646 | 450591492 | 0.000000 | 0.000000
09-04-2025 21:06:45.000 | 87964781 |  | 87.9648 | 34464644 | 15612816 | 32555505 | -99923332 | 50038311 | 98480752 | 445736542 | 0.000000 | 0.000000
09-04-2025 21:06:40.000 | 89154563 |  | 89.1546 | 34929761 | 15608451 | 33005295 | -99923340 | 50004635 | 97249395 | 440874298 | 0.000000 | 0.000000
09-04-2025 21:06:35.000 | 88015805 |  | 88.0158 | 36541375 | 15608296 | 32587104 | -99913925 | 50041889 | 96016318 | 435900238 | 0.000000 | 0.000000
09-04-2025 21:06:30.000 | 86806313 |  | 86.8063 | 31821834 | 15613112 | 32123127 | -99932877 | 50070896 | 94805313 | 431079803 | 0.000000 | 0.000000
09-04-2025 21:06:25.000 | 87554773 |  | 87.5548 | 34634863 | 15610737 | 32408711 | -99921852 | 50042049 | 93594307 | 426633301 | 0.000000 | 0.000000
09-04-2025 21:06:20.000 | 86948297 |  | 86.9483 | 34223247 | 15610442 | 32184414 | -99922630 | 50045757 | 92381055 | 421837250 | 0.000000 | 0.000000
09-04-2025 21:06:15.000 | 86264688 |  | 86.2647 | 36896145 | 15611965 | 31932732 | -99908661 | 50052597 | 91176602 | 416944153 | 0.000000 | 0.000000
09-04-2025 21:06:10.000 | 86084969 |  | 86.085 | 34569451 | 15614730 | 31857134 | -99919464 | 50051773 | 89981846 | 411806366 | 0.000000 | 0.000000
09-04-2025 21:06:05.000 | 86733016 |  | 86.733 | 40459814 | 15613941 | 32108059 | -99891373 | 50030678 | 88780605 | 406695251 | 0.000000 | 0.000000
09-04-2025 21:06:00.000 | 86390836 |  | 86.3908 | 41084512 | 15613661 | 31983218 | -99887108 | 50031494 | 87580566 | 400967926 | 0.000000 | 0.000000
09-04-2025 21:05:55.000 | 87321953 |  | 87.322 | 39822283 | 15615658 | 32320913 | -99896179 | 50011784 | 86376963 | 395409027 | 0.000000 | 0.000000
09-04-2025 21:05:50.000 | 87765328 |  | 87.7653 | 39154177 | 15613724 | 32487161 | -99900635 | 50006435 | 85160967 | 389787231 | 0.000000 | 0.000000
09-04-2025 21:05:45.000 | 88910039 |  | 88.91 | 38155701 | 15612935 | 32910264 | -99908043 | 49984146 | 83934473 | 384536804 | 0.000000 | 0.000000
09-04-2025 21:05:40.000 | 88522203 |  | 88.5222 | 39978000 | 15608584 | 32778894 | -99898178 | 50002869 | 82698818 | 379005859 | 0.000000 | 0.000000
09-04-2025 21:05:35.000 | 87692539 |  | 87.6925 | 38485645 | 15610664 | 32465579 | -99903839 | 50019955 | 81475811 | 373621399 | 0.000000 | 0.000000
09-04-2025 21:05:30.000 | 87537594 |  | 87.5376 | 36412334 | 15610510 | 32405415 | -99913597 | 50027035 | 80258940 | 368423309 | 0.000000 | 0.000000
09-04-2025 21:05:25.000 | 87287898 |  | 87.2879 | 35365195 | 15610170 | 32312129 | -99918022 | 50030182 | 79042573 | 363315826 | 0.000000 | 0.000000
09-04-2025 21:05:20.000 | 86386539 |  | 86.3865 | 35202781 | 15613624 | 31972305 | -99917076 | 50035801 | 77837065 | 358462494 | 0.000000 | 0.000000
09-04-2025 21:05:15.000 | 86306680 |  | 86.3067 | 36213599 | 15614748 | 31941721 | -99912086 | 50029346 | 76638892 | 353560150 | 0.000000 | 0.000000
09-04-2025 21:05:10.000 | 86596359 |  | 86.5964 | 39118887 | 15614671 | 32053545 | -99898125 | 50028030 | 75437583 | 348332397 | 0.000000 | 0.000000
09-04-2025 21:05:05.000 | 87123406 |  | 87.1234 | 38479504 | 15615940 | 32244690 | -99902611 | 50022179 | 74232754 | 342834534 | 0.000000 | 0.000000
09-04-2025 21:05:00.000 | 88226883 |  | 88.2269 | 39764136 | 15612811 | 32660615 | -99898590 | 49988708 | 73015522 | 337458435 | 0.000000 | 0.000000
09-04-2025 21:04:55.000 | 87856602 |  | 87.8566 | 42003560 | 15611928 | 32529734 | -99885910 | 49994450 | 71789619 | 331655579 | 0.000000 | 0.000000
09-04-2025 21:04:50.000 | 87640500 |  | 87.6405 | 40589607 | 15615334 | 32440569 | -99892921 | 50006348 | 70570732 | 325950409 | 0.000000 | 0.000000
09-04-2025 21:04:45.000 | 88196930 |  | 88.1969 | 40589111 | 15614120 | 32648240 | -99894272 | 49995602 | 69349072 | 320352570 | 0.000000 | 0.000000
09-04-2025 21:04:40.000 | 88586813 |  | 88.5868 | 40066545 | 15612521 | 32794629 | -99897873 | 49984123 | 68121177 | 314712494 | 0.000000 | 0.000000
09-04-2025 21:04:35.000 | 88934969 |  | 88.935 | 41263315 | 15609724 | 32931655 | -99892540 | 49979725 | 66888433 | 309072052 | 0.000000 | 0.000000
09-04-2025 21:04:30.000 | 88355547 |  | 88.3555 | 41346489 | 15609873 | 32716997 | -99890686 | 49984425 | 65657183 | 303377075 | 0.000000 | 0.000000
09-04-2025 21:04:25.000 | 87566930 |  | 87.5669 | 41074624 | 15608894 | 32427473 | -99890167 | 50005005 | 64433706 | 297574860 | 0.000000 | 0.000000
09-04-2025 21:04:20.000 | 87315836 |  | 87.3158 | 37875293 | 15608089 | 32330735 | -99906052 | 50003716 | 63218740 | 292096191 | 0.000000 | 0.000000
09-04-2025 21:04:15.000 | 86107711 |  | 86.1077 | 38007000 | 15609909 | 31880806 | -99902733 | 50014439 | 62011777 | 286790558 | 0.000000 | 0.000000
09-04-2025 21:04:10.000 | 85194680 |  | 85.1947 | 40205635 | 15612585 | 31541758 | -99888832 | 50022430 | 60819844 | 281406586 | 0.000000 | 0.000000
09-04-2025 21:04:05.000 | 85038898 |  | 85.0389 | 39606892 | 15616680 | 31475129 | -99891716 | 50020847 | 59639458 | 275849182 | 0.000000 | 0.000000
09-04-2025 21:04:00.000 | 86084836 |  | 86.0848 | 40428745 | 15615092 | 31865828 | -99889900 | 49992058 | 58454458 | 270376801 | 0.000000 | 0.000000
09-04-2025 21:03:55.000 | 86968484 |  | 86.9685 | 42345610 | 15610952 | 32204185 | -99881668 | 49960457 | 57252056 | 264623199 | 0.000000 | 0.000000
09-04-2025 21:03:50.000 | 86992969 |  | 86.993 | 44076152 | 15612336 | 32214512 | -99871895 | 49970211 | 56042705 | 258728149 | 0.000000 | 0.000000
09-04-2025 21:03:45.000 | 86399719 |  | 86.3997 | 41046548 | 15615770 | 31981926 | -99887344 | 49986740 | 54841914 | 252801819 | 0.000000 | 0.000000
09-04-2025 21:03:40.000 | 87691836 |  | 87.6918 | 40616741 | 15617114 | 32455588 | -99892906 | 49958847 | 53637607 | 247163605 | 0.000000 | 0.000000
09-04-2025 21:03:35.000 | 88691320 |  | 88.6913 | 41211553 | 15614603 | 32830828 | -99892220 | 49938721 | 52413589 | 241532028 | 0.000000 | 0.000000
09-04-2025 21:03:30.000 | 89828609 |  | 89.8286 | 40714922 | 15610440 | 33258894 | -99897438 | 49928459 | 51174087 | 235841324 | 0.000000 | 0.000000
09-04-2025 21:03:25.000 | 89983945 |  | 89.9839 | 40962852 | 15605434 | 33327402 | -99896545 | 49933475 | 49923584 | 230088409 | 0.000000 | 0.000000
09-04-2025 21:03:20.000 | 88757438 |  | 88.7574 | 39605037 | 15609293 | 32863977 | -99900597 | 49966312 | 48680410 | 224488800 | 0.000000 | 0.000000
09-04-2025 21:03:15.000 | 87668938 |  | 87.6689 | 40351055 | 15610114 | 32461074 | -99894249 | 49989162 | 47455835 | 218971664 | 0.000000 | 0.000000
09-04-2025 21:03:10.000 | 87221102 |  | 87.2211 | 36919839 | 15614184 | 32281616 | -99910530 | 50004345 | 46243159 | 213545242 | 0.000000 | 0.000000
09-04-2025 21:03:05.000 | 87679359 |  | 87.6794 | 40130396 | 15611653 | 32461396 | -99895424 | 49983837 | 45027397 | 208287842 | 0.000000 | 0.000000
09-04-2025 21:03:00.000 | 87710547 |  | 87.7105 | 38611504 | 15612087 | 32469788 | -99903244 | 49985455 | 43808188 | 202758743 | 0.000000 | 0.000000
09-04-2025 21:02:55.000 | 87291750 |  | 87.2917 | 38190342 | 15611553 | 32315188 | -99904434 | 49992672 | 42591553 | 197385727 | 0.000000 | 0.000000
09-04-2025 21:02:50.000 | 87240711 |  | 87.2407 | 40445286 | 15613194 | 32296770 | -99892708 | 49998943 | 41379272 | 191960266 | 0.000000 | 0.000000
09-04-2025 21:02:45.000 | 87614578 |  | 87.6146 | 41683047 | 15609546 | 32444531 | -99887024 | 49981167 | 40166013 | 186351654 | 0.000000 | 0.000000
09-04-2025 21:02:40.000 | 86666531 |  | 86.6665 | 41598369 | 15610519 | 32092295 | -99885010 | 49996582 | 38952927 | 180569580 | 0.000000 | 0.000000
09-04-2025 21:02:35.000 | 86057586 |  | 86.0576 | 40428633 | 15616521 | 31853330 | -99889832 | 50002285 | 37753877 | 174857498 | 0.000000 | 0.000000
09-04-2025 21:02:30.000 | 86824305 |  | 86.8243 | 40146719 | 15615606 | 32137385 | -99893272 | 49995544 | 36553018 | 169228668 | 0.000000 | 0.000000
09-04-2025 21:02:25.000 | 88243445 |  | 88.2434 | 39350049 | 15612406 | 32666834 | -99900726 | 49968163 | 35340962 | 163800751 | 0.000000 | 0.000000
09-04-2025 21:02:20.000 | 88710781 |  | 88.7108 | 40970415 | 15613981 | 32838872 | -99893524 | 49947933 | 34111006 | 158347565 | 0.000000 | 0.000000
09-04-2025 21:02:15.000 | 88439320 |  | 88.4393 | 42510518 | 15612897 | 32743835 | -99884674 | 49969982 | 32880024 | 152470642 | 0.000000 | 0.000000
09-04-2025 21:02:10.000 | 88849016 |  | 88.849 | 40069182 | 15614354 | 32887676 | -99898460 | 49971573 | 31652300 | 146717087 | 0.000000 | 0.000000
09-04-2025 21:02:05.000 | 89681820 |  | 89.6818 | 43266138 | 15606825 | 33216958 | -99883827 | 49946579 | 30411726 | 140960541 | 0.000000 | 0.000000
09-04-2025 21:02:00.000 | 88301531 |  | 88.3015 | 42579072 | 15606141 | 32707148 | -99883942 | 49974613 | 29173640 | 134989105 | 0.000000 | 0.000000
09-04-2025 21:01:55.000 | 86450234 |  | 86.4502 | 40582878 | 15610728 | 32009941 | -99889999 | 50006004 | 27956414 | 129147095 | 0.000000 | 0.000000
09-04-2025 21:01:50.000 | 85940953 |  | 85.941 | 38883179 | 15613787 | 31812756 | -99897804 | 50002419 | 26758154 | 123665337 | 0.000000 | 0.000000
09-04-2025 21:01:45.000 | 85829156 |  | 85.8292 | 41818257 | 15614198 | 31775754 | -99881516 | 49994339 | 25565295 | 118100830 | 0.000000 | 0.000000
09-04-2025 21:01:40.000 | 85951586 |  | 85.9516 | 40448877 | 15617007 | 31812822 | -99889450 | 49988476 | 24373293 | 112327133 | 0.000000 | 0.000000
09-04-2025 21:01:35.000 | 87702648 |  | 87.7026 | 43313672 | 15611980 | 32474895 | -99878265 | 49953163 | 23168984 | 106537857 | 0.000000 | 0.000000
09-04-2025 21:01:30.000 | 87685367 |  | 87.6854 | 40646475 | 15612612 | 32462424 | -99892731 | 49951862 | 21951177 | 100650719 | 0.000000 | 0.000000
09-04-2025 21:01:25.000 | 87487336 |  | 87.4873 | 41914849 | 15617454 | 32381448 | -99885429 | 49959518 | 20733638 | 95101273 | 0.000000 | 0.000000
09-04-2025 21:01:20.000 | 87981727 |  | 87.9817 | 43691631 | 15615233 | 32571938 | -99876923 | 49960167 | 19515875 | 89071930 | 0.000000 | 0.000000
09-04-2025 21:01:15.000 | 89486594 |  | 89.4866 | 40409392 | 15612199 | 33128220 | -99898201 | 49925621 | 18289561 | 83302429 | 0.000000 | 0.000000
09-04-2025 21:01:10.000 | 89740219 |  | 89.7402 | 41337402 | 15607077 | 33234446 | -99894073 | 49933754 | 17041993 | 77507675 | 0.000000 | 0.000000
09-04-2025 21:01:05.000 | 88743586 |  | 88.7436 | 39442544 | 15607914 | 32862041 | -99901375 | 49958096 | 15802126 | 71928177 | 0.000000 | 0.000000
09-04-2025 21:01:00.000 | 87584883 |  | 87.5849 | 37752288 | 15609774 | 32426484 | -99907234 | 49981602 | 14576209 | 66540565 | 0.000000 | 0.000000
09-04-2025 21:00:55.000 | 87030680 |  | 87.0307 | 36995806 | 15613154 | 32213491 | -99909775 | 49981895 | 13362742 | 61348640 | 0.000000 | 0.000000
09-04-2025 21:00:50.000 | 86629430 |  | 86.6294 | 38235835 | 15614741 | 32064426 | -99902740 | 49985413 | 12156897 | 56102711 | 0.000000 | 0.000000
09-04-2025 21:00:45.000 | 86838328 |  | 86.8383 | 39405576 | 15614546 | 32143462 | -99897202 | 49986401 | 10954875 | 50720119 | 0.000000 | 0.000000
09-04-2025 21:00:40.000 | 87627961 |  | 87.628 | 39733108 | 15614664 | 32435791 | -99897362 | 49968109 | 974564331 | 45289227 | 0.000000 | 0.000000
09-04-2025 21:00:35.000 | 87973406 |  | 87.9734 | 40116846 | 15612268 | 32568689 | -99896187 | 49967617 | 852878540 | 39627701 | 0.000000 | 0.000000
09-04-2025 21:00:30.000 | 88200914 |  | 88.2009 | 40516399 | 15612737 | 32653003 | -99894661 | 49946377 | 730303833 | 34089291 | 0.000000 | 0.000000
09-04-2025 21:00:25.000 | 87978031 |  | 87.978 | 41767280 | 15611342 | 32575266 | -99887497 | 49950146 | 607832336 | 28267067 | 0.000000 | 0.000000
09-04-2025 21:00:20.000 | 87830039 |  | 87.83 | 42297920 | 15610582 | 32523142 | -99884239 | 49959812 | 485642151 | 22345303 | 0.000000 | 0.000000
09-04-2025 21:00:15.000 | 87329305 |  | 87.3293 | 39571934 | 15614841 | 32324519 | -99897491 | 49969887 | 364067719 | 16631767 | 0.000000 | 0.000000
09-04-2025 21:00:10.000 | 87216813 |  | 87.2168 | 40169329 | 15612509 | 32288840 | -99894104 | 49974342 | 242803345 | 10986767 | 0.000000 | 0.000000
09-04-2025 21:00:05.000 | 87335250 |  | 87.3353 | 38972478 | 15614304 | 32326760 | -99900581 | 49978455 | 121744667 | 5434113 | 0.000000 | 0.000000
09-04-2025 21:00:00.000 | 88039578 |  | 88.0396 | 40998140 | 15614210 | 32590642 | -99891747 | 49955799 | 21910686 | 907308899 | 0.000000 | 0.000000
09-04-2025 20:59:55.000 | 88015391 |  | 88.0154 | 41667817 | 15612658 | 32586357 | -99888130 | 49955448 | 21788295 | 901546631 | 0.000000 | 0.000000
09-04-2025 20:59:50.000 | 89257984 |  | 89.258 | 38699678 | 15610116 | 33045584 | -99906143 | 49945320 | 21665328 | 895920715 | 0.000000 | 0.000000
09-04-2025 20:59:45.000 | 89052156 |  | 89.0522 | 40088489 | 15607259 | 32977832 | -99898827 | 49952007 | 21541244 | 890354736 | 0.000000 | 0.000000
09-04-2025 20:59:40.000 | 87698977 |  | 87.699 | 39026396 | 15609814 | 32470552 | -99901131 | 49977985 | 21418398 | 884917908 | 0.000000 | 0.000000
09-04-2025 20:59:35.000 | 87456461 |  | 87.4565 | 39158318 | 15608967 | 32383096 | -99899910 | 49973564 | 21296719 | 879521606 | 0.000000 | 0.000000
09-04-2025 20:59:30.000 | 86821539 |  | 86.8215 | 38602278 | 15609461 | 32146558 | -99901306 | 49978279 | 21175475 | 874152832 | 0.000000 | 0.000000
09-04-2025 20:59:25.000 | 85503891 |  | 85.5039 | 37122493 | 15617937 | 31640317 | -99905884 | 50000984 | 21055754 | 868856323 | 0.000000 | 0.000000
09-04-2025 20:59:20.000 | 86548984 |  | 86.549 | 39373618 | 15617423 | 32030676 | -99896683 | 49980312 | 20936473 | 863572510 | 0.000000 | 0.000000
09-04-2025 20:59:15.000 | 87967555 |  | 87.9676 | 40886335 | 15613405 | 32565713 | -99892159 | 49950630 | 20815334 | 858061401 | 0.000000 | 0.000000
09-04-2025 20:59:10.000 | 88919016 |  | 88.919 | 41039834 | 15610451 | 32923347 | -99893661 | 49942928 | 20692438 | 852428101 | 0.000000 | 0.000000
09-04-2025 20:59:05.000 | 88121484 |  | 88.1215 | 43382524 | 15609022 | 32635891 | -99879036 | 49962265 | 20569063 | 846528381 | 0.000000 | 0.000000
09-04-2025 20:59:00.000 | 87765273 |  | 87.7653 | 42951987 | 15612615 | 32496401 | -99880463 | 49965202 | 20447000 | 840698181 | 0.000000 | 0.000000
09-04-2025 20:58:55.000 | 87591945 |  | 87.5919 | 40166709 | 15610042 | 32432686 | -99895027 | 49973064 | 20325279 | 834849365 | 0.000000 | 0.000000
09-04-2025 20:58:50.000 | 88027211 |  | 88.0272 | 40867944 | 15611760 | 32590859 | -99892403 | 49956837 | 20203141 | 829251282 | 0.000000 | 0.000000
09-04-2025 20:58:45.000 | 87432109 |  | 87.4321 | 41478491 | 15608378 | 32379216 | -99887657 | 49967819 | 20080977 | 823528870 | 0.000000 | 0.000000
09-04-2025 20:58:40.000 | 86327383 |  | 86.3274 | 40102864 | 15614718 | 31955908 | -99892273 | 49992661 | 19960266 | 817825195 | 0.000000 | 0.000000
09-04-2025 20:58:35.000 | 86720844 |  | 86.7208 | 41554966 | 15614162 | 32104849 | -99885391 | 49980831 | 19840492 | 812256958 | 0.000000 | 0.000000
09-04-2025 20:58:30.000 | 86716586 |  | 86.7166 | 39998926 | 15617453 | 32093865 | -99893791 | 49978191 | 19720082 | 806500671 | 0.000000 | 0.000000
09-04-2025 20:58:25.000 | 88007211 |  | 88.0072 | 43249531 | 15614575 | 32581951 | -99879463 | 49949417 | 19598766 | 800807739 | 0.000000 | 0.000000
09-04-2025 20:58:20.000 | 89414203 |  | 89.4142 | 40690967 | 15609672 | 33107351 | -99896606 | 49933315 | 19475596 | 794912964 | 0.000000 | 0.000000
09-04-2025 20:58:15.000 | 89005617 |  | 89.0056 | 38824919 | 15606878 | 32959363 | -99904999 | 49936108 | 19351320 | 789272461 | 0.000000 | 0.000000
09-04-2025 20:58:10.000 | 87196828 |  | 87.1968 | 39138318 | 15608450 | 32288376 | -99899422 | 49975857 | 19228518 | 783779175 | 0.000000 | 0.000000
09-04-2025 20:58:05.000 | 86571219 |  | 86.5712 | 36996548 | 15611699 | 32046702 | -99908806 | 49994041 | 19108104 | 778540833 | 0.000000 | 0.000000
09-04-2025 20:58:00.000 | 86770930 |  | 86.7709 | 37664299 | 15612023 | 32121011 | -99905930 | 49986534 | 18987701 | 773311890 | 0.000000 | 0.000000
09-04-2025 20:57:55.000 | 86634227 |  | 86.6342 | 36152358 | 15612882 | 32066199 | -99913048 | 49986183 | 18867270 | 768126648 | 0.000000 | 0.000000
09-04-2025 20:57:50.000 | 86708188 |  | 86.7082 | 36059307 | 15611777 | 32095808 | -99913635 | 49989292 | 18746873 | 763078369 | 0.000000 | 0.000000
09-04-2025 20:57:45.000 | 87116086 |  | 87.1161 | 34650610 | 15612880 | 32242600 | -99920990 | 49981831 | 18626334 | 758120789 | 0.000000 | 0.000000
09-04-2025 20:57:40.000 | 86897289 |  | 86.8973 | 37589170 | 15613215 | 32164922 | -99906570 | 49982456 | 18505371 | 753125061 | 0.000000 | 0.000000
09-04-2025 20:57:35.000 | 86837461 |  | 86.8375 | 35627751 | 15612657 | 32141411 | -99915939 | 49990227 | 18384660 | 747918274 | 0.000000 | 0.000000
09-04-2025 20:57:30.000 | 86939227 |  | 86.9392 | 38430388 | 15611743 | 32184878 | -99902443 | 49981358 | 18263885 | 742853882 | 0.000000 | 0.000000
09-04-2025 20:57:25.000 | 86631180 |  | 86.6312 | 40029712 | 15609272 | 32079041 | -99893417 | 49991497 | 18143273 | 737364685 | 0.000000 | 0.000000
09-04-2025 20:57:20.000 | 86670453 |  | 86.6705 | 39482749 | 15612593 | 32085798 | -99896400 | 49994316 | 18023162 | 732003540 | 0.000000 | 0.000000
09-04-2025 20:57:15.000 | 86590445 |  | 86.5904 | 38969827 | 15614024 | 32052200 | -99898880 | 50000389 | 17903000 | 726565735 | 0.000000 | 0.000000
09-04-2025 20:57:10.000 | 87191156 |  | 87.1912 | 37860046 | 15618085 | 32264019 | -99905861 | 49993492 | 17782486 | 721224792 | 0.000000 | 0.000000
09-04-2025 20:57:05.000 | 88495148 |  | 88.4951 | 39911489 | 15614329 | 32756702 | -99898453 | 49964516 | 17660609 | 715758667 | 0.000000 | 0.000000
09-04-2025 20:57:00.000 | 88750039 |  | 88.75 | 39986606 | 15611170 | 32857981 | -99898659 | 49945553 | 17537338 | 710208862 | 0.000000 | 0.000000
09-04-2025 20:56:55.000 | 87867664 |  | 87.8677 | 40758179 | 15611853 | 32531626 | -99892593 | 49966946 | 17414518 | 704461365 | 0.000000 | 0.000000
09-04-2025 20:56:50.000 | 88158344 |  | 88.1583 | 36594197 | 15615182 | 32625305 | -99913956 | 49965714 | 17292348 | 698967407 | 0.000000 | 0.000000
09-04-2025 20:56:45.000 | 88859352 |  | 88.8594 | 39776660 | 15613841 | 32892021 | -99899963 | 49965214 | 17169164 | 693732300 | 0.000000 | 0.000000
09-04-2025 20:56:40.000 | 89098016 |  | 89.098 | 39381758 | 15611477 | 32984517 | -99902458 | 49980171 | 17045611 | 688137390 | 0.000000 | 0.000000
09-04-2025 20:56:35.000 | 89465953 |  | 89.466 | 37696370 | 15610254 | 33120491 | -99911354 | 49985168 | 16921582 | 682721558 | 0.000000 | 0.000000
09-04-2025 20:56:30.000 | 89520000 |  | 89.52 | 37701204 | 15608131 | 33144971 | -99911438 | 49991192 | 16797072 | 677504517 | 0.000000 | 0.000000
09-04-2025 20:56:25.000 | 88448898 |  | 88.4489 | 36161487 | 15610447 | 32741775 | -99916527 | 50022991 | 16673273 | 672330627 | 0.000000 | 0.000000
09-04-2025 20:56:20.000 | 88223813 |  | 88.2238 | 35754177 | 15610043 | 32658906 | -99917984 | 50016266 | 16550627 | 667475281 | 0.000000 | 0.000000
09-04-2025 20:56:15.000 | 87758234 |  | 87.7582 | 36688579 | 15609035 | 32490508 | -99912727 | 50026363 | 16428359 | 662355713 | 0.000000 | 0.000000
09-04-2025 20:56:10.000 | 86906609 |  | 86.9066 | 35510669 | 15609188 | 32173564 | -99916626 | 50036846 | 16307014 | 657371155 | 0.000000 | 0.000000
09-04-2025 20:56:05.000 | 86360281 |  | 86.3603 | 36708774 | 15613722 | 31964275 | -99909782 | 50028717 | 16186788 | 652581482 | 0.000000 | 0.000000
09-04-2025 20:56:00.000 | 86144383 |  | 86.1444 | 39071572 | 15614571 | 31886641 | -99897301 | 50033298 | 16067024 | 647269531 | 0.000000 | 0.000000
09-04-2025 20:55:55.000 | 86853977 |  | 86.854 | 39514739 | 15612878 | 32152949 | -99896667 | 50023785 | 15946995 | 641797668 | 0.000000 | 0.000000
09-04-2025 20:55:50.000 | 86920109 |  | 86.9201 | 40540200 | 15612143 | 32180613 | -99891411 | 50018818 | 15826190 | 636226501 | 0.000000 | 0.000000
09-04-2025 20:55:45.000 | 86734203 |  | 86.7342 | 40367576 | 15614758 | 32106497 | -99891869 | 50022995 | 15705586 | 630671082 | 0.000000 | 0.000000
09-04-2025 20:55:40.000 | 86861180 |  | 86.8612 | 42800815 | 15613835 | 32159280 | -99878822 | 50025719 | 15585027 | 624940491 | 0.000000 | 0.000000
09-04-2025 20:55:35.000 | 87495352 |  | 87.4954 | 42392295 | 15614924 | 32390584 | -99882835 | 50014458 | 15464192 | 619055237 | 0.000000 | 0.000000
09-04-2025 20:55:30.000 | 89212125 |  | 89.2121 | 43442144 | 15607505 | 33042202 | -99881645 | 49982010 | 15341722 | 613167114 | 0.000000 | 0.000000
09-04-2025 20:55:25.000 | 88340055 |  | 88.3401 | 42992061 | 15609813 | 32714617 | -99881790 | 49988224 | 15218226 | 607318970 | 0.000000 | 0.000000
09-04-2025 20:55:20.000 | 87299055 |  | 87.2991 | 39785471 | 15612343 | 32318892 | -99896317 | 50020988 | 15095992 | 601416504 | 0.000000 | 0.000000
09-04-2025 20:55:15.000 | 87596328 |  | 87.5963 | 38832888 | 15614968 | 32421953 | -99901878 | 50019157 | 14974818 | 595989014 | 0.000000 | 0.000000
09-04-2025 20:55:10.000 | 88179844 |  | 88.1798 | 37036382 | 15615113 | 32633945 | -99911911 | 50011917 | 14853015 | 590687805 | 0.000000 | 0.000000
09-04-2025 20:55:05.000 | 89119781 |  | 89.1198 | 37250254 | 15612007 | 32988767 | -99912758 | 49997066 | 14729947 | 585449158 | 0.000000 | 0.000000
09-04-2025 20:55:00.000 | 89260422 |  | 89.2604 | 37810640 | 15611237 | 33042529 | -99910400 | 50010754 | 14605905 | 580133972 | 0.000000 | 0.000000
09-04-2025 20:54:55.000 | 89229602 |  | 89.2296 | 36619031 | 15606661 | 33039404 | -99915894 | 50012878 | 14481937 | 574937500 | 0.000000 | 0.000000
09-04-2025 20:54:50.000 | 87877086 |  | 87.8771 | 35377695 | 15609197 | 32531958 | -99919060 | 50039410 | 14358623 | 569939270 | 0.000000 | 0.000000
09-04-2025 20:54:45.000 | 87239578 |  | 87.2396 | 32828975 | 15609020 | 32293472 | -99929268 | 50063812 | 14236978 | 565143555 | 0.000000 | 0.000000
09-04-2025 20:54:40.000 | 86205195 |  | 86.2052 | 32008623 | 15611793 | 31904106 | -99931137 | 50064396 | 14116581 | 560620422 | 0.000000 | 0.000000
09-04-2025 20:54:35.000 | 85691617 |  | 85.6916 | 35719854 | 15614027 | 31715068 | -99913231 | 50060738 | 13996924 | 555883606 | 0.000000 | 0.000000
09-04-2025 20:54:30.000 | 86059445 |  | 86.0594 | 33926147 | 15619717 | 31836665 | -99922386 | 50065697 | 13878023 | 551080261 | 0.000000 | 0.000000
09-04-2025 20:54:25.000 | 87567617 |  | 87.5676 | 38342271 | 15617393 | 32405261 | -99904274 | 50029083 | 13757678 | 545995667 | 0.000000 | 0.000000
09-04-2025 20:54:20.000 | 89470750 |  | 89.4707 | 38237461 | 15610594 | 33122288 | -99908798 | 49990978 | 13634915 | 540740662 | 0.000000 | 0.000000
09-04-2025 20:54:15.000 | 89348289 |  | 89.3483 | 40076973 | 15605139 | 33091636 | -99899551 | 49995720 | 13510568 | 535307129 | 0.000000 | 0.000000
09-04-2025 20:54:10.000 | 87583281 |  | 87.5833 | 34792534 | 15610425 | 32419959 | -99921188 | 50033016 | 13387479 | 529976318 | 0.000000 | 0.000000
09-04-2025 20:54:05.000 | 87340555 |  | 87.3406 | 36250791 | 15609610 | 32334321 | -99913979 | 50037384 | 13265969 | 524996277 | 0.000000 | 0.000000
09-04-2025 20:54:00.000 | 85894117 |  | 85.8941 | 38059434 | 15615860 | 31789854 | -99901978 | 50062321 | 13145851 | 519864746 | 0.000000 | 0.000000
09-04-2025 20:53:55.000 | 86645070 |  | 86.6451 | 39281973 | 15617464 | 32065974 | -99897385 | 50053982 | 13026517 | 514597168 | 0.000000 | 0.000000
09-04-2025 20:53:50.000 | 88165555 |  | 88.1656 | 39482119 | 15612542 | 32638337 | -99899879 | 50017036 | 12905470 | 509114594 | 0.000000 | 0.000000
09-04-2025 20:53:45.000 | 89210852 |  | 89.2109 | 37689841 | 15608299 | 33030164 | -99910873 | 49994030 | 12782223 | 503660828 | 0.000000 | 0.000000
09-04-2025 20:53:40.000 | 88448695 |  | 88.4487 | 38650908 | 15606345 | 32755129 | -99904655 | 50013855 | 12658495 | 498227203 | 0.000000 | 0.000000
09-04-2025 20:53:35.000 | 86860250 |  | 86.8602 | 36540767 | 15611405 | 32153442 | -99911629 | 50049950 | 12536619 | 492968964 | 0.000000 | 0.000000
09-04-2025 20:53:30.000 | 86572461 |  | 86.5725 | 35797683 | 15614927 | 32038958 | -99914619 | 50058258 | 12416166 | 488016937 | 0.000000 | 0.000000
09-04-2025 20:53:25.000 | 87257492 |  | 87.2575 | 36447476 | 15612825 | 32297058 | -99912880 | 50053082 | 12295523 | 482972351 | 0.000000 | 0.000000
09-04-2025 20:53:20.000 | 87598625 |  | 87.5986 | 37209463 | 15611785 | 32426438 | -99909904 | 50036152 | 12173858 | 477770844 | 0.000000 | 0.000000
09-04-2025 20:53:15.000 | 87634242 |  | 87.6342 | 36953025 | 15610665 | 32441772 | -99911217 | 50032555 | 12052048 | 472578461 | 0.000000 | 0.000000
09-04-2025 20:53:10.000 | 86932508 |  | 86.9325 | 38564041 | 15610016 | 32186328 | -99901749 | 50049816 | 11930694 | 467324463 | 0.000000 | 0.000000
09-04-2025 20:53:05.000 | 86764992 |  | 86.765 | 35266802 | 15614543 | 32109856 | -99917496 | 50057972 | 11810198 | 462199310 | 0.000000 | 0.000000
09-04-2025 20:53:00.000 | 87791406 |  | 87.7914 | 35739709 | 15611532 | 32496062 | -99917236 | 50037708 | 11688894 | 457219452 | 0.000000 | 0.000000
09-04-2025 20:52:55.000 | 87620453 |  | 87.6205 | 34914387 | 15613563 | 32427451 | -99920708 | 50043476 | 11566992 | 452285828 | 0.000000 | 0.000000
09-04-2025 20:52:50.000 | 88332094 |  | 88.3321 | 35451572 | 15613792 | 32690732 | -99919556 | 50032272 | 11445037 | 447407593 | 0.000000 | 0.000000
09-04-2025 20:52:45.000 | 88924313 |  | 88.9243 | 36735334 | 15612698 | 32913728 | -99914780 | 50009064 | 11321881 | 442447784 | 0.000000 | 0.000000
09-04-2025 20:52:40.000 | 88257102 |  | 88.2571 | 38117666 | 15610758 | 32674370 | -99906868 | 50016884 | 11198467 | 437271515 | 0.000000 | 0.000000
09-04-2025 20:52:35.000 | 87586258 |  | 87.5863 | 36977354 | 15616218 | 32412388 | -99911003 | 50046623 | 11076401 | 432083069 | 0.000000 | 0.000000
09-04-2025 20:52:30.000 | 88608250 |  | 88.6082 | 36775591 | 15610905 | 32800938 | -99913986 | 50030205 | 10954357 | 426941467 | 0.000000 | 0.000000
09-04-2025 20:52:25.000 | 89118906 |  | 89.1189 | 34726865 | 15608498 | 32991411 | -99924164 | 50029446 | 10830576 | 421895477 | 0.000000 | 0.000000
09-04-2025 20:52:20.000 | 88766875 |  | 88.7669 | 35382395 | 15608768 | 32861780 | -99920654 | 50023811 | 10706931 | 417096924 | 0.000000 | 0.000000
09-04-2025 20:52:15.000 | 87753563 |  | 87.7536 | 34011721 | 15608682 | 32485330 | -99924973 | 50047012 | 10583965 | 412269653 | 0.000000 | 0.000000
09-04-2025 20:52:10.000 | 86802211 |  | 86.8022 | 34206533 | 15611595 | 32128032 | -99922440 | 50059723 | 10462472 | 407529938 | 0.000000 | 0.000000
09-04-2025 20:52:05.000 | 86923422 |  | 86.9234 | 35900708 | 15610668 | 32177502 | -99914818 | 50067070 | 10341826 | 402728729 | 0.000000 | 0.000000
09-04-2025 20:52:00.000 | 86152219 |  | 86.1522 | 35127842 | 15613450 | 31885427 | -99916977 | 50067886 | 10221811 | 397794800 | 0.000000 | 0.000000
09-04-2025 20:51:55.000 | 86420500 |  | 86.4205 | 35908342 | 15617131 | 31978464 | -99913788 | 50055355 | 10102288 | 392912292 | 0.000000 | 0.000000
09-04-2025 20:51:50.000 | 87655281 |  | 87.6553 | 35356597 | 15617706 | 32432200 | -99918747 | 50038460 | 99819111 | 387999725 | 0.000000 | 0.000000
09-04-2025 20:51:45.000 | 89594570 |  | 89.5946 | 37420669 | 15613470 | 33160764 | -99912888 | 50009727 | 98593105 | 383131226 | 0.000000 | 0.000000
09-04-2025 20:51:40.000 | 90298406 |  | 90.2984 | 37758601 | 15606922 | 33435190 | -99912689 | 49992867 | 97342793 | 377928925 | 0.000000 | 0.000000
09-04-2025 20:51:35.000 | 89036953 |  | 89.037 | 35893210 | 15608698 | 32962454 | -99918846 | 50033131 | 96093223 | 372768219 | 0.000000 | 0.000000
09-04-2025 20:51:30.000 | 88090945 |  | 88.0909 | 33436826 | 15610534 | 32605510 | -99928040 | 50046761 | 94865830 | 367965851 | 0.000000 | 0.000000
09-04-2025 20:51:25.000 | 87661906 |  | 87.6619 | 34871584 | 15613465 | 32442908 | -99920975 | 50053020 | 93643926 | 363271606 | 0.000000 | 0.000000
09-04-2025 20:51:20.000 | 87500555 |  | 87.5006 | 32732517 | 15614003 | 32379353 | -99930107 | 50061485 | 92428721 | 358580902 | 0.000000 | 0.000000
09-04-2025 20:51:15.000 | 88147406 |  | 88.1474 | 37008433 | 15612036 | 32628687 | -99911980 | 50052776 | 91208418 | 353833527 | 0.000000 | 0.000000
09-04-2025 20:51:10.000 | 88151000 |  | 88.151 | 33105452 | 15613601 | 32620671 | -99929558 | 50055893 | 89987637 | 348921021 | 0.000000 | 0.000000
09-04-2025 20:51:05.000 | 89199828 |  | 89.1998 | 33028694 | 15608368 | 33019600 | -99931519 | 50035446 | 88755586 | 344390289 | 0.000000 | 0.000000
09-04-2025 20:51:00.000 | 88344000 |  | 88.344 | 31624746 | 15609083 | 32699441 | -99935989 | 50052326 | 87522676 | 339869598 | 0.000000 | 0.000000
09-04-2025 20:50:55.000 | 87825234 |  | 87.8252 | 31565330 | 15609464 | 32506963 | -99935478 | 50067261 | 86296650 | 335434814 | 0.000000 | 0.000000
09-04-2025 20:50:50.000 | 87113461 |  | 87.1135 | 31042856 | 15611272 | 32239338 | -99936569 | 50075504 | 85081738 | 331094513 | 0.000000 | 0.000000
09-04-2025 20:50:45.000 | 86838539 |  | 86.8385 | 30172136 | 15608697 | 32142561 | -99939697 | 50077072 | 83872334 | 326875031 | 0.000000 | 0.000000
09-04-2025 20:50:40.000 | 86037016 |  | 86.037 | 31610295 | 15613698 | 31837478 | -99932579 | 50089386 | 82669307 | 322605286 | 0.000000 | 0.000000
09-04-2025 20:50:35.000 | 85661992 |  | 85.662 | 33039570 | 15618692 | 31690593 | -99925705 | 50095661 | 81479507 | 318219330 | 0.000000 | 0.000000
09-04-2025 20:50:30.000 | 87476680 |  | 87.4767 | 32834458 | 15615754 | 32367117 | -99929626 | 50056492 | 80280244 | 313709167 | 0.000000 | 0.000000
09-04-2025 20:50:25.000 | 88835242 |  | 88.8352 | 34710293 | 15609386 | 32884897 | -99923752 | 50028141 | 79054917 | 308978912 | 0.000000 | 0.000000
09-04-2025 20:50:20.000 | 88320102 |  | 88.3201 | 36579959 | 15607419 | 32701624 | -99914337 | 50038124 | 77821699 | 304140991 | 0.000000 | 0.000000
09-04-2025 20:50:15.000 | 86980914 |  | 86.9809 | 33595037 | 15612717 | 32190801 | -99925491 | 50070705 | 76604448 | 299299957 | 0.000000 | 0.000000
09-04-2025 20:50:10.000 | 86843938 |  | 86.8439 | 33745176 | 15614427 | 32137080 | -99924591 | 50086079 | 75397300 | 294614624 | 0.000000 | 0.000000
09-04-2025 20:50:05.000 | 87210984 |  | 87.211 | 32896299 | 15617050 | 32266018 | -99928932 | 50073910 | 74189800 | 290064178 | 0.000000 | 0.000000
09-04-2025 20:50:00.000 | 88503258 |  | 88.5033 | 33876758 | 15611756 | 32756089 | -99926819 | 50052567 | 72971108 | 285420868 | 0.000000 | 0.000000
09-04-2025 20:49:55.000 | 88581227 |  | 88.5812 | 31396189 | 15610625 | 32783569 | -99937248 | 50039631 | 71739531 | 280846283 | 0.000000 | 0.000000
09-04-2025 20:49:50.000 | 88332781 |  | 88.3328 | 32357004 | 15610801 | 32692815 | -99932976 | 50048622 | 70509497 | 276336426 | 0.000000 | 0.000000
09-04-2025 20:49:45.000 | 87816688 |  | 87.8167 | 33325632 | 15611107 | 32502893 | -99928070 | 50050926 | 69285977 | 271839905 | 0.000000 | 0.000000
09-04-2025 20:49:40.000 | 87599648 |  | 87.5996 | 31118726 | 15610459 | 32420886 | -99936966 | 50069031 | 68069116 | 267295807 | 0.000000 | 0.000000
09-04-2025 20:49:35.000 | 87532727 |  | 87.5327 | 31287134 | 15607478 | 32402520 | -99936180 | 50053223 | 66852090 | 262998718 | 0.000000 | 0.000000
09-04-2025 20:49:30.000 | 86428875 |  | 86.4289 | 31224187 | 15607875 | 31993748 | -99934807 | 50061901 | 65639966 | 258655975 | 0.000000 | 0.000000
09-04-2025 20:49:25.000 | 84733297 |  | 84.7333 | 31965981 | 15610111 | 31363474 | -99928917 | 50092606 | 64450254 | 254229263 | 0.000000 | 0.000000
09-04-2025 20:49:20.000 | 83977211 |  | 83.9772 | 32589421 | 15618794 | 31067441 | -99924782 | 50103569 | 63281240 | 249822754 | 0.000000 | 0.000000
09-04-2025 20:49:15.000 | 84719641 |  | 84.7196 | 35312253 | 15618378 | 31347021 | -99913246 | 50085979 | 62114722 | 245143539 | 0.000000 | 0.000000
09-04-2025 20:49:10.000 | 85999273 |  | 85.9993 | 36579526 | 15622038 | 31813682 | -99909660 | 50054581 | 60931992 | 240111237 | 0.000000 | 0.000000
09-04-2025 20:49:05.000 | 88731594 |  | 88.7316 | 39669744 | 15616823 | 32838630 | -99900208 | 49997711 | 59722051 | 234885162 | 0.000000 | 0.000000
09-04-2025 20:49:00.000 | 89675531 |  | 89.6755 | 43866665 | 15608476 | 33212100 | -99880569 | 49983040 | 58481392 | 229057419 | 0.000000 | 0.000000
09-04-2025 20:48:55.000 | 89287328 |  | 89.2873 | 41207236 | 15611800 | 33056912 | -99893669 | 50012299 | 57238208 | 223164627 | 0.000000 | 0.000000
09-04-2025 20:48:50.000 | 89448063 |  | 89.4481 | 38712510 | 15608788 | 33118767 | -99906479 | 50019436 | 55995962 | 217530853 | 0.000000 | 0.000000
09-04-2025 20:48:45.000 | 89285250 |  | 89.2853 | 37088325 | 15609439 | 33054417 | -99913834 | 50026886 | 54752256 | 212285477 | 0.000000 | 0.000000
09-04-2025 20:48:40.000 | 88117875 |  | 88.1179 | 35675635 | 15611777 | 32616228 | -99918144 | 50054253 | 53519058 | 207053314 | 0.000000 | 0.000000
09-04-2025 20:48:35.000 | 88037766 |  | 88.0378 | 35650508 | 15611207 | 32587664 | -99918114 | 50061886 | 52295249 | 202096695 | 0.000000 | 0.000000
09-04-2025 20:48:30.000 | 87874734 |  | 87.8747 | 34002417 | 15612719 | 32521909 | -99925224 | 50073093 | 51074658 | 197246796 | 0.000000 | 0.000000
09-04-2025 20:48:25.000 | 88284945 |  | 88.2849 | 33751797 | 15610865 | 32677295 | -99927002 | 50056374 | 49852295 | 192567383 | 0.000000 | 0.000000
09-04-2025 20:48:20.000 | 89118281 |  | 89.1183 | 31498774 | 15606271 | 32991689 | -99937592 | 50051346 | 48621289 | 188059418 | 0.000000 | 0.000000
09-04-2025 20:48:15.000 | 88044516 |  | 88.0445 | 30947209 | 15604945 | 32596631 | -99938286 | 50057472 | 47386265 | 183623337 | 0.000000 | 0.000000
09-04-2025 20:48:10.000 | 86207320 |  | 86.2073 | 31083254 | 15607585 | 31912275 | -99935059 | 50088657 | 46172070 | 179290924 | 0.000000 | 0.000000
09-04-2025 20:48:05.000 | 84232078 |  | 84.2321 | 31560830 | 15616002 | 31166340 | -99929878 | 50127491 | 44988120 | 175026596 | 0.000000 | 0.000000
09-04-2025 20:48:00.000 | 84179664 |  | 84.1797 | 29431074 | 15620367 | 31134885 | -99938942 | 50123280 | 43820352 | 170604675 | 0.000000 | 0.000000
09-04-2025 20:47:55.000 | 85746469 |  | 85.7465 | 32508730 | 15619575 | 31719326 | -99928207 | 50086498 | 42642241 | 166268845 | 0.000000 | 0.000000
09-04-2025 20:47:50.000 | 87616922 |  | 87.6169 | 33028684 | 15616773 | 32416941 | -99929024 | 50039101 | 41439600 | 161656967 | 0.000000 | 0.000000
09-04-2025 20:47:45.000 | 88452445 |  | 88.4524 | 37584111 | 15612813 | 32740425 | -99909851 | 50011978 | 40213213 | 156701782 | 0.000000 | 0.000000
09-04-2025 20:47:40.000 | 88062430 |  | 88.0624 | 36284739 | 15611748 | 32596431 | -99915222 | 50029568 | 38985691 | 151433701 | 0.000000 | 0.000000
09-04-2025 20:47:35.000 | 88268445 |  | 88.2684 | 36368608 | 15609572 | 32677415 | -99915230 | 50030788 | 37762446 | 146398010 | 0.000000 | 0.000000
09-04-2025 20:47:30.000 | 88041781 |  | 88.0418 | 35685986 | 15613664 | 32583926 | -99917953 | 50029247 | 36537461 | 141548279 | 0.000000 | 0.000000
09-04-2025 20:47:25.000 | 87959516 |  | 87.9595 | 38123789 | 15613309 | 32558464 | -99906204 | 50035294 | 35316621 | 136426163 | 0.000000 | 0.000000
09-04-2025 20:47:20.000 | 88142352 |  | 88.1424 | 36888540 | 15613229 | 32624229 | -99912537 | 50037338 | 34096001 | 131221420 | 0.000000 | 0.000000
09-04-2025 20:47:15.000 | 89404719 |  | 89.4047 | 37699407 | 15610924 | 33096379 | -99911217 | 50017506 | 32865979 | 126169380 | 0.000000 | 0.000000
09-04-2025 20:47:10.000 | 89317172 |  | 89.3172 | 34415828 | 15607752 | 33066174 | -99925850 | 50022751 | 31623704 | 121152306 | 0.000000 | 0.000000
09-04-2025 20:47:05.000 | 88635102 |  | 88.6351 | 34052141 | 15609393 | 32810059 | -99926285 | 50043777 | 30386101 | 116370255 | 0.000000 | 0.000000
09-04-2025 20:47:00.000 | 88108266 |  | 88.1083 | 32270398 | 15610325 | 32610784 | -99932991 | 50060139 | 29159185 | 111750275 | 0.000000 | 0.000000
09-04-2025 20:46:55.000 | 87639438 |  | 87.6394 | 34120107 | 15609808 | 32441028 | -99924301 | 50057865 | 27938667 | 107216110 | 0.000000 | 0.000000
09-04-2025 20:46:50.000 | 86627844 |  | 86.6278 | 34698599 | 15610318 | 32067029 | -99919876 | 50085506 | 26728911 | 102398560 | 0.000000 | 0.000000
09-04-2025 20:46:45.000 | 86473516 |  | 86.4735 | 30572781 | 15612696 | 31999482 | -99937561 | 50090969 | 25526843 | 97856850 | 0.000000 | 0.000000
09-04-2025 20:46:40.000 | 87295297 |  | 87.2953 | 30590991 | 15611091 | 32306741 | -99938652 | 50066395 | 24319880 | 93620491 | 0.000000 | 0.000000
09-04-2025 20:46:35.000 | 87197750 |  | 87.1977 | 33745479 | 15606883 | 32283518 | -99925201 | 50057720 | 23106260 | 89260910 | 0.000000 | 0.000000
09-04-2025 20:46:30.000 | 85036156 |  | 85.0362 | 33509702 | 15613717 | 31470479 | -99922447 | 50104500 | 21907100 | 84551491 | 0.000000 | 0.000000
09-04-2025 20:46:25.000 | 85410844 |  | 85.4108 | 32911023 | 15619755 | 31595789 | -99925842 | 50087578 | 20727065 | 80097633 | 0.000000 | 0.000000
09-04-2025 20:46:20.000 | 86756500 |  | 86.7565 | 35284324 | 15617213 | 32101348 | -99917397 | 50057796 | 19530970 | 75287369 | 0.000000 | 0.000000
09-04-2025 20:46:15.000 | 88099258 |  | 88.0993 | 36541943 | 15614945 | 32603955 | -99914085 | 50033211 | 18317722 | 70342003 | 0.000000 | 0.000000
09-04-2025 20:46:10.000 | 88523766 |  | 88.5238 | 37462075 | 15610832 | 32770703 | -99910576 | 50024666 | 17093424 | 65137543 | 0.000000 | 0.000000
09-04-2025 20:46:05.000 | 88971641 |  | 88.9716 | 35590383 | 15610438 | 32934187 | -99920090 | 50029476 | 15861998 | 60019512 | 0.000000 | 0.000000
09-04-2025 20:46:00.000 | 89198320 |  | 89.1983 | 36634954 | 15607839 | 33025369 | -99915764 | 50028725 | 14627158 | 55178303 | 0.000000 | 0.000000
09-04-2025 20:45:55.000 | 87656203 |  | 87.6562 | 35402729 | 15611408 | 32445684 | -99918541 | 50067226 | 13396227 | 50173214 | 0.000000 | 0.000000
09-04-2025 20:45:50.000 | 87501992 |  | 87.502 | 32233433 | 15616899 | 32372783 | -99932220 | 50075039 | 12181696 | 45501469 | 0.000000 | 0.000000
09-04-2025 20:45:45.000 | 88508148 |  | 88.5081 | 34827261 | 15613531 | 32755283 | -99922668 | 50050465 | 10961294 | 40869286 | 0.000000 | 0.000000
09-04-2025 20:45:40.000 | 88630391 |  | 88.6304 | 36163003 | 15611468 | 32806941 | -99916862 | 50056164 | 972977234 | 35901535 | 0.000000 | 0.000000
09-04-2025 20:45:35.000 | 88821578 |  | 88.8216 | 33685300 | 15609713 | 32878159 | -99928162 | 50055889 | 850054871 | 31061617 | 0.000000 | 0.000000
09-04-2025 20:45:30.000 | 88920961 |  | 88.921 | 32795454 | 15610094 | 32912224 | -99932060 | 50042770 | 726357178 | 26494970 | 0.000000 | 0.000000
09-04-2025 20:45:25.000 | 88228828 |  | 88.2288 | 32100430 | 15606126 | 32663735 | -99933876 | 50055573 | 603025208 | 21791105 | 0.000000 | 0.000000
09-04-2025 20:45:20.000 | 86504875 |  | 86.5049 | 30393806 | 15610894 | 32015154 | -99938332 | 50090984 | 481180786 | 17345598 | 0.000000 | 0.000000
09-04-2025 20:45:15.000 | 86005813 |  | 86.0058 | 29682625 | 15614304 | 31822039 | -99940498 | 50111538 | 361282227 | 13048637 | 0.000000 | 0.000000
09-04-2025 20:45:10.000 | 86368086 |  | 86.3681 | 30950220 | 15614501 | 31957285 | -99935852 | 50104759 | 241526871 | 8817104 | 0.000000 | 0.000000
09-04-2025 20:45:05.000 | 87007305 |  | 87.0073 | 32537271 | 15612875 | 32198958 | -99930153 | 50090176 | 121186714 | 4442432 | 0.000000 | 0.000000
09-04-2025 20:45:00.000 | 87352680 |  | 87.3527 | 30636177 | 15612792 | 32324092 | -99938553 | 50086411 | 24618744 | 10114786 | 0.000000 | 0.000000
09-04-2025 20:44:55.000 | 87491563 |  | 87.4916 | 33533320 | 15612426 | 32380486 | -99926628 | 50077641 | 24497176 | 10070854 | 0.000000 | 0.000000
09-04-2025 20:44:50.000 | 87869383 |  | 87.8694 | 32271194 | 15615641 | 32511240 | -99932625 | 50080750 | 24375412 | 10025272 | 0.000000 | 0.000000
09-04-2025 20:44:45.000 | 88109375 |  | 88.1094 | 33358074 | 15615313 | 32602080 | -99928406 | 50079376 | 24253293 | 997930359 | 0.000000 | 0.000000
09-04-2025 20:44:40.000 | 89082680 |  | 89.0827 | 31138030 | 15611392 | 32967000 | -99938965 | 50068588 | 24130367 | 993354858 | 0.000000 | 0.000000
09-04-2025 20:44:35.000 | 89193148 |  | 89.1931 | 30635129 | 15608110 | 33014985 | -99941063 | 50081097 | 24006307 | 988972778 | 0.000000 | 0.000000
09-04-2025 20:44:30.000 | 88873031 |  | 88.873 | 29475798 | 15607593 | 32895525 | -99945045 | 50080872 | 23882463 | 984894897 | 0.000000 | 0.000000
09-04-2025 20:44:25.000 | 88114992 |  | 88.115 | 27357866 | 15608363 | 32611021 | -99951836 | 50099651 | 23759566 | 980962646 | 0.000000 | 0.000000
09-04-2025 20:44:20.000 | 87300547 |  | 87.3005 | 27168645 | 15607613 | 32311328 | -99951607 | 50107246 | 23637715 | 977227661 | 0.000000 | 0.000000
09-04-2025 20:44:15.000 | 85604438 |  | 85.6044 | 27246521 | 15611689 | 31676235 | -99949387 | 50130486 | 23517531 | 973505676 | 0.000000 | 0.000000
09-04-2025 20:44:10.000 | 84921938 |  | 84.9219 | 26625337 | 15614143 | 31418145 | -99950890 | 50139019 | 23399070 | 969702942 | 0.000000 | 0.000000
09-04-2025 20:44:05.000 | 84999078 |  | 84.9991 | 29641692 | 15616567 | 31445708 | -99939247 | 50120171 | 23281129 | 965789978 | 0.000000 | 0.000000
09-04-2025 20:44:00.000 | 85361484 |  | 85.3615 | 31974893 | 15615257 | 31585139 | -99929916 | 50105473 | 23163000 | 961549255 | 0.000000 | 0.000000
09-04-2025 20:43:55.000 | 85857516 |  | 85.8575 | 34110403 | 15618137 | 31765623 | -99921173 | 50083172 | 23044352 | 956968933 | 0.000000 | 0.000000
09-04-2025 20:43:50.000 | 86638602 |  | 86.6386 | 36158020 | 15617187 | 32059055 | -99913025 | 50070362 | 22924754 | 952122681 | 0.000000 | 0.000000
09-04-2025 20:43:45.000 | 87623992 |  | 87.624 | 39264980 | 15615814 | 32430845 | -99899750 | 50054123 | 22803748 | 947075317 | 0.000000 | 0.000000
09-04-2025 20:43:40.000 | 88472523 |  | 88.4725 | 38689819 | 15615271 | 32744399 | -99904518 | 50047554 | 22681791 | 941663208 | 0.000000 | 0.000000
09-04-2025 20:43:35.000 | 89866016 |  | 89.866 | 37656072 | 15611561 | 33265354 | -99912323 | 50026871 | 22558111 | 936402527 | 0.000000 | 0.000000
09-04-2025 20:43:30.000 | 90246734 |  | 90.2467 | 36710649 | 15608877 | 33410305 | -99917366 | 50015583 | 22432779 | 931254822 | 0.000000 | 0.000000
09-04-2025 20:43:25.000 | 89523430 |  | 89.5234 | 34353987 | 15604568 | 33148823 | -99926453 | 50051121 | 22307672 | 926172668 | 0.000000 | 0.000000
09-04-2025 20:43:20.000 | 88290625 |  | 88.2906 | 28275627 | 15611248 | 32671399 | -99948761 | 50079998 | 22183939 | 921737427 | 0.000000 | 0.000000
09-04-2025 20:43:15.000 | 87753289 |  | 87.7533 | 29500845 | 15609511 | 32477815 | -99943542 | 50084667 | 22061531 | 917719482 | 0.000000 | 0.000000
09-04-2025 20:43:10.000 | 86988352 |  | 86.9884 | 29529885 | 15611056 | 32191748 | -99942429 | 50104931 | 21940070 | 913671997 | 0.000000 | 0.000000
09-04-2025 20:43:05.000 | 86486133 |  | 86.4861 | 29893298 | 15613932 | 32000701 | -99940315 | 50108028 | 21820016 | 909716614 | 0.000000 | 0.000000
09-04-2025 20:43:00.000 | 87161719 |  | 87.1617 | 30633396 | 15614364 | 32250308 | -99938293 | 50092201 | 21699396 | 905593262 | 0.000000 | 0.000000
09-04-2025 20:42:55.000 | 87124180 |  | 87.1242 | 30658354 | 15611688 | 32241980 | -99938141 | 50093212 | 21578281 | 901190674 | 0.000000 | 0.000000
09-04-2025 20:42:50.000 | 87865719 |  | 87.8657 | 30294622 | 15612436 | 32514089 | -99940613 | 50076859 | 21456855 | 897025146 | 0.000000 | 0.000000
09-04-2025 20:42:45.000 | 87287023 |  | 87.287 | 31319851 | 15609906 | 32307363 | -99935692 | 50082912 | 21335125 | 892755615 | 0.000000 | 0.000000
09-04-2025 20:42:40.000 | 86509313 |  | 86.5093 | 29567344 | 15611281 | 32014158 | -99941643 | 50105770 | 21214479 | 888355652 | 0.000000 | 0.000000
09-04-2025 20:42:35.000 | 86852125 |  | 86.8521 | 30986572 | 15613389 | 32138342 | -99936417 | 50102707 | 21094127 | 884261963 | 0.000000 | 0.000000
09-04-2025 20:42:30.000 | 87458500 |  | 87.4585 | 31190405 | 15611327 | 32367017 | -99936470 | 50087933 | 20973223 | 879964844 | 0.000000 | 0.000000
09-04-2025 20:42:25.000 | 87677133 |  | 87.6771 | 31632529 | 15615482 | 32440137 | -99934982 | 50088242 | 20851596 | 875641052 | 0.000000 | 0.000000
09-04-2025 20:42:20.000 | 87933766 |  | 87.9338 | 32811057 | 15613968 | 32539473 | -99930458 | 50084778 | 20729885 | 871029114 | 0.000000 | 0.000000
09-04-2025 20:42:15.000 | 88971180 |  | 88.9712 | 33641138 | 15612354 | 32927258 | -99928589 | 50065678 | 20607209 | 866462524 | 0.000000 | 0.000000
09-04-2025 20:42:10.000 | 88399477 |  | 88.3995 | 35525435 | 15609721 | 32724106 | -99919350 | 50067753 | 20484098 | 861767517 | 0.000000 | 0.000000
09-04-2025 20:42:05.000 | 88422672 |  | 88.4227 | 31606741 | 15611957 | 32722693 | -99936172 | 50070850 | 20361473 | 857124268 | 0.000000 | 0.000000
09-04-2025 20:42:00.000 | 88648773 |  | 88.6488 | 31667102 | 15609985 | 32810911 | -99936256 | 50062454 | 20238396 | 852782532 | 0.000000 | 0.000000
09-04-2025 20:41:55.000 | 87616203 |  | 87.6162 | 32414077 | 15607826 | 32434407 | -99931633 | 50076466 | 20115816 | 848459351 | 0.000000 | 0.000000
09-04-2025 20:41:50.000 | 86673844 |  | 86.6738 | 28342144 | 15612545 | 32070830 | -99946579 | 50106281 | 19995002 | 844198181 | 0.000000 | 0.000000
09-04-2025 20:41:45.000 | 86799039 |  | 86.799 | 27928374 | 15613724 | 32114187 | -99948273 | 50101059 | 19874619 | 840307190 | 0.000000 | 0.000000
09-04-2025 20:41:40.000 | 87158297 |  | 87.1583 | 28171521 | 15611026 | 32253530 | -99947807 | 50093372 | 19753828 | 836381348 | 0.000000 | 0.000000
09-04-2025 20:41:35.000 | 87106125 |  | 87.1061 | 25338840 | 15611454 | 32229431 | -99957718 | 50095470 | 19632850 | 832642090 | 0.000000 | 0.000000
09-04-2025 20:41:30.000 | 87280930 |  | 87.2809 | 25384517 | 15608538 | 32300117 | -99957733 | 50084145 | 19511844 | 829096008 | 0.000000 | 0.000000
09-04-2025 20:41:25.000 | 86749000 |  | 86.749 | 27260796 | 15610693 | 32102288 | -99950661 | 50099014 | 19390900 | 825417480 | 0.000000 | 0.000000
09-04-2025 20:41:20.000 | 86199555 |  | 86.1996 | 27376702 | 15615576 | 31888398 | -99949608 | 50097073 | 19271096 | 821680359 | 0.000000 | 0.000000
09-04-2025 20:41:15.000 | 86363445 |  | 86.3634 | 28969023 | 15614879 | 31952053 | -99943787 | 50100441 | 19151197 | 817687439 | 0.000000 | 0.000000
09-04-2025 20:41:10.000 | 86533336 |  | 86.5333 | 30321152 | 15613841 | 32018838 | -99938667 | 50094055 | 19031258 | 813519043 | 0.000000 | 0.000000
09-04-2025 20:41:05.000 | 87150891 |  | 87.1509 | 32107058 | 15614788 | 32247393 | -99932205 | 50086990 | 18910492 | 809245728 | 0.000000 | 0.000000
09-04-2025 20:41:00.000 | 87996445 |  | 87.9964 | 31594746 | 15612876 | 32562959 | -99935608 | 50062378 | 18788994 | 804813904 | 0.000000 | 0.000000
09-04-2025 20:40:55.000 | 88359172 |  | 88.3592 | 32197312 | 15608392 | 32707263 | -99933678 | 50050259 | 18666453 | 800369202 | 0.000000 | 0.000000
09-04-2025 20:40:50.000 | 87651523 |  | 87.6515 | 33156433 | 15610232 | 32443384 | -99928528 | 50065815 | 18543957 | 795889099 | 0.000000 | 0.000000
09-04-2025 20:40:45.000 | 86485445 |  | 86.4854 | 33626406 | 15614562 | 32004297 | -99924500 | 50092606 | 18422865 | 791307434 | 0.000000 | 0.000000
09-04-2025 20:40:40.000 | 86826344 |  | 86.8263 | 31433137 | 15614886 | 32126509 | -99934532 | 50095989 | 18302729 | 786739929 | 0.000000 | 0.000000
09-04-2025 20:40:35.000 | 87764555 |  | 87.7646 | 34545046 | 15612779 | 32481946 | -99922623 | 50064842 | 18181486 | 782291992 | 0.000000 | 0.000000
09-04-2025 20:40:30.000 | 87265961 |  | 87.266 | 32477566 | 15613978 | 32292129 | -99930817 | 50083374 | 18059904 | 777562073 | 0.000000 | 0.000000
09-04-2025 20:40:25.000 | 87718727 |  | 87.7187 | 30249138 | 15614364 | 32455688 | -99940598 | 50080105 | 17938299 | 773093872 | 0.000000 | 0.000000
09-04-2025 20:40:20.000 | 88760211 |  | 88.7602 | 30759158 | 15610553 | 32849058 | -99940010 | 50040852 | 17815625 | 768860840 | 0.000000 | 0.000000
09-04-2025 20:40:15.000 | 87917539 |  | 87.9175 | 34251860 | 15606412 | 32551042 | -99924194 | 50053085 | 17692373 | 764239624 | 0.000000 | 0.000000
09-04-2025 20:40:10.000 | 86634531 |  | 86.6345 | 30519858 | 15611813 | 32060649 | -99938004 | 50084633 | 17570998 | 759689880 | 0.000000 | 0.000000
09-04-2025 20:40:05.000 | 85791648 |  | 85.7916 | 32314526 | 15615319 | 31744526 | -99929138 | 50084755 | 17451104 | 755331604 | 0.000000 | 0.000000
09-04-2025 20:40:00.000 | 86472539 |  | 86.4725 | 34065945 | 15614484 | 32000151 | -99922493 | 50081478 | 17331955 | 750754883 | 0.000000 | 0.000000
09-04-2025 20:39:55.000 | 87436594 |  | 87.4366 | 34104846 | 15616729 | 32352075 | -99924019 | 50068806 | 17211477 | 746021606 | 0.000000 | 0.000000
09-04-2025 20:39:50.000 | 89111766 |  | 89.1118 | 33206677 | 15610919 | 32981643 | -99930641 | 50029808 | 17089365 | 741396240 | 0.000000 | 0.000000
09-04-2025 20:39:45.000 | 89338625 |  | 89.3386 | 33413049 | 15610827 | 33065986 | -99930130 | 50034378 | 16965340 | 736814209 | 0.000000 | 0.000000
09-04-2025 20:39:40.000 | 89613172 |  | 89.6132 | 31678428 | 15610753 | 33165864 | -99937576 | 50053669 | 16841096 | 732247253 | 0.000000 | 0.000000
09-04-2025 20:39:35.000 | 89097805 |  | 89.0978 | 30516929 | 15611411 | 32972151 | -99941399 | 50065685 | 16716898 | 727884521 | 0.000000 | 0.000000
09-04-2025 20:39:30.000 | 88237023 |  | 88.237 | 32349346 | 15614847 | 32649036 | -99932861 | 50080891 | 16593568 | 723538086 | 0.000000 | 0.000000
09-04-2025 20:39:25.000 | 88671414 |  | 88.6714 | 31938823 | 15615987 | 32806599 | -99935196 | 50096447 | 16471008 | 719120667 | 0.000000 | 0.000000
09-04-2025 20:39:20.000 | 89082164 |  | 89.0822 | 29784683 | 15618662 | 32949937 | -99944153 | 50097469 | 16347677 | 714778320 | 0.000000 | 0.000000
09-04-2025 20:39:15.000 | 90867773 |  | 90.8678 | 31503994 | 15613023 | 33623870 | -99939957 | 50075813 | 16222738 | 710544495 | 0.000000 | 0.000000
09-04-2025 20:39:10.000 | 90964492 |  | 90.9645 | 33297896 | 15614708 | 33658398 | -99933067 | 50089390 | 16096441 | 706020813 | 0.000000 | 0.000000
09-04-2025 20:39:05.000 | 91395469 |  | 91.3955 | 32557366 | 15617813 | 33810422 | -99936615 | 50103733 | 15970026 | 701444153 | 0.000000 | 0.000000
09-04-2025 20:39:00.000 | 93141148 |  | 93.1411 | 34848445 | 15618504 | 34456428 | -99930084 | 50085342 | 15842181 | 696834839 | 0.000000 | 0.000000
09-04-2025 20:38:55.000 | 94408875 |  | 94.4089 | 37323589 | 15615177 | 34935557 | -99921944 | 50070614 | 15711916 | 691803711 | 0.000000 | 0.000000
09-04-2025 20:38:50.000 | 95819125 |  | 95.8191 | 38021545 | 15616240 | 35455500 | -99921364 | 50066658 | 15579915 | 686553406 | 0.000000 | 0.000000
09-04-2025 20:38:45.000 | 96792969 |  | 96.793 | 40130691 | 15617077 | 35816213 | -99914162 | 50061798 | 15446407 | 681136780 | 0.000000 | 0.000000
09-04-2025 20:38:40.000 | 97755516 |  | 97.7555 | 42233594 | 15615422 | 36178845 | -99906807 | 50058178 | 15311501 | 675414612 | 0.000000 | 0.000000
09-04-2025 20:38:35.000 | 99078148 |  | 99.0781 | 41370420 | 15615115 | 36666650 | -99912941 | 50046478 | 15175056 | 669623230 | 0.000000 | 0.000000
09-04-2025 20:38:30.000 | 99526633 |  | 99.5266 | 40846970 | 15616692 | 36827754 | -99915886 | 50052681 | 15037027 | 663795959 | 0.000000 | 0.000000
09-04-2025 20:38:25.000 | 100518180 |  | 100.5182 | 40269287 | 15613655 | 37200435 | -99919853 | 50054043 | 14898296 | 658131653 | 0.000000 | 0.000000
09-04-2025 20:38:20.000 | 10132080 | 101320800 | 101.3208 | 41233262 | 15610493 | 37506187 | -99917297 | 50031338 | 14758232 | 652501953 | 0.000000 | 0.000000
09-04-2025 20:38:15.000 | 10088857 | 100888570 | 100.8886 | 42808369 | 15612791 | 37343198 | -99910103 | 50060741 | 14617721 | 646678162 | 0.000000 | 0.000000
09-04-2025 20:38:10.000 | 10068377 | 100683770 | 100.6838 | 41378911 | 15617149 | 37255110 | -99915657 | 50095421 | 14477837 | 640781738 | 0.000000 | 0.000000
09-04-2025 20:38:05.000 | 10207200 | 102072000 | 102.072 | 43033838 | 15617559 | 37769717 | -99911247 | 50076336 | 14337377 | 634970581 | 0.000000 | 0.000000
09-04-2025 20:38:00.000 | 10329041 | 103290410 | 103.2904 | 46737734 | 15618279 | 38223347 | -99897781 | 50077000 | 14194751 | 628816040 | 0.000000 | 0.000000
09-04-2025 20:37:55.000 | 10437129 | 104371290 | 104.3713 | 49849536 | 15616246 | 38632920 | -99886139 | 50074093 | 14050808 | 622175232 | 0.000000 | 0.000000
09-04-2025 20:37:50.000 | 10580781 | 105807810 | 105.8078 | 47675107 | 15619510 | 39151523 | -99898643 | 50064785 | 13905312 | 615398560 | 0.000000 | 0.000000
09-04-2025 20:37:45.000 | 10780937 | 107809370 | 107.8094 | 49243032 | 15611814 | 39912822 | -99895851 | 50038631 | 13757142 | 608626038 | 0.000000 | 0.000000
09-04-2025 20:37:40.000 | 10843470 | 108434700 | 108.4347 | 51925596 | 15609066 | 40155549 | -99885544 | 50019058 | 13607015 | 601722595 | 0.000000 | 0.000000
09-04-2025 20:37:35.000 | 10745155 | 107451550 | 107.4515 | 50775000 | 15610632 | 39786548 | -99888542 | 50057392 | 13456800 | 594649536 | 0.000000 | 0.000000
09-04-2025 20:37:30.000 | 10751486 | 107514860 | 107.5149 | 46477251 | 15612305 | 39798374 | -99906693 | 50059994 | 13307850 | 587846008 | 0.000000 | 0.000000
09-04-2025 20:37:25.000 | 10785723 | 107857230 | 107.8572 | 48021206 | 15609161 | 39935427 | -99901031 | 50055546 | 13158214 | 581369568 | 0.000000 | 0.000000
09-04-2025 20:37:20.000 | 10701061 | 107010610 | 107.0106 | 46404790 | 15608621 | 39621187 | -99906105 | 50076035 | 13009101 | 574830750 | 0.000000 | 0.000000
09-04-2025 20:37:15.000 | 10675259 | 106752590 | 106.7526 | 44968545 | 15610641 | 39518540 | -99911392 | 50070187 | 12860752 | 568484924 | 0.000000 | 0.000000
09-04-2025 20:37:10.000 | 10666333 | 106663330 | 106.6633 | 46219126 | 15611760 | 39484792 | -99906250 | 50077126 | 12712473 | 562174500 | 0.000000 | 0.000000
09-04-2025 20:37:05.000 | 10586703 | 105867030 | 105.867 | 46440405 | 15610080 | 39194968 | -99903923 | 50093388 | 12564931 | 555698364 | 0.000000 | 0.000000
09-04-2025 20:37:00.000 | 10605716 | 106057160 | 106.0572 | 45930352 | 15613437 | 39255959 | -99906357 | 50096676 | 12418062 | 549389526 | 0.000000 | 0.000000
09-04-2025 20:36:55.000 | 10624295 | 106242950 | 106.2429 | 45326567 | 15613607 | 39323328 | -99909119 | 50087688 | 12270726 | 543032837 | 0.000000 | 0.000000
09-04-2025 20:36:50.000 | 10644305 | 106443050 | 106.443 | 43922651 | 15613604 | 39395005 | -99914970 | 50091728 | 12123248 | 536781555 | 0.000000 | 0.000000
09-04-2025 20:36:45.000 | 10702019 | 107020190 | 107.0202 | 44275244 | 15614814 | 39606306 | -99914536 | 50077927 | 11974926 | 530696167 | 0.000000 | 0.000000
09-04-2025 20:36:40.000 | 10774484 | 107744840 | 107.7448 | 43565244 | 15607195 | 39891750 | -99918358 | 50043232 | 11825661 | 524578369 | 0.000000 | 0.000000
09-04-2025 20:36:35.000 | 10672430 | 106724300 | 106.7243 | 44641304 | 15605486 | 39520608 | -99912636 | 50060158 | 11676313 | 518424805 | 0.000000 | 0.000000
09-04-2025 20:36:30.000 | 10493560 | 104935600 | 104.9356 | 43939292 | 15609720 | 38847966 | -99912453 | 50097004 | 11528828 | 512355408 | 0.000000 | 0.000000
09-04-2025 20:36:25.000 | 10407737 | 104077370 | 104.0774 | 40934678 | 15614600 | 38514121 | -99922745 | 50108929 | 11383926 | 506414642 | 0.000000 | 0.000000
09-04-2025 20:36:20.000 | 10477245 | 104772450 | 104.7725 | 43663594 | 15617405 | 38768064 | -99913277 | 50085621 | 11238975 | 500529388 | 0.000000 | 0.000000
09-04-2025 20:36:15.000 | 10531609 | 105316090 | 105.3161 | 46263218 | 15612504 | 38985073 | -99903656 | 50065662 | 11092961 | 494252075 | 0.000000 | 0.000000
09-04-2025 20:36:10.000 | 10569316 | 105693160 | 105.6932 | 47404683 | 15612930 | 39125320 | -99899567 | 50066467 | 10946424 | 487744171 | 0.000000 | 0.000000
09-04-2025 20:36:05.000 | 10557296 | 105572960 | 105.573 | 47844585 | 15613650 | 39079783 | -99897469 | 50067150 | 10799844 | 481097229 | 0.000000 | 0.000000
09-04-2025 20:36:00.000 | 10557130 | 105571300 | 105.5713 | 47470298 | 15613146 | 39079751 | -99899063 | 50069309 | 10653331 | 474479248 | 0.000000 | 0.000000
09-04-2025 20:35:55.000 | 10642334 | 106423340 | 106.4233 | 47562207 | 15610959 | 39400076 | -99900284 | 50054756 | 10506175 | 467949646 | 0.000000 | 0.000000
09-04-2025 20:35:50.000 | 10625738 | 106257380 | 106.2574 | 47517012 | 15611814 | 39336589 | -99900162 | 50053146 | 10358440 | 461269958 | 0.000000 | 0.000000
09-04-2025 20:35:45.000 | 10620747 | 106207470 | 106.2075 | 49158950 | 15611663 | 39321287 | -99893051 | 50047291 | 10210694 | 454532227 | 0.000000 | 0.000000
09-04-2025 20:35:40.000 | 10581684 | 105816840 | 105.8168 | 49526563 | 15613670 | 39172922 | -99890648 | 50063114 | 10063441 | 447506805 | 0.000000 | 0.000000
09-04-2025 20:35:35.000 | 10616287 | 106162870 | 106.1629 | 48665410 | 15615416 | 39294758 | -99895096 | 50065510 | 99163184 | 440640167 | 0.000000 | 0.000000
09-04-2025 20:35:30.000 | 10663624 | 106636240 | 106.6362 | 49021465 | 15614664 | 39472502 | -99894501 | 50055271 | 97687725 | 433899780 | 0.000000 | 0.000000
09-04-2025 20:35:25.000 | 10727455 | 107274550 | 107.2746 | 49580342 | 15616444 | 39704111 | -99893364 | 50033142 | 96203174 | 427161530 | 0.000000 | 0.000000
09-04-2025 20:35:20.000 | 10744499 | 107444990 | 107.445 | 50780469 | 15611663 | 39781248 | -99888504 | 50039249 | 94711025 | 420123077 | 0.000000 | 0.000000
09-04-2025 20:35:15.000 | 10800894 | 108008940 | 108.0089 | 49036309 | 15610740 | 39989075 | -99897102 | 50058109 | 93214668 | 413163574 | 0.000000 | 0.000000
09-04-2025 20:35:10.000 | 10780895 | 107808950 | 107.8089 | 44851777 | 15608613 | 39913821 | -99913574 | 50065613 | 91715850 | 406539673 | 0.000000 | 0.000000
09-04-2025 20:35:05.000 | 10800234 | 108002340 | 108.0023 | 45073535 | 15608946 | 39984646 | -99913025 | 50060780 | 90213721 | 400406311 | 0.000000 | 0.000000
09-04-2025 20:35:00.000 | 10766754 | 107667540 | 107.6675 | 46529463 | 15607781 | 39866982 | -99906754 | 50074677 | 88717568 | 394107361 | 0.000000 | 0.000000
09-04-2025 20:34:55.000 | 10623874 | 106238740 | 106.2387 | 46014214 | 15612271 | 39326130 | -99906334 | 50107044 | 87232549 | 387643097 | 0.000000 | 0.000000
09-04-2025 20:34:50.000 | 10634381 | 106343810 | 106.3438 | 43002593 | 15615507 | 39352759 | -99918343 | 50118668 | 85758955 | 381429962 | 0.000000 | 0.000000
09-04-2025 20:34:45.000 | 10767888 | 107678880 | 107.6789 | 45350352 | 15611290 | 39859922 | -99911430 | 50075634 | 84273828 | 375469391 | 0.000000 | 0.000000
09-04-2025 20:34:40.000 | 10767292 | 107672920 | 107.6729 | 45005298 | 15609083 | 39862629 | -99912758 | 50088116 | 82779150 | 369094177 | 0.000000 | 0.000000
09-04-2025 20:34:35.000 | 10736882 | 107368820 | 107.3688 | 44288130 | 15609089 | 39749080 | -99915039 | 50085106 | 81286543 | 362866089 | 0.000000 | 0.000000
09-04-2025 20:34:30.000 | 10729650 | 107296500 | 107.2965 | 44285786 | 15608599 | 39723745 | -99914932 | 50076096 | 79796597 | 356760284 | 0.000000 | 0.000000
09-04-2025 20:34:25.000 | 10632088 | 106320880 | 106.3209 | 45870039 | 15608724 | 39365330 | -99907066 | 50093323 | 78310503 | 350608826 | 0.000000 | 0.000000
09-04-2025 20:34:20.000 | 10458575 | 104585750 | 104.5858 | 46084346 | 15615414 | 38707900 | -99903061 | 50120476 | 76845225 | 344181000 | 0.000000 | 0.000000
09-04-2025 20:34:15.000 | 10508166 | 105081660 | 105.0817 | 46471958 | 15617223 | 38887236 | -99902351 | 50113091 | 75391567 | 337815643 | 0.000000 | 0.000000
09-04-2025 20:34:10.000 | 10655309 | 106553090 | 106.5531 | 46903071 | 15614237 | 39438696 | -99903259 | 50071770 | 73922871 | 331298859 | 0.000000 | 0.000000
09-04-2025 20:34:05.000 | 10706777 | 107067770 | 107.0678 | 47578628 | 15609607 | 39641792 | -99901413 | 50059334 | 72436284 | 324761536 | 0.000000 | 0.000000
09-04-2025 20:34:00.000 | 10657815 | 106578150 | 106.5781 | 47506685 | 15610967 | 39458062 | -99900803 | 50069881 | 70952271 | 318108521 | 0.000000 | 0.000000
09-04-2025 20:33:55.000 | 10613367 | 106133670 | 106.1337 | 47112256 | 15612165 | 39289426 | -99901627 | 50077835 | 69476348 | 311461731 | 0.000000 | 0.000000
09-04-2025 20:33:50.000 | 10602998 | 106029980 | 106.03 | 46679258 | 15611861 | 39251091 | -99903229 | 50083157 | 68001494 | 304963531 | 0.000000 | 0.000000
09-04-2025 20:33:45.000 | 10628702 | 106287020 | 106.287 | 46711992 | 15614560 | 39339448 | -99903564 | 50077812 | 66526465 | 298519897 | 0.000000 | 0.000000
09-04-2025 20:33:40.000 | 10677242 | 106772420 | 106.7724 | 45963682 | 15613188 | 39520879 | -99907471 | 50069477 | 65047109 | 292063385 | 0.000000 | 0.000000
09-04-2025 20:33:35.000 | 10677334 | 106773340 | 106.7733 | 47414736 | 15611700 | 39527656 | -99901550 | 50067337 | 63563696 | 285552979 | 0.000000 | 0.000000
09-04-2025 20:33:30.000 | 10635649 | 106356490 | 106.3565 | 47515566 | 15609223 | 39380581 | -99900352 | 50060577 | 62080439 | 278928925 | 0.000000 | 0.000000
09-04-2025 20:33:25.000 | 10587328 | 105873280 | 105.8733 | 49115454 | 15611180 | 39199080 | -99892570 | 50086014 | 60603838 | 272312531 | 0.000000 | 0.000000
09-04-2025 20:33:20.000 | 10534135 | 105341350 | 105.3414 | 48704731 | 15617219 | 38986821 | -99893288 | 50093346 | 59139800 | 265533783 | 0.000000 | 0.000000
09-04-2025 20:33:15.000 | 10624717 | 106247170 | 106.2472 | 45870122 | 15614948 | 39322351 | -99906937 | 50084972 | 57671763 | 258740448 | 0.000000 | 0.000000
09-04-2025 20:33:10.000 | 10730101 | 107301010 | 107.301 | 49013374 | 15610378 | 39728279 | -99895836 | 50048267 | 56187979 | 252101166 | 0.000000 | 0.000000
09-04-2025 20:33:05.000 | 10714817 | 107148170 | 107.1482 | 48701621 | 15608816 | 39675288 | -99896866 | 50047546 | 54697568 | 245228577 | 0.000000 | 0.000000
09-04-2025 20:33:00.000 | 10623527 | 106235270 | 106.2353 | 48397417 | 15610145 | 39334150 | -99896393 | 50067162 | 53214917 | 238456589 | 0.000000 | 0.000000
09-04-2025 20:32:55.000 | 10602056 | 106020560 | 106.0206 | 47285571 | 15614213 | 39242646 | -99900688 | 50079342 | 51740767 | 231761749 | 0.000000 | 0.000000
09-04-2025 20:32:50.000 | 10638484 | 106384840 | 106.3848 | 48086611 | 15613473 | 39380439 | -99898003 | 50073589 | 50266831 | 225198639 | 0.000000 | 0.000000
09-04-2025 20:32:45.000 | 10653227 | 106532270 | 106.5323 | 48114028 | 15614203 | 39433145 | -99898170 | 50070820 | 48788779 | 218560455 | 0.000000 | 0.000000
09-04-2025 20:32:40.000 | 10750873 | 107508730 | 107.5087 | 47535073 | 15613015 | 39796299 | -99902397 | 50054092 | 47301987 | 211872818 | 0.000000 | 0.000000
09-04-2025 20:32:35.000 | 10724309 | 107243090 | 107.2431 | 47478511 | 15609506 | 39706592 | -99902145 | 50050720 | 45810654 | 205122559 | 0.000000 | 0.000000
09-04-2025 20:32:30.000 | 10677726 | 106777260 | 106.7773 | 48092422 | 15610592 | 39532769 | -99898727 | 50053772 | 44322979 | 198492935 | 0.000000 | 0.000000
09-04-2025 20:32:25.000 | 10677477 | 106774770 | 106.7748 | 48030229 | 15607182 | 39540354 | -99898979 | 50053658 | 42840259 | 191873947 | 0.000000 | 0.000000
09-04-2025 20:32:20.000 | 10582797 | 105827970 | 105.828 | 46124409 | 15612730 | 39173472 | -99905159 | 50073292 | 41361216 | 185340424 | 0.000000 | 0.000000
09-04-2025 20:32:15.000 | 10513559 | 105135590 | 105.1356 | 46060620 | 15614544 | 38913230 | -99904167 | 50085979 | 39894583 | 178841858 | 0.000000 | 0.000000
09-04-2025 20:32:10.000 | 10602118 | 106021180 | 106.0212 | 47096260 | 15613183 | 39245518 | -99901482 | 50076679 | 38430261 | 172466995 | 0.000000 | 0.000000
09-04-2025 20:32:05.000 | 10647418 | 106474180 | 106.4742 | 48227031 | 15611323 | 39419177 | -99897575 | 50053368 | 36954360 | 165812881 | 0.000000 | 0.000000
09-04-2025 20:32:00.000 | 10599578 | 105995780 | 105.9958 | 51333979 | 15612197 | 39245913 | -99882935 | 50059105 | 35476433 | 158917587 | 0.000000 | 0.000000
09-04-2025 20:31:55.000 | 10621384 | 106213840 | 106.2138 | 51902720 | 15613371 | 39324163 | -99880821 | 50074802 | 34005769 | 151837784 | 0.000000 | 0.000000
09-04-2025 20:31:50.000 | 10673220 | 106732200 | 106.7322 | 51205073 | 15616438 | 39506663 | -99885117 | 50059761 | 32529888 | 144796646 | 0.000000 | 0.000000
09-04-2025 20:31:45.000 | 10798043 | 107980430 | 107.9804 | 51686406 | 15611212 | 39982148 | -99885635 | 50038864 | 31040901 | 137604538 | 0.000000 | 0.000000
09-04-2025 20:31:40.000 | 10768657 | 107686570 | 107.6866 | 52891626 | 15608830 | 39881467 | -99879601 | 50039295 | 29541834 | 130394363 | 0.000000 | 0.000000
09-04-2025 20:31:35.000 | 10735216 | 107352160 | 107.3522 | 48717783 | 15608084 | 39752600 | -99897186 | 50051197 | 28049805 | 123335564 | 0.000000 | 0.000000
09-04-2025 20:31:30.000 | 10648612 | 106486120 | 106.4861 | 47568740 | 15612615 | 39419309 | -99900375 | 50065651 | 26564761 | 116610939 | 0.000000 | 0.000000
09-04-2025 20:31:25.000 | 10598761 | 105987610 | 105.9876 | 48162222 | 15614603 | 39230920 | -99896912 | 50083271 | 25089612 | 109927597 | 0.000000 | 0.000000
09-04-2025 20:31:20.000 | 10689948 | 106899480 | 106.8995 | 48441904 | 15616570 | 39563438 | -99897484 | 50073944 | 23613010 | 103328568 | 0.000000 | 0.000000
09-04-2025 20:31:15.000 | 10794451 | 107944510 | 107.9445 | 47888218 | 15608537 | 39969033 | -99901741 | 50057919 | 22123271 | 96642761 | 0.000000 | 0.000000
09-04-2025 20:31:10.000 | 10839582 | 108395820 | 108.3958 | 45332949 | 15607112 | 40135242 | -99912659 | 50046162 | 20620461 | 90151680 | 0.000000 | 0.000000
09-04-2025 20:31:05.000 | 10731333 | 107313330 | 107.3133 | 45729189 | 15603943 | 39744036 | -99909332 | 50063141 | 19119432 | 83853210 | 0.000000 | 0.000000
09-04-2025 20:31:00.000 | 10534204 | 105342040 | 105.342 | 43722573 | 15610851 | 38994924 | -99913979 | 50109478 | 17639521 | 77722900 | 0.000000 | 0.000000
09-04-2025 20:30:55.000 | 10485011 | 104850110 | 104.8501 | 42490298 | 15617132 | 38795759 | -99917992 | 50123444 | 16184158 | 71684563 | 0.000000 | 0.000000
09-04-2025 20:30:50.000 | 10590668 | 105906680 | 105.9067 | 44156978 | 15612691 | 39199460 | -99913193 | 50084473 | 14723934 | 65676041 | 0.000000 | 0.000000
09-04-2025 20:30:45.000 | 10638016 | 106380160 | 106.3802 | 44308813 | 15609834 | 39382029 | -99913368 | 50070148 | 13249758 | 59438416 | 0.000000 | 0.000000
09-04-2025 20:30:40.000 | 10546353 | 105463530 | 105.4635 | 45581606 | 15609602 | 39045869 | -99906731 | 50079659 | 11773715 | 53197701 | 0.000000 | 0.000000
09-04-2025 20:30:35.000 | 10453786 | 104537860 | 104.5379 | 45667817 | 15614551 | 38691567 | -99904716 | 50092651 | 10313091 | 46763218 | 0.000000 | 0.000000
09-04-2025 20:30:30.000 | 10556563 | 105565630 | 105.5656 | 47352314 | 15614692 | 39073677 | -99899551 | 50067986 | 885678650 | 40424793 | 0.000000 | 0.000000
09-04-2025 20:30:25.000 | 10528147 | 105281470 | 105.2815 | 49979980 | 15614877 | 38972825 | -99887505 | 50076767 | 739293213 | 33635044 | 0.000000 | 0.000000
09-04-2025 20:30:20.000 | 10583405 | 105834050 | 105.8341 | 46824385 | 15618236 | 39162944 | -99902267 | 50070946 | 592883789 | 26883789 | 0.000000 | 0.000000
09-04-2025 20:30:15.000 | 10828464 | 108284640 | 108.2846 | 49166553 | 15607722 | 40098806 | -99897079 | 50014175 | 444575653 | 20313662 | 0.000000 | 0.000000
09-04-2025 20:30:10.000 | 10742949 | 107429490 | 107.4295 | 50105576 | 15607931 | 39783779 | -99891411 | 50034294 | 294438873 | 13384825 | 0.000000 | 0.000000
09-04-2025 20:30:05.000 | 10562271 | 105622710 | 105.6227 | 47112769 | 15614135 | 39095710 | -99900665 | 50073200 | 146587341 | 6622887 | 0.000000 | 0.000000
09-04-2025 20:30:00.000 | 10593398 | 105933980 | 105.934 | 47305200 | 15615776 | 39207251 | -99900444 | 50078251 | 26618119 | 13756509 | 0.000000 | 0.000000
09-04-2025 20:29:55.000 | 10769298 | 107692980 | 107.693 | 47684883 | 15613722 | 39862373 | -99902115 | 50052105 | 26470344 | 13691897 | 0.000000 | 0.000000
09-04-2025 20:29:50.000 | 10794083 | 107940830 | 107.9408 | 45463599 | 15610235 | 39959497 | -99911415 | 50055603 | 26320713 | 13626298 | 0.000000 | 0.000000
09-04-2025 20:29:45.000 | 10862127 | 108621270 | 108.6213 | 46463887 | 15609282 | 40214868 | -99908638 | 50034359 | 26170350 | 13564380 | 0.000000 | 0.000000
09-04-2025 20:29:40.000 | 10776231 | 107762310 | 107.7623 | 46903804 | 15603522 | 39913462 | -99905411 | 50058773 | 26019662 | 13498372 | 0.000000 | 0.000000
09-04-2025 20:29:35.000 | 10592029 | 105920290 | 105.9203 | 42909956 | 15610964 | 39206975 | -99918045 | 50109528 | 25871023 | 13435925 | 0.000000 | 0.000000
09-04-2025 20:29:30.000 | 10555667 | 105556670 | 105.5567 | 40227029 | 15611847 | 39066462 | -99927460 | 50121696 | 25724432 | 13377968 | 0.000000 | 0.000000
09-04-2025 20:29:25.000 | 10602216 | 106022160 | 106.0222 | 42488237 | 15612404 | 39240400 | -99919800 | 50106274 | 25577537 | 13321527 | 0.000000 | 0.000000
09-04-2025 20:29:20.000 | 10569789 | 105697890 | 105.6979 | 41152520 | 15609036 | 39127119 | -99924294 | 50112755 | 25430525 | 13262823 | 0.000000 | 0.000000
09-04-2025 20:29:15.000 | 10499427 | 104994270 | 104.9943 | 43389595 | 15610072 | 38867668 | -99914719 | 50111317 | 25283982 | 13204808 | 0.000000 | 0.000000
09-04-2025 20:29:10.000 | 10430328 | 104303280 | 104.3033 | 44682432 | 15611107 | 38611770 | -99908371 | 50114784 | 25138693 | 13144667 | 0.000000 | 0.000000
09-04-2025 20:29:05.000 | 10362373 | 103623730 | 103.6237 | 45417129 | 15613353 | 38356375 | -99904091 | 50116310 | 24994488 | 13082366 | 0.000000 | 0.000000
09-04-2025 20:29:00.000 | 10391576 | 103915760 | 103.9158 | 49994209 | 15616374 | 38464622 | -99884468 | 50105045 | 24850479 | 13017058 | 0.000000 | 0.000000
09-04-2025 20:28:55.000 | 10432875 | 104328750 | 104.3287 | 54051890 | 15619604 | 38616624 | -99866058 | 50082279 | 24705898 | 12945593 | 0.000000 | 0.000000
09-04-2025 20:28:50.000 | 10609741 | 106097410 | 106.0974 | 53954570 | 15610649 | 39292141 | -99870941 | 50044189 | 24559756 | 12869121 | 0.000000 | 0.000000
09-04-2025 20:28:45.000 | 10588504 | 105885040 | 105.885 | 54194331 | 15612479 | 39209299 | -99869278 | 50037449 | 24412324 | 12794706 | 0.000000 | 0.000000
09-04-2025 20:28:40.000 | 10548816 | 105488160 | 105.4882 | 55462969 | 15615390 | 39057852 | -99862068 | 50064854 | 24265451 | 12717428 | 0.000000 | 0.000000
09-04-2025 20:28:35.000 | 10615470 | 106154700 | 106.1547 | 56296089 | 15620156 | 39293918 | -99859673 | 50049244 | 24118926 | 12640247 | 0.000000 | 0.000000
09-04-2025 20:28:30.000 | 10766466 | 107664660 | 107.6647 | 59267583 | 15611348 | 39879207 | -99848831 | 50026936 | 23970592 | 12560529 | 0.000000 | 0.000000
09-04-2025 20:28:25.000 | 10841836 | 108418360 | 108.4184 | 56466377 | 15607799 | 40161143 | -99864647 | 50031208 | 23820508 | 12479434 | 0.000000 | 0.000000
09-04-2025 20:28:20.000 | 10787069 | 107870690 | 107.8707 | 54011392 | 15607979 | 39954685 | -99874886 | 50032288 | 23670248 | 12403303 | 0.000000 | 0.000000
09-04-2025 20:28:15.000 | 10692567 | 106925670 | 106.9257 | 52861343 | 15606463 | 39606409 | -99878021 | 50051048 | 23520746 | 12328203 | 0.000000 | 0.000000
09-04-2025 20:28:10.000 | 10601420 | 106014200 | 106.0142 | 51124121 | 15604068 | 39272661 | -99883926 | 50068188 | 23372746 | 12254357 | 0.000000 | 0.000000
09-04-2025 20:28:05.000 | 10506598 | 105065980 | 105.066 | 47819663 | 15608875 | 38905017 | -99896584 | 50084824 | 23225936 | 12186183 | 0.000000 | 0.000000
09-04-2025 20:28:00.000 | 10366808 | 103668080 | 103.6681 | 45195581 | 15614626 | 38369248 | -99905106 | 50100010 | 23081021 | 12121042 | 0.000000 | 0.000000
09-04-2025 20:27:55.000 | 10417511 | 104175110 | 104.1751 | 46470928 | 15615793 | 38555735 | -99900650 | 50089458 | 22936701 | 12056530 | 0.000000 | 0.000000
09-04-2025 20:27:50.000 | 10486818 | 104868180 | 104.8682 | 49632969 | 15619188 | 38808762 | -99888184 | 50068798 | 22791854 | 11990433 | 0.000000 | 0.000000
09-04-2025 20:27:45.000 | 10628512 | 106285120 | 106.2851 | 52668589 | 15615602 | 39346252 | -99877449 | 50033497 | 22645564 | 11919553 | 0.000000 | 0.000000
09-04-2025 20:27:40.000 | 10779078 | 107790780 | 107.7908 | 52631401 | 15606872 | 39924443 | -99881004 | 50000511 | 22497090 | 11846959 | 0.000000 | 0.000000
09-04-2025 20:27:35.000 | 10712239 | 107122390 | 107.1224 | 52572822 | 15604702 | 39683032 | -99879791 | 50006565 | 22347424 | 11773171 | 0.000000 | 0.000000
09-04-2025 20:27:30.000 | 10583867 | 105838670 | 105.8387 | 50950156 | 15604267 | 39207434 | -99884331 | 50022942 | 22199281 | 11701436 | 0.000000 | 0.000000
09-04-2025 20:27:25.000 | 10349889 | 103498890 | 103.4989 | 50341577 | 15610568 | 38325488 | -99881920 | 50077057 | 22053334 | 11631393 | 0.000000 | 0.000000
09-04-2025 20:27:20.000 | 10282738 | 102827380 | 102.8274 | 48900508 | 15622763 | 38045498 | -99887115 | 50092506 | 21910441 | 11563546 | 0.000000 | 0.000000
09-04-2025 20:27:15.000 | 10485899 | 104858990 | 104.859 | 53506357 | 15618942 | 38813071 | -99870064 | 50035004 | 21766699 | 11493054 | 0.000000 | 0.000000
09-04-2025 20:27:10.000 | 10612086 | 106120860 | 106.1209 | 55947852 | 15617299 | 39288010 | -99861313 | 50025497 | 21620303 | 11416671 | 0.000000 | 0.000000
09-04-2025 20:27:05.000 | 10717278 | 107172780 | 107.1728 | 57766147 | 15616824 | 39680645 | -99855057 | 50009556 | 21472518 | 11337892 | 0.000000 | 0.000000
09-04-2025 20:27:00.000 | 10873655 | 108736550 | 108.7365 | 57590601 | 15610371 | 40274492 | -99860039 | 49977936 | 21322729 | 11258314 | 0.000000 | 0.000000
09-04-2025 20:26:55.000 | 10896140 | 108961400 | 108.9614 | 56858457 | 15602274 | 40377007 | -99864128 | 49972404 | 21171213 | 11177518 | 0.000000 | 0.000000
09-04-2025 20:26:50.000 | 10754714 | 107547140 | 107.5471 | 53230786 | 15602244 | 39849011 | -99877739 | 50003448 | 21020682 | 11101472 | 0.000000 | 0.000000
09-04-2025 20:26:45.000 | 10566770 | 105667700 | 105.6677 | 51292988 | 15606749 | 39138040 | -99882393 | 50045864 | 20872326 | 11028308 | 0.000000 | 0.000000
09-04-2025 20:26:40.000 | 10431686 | 104316860 | 104.3169 | 49390562 | 15615475 | 38613870 | -99888100 | 50059361 | 20726428 | 10958511 | 0.000000 | 0.000000
09-04-2025 20:26:35.000 | 10428328 | 104283280 | 104.2833 | 51598135 | 15616269 | 38603403 | -99877815 | 50058590 | 20581586 | 10887791 | 0.000000 | 0.000000
09-04-2025 20:26:30.000 | 10504366 | 105043660 | 105.0437 | 54596187 | 15618610 | 38884314 | -99865204 | 50033604 | 20436611 | 10814596 | 0.000000 | 0.000000
09-04-2025 20:26:25.000 | 10647551 | 106475510 | 106.4755 | 56206958 | 15619753 | 39412844 | -99860962 | 50014099 | 20290045 | 10738915 | 0.000000 | 0.000000
09-04-2025 20:26:20.000 | 10788160 | 107881600 | 107.8816 | 60400864 | 15614994 | 39952351 | -99843636 | 49985474 | 20141553 | 10658937 | 0.000000 | 0.000000
09-04-2025 20:26:15.000 | 10879775 | 108797750 | 108.7977 | 58703716 | 15611023 | 40297380 | -99854752 | 49976013 | 19991322 | 10575081 | 0.000000 | 0.000000
09-04-2025 20:26:10.000 | 10927073 | 109270730 | 109.2707 | 57678545 | 15606227 | 40482434 | -99860977 | 49959904 | 19839848 | 10494672 | 0.000000 | 0.000000
09-04-2025 20:26:05.000 | 10749405 | 107494050 | 107.4941 | 57036162 | 15607650 | 39821265 | -99859528 | 50005535 | 19688961 | 10414089 | 0.000000 | 0.000000
09-04-2025 20:26:00.000 | 10670724 | 106707240 | 106.7072 | 55008682 | 15612253 | 39514934 | -99867386 | 50032032 | 19540219 | 10336577 | 0.000000 | 0.000000
09-04-2025 20:25:55.000 | 10708566 | 107085660 | 107.0857 | 53228198 | 15611501 | 39653296 | -99876694 | 50032536 | 19392053 | 10261365 | 0.000000 | 0.000000
09-04-2025 20:25:50.000 | 10760738 | 107607380 | 107.6074 | 55189517 | 15608228 | 39858052 | -99868736 | 50015469 | 19242973 | 10186568 | 0.000000 | 0.000000
09-04-2025 20:25:45.000 | 10685273 | 106852730 | 106.8527 | 56135615 | 15607023 | 39584312 | -99862289 | 50021591 | 19093799 | 10109694 | 0.000000 | 0.000000
09-04-2025 20:25:40.000 | 10542621 | 105426210 | 105.4262 | 53393496 | 15611425 | 39040964 | -99872002 | 50039066 | 18946141 | 10032477 | 0.000000 | 0.000000
09-04-2025 20:25:35.000 | 10467508 | 104675080 | 104.6751 | 55675156 | 15610683 | 38769685 | -99858849 | 50045727 | 18800219 | 995625977 | 0.000000 | 0.000000
09-04-2025 20:25:30.000 | 10441209 | 104412090 | 104.4121 | 55949028 | 15616093 | 38659717 | -99856743 | 50032715 | 18655205 | 987965027 | 0.000000 | 0.000000
09-04-2025 20:25:25.000 | 10459012 | 104590120 | 104.5901 | 58507583 | 15617327 | 38728425 | -99843903 | 50030605 | 18509906 | 979909790 | 0.000000 | 0.000000
09-04-2025 20:25:20.000 | 10645238 | 106452380 | 106.4524 | 59779033 | 15617360 | 39417837 | -99842697 | 49994984 | 18363791 | 971850891 | 0.000000 | 0.000000
09-04-2025 20:25:15.000 | 10781671 | 107816710 | 107.8167 | 58952231 | 15614506 | 39926846 | -99850845 | 49949100 | 18214838 | 963575195 | 0.000000 | 0.000000
09-04-2025 20:25:10.000 | 10797181 | 107971810 | 107.9718 | 61808535 | 15606920 | 40009285 | -99836555 | 49950550 | 18064846 | 955072632 | 0.000000 | 0.000000
09-04-2025 20:25:05.000 | 10712165 | 107121650 | 107.1217 | 58240176 | 15608330 | 39684348 | -99852531 | 49963600 | 17915625 | 946802917 | 0.000000 | 0.000000
09-04-2025 20:25:00.000 | 10645973 | 106459730 | 106.4597 | 59460884 | 15609091 | 39440352 | -99844383 | 49977654 | 17767252 | 938765442 | 0.000000 | 0.000000
09-04-2025 20:24:55.000 | 10574102 | 105741020 | 105.741 | 58753823 | 15614028 | 39161157 | -99845993 | 50000149 | 17619875 | 930486755 | 0.000000 | 0.000000
09-04-2025 20:24:50.000 | 10611877 | 106118770 | 106.1188 | 59156680 | 15616637 | 39294875 | -99844978 | 50002327 | 17472785 | 922294739 | 0.000000 | 0.000000
09-04-2025 20:24:45.000 | 10754264 | 107542640 | 107.5426 | 58668184 | 15617297 | 39817781 | -99851524 | 49983669 | 17324836 | 914147522 | 0.000000 | 0.000000
09-04-2025 20:24:40.000 | 10916630 | 109166300 | 109.1663 | 60239956 | 15612724 | 40432290 | -99848099 | 49952419 | 17174297 | 905903442 | 0.000000 | 0.000000
09-04-2025 20:24:35.000 | 10900259 | 109002590 | 109.0026 | 59546152 | 15606820 | 40385608 | -99851120 | 49956905 | 17022656 | 897483521 | 0.000000 | 0.000000
09-04-2025 20:24:30.000 | 10825533 | 108255330 | 108.2553 | 59064297 | 15605541 | 40112080 | -99851494 | 49982548 | 16871674 | 889345642 | 0.000000 | 0.000000
09-04-2025 20:24:25.000 | 10710286 | 107102860 | 107.1029 | 55174707 | 15609808 | 39667727 | -99867569 | 50005974 | 16722074 | 881293030 | 0.000000 | 0.000000
09-04-2025 20:24:20.000 | 10636946 | 106369460 | 106.3695 | 56143828 | 15609502 | 39400645 | -99860992 | 50021915 | 16573840 | 873522034 | 0.000000 | 0.000000
09-04-2025 20:24:15.000 | 10544391 | 105443910 | 105.4439 | 57329692 | 15611166 | 39055698 | -99852524 | 50035545 | 16426760 | 865663330 | 0.000000 | 0.000000
09-04-2025 20:24:10.000 | 10540376 | 105403760 | 105.4038 | 55631973 | 15611306 | 39037275 | -99861008 | 50039265 | 16280184 | 857827576 | 0.000000 | 0.000000
09-04-2025 20:24:05.000 | 10515132 | 105151320 | 105.1513 | 57247363 | 15614151 | 38940276 | -99852127 | 50032536 | 16133993 | 850090027 | 0.000000 | 0.000000
09-04-2025 20:24:00.000 | 10562801 | 105628010 | 105.628 | 56263584 | 15613159 | 39116670 | -99858437 | 50028351 | 15987864 | 842223267 | 0.000000 | 0.000000
09-04-2025 20:23:55.000 | 10662998 | 106629980 | 106.63 | 55345322 | 15614322 | 39482061 | -99865570 | 50002338 | 15840576 | 834561523 | 0.000000 | 0.000000
09-04-2025 20:23:50.000 | 10667790 | 106677900 | 106.6779 | 55718994 | 15615308 | 39497778 | -99863876 | 50001884 | 15692396 | 826819397 | 0.000000 | 0.000000
09-04-2025 20:23:45.000 | 10690504 | 106905040 | 106.905 | 57467622 | 15612429 | 39592490 | -99855827 | 49998379 | 15544079 | 818973755 | 0.000000 | 0.000000
09-04-2025 20:23:40.000 | 10744963 | 107449630 | 107.4496 | 56542744 | 15612669 | 39791064 | -99861832 | 49995640 | 15395465 | 811096558 | 0.000000 | 0.000000
09-04-2025 20:23:35.000 | 10789541 | 107895410 | 107.8954 | 58476938 | 15606262 | 39976228 | -99853455 | 49991001 | 15245944 | 803189270 | 0.000000 | 0.000000
09-04-2025 20:23:30.000 | 10720034 | 107200340 | 107.2003 | 56550625 | 15606000 | 39717004 | -99861153 | 49999207 | 15096345 | 795389709 | 0.000000 | 0.000000
09-04-2025 20:23:25.000 | 10601728 | 106017280 | 106.0173 | 55300322 | 15609161 | 39268689 | -99864235 | 50030178 | 14948054 | 787607422 | 0.000000 | 0.000000
09-04-2025 20:23:20.000 | 10521716 | 105217160 | 105.2172 | 56080801 | 15614024 | 38962769 | -99858253 | 50035080 | 14801396 | 779943848 | 0.000000 | 0.000000
09-04-2025 20:23:15.000 | 10498171 | 104981710 | 104.9817 | 55463276 | 15614474 | 38873093 | -99860733 | 50038429 | 14655736 | 772223389 | 0.000000 | 0.000000
09-04-2025 20:23:10.000 | 10595303 | 105953030 | 105.953 | 53465093 | 15614313 | 39228376 | -99872925 | 50021534 | 14509401 | 764565002 | 0.000000 | 0.000000
09-04-2025 20:23:05.000 | 10680980 | 106809800 | 106.8098 | 56923965 | 15613136 | 39554314 | -99858284 | 49994717 | 14361509 | 757015808 | 0.000000 | 0.000000
09-04-2025 20:23:00.000 | 10666710 | 106667100 | 106.6671 | 59584375 | 15612540 | 39508652 | -99844345 | 50009602 | 14213335 | 748956970 | 0.000000 | 0.000000
09-04-2025 20:22:55.000 | 10693488 | 106934880 | 106.9349 | 60564424 | 15615325 | 39602651 | -99839996 | 50011387 | 14065160 | 740678955 | 0.000000 | 0.000000
09-04-2025 20:22:50.000 | 10805712 | 108057120 | 108.0571 | 59975996 | 15609275 | 40031372 | -99846321 | 49992664 | 13916115 | 732213806 | 0.000000 | 0.000000
09-04-2025 20:22:45.000 | 10858941 | 108589410 | 108.5894 | 59237090 | 15603773 | 40240154 | -99851540 | 49969265 | 13765330 | 724006897 | 0.000000 | 0.000000
09-04-2025 20:22:40.000 | 10685198 | 106851980 | 106.852 | 57820801 | 15604513 | 39593555 | -99853912 | 50000481 | 13615144 | 715826172 | 0.000000 | 0.000000
09-04-2025 20:22:35.000 | 10510801 | 105108010 | 105.108 | 56377168 | 15609934 | 38933379 | -99856461 | 50046539 | 13467920 | 707863098 | 0.000000 | 0.000000
09-04-2025 20:22:30.000 | 10423791 | 104237910 | 104.2379 | 54102275 | 15620689 | 38580769 | -99865578 | 50061665 | 13322993 | 700196533 | 0.000000 | 0.000000
09-04-2025 20:22:25.000 | 10626135 | 106261350 | 106.2613 | 57208774 | 15618612 | 39338709 | -99855392 | 50012905 | 13177192 | 692536621 | 0.000000 | 0.000000
09-04-2025 20:22:20.000 | 10731342 | 107313420 | 107.3134 | 60834238 | 15613271 | 39748008 | -99839706 | 49992123 | 13028977 | 684341919 | 0.000000 | 0.000000
09-04-2025 20:22:15.000 | 10835409 | 108354090 | 108.3541 | 60206680 | 15608596 | 40142852 | -99845985 | 49980919 | 12879321 | 675956116 | 0.000000 | 0.000000
09-04-2025 20:22:10.000 | 10848626 | 108486260 | 108.4863 | 57328145 | 15606633 | 40191169 | -99860672 | 49982437 | 12728589 | 667835693 | 0.000000 | 0.000000
09-04-2025 20:22:05.000 | 10745448 | 107454480 | 107.4545 | 58687832 | 15605389 | 39816211 | -99851189 | 49998138 | 12578521 | 659867065 | 0.000000 | 0.000000
09-04-2025 20:22:00.000 | 10576793 | 105767930 | 105.7679 | 56614790 | 15611587 | 39173223 | -99857048 | 50038578 | 12430423 | 651904236 | 0.000000 | 0.000000
09-04-2025 20:21:55.000 | 10527422 | 105274220 | 105.2742 | 56057026 | 15613081 | 38985857 | -99858528 | 50039776 | 12284021 | 644135803 | 0.000000 | 0.000000
09-04-2025 20:21:50.000 | 10532965 | 105329650 | 105.3297 | 59262432 | 15613701 | 39011262 | -99842094 | 50011402 | 12137774 | 636201416 | 0.000000 | 0.000000
09-04-2025 20:21:45.000 | 10486021 | 104860210 | 104.8602 | 59036353 | 15616207 | 38831746 | -99841888 | 50022625 | 11991821 | 627982727 | 0.000000 | 0.000000
09-04-2025 20:21:40.000 | 10591288 | 105912880 | 105.9129 | 59724771 | 15617797 | 39217444 | -99841385 | 50004040 | 11845655 | 619818420 | 0.000000 | 0.000000
09-04-2025 20:21:35.000 | 10718646 | 107186460 | 107.1865 | 61805762 | 15615933 | 39696296 | -99834167 | 49973583 | 11697859 | 611429321 | 0.000000 | 0.000000
09-04-2025 20:21:30.000 | 10784721 | 107847210 | 107.8472 | 63487095 | 15612305 | 39953721 | -99827179 | 49970676 | 11548556 | 602699646 | 0.000000 | 0.000000
09-04-2025 20:21:25.000 | 10828791 | 108287910 | 108.2879 | 63046787 | 15609873 | 40121040 | -99830940 | 49965828 | 11398428 | 593971741 | 0.000000 | 0.000000
09-04-2025 20:21:20.000 | 10789371 | 107893710 | 107.8937 | 58841631 | 15607110 | 39973748 | -99851616 | 49978195 | 11247852 | 585317139 | 0.000000 | 0.000000
09-04-2025 20:21:15.000 | 10666373 | 106663730 | 106.6637 | 57288198 | 15606777 | 39518022 | -99856079 | 50002819 | 11098599 | 577234314 | 0.000000 | 0.000000
09-04-2025 20:21:10.000 | 10602459 | 106024590 | 106.0246 | 54143647 | 15609260 | 39268806 | -99869865 | 50020954 | 10950967 | 569506042 | 0.000000 | 0.000000
09-04-2025 20:21:05.000 | 10560359 | 105603590 | 105.6036 | 56180088 | 15611817 | 39111614 | -99858795 | 50016144 | 10803785 | 562024353 | 0.000000 | 0.000000
09-04-2025 20:21:00.000 | 10472502 | 104725020 | 104.725 | 55612690 | 15614468 | 38778892 | -99859299 | 50033787 | 10657554 | 554148315 | 0.000000 | 0.000000
09-04-2025 20:20:55.000 | 10536546 | 105365460 | 105.3655 | 56543428 | 15611729 | 39023821 | -99856316 | 50024006 | 10511664 | 546329468 | 0.000000 | 0.000000
09-04-2025 20:20:50.000 | 10602684 | 106026840 | 106.0268 | 55472598 | 15613426 | 39261755 | -99863411 | 50004555 | 10364903 | 538762085 | 0.000000 | 0.000000
09-04-2025 20:20:45.000 | 10568454 | 105684540 | 105.6845 | 55950308 | 15613525 | 39135952 | -99860161 | 50015560 | 10217762 | 530974670 | 0.000000 | 0.000000
09-04-2025 20:20:40.000 | 10577289 | 105772890 | 105.7729 | 54769307 | 15613419 | 39166787 | -99866211 | 50027294 | 10070939 | 523307983 | 0.000000 | 0.000000
09-04-2025 20:20:35.000 | 10634705 | 106347050 | 106.347 | 53237227 | 15615318 | 39371118 | -99874939 | 50010193 | 99237188 | 515721436 | 0.000000 | 0.000000
09-04-2025 20:20:30.000 | 10739943 | 107399430 | 107.3994 | 53271826 | 15610085 | 39773328 | -99877213 | 49984211 | 97753877 | 508371796 | 0.000000 | 0.000000
09-04-2025 20:20:25.000 | 10683890 | 106838900 | 106.8389 | 53376567 | 15608243 | 39571240 | -99875435 | 49988331 | 96263740 | 500939301 | 0.000000 | 0.000000
09-04-2025 20:20:20.000 | 10566230 | 105662300 | 105.6623 | 54527397 | 15611198 | 39130811 | -99867111 | 50012001 | 94785088 | 493456970 | 0.000000 | 0.000000
09-04-2025 20:20:15.000 | 10558310 | 105583100 | 105.5831 | 54645010 | 15611204 | 39101736 | -99866341 | 50012474 | 93320830 | 486042114 | 0.000000 | 0.000000
09-04-2025 20:20:10.000 | 10573704 | 105737040 | 105.737 | 54064443 | 15613857 | 39152024 | -99869537 | 50001144 | 91853965 | 478483032 | 0.000000 | 0.000000
09-04-2025 20:20:05.000 | 10590613 | 105906130 | 105.9061 | 56549097 | 15610473 | 39226704 | -99857750 | 50001179 | 90385986 | 470836639 | 0.000000 | 0.000000
09-04-2025 20:20:00.000 | 10562805 | 105628050 | 105.6281 | 54735981 | 15610038 | 39121548 | -99866005 | 50003426 | 88919668 | 463128082 | 0.000000 | 0.000000
09-04-2025 20:19:55.000 | 10551228 | 105512280 | 105.5123 | 55994541 | 15613414 | 39072688 | -99859482 | 50002655 | 87451904 | 455531250 | 0.000000 | 0.000000
09-04-2025 20:19:50.000 | 10563803 | 105638030 | 105.638 | 55233628 | 15613864 | 39116526 | -99863586 | 50009502 | 85986426 | 447787079 | 0.000000 | 0.000000
09-04-2025 20:19:45.000 | 10584485 | 105844850 | 105.8448 | 56313965 | 15614657 | 39193103 | -99858765 | 50001099 | 84519063 | 440158447 | 0.000000 | 0.000000
09-04-2025 20:19:40.000 | 10619925 | 106199250 | 106.1993 | 55800273 | 15616373 | 39318735 | -99862244 | 50001450 | 83048398 | 432446564 | 0.000000 | 0.000000
09-04-2025 20:19:35.000 | 10692282 | 106922820 | 106.9228 | 55632407 | 15615409 | 39587908 | -99864914 | 49992317 | 81570850 | 424641174 | 0.000000 | 0.000000
09-04-2025 20:19:30.000 | 10815508 | 108155080 | 108.1551 | 56626489 | 15613105 | 40050535 | -99863220 | 49972294 | 80078315 | 416920227 | 0.000000 | 0.000000
09-04-2025 20:19:25.000 | 10848373 | 108483730 | 108.4837 | 56487832 | 15607893 | 40186147 | -99864708 | 49979469 | 78571719 | 408894287 | 0.000000 | 0.000000
09-04-2025 20:19:20.000 | 10847623 | 108476230 | 108.4762 | 56748311 | 15605573 | 40188948 | -99863441 | 49987362 | 77064590 | 401085693 | 0.000000 | 0.000000
09-04-2025 20:19:15.000 | 10754428 | 107544280 | 107.5443 | 54802539 | 15605176 | 39842156 | -99870415 | 49996239 | 75566235 | 393443298 | 0.000000 | 0.000000
09-04-2025 20:19:10.000 | 10583348 | 105833480 | 105.8335 | 54257720 | 15605948 | 39206914 | -99868843 | 50032261 | 74081147 | 385763947 | 0.000000 | 0.000000
09-04-2025 20:19:05.000 | 10442637 | 104426370 | 104.4264 | 52347598 | 15612804 | 38666230 | -99874596 | 50056778 | 72620869 | 378402863 | 0.000000 | 0.000000
09-04-2025 20:19:00.000 | 10470974 | 104709740 | 104.7097 | 53225830 | 15616728 | 38762810 | -99871056 | 50044220 | 71171587 | 371142853 | 0.000000 | 0.000000
09-04-2025 20:18:55.000 | 10565151 | 105651510 | 105.6515 | 56769634 | 15615476 | 39121731 | -99855949 | 50007950 | 69713438 | 363645294 | 0.000000 | 0.000000
09-04-2025 20:18:50.000 | 10666777 | 106667770 | 106.6678 | 60131973 | 15610618 | 39515159 | -99841484 | 49988621 | 68239741 | 355589569 | 0.000000 | 0.000000
09-04-2025 20:18:45.000 | 10650183 | 106501830 | 106.5018 | 57234111 | 15611165 | 39446250 | -99855911 | 49984379 | 66758740 | 347469543 | 0.000000 | 0.000000
09-04-2025 20:18:40.000 | 10637291 | 106372910 | 106.3729 | 55946812 | 15613171 | 39391082 | -99861977 | 49995636 | 65279028 | 339532776 | 0.000000 | 0.000000
09-04-2025 20:18:35.000 | 10667349 | 106673490 | 106.6735 | 56801313 | 15611666 | 39507627 | -99858536 | 49995144 | 63800190 | 331694855 | 0.000000 | 0.000000
09-04-2025 20:18:30.000 | 10714588 | 107145880 | 107.1459 | 56832256 | 15611519 | 39682947 | -99859627 | 49982670 | 62317666 | 323824371 | 0.000000 | 0.000000
09-04-2025 20:18:25.000 | 10708958 | 107089580 | 107.0896 | 55418047 | 15611520 | 39658862 | -99866371 | 49975861 | 60828311 | 316008789 | 0.000000 | 0.000000
09-04-2025 20:18:20.000 | 10682898 | 106828980 | 106.829 | 56525068 | 15611710 | 39564331 | -99860313 | 49990841 | 59339858 | 308175629 | 0.000000 | 0.000000
09-04-2025 20:18:15.000 | 10707773 | 107077730 | 107.0777 | 56101123 | 15611830 | 39655259 | -99863029 | 49989811 | 57855288 | 300279877 | 0.000000 | 0.000000
09-04-2025 20:18:10.000 | 10786818 | 107868180 | 107.8682 | 56978926 | 15608224 | 39958120 | -99860779 | 49964512 | 56364282 | 292643890 | 0.000000 | 0.000000
09-04-2025 20:18:05.000 | 10676014 | 106760140 | 106.7601 | 57034678 | 15609296 | 39546692 | -99857605 | 49995331 | 54869814 | 284572906 | 0.000000 | 0.000000
09-04-2025 20:18:00.000 | 10626229 | 106262290 | 106.2623 | 53883315 | 15608076 | 39359863 | -99871681 | 50002411 | 53388784 | 276793518 | 0.000000 | 0.000000
09-04-2025 20:17:55.000 | 10604937 | 106049370 | 106.0494 | 54320640 | 15605853 | 39287061 | -99869072 | 49997940 | 51910859 | 269329559 | 0.000000 | 0.000000
09-04-2025 20:17:50.000 | 10465234 | 104652340 | 104.6523 | 55589365 | 15610487 | 38761785 | -99859222 | 50026005 | 50448589 | 261832031 | 0.000000 | 0.000000
09-04-2025 20:17:45.000 | 10404279 | 104042790 | 104.0428 | 53034795 | 15617618 | 38514026 | -99870338 | 50028412 | 49004272 | 254338852 | 0.000000 | 0.000000
09-04-2025 20:17:40.000 | 10529152 | 105291520 | 105.2915 | 55084116 | 15615352 | 38984663 | -99863434 | 49991371 | 47553306 | 246837952 | 0.000000 | 0.000000
09-04-2025 20:17:35.000 | 10601406 | 106014060 | 106.0141 | 59539561 | 15615033 | 39261006 | -99842667 | 49978733 | 46086045 | 238935776 | 0.000000 | 0.000000
09-04-2025 20:17:30.000 | 10616832 | 106168320 | 106.1683 | 58499453 | 15618297 | 39307583 | -99848541 | 49981857 | 44612383 | 230687088 | 0.000000 | 0.000000
09-04-2025 20:17:25.000 | 10729644 | 107296440 | 107.2964 | 59039302 | 15617101 | 39728125 | -99848961 | 49967770 | 43130288 | 222442444 | 0.000000 | 0.000000
09-04-2025 20:17:20.000 | 10835570 | 108355700 | 108.3557 | 60883809 | 15612554 | 40134902 | -99842514 | 49953392 | 41633008 | 214131561 | 0.000000 | 0.000000
09-04-2025 20:17:15.000 | 10887073 | 108870730 | 108.8707 | 61073457 | 15612433 | 40325977 | -99843025 | 49958126 | 40125146 | 205648621 | 0.000000 | 0.000000
09-04-2025 20:17:10.000 | 10933331 | 109333310 | 109.3333 | 61171338 | 15609588 | 40503821 | -99843849 | 49957996 | 38609290 | 197130264 | 0.000000 | 0.000000
09-04-2025 20:17:05.000 | 10910481 | 109104810 | 109.1048 | 59019834 | 15606311 | 40423494 | -99854012 | 49973995 | 37090750 | 188685532 | 0.000000 | 0.000000
09-04-2025 20:17:00.000 | 10849688 | 108496880 | 108.4969 | 54974517 | 15604325 | 40196790 | -99871880 | 49998516 | 35578916 | 180802475 | 0.000000 | 0.000000
09-04-2025 20:16:55.000 | 10680763 | 106807630 | 106.8076 | 54314736 | 15607729 | 39562566 | -99870949 | 50029671 | 34079580 | 173211609 | 0.000000 | 0.000000
09-04-2025 20:16:50.000 | 10553552 | 105535520 | 105.5355 | 52725547 | 15614728 | 39071887 | -99875435 | 50053532 | 32604583 | 165755356 | 0.000000 | 0.000000
09-04-2025 20:16:45.000 | 10590566 | 105905660 | 105.9057 | 54024824 | 15612371 | 39217463 | -99870140 | 50035061 | 31137847 | 158360703 | 0.000000 | 0.000000
09-04-2025 20:16:40.000 | 10576986 | 105769860 | 105.7699 | 54700352 | 15610892 | 39171707 | -99866539 | 50023983 | 29666191 | 150810150 | 0.000000 | 0.000000
09-04-2025 20:16:35.000 | 10558305 | 105583050 | 105.5831 | 52221953 | 15612005 | 39095330 | -99877907 | 50033958 | 28200718 | 143367004 | 0.000000 | 0.000000
09-04-2025 20:16:30.000 | 10564132 | 105641320 | 105.6413 | 54712427 | 15610100 | 39126294 | -99866158 | 50025967 | 26734023 | 135895111 | 0.000000 | 0.000000
09-04-2025 20:16:25.000 | 10529770 | 105297700 | 105.2977 | 56082852 | 15614711 | 38990957 | -99858459 | 50023891 | 25269937 | 128325043 | 0.000000 | 0.000000
09-04-2025 20:16:20.000 | 10554140 | 105541400 | 105.5414 | 56305229 | 15617838 | 39072991 | -99857994 | 50017536 | 23808081 | 120485443 | 0.000000 | 0.000000
09-04-2025 20:16:15.000 | 10627386 | 106273860 | 106.2739 | 55407417 | 15617305 | 39343035 | -99864365 | 50008541 | 22338206 | 112677895 | 0.000000 | 0.000000
09-04-2025 20:16:10.000 | 10786738 | 107867380 | 107.8674 | 55382158 | 15616122 | 39934180 | -99868454 | 49990341 | 20854177 | 104923561 | 0.000000 | 0.000000
09-04-2025 20:16:05.000 | 10936448 | 109364480 | 109.3645 | 59230928 | 15608479 | 40514656 | -99853661 | 49960083 | 19347065 | 97030518 | 0.000000 | 0.000000
09-04-2025 20:16:00.000 | 10886355 | 108863550 | 108.8636 | 57419458 | 15603271 | 40339285 | -99861191 | 49975712 | 17828945 | 88839813 | 0.000000 | 0.000000
09-04-2025 20:15:55.000 | 10750003 | 107500030 | 107.5 | 52730718 | 15607326 | 39816155 | -99879913 | 50016499 | 16323257 | 81207863 | 0.000000 | 0.000000
09-04-2025 20:15:50.000 | 10670977 | 106709770 | 106.7098 | 53349536 | 15611060 | 39515752 | -99875259 | 50026276 | 14834518 | 73953362 | 0.000000 | 0.000000
09-04-2025 20:15:45.000 | 10617434 | 106174340 | 106.1743 | 51218389 | 15614560 | 39305732 | -99883850 | 50046093 | 13354877 | 66665924 | 0.000000 | 0.000000
09-04-2025 20:15:40.000 | 10682167 | 106821670 | 106.8217 | 52602529 | 15612726 | 39551565 | -99878975 | 50028591 | 11877047 | 59498032 | 0.000000 | 0.000000
09-04-2025 20:15:35.000 | 10659209 | 106592090 | 106.5921 | 52524707 | 15614562 | 39462288 | -99878815 | 50034855 | 10395201 | 52203598 | 0.000000 | 0.000000
09-04-2025 20:15:30.000 | 10689276 | 106892760 | 106.8928 | 51922847 | 15613354 | 39575002 | -99882233 | 50033939 | 891304626 | 44908043 | 0.000000 | 0.000000
09-04-2025 20:15:25.000 | 10707059 | 107070590 | 107.0706 | 52938584 | 15611365 | 39647847 | -99877998 | 50023762 | 742424194 | 37533703 | 0.000000 | 0.000000
09-04-2025 20:15:20.000 | 10686288 | 106862880 | 106.8629 | 54319248 | 15611030 | 39574263 | -99871063 | 50028141 | 593548523 | 30093164 | 0.000000 | 0.000000
09-04-2025 20:15:15.000 | 10663803 | 106638030 | 106.638 | 53604453 | 15612480 | 39486216 | -99873894 | 50030437 | 445170013 | 22697237 | 0.000000 | 0.000000
09-04-2025 20:15:10.000 | 10649993 | 106499930 | 106.4999 | 54928735 | 15614849 | 39431794 | -99867256 | 50042683 | 297147736 | 15236087 | 0.000000 | 0.000000
09-04-2025 20:15:05.000 | 10690920 | 106909200 | 106.9092 | 54809653 | 15612969 | 39587563 | -99868843 | 50031551 | 149032867 | 7641937 | 0.000000 | 0.000000
09-04-2025 20:15:00.000 | 10773504 | 107735040 | 107.735 | 56021929 | 15609089 | 39904531 | -99865074 | 50006271 | 26672102 | 14149238 | 0.000000 | 0.000000
09-04-2025 20:14:55.000 | 10728223 | 107282230 | 107.2822 | 55371357 | 15607213 | 39740791 | -99867073 | 50014618 | 26522693 | 14071943 | 0.000000 | 0.000000
09-04-2025 20:14:50.000 | 10665649 | 106656490 | 106.6565 | 53108022 | 15607704 | 39504185 | -99876259 | 50034409 | 26374236 | 13996459 | 0.000000 | 0.000000
09-04-2025 20:14:45.000 | 10609761 | 106097610 | 106.0976 | 52155532 | 15610612 | 39289592 | -99879395 | 50043034 | 26226533 | 13923871 | 0.000000 | 0.000000
09-04-2025 20:14:40.000 | 10513788 | 105137880 | 105.1379 | 52034092 | 15611481 | 38931951 | -99877754 | 50043148 | 26079977 | 13853075 | 0.000000 | 0.000000
09-04-2025 20:14:35.000 | 10474608 | 104746080 | 104.7461 | 53256904 | 15615707 | 38779065 | -99870995 | 50052574 | 25934355 | 13780468 | 0.000000 | 0.000000
09-04-2025 20:14:30.000 | 10588276 | 105882760 | 105.8828 | 52202896 | 15614014 | 39200940 | -99878685 | 50029869 | 25788549 | 13707792 | 0.000000 | 0.000000
09-04-2025 20:14:25.000 | 10698338 | 106983380 | 106.9834 | 52191455 | 15612959 | 39609998 | -99881218 | 49994179 | 25640871 | 13635455 | 0.000000 | 0.000000
09-04-2025 20:14:20.000 | 10691991 | 106919910 | 106.9199 | 53748184 | 15611015 | 39594304 | -99873886 | 49996571 | 25492006 | 13560546 | 0.000000 | 0.000000
09-04-2025 20:14:15.000 | 10666010 | 106660100 | 106.6601 | 54251621 | 15613345 | 39493389 | -99870895 | 50005234 | 25343709 | 13485802 | 0.000000 | 0.000000
09-04-2025 20:14:10.000 | 10719373 | 107193730 | 107.1937 | 54372075 | 15613407 | 39690540 | -99871605 | 50003246 | 25195350 | 13410400 | 0.000000 | 0.000000
09-04-2025 20:14:05.000 | 10768838 | 107688380 | 107.6884 | 54376392 | 15616788 | 39864712 | -99872757 | 49998215 | 25046453 | 13334440 | 0.000000 | 0.000000
09-04-2025 20:14:00.000 | 10871959 | 108719590 | 108.7196 | 58851587 | 15608382 | 40275984 | -99853813 | 49985744 | 24896297 | 13256652 | 0.000000 | 0.000000
09-04-2025 20:13:55.000 | 10837715 | 108377150 | 108.3772 | 52842744 | 15611771 | 40129480 | -99881340 | 50004154 | 24745646 | 13179363 | 0.000000 | 0.000000
09-04-2025 20:13:50.000 | 10818798 | 108187980 | 108.188 | 52736851 | 15606423 | 40072607 | -99881401 | 50019348 | 24595137 | 13105291 | 0.000000 | 0.000000
09-04-2025 20:13:45.000 | 10753191 | 107531910 | 107.5319 | 49972676 | 15606650 | 39824788 | -99892189 | 50038975 | 24445047 | 13034473 | 0.000000 | 0.000000
09-04-2025 20:13:40.000 | 10663832 | 106638320 | 106.6383 | 49685615 | 15605295 | 39497861 | -99891632 | 50044636 | 24296225 | 12965436 | 0.000000 | 0.000000
09-04-2025 20:13:35.000 | 10502929 | 105029290 | 105.0293 | 48886318 | 15609631 | 38891338 | -99891853 | 50066517 | 24148682 | 12896925 | 0.000000 | 0.000000
09-04-2025 20:13:30.000 | 10410575 | 104105750 | 104.1058 | 47089902 | 15609546 | 38546675 | -99897858 | 50092186 | 24003453 | 12829615 | 0.000000 | 0.000000
09-04-2025 20:13:25.000 | 10394462 | 103944620 | 103.9446 | 46487456 | 15617436 | 38466658 | -99900139 | 50081573 | 23859270 | 12766105 | 0.000000 | 0.000000
09-04-2025 20:13:20.000 | 10471770 | 104717700 | 104.7177 | 50191782 | 15615480 | 38763774 | -99885330 | 50054974 | 23714650 | 12699000 | 0.000000 | 0.000000
09-04-2025 20:13:15.000 | 10539470 | 105394700 | 105.3947 | 53140649 | 15616564 | 39015955 | -99873131 | 50044048 | 23568992 | 12628198 | 0.000000 | 0.000000
09-04-2025 20:13:10.000 | 10676620 | 106766200 | 106.7662 | 56098716 | 15614817 | 39532373 | -99862244 | 50015926 | 23421943 | 12553812 | 0.000000 | 0.000000
09-04-2025 20:13:05.000 | 10760342 | 107603420 | 107.6034 | 56385420 | 15613563 | 39845464 | -99862991 | 50002079 | 23273283 | 12474609 | 0.000000 | 0.000000
09-04-2025 20:13:00.000 | 10858866 | 108588660 | 108.5887 | 58066729 | 15606718 | 40229932 | -99857330 | 49974361 | 23123074 | 12397029 | 0.000000 | 0.000000
09-04-2025 20:12:55.000 | 10713521 | 107135210 | 107.1352 | 53552412 | 15607490 | 39682566 | -99875305 | 50023014 | 22972748 | 12318342 | 0.000000 | 0.000000
09-04-2025 20:12:50.000 | 10649559 | 106495590 | 106.4956 | 50689092 | 15615789 | 39420190 | -99886917 | 50036411 | 22824354 | 12245476 | 0.000000 | 0.000000
09-04-2025 20:12:45.000 | 10775655 | 107756550 | 107.7566 | 52056221 | 15611688 | 39899036 | -99883514 | 50011322 | 22675578 | 12174927 | 0.000000 | 0.000000
09-04-2025 20:12:40.000 | 10760691 | 107606910 | 107.6069 | 50582407 | 15611753 | 39840701 | -99889702 | 50021996 | 22525852 | 12102378 | 0.000000 | 0.000000
09-04-2025 20:12:35.000 | 10739428 | 107394280 | 107.3943 | 51299165 | 15611448 | 39764807 | -99886108 | 50025646 | 22376570 | 12031417 | 0.000000 | 0.000000
09-04-2025 20:12:30.000 | 10683601 | 106836010 | 106.836 | 52481826 | 15615328 | 39550759 | -99879562 | 50044510 | 22228092 | 11959935 | 0.000000 | 0.000000
09-04-2025 20:12:25.000 | 10747148 | 107471480 | 107.4715 | 50747900 | 15613619 | 39786697 | -99888702 | 50035965 | 22079617 | 11888159 | 0.000000 | 0.000000
09-04-2025 20:12:20.000 | 10843849 | 108438490 | 108.4385 | 49411499 | 15609176 | 40152312 | -99896347 | 50026058 | 21929809 | 11818579 | 0.000000 | 0.000000
09-04-2025 20:12:15.000 | 10828192 | 108281920 | 108.2819 | 47938296 | 15606607 | 40098757 | -99902145 | 50026093 | 21779256 | 11751426 | 0.000000 | 0.000000
09-04-2025 20:12:10.000 | 10715475 | 107154750 | 107.1548 | 47728413 | 15605346 | 39684929 | -99900948 | 50039520 | 21629492 | 11685374 | 0.000000 | 0.000000
09-04-2025 20:12:05.000 | 10514549 | 105145490 | 105.1455 | 46453442 | 15607084 | 38936335 | -99902550 | 50074997 | 21481617 | 11619663 | 0.000000 | 0.000000
09-04-2025 20:12:00.000 | 10414213 | 104142130 | 104.1421 | 42237681 | 15613020 | 38545049 | -99917854 | 50095360 | 21336174 | 11557429 | 0.000000 | 0.000000
09-04-2025 20:11:55.000 | 10447719 | 104477190 | 104.4772 | 46353271 | 15619560 | 38657947 | -99901726 | 50075302 | 21191232 | 11496996 | 0.000000 | 0.000000
09-04-2025 20:11:50.000 | 10514170 | 105141700 | 105.1417 | 52091875 | 15615279 | 38924233 | -99877495 | 50057018 | 21045881 | 11428691 | 0.000000 | 0.000000
09-04-2025 20:11:45.000 | 10594877 | 105948770 | 105.9488 | 51745327 | 15614400 | 39224375 | -99880943 | 50033497 | 20899525 | 11357852 | 0.000000 | 0.000000
09-04-2025 20:11:40.000 | 10654681 | 106546810 | 106.5468 | 57048169 | 15612456 | 39459138 | -99856964 | 50010353 | 20751730 | 11283750 | 0.000000 | 0.000000
09-04-2025 20:11:35.000 | 10602951 | 106029510 | 106.0295 | 57347461 | 15613104 | 39267371 | -99854057 | 50030964 | 20604090 | 11204767 | 0.000000 | 0.000000
09-04-2025 20:11:30.000 | 10625829 | 106258290 | 106.2583 | 55033555 | 15617243 | 39336934 | -99866150 | 50028381 | 20456820 | 11126780 | 0.000000 | 0.000000
09-04-2025 20:11:25.000 | 10720695 | 107206950 | 107.207 | 54770845 | 15617139 | 39686814 | -99869751 | 50012379 | 20308533 | 11049469 | 0.000000 | 0.000000
09-04-2025 20:11:20.000 | 10884369 | 108843690 | 108.8437 | 56901367 | 15607485 | 40320015 | -99863632 | 49983925 | 20158471 | 10972250 | 0.000000 | 0.000000
09-04-2025 20:11:15.000 | 10869635 | 108696350 | 108.6963 | 55001299 | 15606933 | 40263323 | -99872223 | 50007080 | 20007357 | 10894279 | 0.000000 | 0.000000
09-04-2025 20:11:10.000 | 10788736 | 107887360 | 107.8874 | 53706011 | 15610974 | 39951653 | -99876328 | 50023220 | 19856811 | 10818610 | 0.000000 | 0.000000
09-04-2025 20:11:05.000 | 10730309 | 107303090 | 107.3031 | 51136387 | 15611592 | 39729739 | -99886635 | 50036892 | 19707391 | 10745242 | 0.000000 | 0.000000
09-04-2025 20:11:00.000 | 10723071 | 107230710 | 107.2307 | 50459009 | 15611541 | 39702712 | -99889465 | 50039265 | 19558582 | 10675481 | 0.000000 | 0.000000
09-04-2025 20:10:55.000 | 10647942 | 106479420 | 106.4794 | 48186147 | 15610355 | 39423389 | -99897758 | 50052647 | 19409957 | 10606357 | 0.000000 | 0.000000
09-04-2025 20:10:50.000 | 10657758 | 106577580 | 106.5776 | 50355161 | 15608838 | 39467375 | -99888573 | 50044941 | 19261996 | 10538719 | 0.000000 | 0.000000
09-04-2025 20:10:45.000 | 10582830 | 105828300 | 105.8283 | 50217715 | 15607652 | 39193452 | -99887604 | 50058083 | 19114275 | 10468662 | 0.000000 | 0.000000
09-04-2025 20:10:40.000 | 10500284 | 105002840 | 105.0028 | 47480083 | 15613575 | 38868987 | -99897926 | 50071842 | 18967566 | 10400481 | 0.000000 | 0.000000
09-04-2025 20:10:35.000 | 10475781 | 104757810 | 104.7578 | 49464023 | 15616269 | 38775002 | -99888710 | 50065975 | 18821676 | 10332212 | 0.000000 | 0.000000
09-04-2025 20:10:30.000 | 10529617 | 105296170 | 105.2962 | 53164565 | 15615438 | 38982578 | -99872780 | 50059330 | 18675650 | 10261504 | 0.000000 | 0.000000
09-04-2025 20:10:25.000 | 10597719 | 105977190 | 105.9772 | 52078857 | 15615021 | 39233108 | -99879471 | 50055756 | 18529211 | 10188477 | 0.000000 | 0.000000
09-04-2025 20:10:20.000 | 10693285 | 106932850 | 106.9329 | 53017046 | 15615834 | 39585542 | -99877319 | 50033867 | 18381527 | 10115537 | 0.000000 | 0.000000
09-04-2025 20:10:15.000 | 10812266 | 108122660 | 108.1227 | 56511870 | 15613724 | 40037122 | -99863693 | 50017780 | 18232490 | 10039525 | 0.000000 | 0.000000
09-04-2025 20:10:10.000 | 10857087 | 108570870 | 108.5709 | 55071875 | 15608527 | 40213013 | -99871597 | 50012047 | 18082115 | 996212952 | 0.000000 | 0.000000
09-04-2025 20:10:05.000 | 10803323 | 108033230 | 108.0332 | 53426992 | 15607229 | 40014724 | -99877937 | 50032726 | 17931521 | 988666992 | 0.000000 | 0.000000
09-04-2025 20:10:00.000 | 10751048 | 107510480 | 107.5105 | 52398799 | 15609254 | 39814490 | -99881439 | 50034397 | 17781705 | 981410095 | 0.000000 | 0.000000
09-04-2025 20:09:55.000 | 10652920 | 106529200 | 106.5292 | 52907202 | 15609461 | 39452397 | -99876900 | 50060139 | 17632920 | 974084106 | 0.000000 | 0.000000
09-04-2025 20:09:50.000 | 10614248 | 106142480 | 106.1425 | 51587314 | 15612171 | 39300330 | -99882103 | 50076462 | 17485096 | 966788513 | 0.000000 | 0.000000
09-04-2025 20:09:45.000 | 10679563 | 106795630 | 106.7956 | 52146914 | 15611441 | 39544475 | -99881004 | 50059223 | 17337279 | 959548401 | 0.000000 | 0.000000
09-04-2025 20:09:40.000 | 10693171 | 106931710 | 106.9317 | 52102520 | 15606007 | 39608438 | -99881508 | 50039291 | 17188723 | 952312805 | 0.000000 | 0.000000
09-04-2025 20:09:35.000 | 10583032 | 105830320 | 105.8303 | 51658315 | 15607347 | 39197234 | -99881081 | 50068726 | 17040641 | 945066345 | 0.000000 | 0.000000
09-04-2025 20:09:30.000 | 10427628 | 104276280 | 104.2763 | 48545815 | 15615255 | 38598301 | -99891808 | 50088299 | 16894760 | 938183167 | 0.000000 | 0.000000
09-04-2025 20:09:25.000 | 10465621 | 104656210 | 104.6562 | 49660127 | 15618611 | 38732368 | -99887611 | 50086483 | 16749980 | 931424438 | 0.000000 | 0.000000
09-04-2025 20:09:20.000 | 10589245 | 105892450 | 105.8924 | 55035986 | 15617416 | 39201589 | -99865211 | 50045036 | 16604172 | 924319092 | 0.000000 | 0.000000
09-04-2025 20:09:15.000 | 10739587 | 107395870 | 107.3959 | 58092417 | 15614399 | 39769795 | -99854027 | 50015877 | 16456303 | 916523499 | 0.000000 | 0.000000
09-04-2025 20:09:10.000 | 10797530 | 107975300 | 107.9753 | 57291133 | 15613392 | 39984861 | -99859528 | 50019478 | 16306857 | 908437134 | 0.000000 | 0.000000
09-04-2025 20:09:05.000 | 10840048 | 108400480 | 108.4005 | 57170195 | 15608194 | 40154880 | -99861214 | 50014545 | 16156700 | 900465515 | 0.000000 | 0.000000
09-04-2025 20:09:00.000 | 10809172 | 108091720 | 108.0917 | 54616431 | 15609996 | 40031294 | -99872589 | 50027630 | 16006100 | 892716492 | 0.000000 | 0.000000
09-04-2025 20:08:55.000 | 10753453 | 107534530 | 107.5345 | 54875942 | 15608641 | 39829949 | -99870049 | 50057049 | 15856231 | 885064941 | 0.000000 | 0.000000
09-04-2025 20:08:50.000 | 10668663 | 106686630 | 106.6866 | 54366846 | 15611540 | 39507913 | -99870407 | 50073578 | 15707691 | 877537903 | 0.000000 | 0.000000
09-04-2025 20:08:45.000 | 10677899 | 106778990 | 106.779 | 53794243 | 15613035 | 39537231 | -99873337 | 50067337 | 15559493 | 870051147 | 0.000000 | 0.000000
09-04-2025 20:08:40.000 | 10719641 | 107196410 | 107.1964 | 55260566 | 15612006 | 39696680 | -99867393 | 50060764 | 15410911 | 862442688 | 0.000000 | 0.000000
09-04-2025 20:08:35.000 | 10662203 | 106622030 | 106.622 | 55747104 | 15611486 | 39486929 | -99863594 | 50067326 | 15262205 | 854696533 | 0.000000 | 0.000000
09-04-2025 20:08:30.000 | 10649159 | 106491590 | 106.4916 | 58146040 | 15612646 | 39440586 | -99851265 | 50064674 | 15113934 | 846792053 | 0.000000 | 0.000000
09-04-2025 20:08:25.000 | 10633697 | 106336970 | 106.337 | 58662007 | 15612332 | 39386411 | -99848183 | 50081806 | 14966170 | 838581360 | 0.000000 | 0.000000
09-04-2025 20:08:20.000 | 10632828 | 106328280 | 106.3283 | 60445107 | 15616445 | 39375410 | -99838806 | 50083588 | 14818563 | 830328430 | 0.000000 | 0.000000
09-04-2025 20:08:15.000 | 10710185 | 107101850 | 107.1018 | 60904028 | 15615008 | 39665908 | -99838707 | 50058128 | 14670382 | 821908569 | 0.000000 | 0.000000
09-04-2025 20:08:10.000 | 10755256 | 107552560 | 107.5526 | 62178735 | 15608296 | 39851836 | -99833305 | 50051128 | 14521284 | 813366882 | 0.000000 | 0.000000
09-04-2025 20:08:05.000 | 10641480 | 106414800 | 106.4148 | 61505024 | 15612096 | 39420710 | -99833389 | 50075504 | 14372638 | 804770691 | 0.000000 | 0.000000
09-04-2025 20:08:00.000 | 10626401 | 106264010 | 106.264 | 59619551 | 15616076 | 39351304 | -99842979 | 50090439 | 14225179 | 796257080 | 0.000000 | 0.000000
09-04-2025 20:07:55.000 | 10728589 | 107285890 | 107.2859 | 59989692 | 15613836 | 39734993 | -99844040 | 50062824 | 14076924 | 787971985 | 0.000000 | 0.000000
09-04-2025 20:07:50.000 | 10787728 | 107877280 | 107.8773 | 61437109 | 15607427 | 39972366 | -99838226 | 50054916 | 13927213 | 779521606 | 0.000000 | 0.000000
09-04-2025 20:07:45.000 | 10712991 | 107129910 | 107.1299 | 60622188 | 15609317 | 39690264 | -99840279 | 50062698 | 13777680 | 771138123 | 0.000000 | 0.000000
09-04-2025 20:07:40.000 | 10702330 | 107023300 | 107.0233 | 58022725 | 15609083 | 39645945 | -99853363 | 50076115 | 13628740 | 762940430 | 0.000000 | 0.000000
09-04-2025 20:07:35.000 | 10674945 | 106749450 | 106.7494 | 54688809 | 15610487 | 39534512 | -99869026 | 50070866 | 13480208 | 755144470 | 0.000000 | 0.000000
09-04-2025 20:07:30.000 | 10625391 | 106253910 | 106.2539 | 57598613 | 15607064 | 39365974 | -99853394 | 50079216 | 13332187 | 747262390 | 0.000000 | 0.000000
09-04-2025 20:07:25.000 | 10557369 | 105573690 | 105.5737 | 55217100 | 15611579 | 39098586 | -99863503 | 50100422 | 13184937 | 739399414 | 0.000000 | 0.000000
09-04-2025 20:07:20.000 | 10585039 | 105850390 | 105.8504 | 56895469 | 15611934 | 39203687 | -99855858 | 50090679 | 13038418 | 731671204 | 0.000000 | 0.000000
09-04-2025 20:07:15.000 | 10610875 | 106108750 | 106.1088 | 57400742 | 15611515 | 39300664 | -99854004 | 50082207 | 12891241 | 723786316 | 0.000000 | 0.000000
09-04-2025 20:07:10.000 | 10587442 | 105874420 | 105.8744 | 59154932 | 15613261 | 39213154 | -99844276 | 50081669 | 12743934 | 715803894 | 0.000000 | 0.000000
09-04-2025 20:07:05.000 | 10603244 | 106032440 | 106.0324 | 59472578 | 15614766 | 39268389 | -99843071 | 50099487 | 12596928 | 707508972 | 0.000000 | 0.000000
09-04-2025 20:07:00.000 | 10691042 | 106910420 | 106.9104 | 58502188 | 15616872 | 39585271 | -99850616 | 50074104 | 12449450 | 699433838 | 0.000000 | 0.000000
09-04-2025 20:06:55.000 | 10785380 | 107853800 | 107.8538 | 61684365 | 15609424 | 39959268 | -99836853 | 50058270 | 12300146 | 691065796 | 0.000000 | 0.000000
09-04-2025 20:06:50.000 | 10778679 | 107786790 | 107.7868 | 58168979 | 15610205 | 39924993 | -99854698 | 50061459 | 12150382 | 682772888 | 0.000000 | 0.000000
09-04-2025 20:06:45.000 | 10740201 | 107402010 | 107.402 | 60152251 | 15610402 | 39786538 | -99843529 | 50063992 | 12000854 | 674606628 | 0.000000 | 0.000000
09-04-2025 20:06:40.000 | 10688151 | 106881510 | 106.8815 | 59854126 | 15610993 | 39592168 | -99843567 | 50078293 | 11852006 | 666237488 | 0.000000 | 0.000000
09-04-2025 20:06:35.000 | 10705707 | 107057070 | 107.0571 | 59998940 | 15610212 | 39660210 | -99843323 | 50079815 | 11703366 | 657970154 | 0.000000 | 0.000000
09-04-2025 20:06:30.000 | 10732286 | 107322860 | 107.3229 | 61006602 | 15610747 | 39758279 | -99838829 | 50071041 | 11554747 | 649656860 | 0.000000 | 0.000000
09-04-2025 20:06:25.000 | 10734848 | 107348480 | 107.3485 | 58626279 | 15610808 | 39762605 | -99851204 | 50067432 | 11405836 | 641389832 | 0.000000 | 0.000000
09-04-2025 20:06:20.000 | 10671786 | 106717860 | 106.7179 | 59771621 | 15609873 | 39534456 | -99843521 | 50073021 | 11256881 | 633081970 | 0.000000 | 0.000000
09-04-2025 20:06:15.000 | 10583176 | 105831760 | 105.8318 | 60523804 | 15610581 | 39207629 | -99836876 | 50089737 | 11109022 | 624739014 | 0.000000 | 0.000000
09-04-2025 20:06:10.000 | 10540343 | 105403430 | 105.4034 | 59880747 | 15613871 | 39039319 | -99839012 | 50108234 | 10962120 | 616512512 | 0.000000 | 0.000000
09-04-2025 20:06:05.000 | 10570353 | 105703530 | 105.7035 | 59569194 | 15615611 | 39145242 | -99841583 | 50103176 | 10815722 | 608227356 | 0.000000 | 0.000000
09-04-2025 20:06:00.000 | 10636109 | 106361090 | 106.3611 | 59842354 | 15613816 | 39392800 | -99842094 | 50096508 | 10668382 | 599921692 | 0.000000 | 0.000000
09-04-2025 20:05:55.000 | 10753132 | 107531320 | 107.5313 | 59235806 | 15610967 | 39830845 | -99848618 | 50066174 | 10519939 | 591622314 | 0.000000 | 0.000000
09-04-2025 20:05:50.000 | 10771802 | 107718020 | 107.718 | 57761445 | 15610268 | 39898689 | -99856537 | 50062828 | 10370551 | 583386414 | 0.000000 | 0.000000
09-04-2025 20:05:45.000 | 10726280 | 107262800 | 107.2628 | 59792461 | 15610236 | 39735295 | -99844994 | 50069115 | 10221119 | 575240784 | 0.000000 | 0.000000
09-04-2025 20:05:40.000 | 10651195 | 106511950 | 106.5119 | 58529575 | 15609073 | 39458433 | -99849358 | 50078243 | 10072720 | 567058228 | 0.000000 | 0.000000
09-04-2025 20:05:35.000 | 10616933 | 106169330 | 106.1693 | 58247842 | 15609429 | 39330278 | -99849838 | 50087933 | 99250859 | 559032593 | 0.000000 | 0.000000
09-04-2025 20:05:30.000 | 10499834 | 104998340 | 104.9983 | 57626680 | 15614330 | 38883936 | -99849731 | 50099697 | 97783496 | 551022461 | 0.000000 | 0.000000
09-04-2025 20:05:25.000 | 10549491 | 105494910 | 105.4949 | 57969531 | 15614253 | 39068372 | -99849365 | 50084175 | 96324199 | 543070251 | 0.000000 | 0.000000
09-04-2025 20:05:20.000 | 10501280 | 105012800 | 105.0128 | 61842661 | 15614527 | 38897649 | -99827042 | 50087788 | 94860342 | 534651001 | 0.000000 | 0.000000
09-04-2025 20:05:15.000 | 10537105 | 105371050 | 105.371 | 62490176 | 15615962 | 39027686 | -99824608 | 50081589 | 93403652 | 525998108 | 0.000000 | 0.000000
09-04-2025 20:05:10.000 | 10690414 | 106904140 | 106.9041 | 61756709 | 15613328 | 39598699 | -99833557 | 50051872 | 91930391 | 517317139 | 0.000000 | 0.000000
09-04-2025 20:05:05.000 | 10774329 | 107743290 | 107.7433 | 63514707 | 15611265 | 39917712 | -99826698 | 50027729 | 90441201 | 508657349 | 0.000000 | 0.000000
09-04-2025 20:05:00.000 | 10693965 | 106939650 | 106.9397 | 62333271 | 15611965 | 39616431 | -99830559 | 50037647 | 88950342 | 499828339 | 0.000000 | 0.000000
09-04-2025 20:04:55.000 | 10646974 | 106469740 | 106.4697 | 61226646 | 15609867 | 39445923 | -99835060 | 50044945 | 87467070 | 491192352 | 0.000000 | 0.000000
09-04-2025 20:04:50.000 | 10659930 | 106599300 | 106.5993 | 58542778 | 15611455 | 39484324 | -99849541 | 50048176 | 85988193 | 482920929 | 0.000000 | 0.000000
09-04-2025 20:04:45.000 | 10609777 | 106097770 | 106.0978 | 60291904 | 15612087 | 39301069 | -99838928 | 50058197 | 84508994 | 474586517 | 0.000000 | 0.000000
09-04-2025 20:04:40.000 | 10622630 | 106226300 | 106.2263 | 61285801 | 15613476 | 39346968 | -99833984 | 50055161 | 83035977 | 466229126 | 0.000000 | 0.000000
09-04-2025 20:04:35.000 | 10640921 | 106409210 | 106.4092 | 61992964 | 15613662 | 39415969 | -99830727 | 50055241 | 81560889 | 457705139 | 0.000000 | 0.000000
09-04-2025 20:04:30.000 | 10711470 | 107114700 | 107.1147 | 61330674 | 15615416 | 39670208 | -99836487 | 50049202 | 80078706 | 449189880 | 0.000000 | 0.000000
09-04-2025 20:04:25.000 | 10744747 | 107447470 | 107.4475 | 62132505 | 15612823 | 39801440 | -99833229 | 50048588 | 78588608 | 440530212 | 0.000000 | 0.000000
09-04-2025 20:04:20.000 | 10803320 | 108033200 | 108.0332 | 61143423 | 15613664 | 40013579 | -99840225 | 50049290 | 77092759 | 431945526 | 0.000000 | 0.000000
09-04-2025 20:04:15.000 | 10824448 | 108244480 | 108.2445 | 60399976 | 15610153 | 40098992 | -99844681 | 50056263 | 75591401 | 423430939 | 0.000000 | 0.000000
09-04-2025 20:04:10.000 | 10772020 | 107720200 | 107.7202 | 59503555 | 15610730 | 39901963 | -99847778 | 50072353 | 74091636 | 415100800 | 0.000000 | 0.000000
09-04-2025 20:04:05.000 | 10787428 | 107874280 | 107.8743 | 59015532 | 15609937 | 39960093 | -99850685 | 50063049 | 72596968 | 406987976 | 0.000000 | 0.000000
09-04-2025 20:04:00.000 | 10749738 | 107497380 | 107.4974 | 60509136 | 15607543 | 39829736 | -99841949 | 50070297 | 71101528 | 398713684 | 0.000000 | 0.000000
09-04-2025 20:03:55.000 | 10691143 | 106911430 | 106.9114 | 56705342 | 15610383 | 39598640 | -99859634 | 50082565 | 69609746 | 390506042 | 0.000000 | 0.000000
09-04-2025 20:03:50.000 | 10649072 | 106490720 | 106.4907 | 56646763 | 15610054 | 39444172 | -99858818 | 50078362 | 68123447 | 382577332 | 0.000000 | 0.000000
09-04-2025 20:03:45.000 | 10637401 | 106374010 | 106.374 | 56069604 | 15607025 | 39409531 | -99861374 | 50095512 | 66643804 | 374690948 | 0.000000 | 0.000000
09-04-2025 20:03:40.000 | 10487624 | 104876240 | 104.8762 | 54980620 | 15610872 | 38843333 | -99862869 | 50103539 | 65176758 | 366896759 | 0.000000 | 0.000000
09-04-2025 20:03:35.000 | 10481415 | 104814150 | 104.8141 | 57061982 | 15610979 | 38823428 | -99852135 | 50093620 | 63719595 | 359139496 | 0.000000 | 0.000000
09-04-2025 20:03:30.000 | 10373524 | 103735240 | 103.7352 | 59093159 | 15611531 | 38427732 | -99838142 | 50098839 | 62270151 | 351046814 | 0.000000 | 0.000000
09-04-2025 20:03:25.000 | 10315395 | 103153950 | 103.1539 | 56171255 | 15620192 | 38185759 | -99852066 | 50124008 | 60835054 | 343185608 | 0.000000 | 0.000000
09-04-2025 20:03:20.000 | 10440560 | 104405600 | 104.4056 | 60753608 | 15621852 | 38653499 | -99831123 | 50080460 | 59398525 | 335224121 | 0.000000 | 0.000000
09-04-2025 20:03:15.000 | 10649756 | 106497560 | 106.4976 | 65851250 | 15618043 | 39445688 | -99809380 | 50031929 | 57936060 | 326561035 | 0.000000 | 0.000000
09-04-2025 20:03:10.000 | 10769395 | 107693950 | 107.694 | 66787490 | 15610320 | 39909148 | -99808250 | 50017574 | 56449038 | 317303986 | 0.000000 | 0.000000
09-04-2025 20:03:05.000 | 10753573 | 107535730 | 107.5357 | 65824414 | 15608115 | 39854111 | -99813179 | 50019733 | 54951138 | 308064056 | 0.000000 | 0.000000
09-04-2025 20:03:00.000 | 10668738 | 106687380 | 106.6874 | 64687764 | 15611878 | 39529111 | -99816689 | 50038834 | 53459956 | 298908783 | 0.000000 | 0.000000
09-04-2025 20:02:55.000 | 10711513 | 107115130 | 107.1151 | 60881401 | 15611272 | 39680867 | -99838867 | 50030132 | 51974521 | 290175049 | 0.000000 | 0.000000
09-04-2025 20:02:50.000 | 10704342 | 107043420 | 107.0434 | 60750103 | 15609884 | 39656931 | -99839348 | 50028351 | 50485830 | 281678650 | 0.000000 | 0.000000
09-04-2025 20:02:45.000 | 10652205 | 106522050 | 106.522 | 59463174 | 15611553 | 39457336 | -99844559 | 50032921 | 49002129 | 273364075 | 0.000000 | 0.000000
09-04-2025 20:02:40.000 | 10607606 | 106076060 | 106.0761 | 59401548 | 15610200 | 39295752 | -99843575 | 50047737 | 47525093 | 265066711 | 0.000000 | 0.000000
09-04-2025 20:02:35.000 | 10546388 | 105463880 | 105.4639 | 61459946 | 15614896 | 39063245 | -99830627 | 50065010 | 46053608 | 256779572 | 0.000000 | 0.000000
09-04-2025 20:02:30.000 | 10617640 | 106176400 | 106.1764 | 61253550 | 15617714 | 39318372 | -99834007 | 50056934 | 44585322 | 248227432 | 0.000000 | 0.000000
09-04-2025 20:02:25.000 | 10725016 | 107250160 | 107.2502 | 63045708 | 15614324 | 39726768 | -99827667 | 50031704 | 43104673 | 239619781 | 0.000000 | 0.000000
09-04-2025 20:02:20.000 | 10796611 | 107966110 | 107.9661 | 61941528 | 15609622 | 40001206 | -99835831 | 50024330 | 41610005 | 230884399 | 0.000000 | 0.000000
09-04-2025 20:02:15.000 | 10804409 | 108044090 | 108.0441 | 61513208 | 15608569 | 40031252 | -99838326 | 50022934 | 40107773 | 222287888 | 0.000000 | 0.000000
09-04-2025 20:02:10.000 | 10647274 | 106472740 | 106.4727 | 61527158 | 15610320 | 39446755 | -99833450 | 50053291 | 38613154 | 213685104 | 0.000000 | 0.000000
09-04-2025 20:02:05.000 | 10610350 | 106103500 | 106.1035 | 60050933 | 15616487 | 39292009 | -99840225 | 50079376 | 37137463 | 205190369 | 0.000000 | 0.000000
09-04-2025 20:02:00.000 | 10717074 | 107170740 | 107.1707 | 59600137 | 15615202 | 39688130 | -99845718 | 50057526 | 35659790 | 196863998 | 0.000000 | 0.000000
09-04-2025 20:01:55.000 | 10862458 | 108624580 | 108.6246 | 59606792 | 15607663 | 40243906 | -99849777 | 50033768 | 34159802 | 188609756 | 0.000000 | 0.000000
09-04-2025 20:01:50.000 | 10774852 | 107748520 | 107.7485 | 57996147 | 15606693 | 39919509 | -99855453 | 50049282 | 32653533 | 180401489 | 0.000000 | 0.000000
09-04-2025 20:01:45.000 | 10685061 | 106850610 | 106.8506 | 55589482 | 15608101 | 39580698 | -99864944 | 50067841 | 31161865 | 172484390 | 0.000000 | 0.000000
09-04-2025 20:01:40.000 | 10639116 | 106391160 | 106.3912 | 56333462 | 15609541 | 39408167 | -99860115 | 50081577 | 29682759 | 164695770 | 0.000000 | 0.000000
09-04-2025 20:01:35.000 | 10609209 | 106092090 | 106.0921 | 56227656 | 15613060 | 39288655 | -99859848 | 50091778 | 28209617 | 156919312 | 0.000000 | 0.000000
09-04-2025 20:01:30.000 | 10585295 | 105852950 | 105.853 | 55660425 | 15610340 | 39205999 | -99862038 | 50083412 | 26740037 | 149120377 | 0.000000 | 0.000000
09-04-2025 20:01:25.000 | 10509236 | 105092360 | 105.0924 | 58720723 | 15614531 | 38920383 | -99844261 | 50095192 | 25270205 | 141152817 | 0.000000 | 0.000000
09-04-2025 20:01:20.000 | 10526970 | 105269700 | 105.2697 | 58126699 | 15614081 | 38985806 | -99847900 | 50091949 | 23812478 | 133001938 | 0.000000 | 0.000000
09-04-2025 20:01:15.000 | 10641962 | 106419620 | 106.4196 | 57314175 | 15614773 | 39407136 | -99855286 | 50070797 | 22344668 | 125000191 | 0.000000 | 0.000000
09-04-2025 20:01:10.000 | 10692461 | 106924610 | 106.9246 | 57389678 | 15612054 | 39600437 | -99856270 | 50052780 | 20863760 | 117053299 | 0.000000 | 0.000000
09-04-2025 20:01:05.000 | 10704770 | 107047700 | 107.0477 | 57955103 | 15612211 | 39646575 | -99853767 | 50047646 | 19377478 | 109114037 | 0.000000 | 0.000000
09-04-2025 20:01:00.000 | 10694169 | 106941690 | 106.9417 | 59853286 | 15610185 | 39616533 | -99843742 | 50046303 | 17891160 | 101047104 | 0.000000 | 0.000000
09-04-2025 20:00:55.000 | 10606199 | 106061990 | 106.062 | 57198232 | 15612812 | 39279929 | -99854897 | 50070385 | 16410099 | 92895676 | 0.000000 | 0.000000
09-04-2025 20:00:50.000 | 10608539 | 106085390 | 106.0854 | 57411060 | 15615328 | 39282417 | -99853882 | 50072285 | 14937062 | 84935928 | 0.000000 | 0.000000
09-04-2025 20:00:45.000 | 10717144 | 107171440 | 107.1714 | 58375293 | 15611326 | 39695667 | -99851982 | 50050812 | 13457059 | 76864075 | 0.000000 | 0.000000
09-04-2025 20:00:40.000 | 10694801 | 106948010 | 106.948 | 58699033 | 15609304 | 39619194 | -99849716 | 50042137 | 11967880 | 68746681 | 0.000000 | 0.000000
09-04-2025 20:00:35.000 | 10617220 | 106172200 | 106.1722 | 59638286 | 15611592 | 39328442 | -99842613 | 50066292 | 10487075 | 60548138 | 0.000000 | 0.000000
09-04-2025 20:00:30.000 | 10556406 | 105564060 | 105.5641 | 59959429 | 15615407 | 39096028 | -99839081 | 50071056 | 901680359 | 52370899 | 0.000000 | 0.000000
09-04-2025 20:00:25.000 | 10592532 | 105925320 | 105.9253 | 62624063 | 15616600 | 39231216 | -99825691 | 50080894 | 754596191 | 43982246 | 0.000000 | 0.000000
09-04-2025 20:00:20.000 | 10683698 | 106836980 | 106.837 | 62619448 | 15621445 | 39555425 | -99828674 | 50068726 | 607074585 | 35305237 | 0.000000 | 0.000000
09-04-2025 20:00:15.000 | 10899756 | 108997560 | 108.9976 | 64671162 | 15614586 | 40374736 | -99824448 | 50033081 | 457476715 | 26400768 | 0.000000 | 0.000000
09-04-2025 20:00:10.000 | 11033210 | 110332100 | 110.3321 | 64684595 | 15607685 | 40885881 | -99828583 | 50017406 | 305298706 | 17394588 | 0.000000 | 0.000000
09-04-2025 20:00:05.000 | 10993548 | 109935480 | 109.9355 | 61196572 | 15606819 | 40733699 | -99845421 | 50033928 | 152213394 | 8549006 | 0.000000 | 0.000000
09-04-2025 20:00:00.000 | 10877254 | 108772540 | 108.7725 | 61207788 | 15606062 | 40306072 | -99842049 | 50068645 | 26622117 | 15566564 | 0.000000 | 0.000000
09-04-2025 19:59:55.000 | 10804320 | 108043200 | 108.0432 | 57462202 | 15609752 | 40019592 | -99858871 | 50091320 | 26471607 | 15484924 | 0.000000 | 0.000000
09-04-2025 19:59:50.000 | 10761998 | 107619980 | 107.62 | 55583154 | 15610656 | 39857349 | -99866890 | 50102867 | 26321756 | 15405479 | 0.000000 | 0.000000
09-04-2025 19:59:45.000 | 10751788 | 107517880 | 107.5179 | 55240034 | 15608245 | 39825315 | -99868279 | 50095669 | 26172434 | 15329110 | 0.000000 | 0.000000
09-04-2025 19:59:40.000 | 10697039 | 106970390 | 106.9704 | 53690542 | 15608382 | 39619902 | -99874275 | 50104115 | 26023227 | 15254023 | 0.000000 | 0.000000
09-04-2025 19:59:35.000 | 10622765 | 106227650 | 106.2276 | 53889277 | 15610416 | 39340605 | -99871574 | 50120586 | 25874971 | 15179750 | 0.000000 | 0.000000
09-04-2025 19:59:30.000 | 10548898 | 105488980 | 105.489 | 53069419 | 15610859 | 39065029 | -99873695 | 50134789 | 25727609 | 15105121 | 0.000000 | 0.000000
09-04-2025 19:59:25.000 | 10520339 | 105203390 | 105.2034 | 52295488 | 15614654 | 38948809 | -99876678 | 50141418 | 25581117 | 15031887 | 0.000000 | 0.000000
09-04-2025 19:59:20.000 | 10524828 | 105248280 | 105.2483 | 54853540 | 15613641 | 38972998 | -99864464 | 50129383 | 25435020 | 14957434 | 0.000000 | 0.000000
09-04-2025 19:59:15.000 | 10566839 | 105668390 | 105.6684 | 56965815 | 15615350 | 39127739 | -99855003 | 50121117 | 25288473 | 14879723 | 0.000000 | 0.000000
09-04-2025 19:59:10.000 | 10634865 | 106348650 | 106.3487 | 60187524 | 15613266 | 39390720 | -99840233 | 50112225 | 25141559 | 14799222 | 0.000000 | 0.000000
09-04-2025 19:59:05.000 | 10590502 | 105905020 | 105.905 | 61445664 | 15616228 | 39222036 | -99832108 | 50123745 | 24994268 | 14714563 | 0.000000 | 0.000000
09-04-2025 19:59:00.000 | 10676803 | 106768030 | 106.768 | 63547075 | 15617054 | 39543474 | -99823341 | 50114555 | 24846688 | 14627938 | 0.000000 | 0.000000
09-04-2025 19:58:55.000 | 10778361 | 107783610 | 107.7836 | 63117412 | 15613648 | 39925894 | -99828979 | 50099815 | 24698064 | 14539741 | 0.000000 | 0.000000
09-04-2025 19:58:50.000 | 10938198 | 109381980 | 109.382 | 61183862 | 15611906 | 40516924 | -99843925 | 50065399 | 24547438 | 14454994 | 0.000000 | 0.000000
09-04-2025 19:58:45.000 | 10867255 | 108672550 | 108.6726 | 61068779 | 15606480 | 40268035 | -99842476 | 50091862 | 24395682 | 14369816 | 0.000000 | 0.000000
09-04-2025 19:58:40.000 | 10738301 | 107383010 | 107.383 | 57275313 | 15613790 | 39765444 | -99858055 | 50131069 | 24245809 | 14287465 | 0.000000 | 0.000000
09-04-2025 19:58:35.000 | 10792793 | 107927930 | 107.9279 | 54811792 | 15612731 | 39964866 | -99871292 | 50114460 | 24096516 | 14210249 | 0.000000 | 0.000000
09-04-2025 19:58:30.000 | 10856720 | 108567200 | 108.5672 | 55026318 | 15607105 | 40215584 | -99871803 | 50107773 | 23945877 | 14133418 | 0.000000 | 0.000000
09-04-2025 19:58:25.000 | 10769066 | 107690660 | 107.6907 | 54343677 | 15605750 | 39893757 | -99872917 | 50132004 | 23795457 | 14056874 | 0.000000 | 0.000000
09-04-2025 19:58:20.000 | 10633949 | 106339490 | 106.3395 | 51548076 | 15609690 | 39379937 | -99882713 | 50155018 | 23646674 | 13982999 | 0.000000 | 0.000000
09-04-2025 19:58:15.000 | 10591722 | 105917220 | 105.9172 | 52705674 | 15609859 | 39225056 | -99876419 | 50161018 | 23499010 | 13911331 | 0.000000 | 0.000000
09-04-2025 19:58:10.000 | 10509506 | 105095060 | 105.0951 | 53154614 | 15614156 | 38912258 | -99872337 | 50171551 | 23352438 | 13838076 | 0.000000 | 0.000000
09-04-2025 19:58:05.000 | 10492243 | 104922430 | 104.9224 | 53560225 | 15619236 | 38836267 | -99869965 | 50168522 | 23206678 | 13764095 | 0.000000 | 0.000000
09-04-2025 19:58:00.000 | 10549992 | 105499920 | 105.4999 | 57501997 | 15617186 | 39062446 | -99851791 | 50155777 | 23060650 | 13685767 | 0.000000 | 0.000000
09-04-2025 19:57:55.000 | 10688754 | 106887540 | 106.8875 | 61434307 | 15618099 | 39579834 | -99835236 | 50129154 | 22913252 | 13603733 | 0.000000 | 0.000000
09-04-2025 19:57:50.000 | 10852447 | 108524470 | 108.5245 | 63831743 | 15612909 | 40202722 | -99827469 | 50106125 | 22763922 | 13517686 | 0.000000 | 0.000000
09-04-2025 19:57:45.000 | 10883031 | 108830310 | 108.8303 | 62855000 | 15608055 | 40326414 | -99833633 | 50103283 | 22612996 | 13428744 | 0.000000 | 0.000000
09-04-2025 19:57:40.000 | 10862880 | 108628800 | 108.6288 | 60366699 | 15607796 | 40246787 | -99845947 | 50122154 | 22461900 | 13342911 | 0.000000 | 0.000000
09-04-2025 19:57:35.000 | 10762172 | 107621720 | 107.6217 | 57683052 | 15609160 | 39866143 | -99856674 | 50144070 | 22311813 | 13260560 | 0.000000 | 0.000000
09-04-2025 19:57:30.000 | 10677604 | 106776040 | 106.776 | 57958301 | 15609313 | 39553782 | -99853004 | 50155312 | 22162898 | 13179313 | 0.000000 | 0.000000
09-04-2025 19:57:25.000 | 10623033 | 106230330 | 106.2303 | 56666968 | 15613129 | 39340310 | -99858025 | 50176250 | 22014865 | 13099089 | 0.000000 | 0.000000
09-04-2025 19:57:20.000 | 10644474 | 106444740 | 106.4447 | 54890972 | 15613741 | 39414675 | -99867302 | 50174786 | 21867404 | 13021815 | 0.000000 | 0.000000
09-04-2025 19:57:15.000 | 10668206 | 106682060 | 106.6821 | 54877129 | 15611133 | 39508660 | -99867958 | 50158588 | 21719434 | 12946199 | 0.000000 | 0.000000
09-04-2025 19:57:10.000 | 10622673 | 106226730 | 106.2267 | 54448096 | 15609734 | 39343047 | -99868896 | 50165127 | 21571465 | 12870150 | 0.000000 | 0.000000
09-04-2025 19:57:05.000 | 10577301 | 105773010 | 105.773 | 52292813 | 15610821 | 39168853 | -99878014 | 50176163 | 21424016 | 12795294 | 0.000000 | 0.000000
09-04-2025 19:57:00.000 | 10554266 | 105542660 | 105.5427 | 52735503 | 15610699 | 39084905 | -99875404 | 50179539 | 21277127 | 12721646 | 0.000000 | 0.000000
09-04-2025 19:56:55.000 | 10519230 | 105192300 | 105.1923 | 54700137 | 15613204 | 38953320 | -99865074 | 50176571 | 21130656 | 12647222 | 0.000000 | 0.000000
09-04-2025 19:56:50.000 | 10503115 | 105031150 | 105.0311 | 57436396 | 15617381 | 38888848 | -99850815 | 50176842 | 20984777 | 12569968 | 0.000000 | 0.000000
09-04-2025 19:56:45.000 | 10560877 | 105608770 | 105.6088 | 59324419 | 15618082 | 39103425 | -99842598 | 50162613 | 20838809 | 12488955 | 0.000000 | 0.000000
09-04-2025 19:56:40.000 | 10663827 | 106638270 | 106.6383 | 61449155 | 15614316 | 39497366 | -99834389 | 50142582 | 20691555 | 12404789 | 0.000000 | 0.000000
09-04-2025 19:56:35.000 | 10704896 | 107048960 | 107.049 | 61538477 | 15613173 | 39652419 | -99835175 | 50128468 | 20543221 | 12318296 | 0.000000 | 0.000000
09-04-2025 19:56:30.000 | 10736397 | 107363970 | 107.364 | 62231563 | 15610309 | 39777673 | -99832436 | 50115917 | 20393953 | 12232964 | 0.000000 | 0.000000
09-04-2025 19:56:25.000 | 10745914 | 107459140 | 107.4591 | 61087412 | 15607853 | 39818130 | -99838814 | 50124172 | 20244883 | 12147769 | 0.000000 | 0.000000
09-04-2025 19:56:20.000 | 10610167 | 106101670 | 106.1017 | 61633066 | 15612799 | 39303960 | -99831711 | 50152298 | 20096527 | 12062722 | 0.000000 | 0.000000
09-04-2025 19:56:15.000 | 10634919 | 106349190 | 106.3492 | 63837217 | 15614235 | 39396255 | -99820328 | 50147133 | 19949004 | 11977136 | 0.000000 | 0.000000
09-04-2025 19:56:10.000 | 10675585 | 106755850 | 106.7558 | 62952437 | 15613321 | 39547251 | -99826584 | 50143257 | 19800893 | 11889559 | 0.000000 | 0.000000
09-04-2025 19:56:05.000 | 10743366 | 107433660 | 107.4337 | 64909785 | 15612229 | 39804063 | -99817978 | 50132847 | 19652414 | 11801803 | 0.000000 | 0.000000
09-04-2025 19:56:00.000 | 10743743 | 107437430 | 107.4374 | 64529551 | 15612430 | 39804045 | -99820114 | 50127342 | 19503354 | 11712600 | 0.000000 | 0.000000
09-04-2025 19:55:55.000 | 10766191 | 107661910 | 107.6619 | 62717729 | 15609901 | 39889309 | -99830750 | 50124279 | 19353953 | 11623372 | 0.000000 | 0.000000
09-04-2025 19:55:50.000 | 10728859 | 107288590 | 107.2886 | 61551655 | 15610207 | 39748208 | -99835838 | 50120529 | 19204609 | 11537095 | 0.000000 | 0.000000
09-04-2025 19:55:45.000 | 10666385 | 106663850 | 106.6638 | 61521318 | 15611923 | 39514072 | -99834076 | 50139431 | 19055670 | 11449823 | 0.000000 | 0.000000
09-04-2025 19:55:40.000 | 10654258 | 106542580 | 106.5426 | 60212280 | 15609376 | 39472144 | -99840683 | 50140110 | 18907555 | 11365092 | 0.000000 | 0.000000
09-04-2025 19:55:35.000 | 10636720 | 106367200 | 106.3672 | 59106558 | 15609575 | 39404702 | -99845963 | 50139820 | 18759832 | 11282163 | 0.000000 | 0.000000
09-04-2025 19:55:30.000 | 10539998 | 105399980 | 105.4 | 59617549 | 15611370 | 39043999 | -99840416 | 50148037 | 18612449 | 11199751 | 0.000000 | 0.000000
09-04-2025 19:55:25.000 | 10478045 | 104780450 | 104.7805 | 59436938 | 15613990 | 38808276 | -99839500 | 50154091 | 18466531 | 11116840 | 0.000000 | 0.000000
09-04-2025 19:55:20.000 | 10511294 | 105112940 | 105.1129 | 62331279 | 15616427 | 38930994 | -99824638 | 50142914 | 18321111 | 11033605 | 0.000000 | 0.000000
09-04-2025 19:55:15.000 | 10530521 | 105305210 | 105.3052 | 62313311 | 15615500 | 39004355 | -99825378 | 50145741 | 18175146 | 10946382 | 0.000000 | 0.000000
09-04-2025 19:55:10.000 | 10610837 | 106108370 | 106.1084 | 65404683 | 15615442 | 39307878 | -99810570 | 50124851 | 18028402 | 10857919 | 0.000000 | 0.000000
09-04-2025 19:55:05.000 | 10704549 | 107045490 | 107.0455 | 65110679 | 15615878 | 39652085 | -99815529 | 50115993 | 17880684 | 10766895 | 0.000000 | 0.000000
09-04-2025 19:55:00.000 | 10796034 | 107960340 | 107.9603 | 66516719 | 15610216 | 40007490 | -99810738 | 50097504 | 17731559 | 10676272 | 0.000000 | 0.000000
09-04-2025 19:54:55.000 | 10810170 | 108101700 | 108.1017 | 63673765 | 15608484 | 40058228 | -99826981 | 50106407 | 17581615 | 10585571 | 0.000000 | 0.000000
09-04-2025 19:54:50.000 | 10711768 | 107117680 | 107.1177 | 62454307 | 15610243 | 39686909 | -99830460 | 50125553 | 17432141 | 10497550 | 0.000000 | 0.000000
09-04-2025 19:54:45.000 | 10707691 | 107076910 | 107.0769 | 61003721 | 15613617 | 39660354 | -99838104 | 50139973 | 17283383 | 10411354 | 0.000000 | 0.000000
09-04-2025 19:54:40.000 | 10847179 | 108471790 | 108.4718 | 60424814 | 15611044 | 40180593 | -99845207 | 50110226 | 17134221 | 10327695 | 0.000000 | 0.000000
09-04-2025 19:54:35.000 | 10790021 | 107900210 | 107.9002 | 64247026 | 15608103 | 39985254 | -99823204 | 50116180 | 16983766 | 10241183 | 0.000000 | 0.000000
09-04-2025 19:54:30.000 | 10675943 | 106759430 | 106.7594 | 62740986 | 15608158 | 39560886 | -99827759 | 50143440 | 16834795 | 10153196 | 0.000000 | 0.000000
09-04-2025 19:54:25.000 | 10571980 | 105719800 | 105.7198 | 58803164 | 15610744 | 39162415 | -99845673 | 50161385 | 16687322 | 10067821 | 0.000000 | 0.000000
09-04-2025 19:54:20.000 | 10559274 | 105592740 | 105.5927 | 58605757 | 15612263 | 39110649 | -99846336 | 50171291 | 16540547 | 998548767 | 0.000000 | 0.000000
09-04-2025 19:54:15.000 | 10611650 | 106116500 | 106.1165 | 58808203 | 15612040 | 39305005 | -99846794 | 50150372 | 16393508 | 990487427 | 0.000000 | 0.000000
09-04-2025 19:54:10.000 | 10581441 | 105814410 | 105.8144 | 58638701 | 15612657 | 39191555 | -99846802 | 50154034 | 16245979 | 982263611 | 0.000000 | 0.000000
09-04-2025 19:54:05.000 | 10554796 | 105547960 | 105.548 | 59693701 | 15613607 | 39093064 | -99840454 | 50153652 | 16099150 | 974066895 | 0.000000 | 0.000000
09-04-2025 19:54:00.000 | 10617051 | 106170510 | 106.1705 | 58456982 | 15613489 | 39321035 | -99848763 | 50133087 | 15952519 | 965848877 | 0.000000 | 0.000000
09-04-2025 19:53:55.000 | 10639149 | 106391490 | 106.3915 | 61865635 | 15611074 | 39415493 | -99831360 | 50116978 | 15804913 | 957477539 | 0.000000 | 0.000000
09-04-2025 19:53:50.000 | 10586820 | 105868200 | 105.8682 | 63386348 | 15613576 | 39219211 | -99821243 | 50136597 | 15657534 | 948816223 | 0.000000 | 0.000000
09-04-2025 19:53:45.000 | 10584837 | 105848370 | 105.8484 | 62382603 | 15614360 | 39208108 | -99826782 | 50136024 | 15510686 | 940070557 | 0.000000 | 0.000000
09-04-2025 19:53:40.000 | 10619862 | 106198620 | 106.1986 | 63895581 | 15616701 | 39334568 | -99819489 | 50131836 | 15363396 | 931365479 | 0.000000 | 0.000000
09-04-2025 19:53:35.000 | 10677820 | 106778200 | 106.7782 | 64975977 | 15616820 | 39550413 | -99815369 | 50131908 | 15215563 | 922431335 | 0.000000 | 0.000000
09-04-2025 19:53:30.000 | 10792152 | 107921520 | 107.9215 | 63374092 | 15610498 | 39985483 | -99828026 | 50103527 | 15066613 | 913556519 | 0.000000 | 0.000000
09-04-2025 19:53:25.000 | 10865944 | 108659440 | 108.6594 | 63050195 | 15606848 | 40266213 | -99832077 | 50091358 | 14915867 | 904826416 | 0.000000 | 0.000000
09-04-2025 19:53:20.000 | 10722548 | 107225480 | 107.2255 | 58553320 | 15606411 | 39728347 | -99851234 | 50130947 | 14765463 | 896201965 | 0.000000 | 0.000000
09-04-2025 19:53:15.000 | 10635256 | 106352560 | 106.3526 | 56760923 | 15609471 | 39395273 | -99857880 | 50140175 | 14616882 | 888204529 | 0.000000 | 0.000000
09-04-2025 19:53:10.000 | 10545233 | 105452330 | 105.4523 | 57937339 | 15609169 | 39065127 | -99849411 | 50162788 | 14469415 | 880215942 | 0.000000 | 0.000000
09-04-2025 19:53:05.000 | 10519719 | 105197190 | 105.1972 | 55858911 | 15615751 | 38950525 | -99859322 | 50168491 | 14323395 | 872276794 | 0.000000 | 0.000000
09-04-2025 19:53:00.000 | 10601980 | 106019800 | 106.0198 | 58025083 | 15614435 | 39263022 | -99850563 | 50143127 | 14177117 | 864474915 | 0.000000 | 0.000000
09-04-2025 19:52:55.000 | 10630051 | 106300510 | 106.3005 | 59668911 | 15613344 | 39371899 | -99842827 | 50136211 | 14029729 | 856246704 | 0.000000 | 0.000000
09-04-2025 19:52:50.000 | 10676792 | 106767920 | 106.7679 | 61064746 | 15615700 | 39540923 | -99836845 | 50125813 | 13881773 | 847894226 | 0.000000 | 0.000000
09-04-2025 19:52:45.000 | 10702956 | 107029560 | 107.0296 | 60954312 | 15609469 | 39653201 | -99838226 | 50115482 | 13733210 | 839234070 | 0.000000 | 0.000000
09-04-2025 19:52:40.000 | 10707346 | 107073460 | 107.0735 | 58852227 | 15606759 | 39671831 | -99849289 | 50104931 | 13584190 | 830995728 | 0.000000 | 0.000000
09-04-2025 19:52:35.000 | 10623762 | 106237620 | 106.2376 | 58997402 | 15606837 | 39363748 | -99846161 | 50120571 | 13435875 | 822792236 | 0.000000 | 0.000000
09-04-2025 19:52:30.000 | 10452248 | 104522480 | 104.5225 | 58711968 | 15611587 | 38717649 | -99842613 | 50145325 | 13289044 | 814637756 | 0.000000 | 0.000000
09-04-2025 19:52:25.000 | 10440152 | 104401520 | 104.4015 | 58053496 | 15617431 | 38657146 | -99845757 | 50158531 | 13144073 | 806525085 | 0.000000 | 0.000000
09-04-2025 19:52:20.000 | 10551023 | 105510230 | 105.5102 | 60697622 | 15618828 | 39068328 | -99834938 | 50132549 | 12998935 | 798389709 | 0.000000 | 0.000000
09-04-2025 19:52:15.000 | 10711243 | 107112430 | 107.1124 | 64775366 | 15616987 | 39672927 | -99817642 | 50090950 | 12851636 | 789811096 | 0.000000 | 0.000000
09-04-2025 19:52:10.000 | 10811511 | 108115110 | 108.1151 | 66980215 | 15611720 | 40062300 | -99808647 | 50081734 | 12702530 | 780790283 | 0.000000 | 0.000000
09-04-2025 19:52:05.000 | 10821747 | 108217470 | 108.2175 | 66405771 | 15611891 | 40097671 | -99812256 | 50087460 | 12552492 | 771651428 | 0.000000 | 0.000000
09-04-2025 19:52:00.000 | 10874004 | 108740040 | 108.74 | 63760767 | 15610554 | 40287900 | -99828537 | 50100311 | 12402019 | 762531067 | 0.000000 | 0.000000
09-04-2025 19:51:55.000 | 10911846 | 109118460 | 109.1185 | 61779272 | 15604184 | 40439907 | -99840111 | 50081623 | 12250506 | 753802795 | 0.000000 | 0.000000
09-04-2025 19:51:50.000 | 10806968 | 108069680 | 108.0697 | 58592764 | 15603520 | 40047593 | -99853348 | 50108376 | 12099432 | 745469360 | 0.000000 | 0.000000
09-04-2025 19:51:45.000 | 10611302 | 106113020 | 106.113 | 56321230 | 15608311 | 39308579 | -99859444 | 50151325 | 11950389 | 737511292 | 0.000000 | 0.000000
09-04-2025 19:51:40.000 | 10494735 | 104947350 | 104.9474 | 55926831 | 15613283 | 38864392 | -99858307 | 50163502 | 11803842 | 729828247 | 0.000000 | 0.000000
09-04-2025 19:51:35.000 | 10467001 | 104670010 | 104.67 | 57393955 | 15611521 | 38769658 | -99850006 | 50159576 | 11658392 | 721990051 | 0.000000 | 0.000000
09-04-2025 19:51:30.000 | 10448189 | 104481890 | 104.4819 | 58884390 | 15612792 | 38700164 | -99841560 | 50158482 | 11513472 | 714067627 | 0.000000 | 0.000000
09-04-2025 19:51:25.000 | 10453537 | 104535370 | 104.5354 | 58208311 | 15615466 | 38711807 | -99845329 | 50132355 | 11368426 | 705993652 | 0.000000 | 0.000000
09-04-2025 19:51:20.000 | 10494897 | 104948970 | 104.949 | 63575713 | 15612689 | 38882729 | -99817017 | 50107632 | 11222421 | 697596802 | 0.000000 | 0.000000
09-04-2025 19:51:15.000 | 10451990 | 104519900 | 104.5199 | 61452168 | 15616800 | 38709919 | -99827606 | 50114445 | 11076886 | 688839722 | 0.000000 | 0.000000
09-04-2025 19:51:10.000 | 10536625 | 105366250 | 105.3662 | 63770620 | 15616552 | 39027896 | -99817352 | 50092178 | 10931194 | 680241211 | 0.000000 | 0.000000
09-04-2025 19:51:05.000 | 10646584 | 106465840 | 106.4658 | 65207051 | 15613447 | 39444258 | -99812965 | 50065353 | 10784141 | 671373901 | 0.000000 | 0.000000
09-04-2025 19:51:00.000 | 10730303 | 107303030 | 107.303 | 65568496 | 15611710 | 39758506 | -99813828 | 50050205 | 10635806 | 662326599 | 0.000000 | 0.000000
09-04-2025 19:50:55.000 | 10695410 | 106954100 | 106.9541 | 67646426 | 15612385 | 39632878 | -99800583 | 50056786 | 10486861 | 653022034 | 0.000000 | 0.000000
09-04-2025 19:50:50.000 | 10690557 | 106905570 | 106.9056 | 67145542 | 15614277 | 39609089 | -99803337 | 50058022 | 10338377 | 643661499 | 0.000000 | 0.000000
09-04-2025 19:50:45.000 | 10783573 | 107835730 | 107.8357 | 67084087 | 15611663 | 39958799 | -99807060 | 50044697 | 10189543 | 634364929 | 0.000000 | 0.000000
09-04-2025 19:50:40.000 | 10827087 | 108270870 | 108.2709 | 63296860 | 15607881 | 40120740 | -99829552 | 50054852 | 10039505 | 625240540 | 0.000000 | 0.000000
09-04-2025 19:50:35.000 | 10777192 | 107771920 | 107.7719 | 59753013 | 15610784 | 39921406 | -99846649 | 50071510 | 98895859 | 616646118 | 0.000000 | 0.000000
09-04-2025 19:50:30.000 | 10774032 | 107740320 | 107.7403 | 59163745 | 15608534 | 39914783 | -99849564 | 50078999 | 97399238 | 608353027 | 0.000000 | 0.000000
09-04-2025 19:50:25.000 | 10730751 | 107307510 | 107.3075 | 60037593 | 15606094 | 39762876 | -99843849 | 50089119 | 95902969 | 600081787 | 0.000000 | 0.000000
09-04-2025 19:50:20.000 | 10568511 | 105685110 | 105.6851 | 55119609 | 15609829 | 39143943 | -99864273 | 50118401 | 94421084 | 591881348 | 0.000000 | 0.000000
09-04-2025 19:50:15.000 | 10520641 | 105206410 | 105.2064 | 55739810 | 15613978 | 38958281 | -99859947 | 50119659 | 92954609 | 584157654 | 0.000000 | 0.000000
09-04-2025 19:50:10.000 | 10529813 | 105298130 | 105.2981 | 58789795 | 15614732 | 38996465 | -99844505 | 50115376 | 91495830 | 576233826 | 0.000000 | 0.000000
09-04-2025 19:50:05.000 | 10530006 | 105300060 | 105.3001 | 60168960 | 15617593 | 38992551 | -99837151 | 50106716 | 90036172 | 567925537 | 0.000000 | 0.000000
09-04-2025 19:50:00.000 | 10661644 | 106616440 | 106.6164 | 63463828 | 15613226 | 39496580 | -99823303 | 50089115 | 88569121 | 559351868 | 0.000000 | 0.000000
09-04-2025 19:49:55.000 | 10688853 | 106888530 | 106.8885 | 63969536 | 15613456 | 39597517 | -99821396 | 50079662 | 87088955 | 550492004 | 0.000000 | 0.000000
09-04-2025 19:49:50.000 | 10731658 | 107316580 | 107.3166 | 64172495 | 15609225 | 39767305 | -99821693 | 50051403 | 85601748 | 541616821 | 0.000000 | 0.000000
09-04-2025 19:49:45.000 | 10716451 | 107164510 | 107.1645 | 61027666 | 15609174 | 39703926 | -99838242 | 50060062 | 84109775 | 532879089 | 0.000000 | 0.000000
09-04-2025 19:49:40.000 | 10629202 | 106292020 | 106.292 | 61269722 | 15609127 | 39382502 | -99834282 | 50072990 | 82625088 | 524405823 | 0.000000 | 0.000000
09-04-2025 19:49:35.000 | 10574765 | 105747650 | 105.7476 | 63432432 | 15608796 | 39187112 | -99820572 | 50080303 | 81150376 | 515772034 | 0.000000 | 0.000000
09-04-2025 19:49:30.000 | 10470932 | 104709320 | 104.7093 | 62329526 | 15611823 | 38793936 | -99823303 | 50095837 | 79687905 | 507074799 | 0.000000 | 0.000000
09-04-2025 19:49:25.000 | 10475584 | 104755840 | 104.7558 | 60642998 | 15616704 | 38795042 | -99832855 | 50084297 | 78233633 | 498660828 | 0.000000 | 0.000000
09-04-2025 19:49:20.000 | 10609702 | 106097020 | 106.097 | 62115278 | 15612089 | 39304885 | -99829056 | 50060261 | 76771167 | 490211548 | 0.000000 | 0.000000
09-04-2025 19:49:15.000 | 10600077 | 106000770 | 106.0008 | 63802275 | 15613487 | 39270217 | -99819344 | 50058456 | 75299736 | 481503571 | 0.000000 | 0.000000
09-04-2025 19:49:10.000 | 10567725 | 105677250 | 105.6773 | 64267261 | 15615026 | 39147253 | -99815590 | 50066353 | 73829771 | 472652863 | 0.000000 | 0.000000
09-04-2025 19:49:05.000 | 10650130 | 106501300 | 106.5013 | 64329155 | 15615080 | 39451555 | -99818077 | 50054771 | 72357378 | 463777740 | 0.000000 | 0.000000
09-04-2025 19:49:00.000 | 10698701 | 106987010 | 106.987 | 67499248 | 15611120 | 39648267 | -99801567 | 50042801 | 70874312 | 454703094 | 0.000000 | 0.000000
09-04-2025 19:48:55.000 | 10685066 | 106850660 | 106.8507 | 65250127 | 15609183 | 39597422 | -99814064 | 50040649 | 69390610 | 445431549 | 0.000000 | 0.000000
09-04-2025 19:48:50.000 | 10649020 | 106490200 | 106.4902 | 65234766 | 15608764 | 39465227 | -99812897 | 50039070 | 67907686 | 436439667 | 0.000000 | 0.000000
09-04-2025 19:48:45.000 | 10549843 | 105498430 | 105.4984 | 65361182 | 15611319 | 39092983 | -99808632 | 50057144 | 66433687 | 427259125 | 0.000000 | 0.000000
09-04-2025 19:48:40.000 | 10534438 | 105344380 | 105.3444 | 64290757 | 15613807 | 39027747 | -99814293 | 50061852 | 64970054 | 418264099 | 0.000000 | 0.000000
09-04-2025 19:48:35.000 | 10577338 | 105773380 | 105.7734 | 64066006 | 15609402 | 39196382 | -99817070 | 50048031 | 63505972 | 409351868 | 0.000000 | 0.000000
09-04-2025 19:48:30.000 | 10523481 | 105234810 | 105.2348 | 64341626 | 15610045 | 38996672 | -99813614 | 50038330 | 62037837 | 400487701 | 0.000000 | 0.000000
09-04-2025 19:48:25.000 | 10434833 | 104348330 | 104.3483 | 63290977 | 15611894 | 38662593 | -99816566 | 50048195 | 60581289 | 391528595 | 0.000000 | 0.000000
09-04-2025 19:48:20.000 | 10396815 | 103968150 | 103.9681 | 66115225 | 15614496 | 38522058 | -99798416 | 50049370 | 59132549 | 382566833 | 0.000000 | 0.000000
09-04-2025 19:48:15.000 | 10417163 | 104171630 | 104.1716 | 65410396 | 15616362 | 38591072 | -99803444 | 50040928 | 57687798 | 373427856 | 0.000000 | 0.000000
09-04-2025 19:48:10.000 | 10500683 | 105006830 | 105.0068 | 70459927 | 15618109 | 38906924 | -99775635 | 50010303 | 56237305 | 364141418 | 0.000000 | 0.000000
09-04-2025 19:48:05.000 | 10612278 | 106122780 | 106.1228 | 71973174 | 15615623 | 39328318 | -99770805 | 49995255 | 54772412 | 354190277 | 0.000000 | 0.000000
09-04-2025 19:48:00.000 | 10706024 | 107060240 | 107.0602 | 73420610 | 15614569 | 39680410 | -99765671 | 49968391 | 53292471 | 344136780 | 0.000000 | 0.000000
09-04-2025 19:47:55.000 | 10791948 | 107919480 | 107.9195 | 73998281 | 15611208 | 40007373 | -99765747 | 49967190 | 51800420 | 333799438 | 0.000000 | 0.000000
09-04-2025 19:47:50.000 | 10754862 | 107548620 | 107.5486 | 71455415 | 15609823 | 39868044 | -99780014 | 49980129 | 50303008 | 323596924 | 0.000000 | 0.000000
09-04-2025 19:47:45.000 | 10709516 | 107095160 | 107.0952 | 71377451 | 15612678 | 39693105 | -99778633 | 49988682 | 48812021 | 313757751 | 0.000000 | 0.000000
09-04-2025 19:47:40.000 | 10711059 | 107110590 | 107.1106 | 69633247 | 15613971 | 39691111 | -99789345 | 49992744 | 47325444 | 303940033 | 0.000000 | 0.000000
09-04-2025 19:47:35.000 | 10767454 | 107674540 | 107.6745 | 68851206 | 15610645 | 39906492 | -99796181 | 49986767 | 45832988 | 294261292 | 0.000000 | 0.000000
09-04-2025 19:47:30.000 | 10753425 | 107534250 | 107.5343 | 69346377 | 15611298 | 39853616 | -99792709 | 49988636 | 44338179 | 284696167 | 0.000000 | 0.000000
09-04-2025 19:47:25.000 | 10757455 | 107574550 | 107.5746 | 68503477 | 15611645 | 39865603 | -99797859 | 49987507 | 42844800 | 275133759 | 0.000000 | 0.000000
09-04-2025 19:47:20.000 | 10776343 | 107763430 | 107.7634 | 68528931 | 15609769 | 39940115 | -99798416 | 49983006 | 41350591 | 265666870 | 0.000000 | 0.000000
09-04-2025 19:47:15.000 | 10727663 | 107276630 | 107.2766 | 67497759 | 15607355 | 39764622 | -99802643 | 49987637 | 39856331 | 256149414 | 0.000000 | 0.000000
09-04-2025 19:47:10.000 | 10720884 | 107208840 | 107.2088 | 67041748 | 15606743 | 39739988 | -99805046 | 49984539 | 38365000 | 246955109 | 0.000000 | 0.000000
09-04-2025 19:47:05.000 | 10607250 | 106072500 | 106.0725 | 67616982 | 15604682 | 39326790 | -99797440 | 50006340 | 36882053 | 237698975 | 0.000000 | 0.000000
09-04-2025 19:47:00.000 | 10422296 | 104222960 | 104.223 | 65029199 | 15612270 | 38619590 | -99805916 | 50037338 | 35422585 | 228438263 | 0.000000 | 0.000000
09-04-2025 19:46:55.000 | 10438649 | 104386490 | 104.3865 | 65768960 | 15616479 | 38670632 | -99802109 | 50021324 | 33976611 | 219547989 | 0.000000 | 0.000000
09-04-2025 19:46:50.000 | 10475238 | 104752380 | 104.7524 | 68142002 | 15619922 | 38802773 | -99789093 | 50009651 | 32524556 | 210345200 | 0.000000 | 0.000000
09-04-2025 19:46:45.000 | 10582271 | 105822710 | 105.8227 | 70819932 | 15618925 | 39206436 | -99776817 | 49999710 | 31063735 | 200628876 | 0.000000 | 0.000000
09-04-2025 19:46:40.000 | 10756737 | 107567370 | 107.5674 | 71919736 | 15618157 | 39854763 | -99777229 | 49963821 | 29585386 | 190808212 | 0.000000 | 0.000000
09-04-2025 19:46:35.000 | 10922041 | 109220410 | 109.2204 | 71751812 | 15608561 | 40488657 | -99784904 | 49940441 | 28080403 | 180641403 | 0.000000 | 0.000000
09-04-2025 19:46:30.000 | 10945373 | 109453730 | 109.4537 | 70555034 | 15604821 | 40581704 | -99792885 | 49929970 | 26560371 | 170673630 | 0.000000 | 0.000000
09-04-2025 19:46:25.000 | 10806516 | 108065160 | 108.0652 | 69131616 | 15602635 | 40071240 | -99796005 | 49967018 | 25042849 | 160887787 | 0.000000 | 0.000000
09-04-2025 19:46:20.000 | 10626435 | 106264350 | 106.2643 | 65236680 | 15608910 | 39381545 | -99812088 | 50009010 | 23553140 | 151548721 | 0.000000 | 0.000000
09-04-2025 19:46:15.000 | 10554851 | 105548510 | 105.5485 | 64251675 | 15611877 | 39107405 | -99815231 | 50026680 | 22080471 | 142519287 | 0.000000 | 0.000000
09-04-2025 19:46:10.000 | 10525629 | 105256290 | 105.2563 | 64627471 | 15616133 | 38990212 | -99812035 | 50023796 | 20617771 | 133562363 | 0.000000 | 0.000000
09-04-2025 19:46:05.000 | 10589845 | 105898450 | 105.8984 | 64314043 | 15614197 | 39230911 | -99816093 | 50011967 | 19153461 | 124571419 | 0.000000 | 0.000000
09-04-2025 19:46:00.000 | 10653642 | 106536420 | 106.5364 | 65012095 | 15610035 | 39478408 | -99814323 | 49991051 | 17676829 | 115600906 | 0.000000 | 0.000000
09-04-2025 19:45:55.000 | 10629257 | 106292570 | 106.2926 | 66568027 | 15608490 | 39396357 | -99804466 | 49986137 | 16196134 | 106520447 | 0.000000 | 0.000000
09-04-2025 19:45:50.000 | 10527434 | 105274340 | 105.2743 | 66485986 | 15609373 | 39017595 | -99801170 | 50004639 | 14722815 | 97243668 | 0.000000 | 0.000000
09-04-2025 19:45:45.000 | 10492387 | 104923870 | 104.9239 | 67335269 | 15615468 | 38875039 | -99794708 | 50006027 | 13263555 | 87907204 | 0.000000 | 0.000000
09-04-2025 19:45:40.000 | 10469808 | 104698080 | 104.6981 | 68330913 | 15614919 | 38795437 | -99787704 | 50006207 | 11809448 | 78411705 | 0.000000 | 0.000000
09-04-2025 19:45:35.000 | 10586983 | 105869830 | 105.8698 | 68808818 | 15616704 | 39224963 | -99789459 | 49982117 | 10350684 | 68943970 | 0.000000 | 0.000000
09-04-2025 19:45:30.000 | 10686641 | 106866410 | 106.8664 | 71149614 | 15610556 | 39613354 | -99779099 | 49954826 | 887338806 | 59220417 | 0.000000 | 0.000000
09-04-2025 19:45:25.000 | 10624995 | 106249950 | 106.2499 | 71406147 | 15609546 | 39389312 | -99774933 | 49955429 | 739240051 | 49357052 | 0.000000 | 0.000000
09-04-2025 19:45:20.000 | 10515789 | 105157890 | 105.1579 | 70926230 | 15614656 | 38972180 | -99773315 | 49965885 | 592159668 | 39459854 | 0.000000 | 0.000000
09-04-2025 19:45:15.000 | 10528689 | 105286890 | 105.2869 | 70505449 | 15616402 | 39014509 | -99776535 | 49977272 | 445999756 | 29528948 | 0.000000 | 0.000000
09-04-2025 19:45:10.000 | 10643928 | 106439280 | 106.4393 | 69688086 | 15621009 | 39426042 | -99786354 | 49954418 | 299306885 | 19848507 | 0.000000 | 0.000000
09-04-2025 19:45:05.000 | 10815011 | 108150110 | 108.1501 | 71342515 | 15613148 | 40080933 | -99783127 | 49932446 | 150332062 | 9914593 | 0.000000 | 0.000000
09-04-2025 19:45:00.000 | 10852058 | 108520580 | 108.5206 | 70969985 | 15608444 | 40228752 | -99786842 | 49926510 | 26662010 | 17704384 | 0.000000 | 0.000000
09-04-2025 19:44:55.000 | 10819611 | 108196110 | 108.1961 | 69113091 | 15604679 | 40114265 | -99796608 | 49939602 | 26511279 | 17607120 | 0.000000 | 0.000000
09-04-2025 19:44:50.000 | 10726810 | 107268100 | 107.2681 | 67512715 | 15604162 | 39769277 | -99802528 | 49950905 | 26361623 | 17512915 | 0.000000 | 0.000000
09-04-2025 19:44:45.000 | 10517284 | 105172840 | 105.1728 | 64080850 | 15610020 | 38973132 | -99814896 | 49990932 | 26213961 | 17420892 | 0.000000 | 0.000000
09-04-2025 19:44:40.000 | 10414362 | 104143620 | 104.1436 | 64415811 | 15615869 | 38579458 | -99809258 | 50016426 | 26068854 | 17331479 | 0.000000 | 0.000000
09-04-2025 19:44:35.000 | 10503334 | 105033340 | 105.0333 | 65217505 | 15618729 | 38902515 | -99807785 | 49988651 | 25923857 | 17241909 | 0.000000 | 0.000000
09-04-2025 19:44:30.000 | 10645888 | 106458880 | 106.4589 | 67852217 | 15614487 | 39445203 | -99797508 | 49948425 | 25776990 | 17149291 | 0.000000 | 0.000000
09-04-2025 19:44:25.000 | 10677303 | 106773030 | 106.773 | 68434399 | 15610321 | 39572905 | -99795235 | 49937481 | 25628809 | 17054408 | 0.000000 | 0.000000
09-04-2025 19:44:20.000 | 10627306 | 106273060 | 106.2731 | 70012104 | 15608748 | 39396301 | -99783699 | 49944702 | 25480639 | 16958354 | 0.000000 | 0.000000
09-04-2025 19:44:15.000 | 10547101 | 105471010 | 105.471 | 70628403 | 15611804 | 39094119 | -99776535 | 49957531 | 25333266 | 16860884 | 0.000000 | 0.000000
09-04-2025 19:44:10.000 | 10511220 | 105112200 | 105.1122 | 70323057 | 15616479 | 38949275 | -99776947 | 49966629 | 25187137 | 16762308 | 0.000000 | 0.000000
09-04-2025 19:44:05.000 | 10594423 | 105944230 | 105.9442 | 71526997 | 15614751 | 39263418 | -99772873 | 49952499 | 25040754 | 16663077 | 0.000000 | 0.000000
09-04-2025 19:44:00.000 | 10703778 | 107037780 | 107.0378 | 71859766 | 15613561 | 39670972 | -99775406 | 49932323 | 24892869 | 16563881 | 0.000000 | 0.000000
09-04-2025 19:43:55.000 | 10720721 | 107207210 | 107.2072 | 69927583 | 15613013 | 39730427 | -99787949 | 49925797 | 24744055 | 16464106 | 0.000000 | 0.000000
09-04-2025 19:43:50.000 | 10812253 | 108122530 | 108.1225 | 69227676 | 15607449 | 40080872 | -99795654 | 49911995 | 24594631 | 16367598 | 0.000000 | 0.000000
09-04-2025 19:43:45.000 | 10724388 | 107243880 | 107.2439 | 69429321 | 15608735 | 39753159 | -99791092 | 49933388 | 24444814 | 16271853 | 0.000000 | 0.000000
09-04-2025 19:43:40.000 | 10632931 | 106329310 | 106.3293 | 68246191 | 15611131 | 39406870 | -99794655 | 49954575 | 24296441 | 16176652 | 0.000000 | 0.000000
09-04-2025 19:43:35.000 | 10561932 | 105619320 | 105.6193 | 67008877 | 15613630 | 39135852 | -99799347 | 49970627 | 24149295 | 16081866 | 0.000000 | 0.000000
09-04-2025 19:43:30.000 | 10607130 | 106071300 | 106.0713 | 67152788 | 15610472 | 39310552 | -99800201 | 49958984 | 24002232 | 15988390 | 0.000000 | 0.000000
09-04-2025 19:43:25.000 | 10623414 | 106234140 | 106.2341 | 68411992 | 15608949 | 39377883 | -99793289 | 49956783 | 23854725 | 15893945 | 0.000000 | 0.000000
09-04-2025 19:43:20.000 | 10555816 | 105558160 | 105.5582 | 68064351 | 15613143 | 39116804 | -99792763 | 49971008 | 23707791 | 15799753 | 0.000000 | 0.000000
09-04-2025 19:43:15.000 | 10561769 | 105617690 | 105.6177 | 67789980 | 15617165 | 39128081 | -99794655 | 49972664 | 23561465 | 15705094 | 0.000000 | 0.000000
09-04-2025 19:43:10.000 | 10679127 | 106791270 | 106.7913 | 69730054 | 15616368 | 39567888 | -99787506 | 49945808 | 23414445 | 15610579 | 0.000000 | 0.000000
09-04-2025 19:43:05.000 | 10805766 | 108057660 | 108.0577 | 71160605 | 15611087 | 40051626 | -99783867 | 49922756 | 23265627 | 15513804 | 0.000000 | 0.000000
09-04-2025 19:43:00.000 | 10814977 | 108149770 | 108.1498 | 70645186 | 15606207 | 40097185 | -99787338 | 49926834 | 23115361 | 15415203 | 0.000000 | 0.000000
09-04-2025 19:42:55.000 | 10682717 | 106827170 | 106.8272 | 71406328 | 15607427 | 39607708 | -99777344 | 49945679 | 22965813 | 15317311 | 0.000000 | 0.000000
09-04-2025 19:42:50.000 | 10555283 | 105552830 | 105.5528 | 69735874 | 15613069 | 39118860 | -99782471 | 49987438 | 22818389 | 15219238 | 0.000000 | 0.000000
09-04-2025 19:42:45.000 | 10607934 | 106079340 | 106.0793 | 67906797 | 15614214 | 39305815 | -99795731 | 49982662 | 22671814 | 15123590 | 0.000000 | 0.000000
09-04-2025 19:42:40.000 | 10714527 | 107145270 | 107.1453 | 68136367 | 15611640 | 39707581 | -99798409 | 49958660 | 22523957 | 15028990 | 0.000000 | 0.000000
09-04-2025 19:42:35.000 | 10709495 | 107094950 | 107.0949 | 68919043 | 15607289 | 39700608 | -99793571 | 49953403 | 22375285 | 14933652 | 0.000000 | 0.000000
09-04-2025 19:42:30.000 | 10637774 | 106377740 | 106.3777 | 67590146 | 15610363 | 39426003 | -99798759 | 49969738 | 22227199 | 14839225 | 0.000000 | 0.000000
09-04-2025 19:42:25.000 | 10541910 | 105419100 | 105.4191 | 69017510 | 15612380 | 39069617 | -99786369 | 49966160 | 22080316 | 14744506 | 0.000000 | 0.000000
09-04-2025 19:42:20.000 | 10525127 | 105251270 | 105.2513 | 69909775 | 15613661 | 39006650 | -99780136 | 49961754 | 21934072 | 14648195 | 0.000000 | 0.000000
09-04-2025 19:42:15.000 | 10570512 | 105705120 | 105.7051 | 69793325 | 15611779 | 39178381 | -99782738 | 49952126 | 21787574 | 14550845 | 0.000000 | 0.000000
09-04-2025 19:42:10.000 | 10570820 | 105708200 | 105.7082 | 70599736 | 15609896 | 39186270 | -99777718 | 49953129 | 21640717 | 14452742 | 0.000000 | 0.000000
09-04-2025 19:42:05.000 | 10556619 | 105566190 | 105.5662 | 70339360 | 15612971 | 39125486 | -99778755 | 49945938 | 21493871 | 14355349 | 0.000000 | 0.000000
09-04-2025 19:42:00.000 | 10488515 | 104885150 | 104.8851 | 72863398 | 15614216 | 38877468 | -99759567 | 49961071 | 21347424 | 14254872 | 0.000000 | 0.000000
09-04-2025 19:41:55.000 | 10584217 | 105842170 | 105.8422 | 72561563 | 15618591 | 39218806 | -99765823 | 49952381 | 21201537 | 14154248 | 0.000000 | 0.000000
09-04-2025 19:41:50.000 | 10775377 | 107753770 | 107.7538 | 75121440 | 15613063 | 39944338 | -99757866 | 49913506 | 21053582 | 14051979 | 0.000000 | 0.000000
09-04-2025 19:41:45.000 | 10845831 | 108458310 | 108.4583 | 74321401 | 15610676 | 40208320 | -99766037 | 49907169 | 20903600 | 13947517 | 0.000000 | 0.000000
09-04-2025 19:41:40.000 | 10841297 | 108412970 | 108.413 | 73072100 | 15607505 | 40196584 | -99773621 | 49909981 | 20752832 | 13844816 | 0.000000 | 0.000000
09-04-2025 19:41:35.000 | 10725038 | 107250380 | 107.2504 | 72641338 | 15613336 | 39751643 | -99771416 | 49945229 | 20602926 | 13742308 | 0.000000 | 0.000000
09-04-2025 19:41:30.000 | 10760120 | 107601200 | 107.6012 | 70987773 | 15609992 | 39885913 | -99783089 | 49937439 | 20454006 | 13642255 | 0.000000 | 0.000000
09-04-2025 19:41:25.000 | 10748571 | 107485710 | 107.4857 | 71541543 | 15606205 | 39854304 | -99779228 | 49940945 | 20304090 | 13543257 | 0.000000 | 0.000000
09-04-2025 19:41:20.000 | 10627246 | 106272460 | 106.2725 | 69611045 | 15610532 | 39390747 | -99786156 | 49971188 | 20155406 | 13445132 | 0.000000 | 0.000000
09-04-2025 19:41:15.000 | 10508273 | 105082730 | 105.0827 | 68953550 | 15612263 | 38945642 | -99785408 | 49991241 | 20008566 | 13347955 | 0.000000 | 0.000000
09-04-2025 19:41:10.000 | 10483205 | 104832050 | 104.832 | 69267227 | 15614549 | 38848125 | -99782417 | 49979084 | 19862889 | 13252699 | 0.000000 | 0.000000
09-04-2025 19:41:05.000 | 10565182 | 105651820 | 105.6518 | 70603086 | 15614690 | 39153408 | -99777458 | 49965046 | 19716699 | 13154552 | 0.000000 | 0.000000
09-04-2025 19:41:00.000 | 10621181 | 106211810 | 106.2118 | 72167632 | 15612638 | 39369478 | -99769958 | 49956501 | 19569736 | 13055629 | 0.000000 | 0.000000
09-04-2025 19:40:55.000 | 10609973 | 106099730 | 106.0997 | 71400020 | 15611134 | 39329705 | -99774338 | 49955494 | 19422348 | 12955635 | 0.000000 | 0.000000
09-04-2025 19:40:50.000 | 10612800 | 106128000 | 106.128 | 71454756 | 15612431 | 39337051 | -99774109 | 49954006 | 19274834 | 12856544 | 0.000000 | 0.000000
09-04-2025 19:40:45.000 | 10559109 | 105591090 | 105.5911 | 70336602 | 15615113 | 39129353 | -99778877 | 49967190 | 19127572 | 12757443 | 0.000000 | 0.000000
09-04-2025 19:40:40.000 | 10602155 | 106021550 | 106.0216 | 73088848 | 15615097 | 39295247 | -99763222 | 49958065 | 18980764 | 12658261 | 0.000000 | 0.000000
09-04-2025 19:40:35.000 | 10655607 | 106556070 | 106.5561 | 73397261 | 15613203 | 39497712 | -99763611 | 49950005 | 18833219 | 12556351 | 0.000000 | 0.000000
09-04-2025 19:40:30.000 | 10700845 | 107008450 | 107.0084 | 73927549 | 15614371 | 39663101 | -99762207 | 49941051 | 18684889 | 12454512 | 0.000000 | 0.000000
09-04-2025 19:40:25.000 | 10725415 | 107254150 | 107.2541 | 74674526 | 15612292 | 39760940 | -99758507 | 49940018 | 18536102 | 12350632 | 0.000000 | 0.000000
09-04-2025 19:40:20.000 | 10762255 | 107622550 | 107.6226 | 74878154 | 15610704 | 39901658 | -99758842 | 49934605 | 18387295 | 12247294 | 0.000000 | 0.000000
09-04-2025 19:40:15.000 | 10768705 | 107687050 | 107.687 | 71557075 | 15610428 | 39917507 | -99779953 | 49945641 | 18237910 | 12145038 | 0.000000 | 0.000000
09-04-2025 19:40:10.000 | 10820411 | 108204110 | 108.2041 | 68633936 | 15607585 | 40108643 | -99799438 | 49938320 | 18087980 | 12047699 | 0.000000 | 0.000000
09-04-2025 19:40:05.000 | 10697777 | 106977770 | 106.9778 | 70029014 | 15607357 | 39659934 | -99786430 | 49961090 | 17938045 | 11950728 | 0.000000 | 0.000000
09-04-2025 19:40:00.000 | 10607670 | 106076700 | 106.0767 | 70360972 | 15611199 | 39318445 | -99780739 | 49980217 | 17790025 | 11853461 | 0.000000 | 0.000000
09-04-2025 19:39:55.000 | 10567574 | 105675740 | 105.6757 | 67882783 | 15611353 | 39164114 | -99794319 | 49986008 | 17642865 | 11758018 | 0.000000 | 0.000000
09-04-2025 19:39:50.000 | 10541754 | 105417540 | 105.4175 | 70601875 | 15610888 | 39076863 | -99776482 | 49977242 | 17496244 | 11663008 | 0.000000 | 0.000000
09-04-2025 19:39:45.000 | 10494006 | 104940060 | 104.9401 | 70756870 | 15613708 | 38893955 | -99773460 | 49976620 | 17350197 | 11565072 | 0.000000 | 0.000000
09-04-2025 19:39:40.000 | 10504057 | 105040570 | 105.0406 | 72158042 | 15614797 | 38932017 | -99764877 | 49969715 | 17204438 | 11465977 | 0.000000 | 0.000000
09-04-2025 19:39:35.000 | 10644945 | 106449450 | 106.4494 | 71475732 | 15614136 | 39451160 | -99775337 | 49937031 | 17057779 | 11366841 | 0.000000 | 0.000000
09-04-2025 19:39:30.000 | 10641977 | 106419770 | 106.4198 | 72256670 | 15613763 | 39443154 | -99770287 | 49927830 | 16909941 | 11266965 | 0.000000 | 0.000000
09-04-2025 19:39:25.000 | 10611920 | 106119200 | 106.1192 | 74494849 | 15614586 | 39335889 | -99754509 | 49952766 | 16762355 | 11164807 | 0.000000 | 0.000000
09-04-2025 19:39:20.000 | 10726620 | 107266200 | 107.2662 | 71372109 | 15616959 | 39745115 | -99779373 | 49937618 | 16614863 | 11064685 | 0.000000 | 0.000000
09-04-2025 19:39:15.000 | 10829166 | 108291660 | 108.2917 | 74169214 | 15610621 | 40147820 | -99766273 | 49914886 | 16464990 | 10963074 | 0.000000 | 0.000000
09-04-2025 19:39:10.000 | 10876419 | 108764190 | 108.7642 | 73578730 | 15605054 | 40334006 | -99771957 | 49907104 | 16314013 | 10859586 | 0.000000 | 0.000000
09-04-2025 19:39:05.000 | 10729250 | 107292500 | 107.2925 | 71429282 | 15603563 | 39789080 | -99779129 | 49936852 | 16163196 | 10757274 | 0.000000 | 0.000000
09-04-2025 19:39:00.000 | 10501710 | 105017100 | 105.0171 | 70556304 | 15612449 | 38925032 | -99775063 | 49993401 | 16015443 | 10658420 | 0.000000 | 0.000000
09-04-2025 19:38:55.000 | 10495055 | 104950550 | 104.9506 | 69964878 | 15616685 | 38888333 | -99778526 | 49986950 | 15869869 | 10561288 | 0.000000 | 0.000000
09-04-2025 19:38:50.000 | 10616016 | 106160160 | 106.1602 | 71402891 | 15612246 | 39349180 | -99774574 | 49964779 | 15723487 | 10462960 | 0.000000 | 0.000000
09-04-2025 19:38:45.000 | 10632114 | 106321140 | 106.3211 | 71190361 | 15612949 | 39406438 | -99776581 | 49963291 | 15576132 | 10364390 | 0.000000 | 0.000000
09-04-2025 19:38:40.000 | 10625688 | 106256880 | 106.2569 | 70690205 | 15609760 | 39389302 | -99779434 | 49957169 | 15428644 | 10265723 | 0.000000 | 0.000000
09-04-2025 19:38:35.000 | 10583461 | 105834610 | 105.8346 | 70482798 | 15611859 | 39227813 | -99778976 | 49959595 | 15280943 | 10167603 | 0.000000 | 0.000000
09-04-2025 19:38:30.000 | 10514846 | 105148460 | 105.1485 | 71991577 | 15612659 | 38976240 | -99766434 | 49958923 | 15134202 | 10068369 | 0.000000 | 0.000000
09-04-2025 19:38:25.000 | 10480930 | 104809300 | 104.8093 | 73134146 | 15614023 | 38850852 | -99757439 | 49965233 | 14988446 | 996796143 | 0.000000 | 0.000000
09-04-2025 19:38:20.000 | 10544285 | 105442850 | 105.4429 | 71385088 | 15618076 | 39069797 | -99771622 | 49954926 | 14842734 | 986848450 | 0.000000 | 0.000000
09-04-2025 19:38:15.000 | 10750559 | 107505590 | 107.5056 | 72101064 | 15613708 | 39843833 | -99775856 | 49912014 | 14695269 | 976940796 | 0.000000 | 0.000000
09-04-2025 19:38:10.000 | 10815308 | 108153080 | 108.1531 | 73789419 | 15612783 | 40088921 | -99768066 | 49903831 | 14545616 | 966878296 | 0.000000 | 0.000000
09-04-2025 19:38:05.000 | 10832737 | 108327370 | 108.3274 | 74964985 | 15610721 | 40161438 | -99761406 | 49913700 | 14395300 | 956476624 | 0.000000 | 0.000000
09-04-2025 19:38:00.000 | 10780552 | 107805520 | 107.8055 | 71556299 | 15611681 | 39958140 | -99780441 | 49929989 | 14245512 | 946198303 | 0.000000 | 0.000000
09-04-2025 19:37:55.000 | 10807323 | 108073230 | 108.0732 | 70134077 | 15607636 | 40063958 | -99790092 | 49924236 | 14095501 | 936375732 | 0.000000 | 0.000000
09-04-2025 19:37:50.000 | 10761845 | 107618450 | 107.6184 | 72024756 | 15607263 | 39901501 | -99776794 | 49924122 | 13945570 | 926630310 | 0.000000 | 0.000000
09-04-2025 19:37:45.000 | 10583085 | 105830850 | 105.8308 | 70030840 | 15609933 | 39230076 | -99781776 | 49959282 | 13797001 | 916701355 | 0.000000 | 0.000000
09-04-2025 19:37:40.000 | 10486441 | 104864410 | 104.8644 | 70815786 | 15615437 | 38861638 | -99772758 | 49979210 | 13650592 | 906965576 | 0.000000 | 0.000000
09-04-2025 19:37:35.000 | 10548591 | 105485910 | 105.4859 | 69382256 | 15617933 | 39081108 | -99784386 | 49970894 | 13504549 | 897219299 | 0.000000 | 0.000000
09-04-2025 19:37:30.000 | 10640381 | 106403810 | 106.4038 | 72515215 | 15615702 | 39433052 | -99768578 | 49949051 | 13357369 | 887281250 | 0.000000 | 0.000000
09-04-2025 19:37:25.000 | 10680616 | 106806160 | 106.8062 | 74193491 | 15613817 | 39590837 | -99759598 | 49941689 | 13209066 | 877055786 | 0.000000 | 0.000000
09-04-2025 19:37:20.000 | 10708734 | 107087340 | 107.0873 | 71274204 | 15612414 | 39690857 | -99779243 | 49939545 | 13060792 | 866878174 | 0.000000 | 0.000000
09-04-2025 19:37:15.000 | 10747333 | 107473330 | 107.4733 | 72806987 | 15612756 | 39837122 | -99771324 | 49935089 | 12911751 | 856987610 | 0.000000 | 0.000000
09-04-2025 19:37:10.000 | 10736688 | 107366880 | 107.3669 | 69538354 | 15614961 | 39782788 | -99790916 | 49956482 | 12762620 | 846904480 | 0.000000 | 0.000000
09-04-2025 19:37:05.000 | 10768609 | 107686090 | 107.6861 | 73036099 | 15612762 | 39914829 | -99770790 | 49954136 | 12613285 | 837046204 | 0.000000 | 0.000000
09-04-2025 19:37:00.000 | 10790682 | 107906820 | 107.9068 | 72378159 | 15609902 | 40002241 | -99775803 | 49960373 | 12463557 | 826923218 | 0.000000 | 0.000000
09-04-2025 19:36:55.000 | 10831917 | 108319170 | 108.3192 | 71247979 | 15608514 | 40154934 | -99784378 | 49960396 | 12313296 | 816966858 | 0.000000 | 0.000000
09-04-2025 19:36:50.000 | 10755355 | 107553550 | 107.5536 | 75176699 | 15606872 | 39886570 | -99756615 | 49981655 | 12162927 | 806841614 | 0.000000 | 0.000000
09-04-2025 19:36:45.000 | 10652672 | 106526720 | 106.5267 | 74305630 | 15611532 | 39493633 | -99757607 | 49999947 | 12014158 | 796465576 | 0.000000 | 0.000000
09-04-2025 19:36:40.000 | 10591421 | 105914210 | 105.9142 | 76272153 | 15611188 | 39273718 | -99741707 | 50010876 | 11866360 | 786014954 | 0.000000 | 0.000000
09-04-2025 19:36:35.000 | 10523843 | 105238430 | 105.2384 | 74019761 | 15613724 | 39011934 | -99753563 | 50027088 | 11719864 | 775401123 | 0.000000 | 0.000000
09-04-2025 19:36:30.000 | 10583943 | 105839430 | 105.8394 | 74379585 | 15616740 | 39227053 | -99753975 | 50005310 | 11573609 | 765239136 | 0.000000 | 0.000000
09-04-2025 19:36:25.000 | 10678730 | 106787300 | 106.7873 | 76407021 | 15614284 | 39588889 | -99745003 | 49987682 | 11425964 | 754773193 | 0.000000 | 0.000000
09-04-2025 19:36:20.000 | 10789465 | 107894650 | 107.8946 | 72801909 | 15613058 | 39990361 | -99773132 | 49977451 | 11277165 | 744341797 | 0.000000 | 0.000000
09-04-2025 19:36:15.000 | 10797509 | 107975090 | 107.9751 | 74175996 | 15606406 | 40040928 | -99764862 | 49968384 | 11126918 | 734092041 | 0.000000 | 0.000000
09-04-2025 19:36:10.000 | 10665442 | 106654420 | 106.6544 | 75395151 | 15606576 | 39556753 | -99751068 | 50004436 | 10977620 | 723625427 | 0.000000 | 0.000000
09-04-2025 19:36:05.000 | 10507935 | 105079350 | 105.0794 | 72056968 | 15614879 | 38946167 | -99765709 | 50036869 | 10830270 | 713409302 | 0.000000 | 0.000000
09-04-2025 19:36:00.000 | 10616404 | 106164040 | 106.164 | 68666777 | 15614177 | 39339165 | -99791481 | 50007893 | 10683618 | 703659973 | 0.000000 | 0.000000
09-04-2025 19:35:55.000 | 10720613 | 107206130 | 107.2061 | 70712017 | 15608382 | 39743210 | -99783180 | 49980602 | 10535359 | 694038818 | 0.000000 | 0.000000
09-04-2025 19:35:50.000 | 10583330 | 105833300 | 105.8333 | 71905381 | 15611854 | 39230684 | -99769989 | 50010983 | 10387104 | 684035400 | 0.000000 | 0.000000
09-04-2025 19:35:45.000 | 10606893 | 106068930 | 106.0689 | 70203477 | 15616826 | 39301458 | -99781685 | 50017960 | 10240194 | 674208191 | 0.000000 | 0.000000
09-04-2025 19:35:40.000 | 10695404 | 106954040 | 106.954 | 71425449 | 15614118 | 39637300 | -99777756 | 49998924 | 10092545 | 664428589 | 0.000000 | 0.000000
09-04-2025 19:35:35.000 | 10756788 | 107567880 | 107.5679 | 72991489 | 15612923 | 39871018 | -99770569 | 49984596 | 99435469 | 654516541 | 0.000000 | 0.000000
09-04-2025 19:35:30.000 | 10797741 | 107977410 | 107.9774 | 72602861 | 15612757 | 40021602 | -99774712 | 49985870 | 97939082 | 644368469 | 0.000000 | 0.000000
09-04-2025 19:35:25.000 | 10819574 | 108195740 | 108.1957 | 71377139 | 15610136 | 40105930 | -99783104 | 49986938 | 96437236 | 634440186 | 0.000000 | 0.000000
09-04-2025 19:35:20.000 | 10725650 | 107256500 | 107.2565 | 70202451 | 15608951 | 39758992 | -99786484 | 50006718 | 94936465 | 624497498 | 0.000000 | 0.000000
09-04-2025 19:35:15.000 | 10632981 | 106329810 | 106.3298 | 69856182 | 15608794 | 39416934 | -99784889 | 50031727 | 93451172 | 614638611 | 0.000000 | 0.000000
09-04-2025 19:35:10.000 | 10624010 | 106240100 | 106.2401 | 68392949 | 15609949 | 39377173 | -99793427 | 50031979 | 91976377 | 605100098 | 0.000000 | 0.000000
09-04-2025 19:35:05.000 | 10571746 | 105717460 | 105.7175 | 67940771 | 15611374 | 39179707 | -99794128 | 50036545 | 90504326 | 595569275 | 0.000000 | 0.000000
09-04-2025 19:35:00.000 | 10517475 | 105174750 | 105.1748 | 70471890 | 15616647 | 38972356 | -99776276 | 50047615 | 89040205 | 585966980 | 0.000000 | 0.000000
09-04-2025 19:34:55.000 | 10564279 | 105642790 | 105.6428 | 70802720 | 15619004 | 39139709 | -99776161 | 50050247 | 87577588 | 576174561 | 0.000000 | 0.000000
09-04-2025 19:34:50.000 | 10700140 | 107001400 | 107.0014 | 70281748 | 15616914 | 39644973 | -99784981 | 50022202 | 86102578 | 566264832 | 0.000000 | 0.000000
09-04-2025 19:34:45.000 | 10886371 | 108863710 | 108.8637 | 72030884 | 15606446 | 40363215 | -99781822 | 49975208 | 84603389 | 556476379 | 0.000000 | 0.000000
09-04-2025 19:34:40.000 | 10821681 | 108216810 | 108.2168 | 69735483 | 15604037 | 40124998 | -99793015 | 49993370 | 83091211 | 546525269 | 0.000000 | 0.000000
09-04-2025 19:34:35.000 | 10647805 | 106478050 | 106.478 | 69687173 | 15605123 | 39480220 | -99786514 | 50031956 | 81597559 | 536821472 | 0.000000 | 0.000000
09-04-2025 19:34:30.000 | 10532770 | 105327700 | 105.3277 | 67319102 | 15614165 | 39027451 | -99796371 | 50053471 | 80127212 | 527379639 | 0.000000 | 0.000000
09-04-2025 19:34:25.000 | 10490787 | 104907870 | 104.9079 | 67434204 | 15616868 | 38866426 | -99794044 | 50057354 | 78667798 | 517969177 | 0.000000 | 0.000000
09-04-2025 19:34:20.000 | 10628109 | 106281090 | 106.2811 | 69671709 | 15615963 | 39380811 | -99785820 | 50032475 | 77205947 | 508628204 | 0.000000 | 0.000000
09-04-2025 19:34:15.000 | 10711044 | 107110440 | 107.1104 | 73958535 | 15612879 | 39704548 | -99762459 | 50007893 | 75724697 | 498769104 | 0.000000 | 0.000000
09-04-2025 19:34:10.000 | 10680492 | 106804920 | 106.8049 | 76667783 | 15609722 | 39606790 | -99743355 | 50007023 | 74238032 | 488319702 | 0.000000 | 0.000000
09-04-2025 19:34:05.000 | 10677054 | 106770540 | 106.7705 | 74108013 | 15610565 | 39585420 | -99759987 | 50013924 | 72756138 | 477771790 | 0.000000 | 0.000000
09-04-2025 19:34:00.000 | 10652163 | 106521630 | 106.5216 | 73536235 | 15607509 | 39499841 | -99762566 | 50011414 | 71275854 | 467584961 | 0.000000 | 0.000000
09-04-2025 19:33:55.000 | 10626290 | 106262900 | 106.2629 | 70850923 | 15613180 | 39383279 | -99778458 | 50019257 | 69799595 | 457634003 | 0.000000 | 0.000000
09-04-2025 19:33:50.000 | 10638322 | 106383220 | 106.3832 | 70869863 | 15613875 | 39425850 | -99778839 | 50018978 | 68322744 | 447757690 | 0.000000 | 0.000000
09-04-2025 19:33:45.000 | 10670191 | 106701910 | 106.7019 | 71909033 | 15616732 | 39538970 | -99773682 | 50018383 | 66843311 | 437857666 | 0.000000 | 0.000000
09-04-2025 19:33:40.000 | 10784384 | 107843840 | 107.8438 | 72671108 | 15613253 | 39970964 | -99773727 | 49997574 | 65355566 | 427767639 | 0.000000 | 0.000000
09-04-2025 19:33:35.000 | 10834254 | 108342540 | 108.3425 | 72087017 | 15611893 | 40156885 | -99779381 | 49997490 | 63853140 | 417702942 | 0.000000 | 0.000000
09-04-2025 19:33:30.000 | 10784881 | 107848810 | 107.8488 | 73101738 | 15609324 | 39983774 | -99771072 | 50013184 | 62352261 | 407538666 | 0.000000 | 0.000000
09-04-2025 19:33:25.000 | 10720748 | 107207480 | 107.2075 | 70419624 | 15613403 | 39730134 | -99784966 | 50026279 | 60860244 | 397523499 | 0.000000 | 0.000000
09-04-2025 19:33:20.000 | 10771213 | 107712130 | 107.7121 | 70615112 | 15611020 | 39922891 | -99785789 | 50008541 | 59368184 | 387812561 | 0.000000 | 0.000000
09-04-2025 19:33:15.000 | 10734884 | 107348840 | 107.3488 | 70044512 | 15610421 | 39789534 | -99787804 | 50008450 | 57872207 | 378002380 | 0.000000 | 0.000000
09-04-2025 19:33:10.000 | 10637216 | 106372160 | 106.3722 | 68352173 | 15605285 | 39438340 | -99794182 | 50032951 | 56384053 | 368183044 | 0.000000 | 0.000000
09-04-2025 19:33:05.000 | 10541957 | 105419570 | 105.4196 | 66207813 | 15608681 | 39072576 | -99803360 | 50042675 | 54909658 | 358798126 | 0.000000 | 0.000000
09-04-2025 19:33:00.000 | 10434789 | 104347890 | 104.3479 | 67728760 | 15609702 | 38677659 | -99790016 | 50047325 | 53450044 | 349472534 | 0.000000 | 0.000000
09-04-2025 19:32:55.000 | 10387895 | 103878950 | 103.879 | 68557295 | 15617189 | 38488447 | -99782928 | 50051502 | 52003838 | 340103119 | 0.000000 | 0.000000
09-04-2025 19:32:50.000 | 10449930 | 104499300 | 104.4993 | 71017295 | 15618356 | 38720410 | -99769875 | 50046062 | 50559004 | 330393311 | 0.000000 | 0.000000
09-04-2025 19:32:45.000 | 10646565 | 106465650 | 106.4656 | 72806509 | 15617118 | 39453125 | -99766991 | 49996044 | 49100786 | 320691254 | 0.000000 | 0.000000
09-04-2025 19:32:40.000 | 10743964 | 107439640 | 107.4396 | 75973945 | 15611824 | 39833779 | -99750916 | 49963364 | 47616377 | 310504059 | 0.000000 | 0.000000
09-04-2025 19:32:35.000 | 10729836 | 107298360 | 107.2984 | 75088521 | 15613076 | 39776228 | -99756027 | 49969570 | 46125972 | 300058319 | 0.000000 | 0.000000
09-04-2025 19:32:30.000 | 10759375 | 107593750 | 107.5938 | 74332983 | 15611135 | 39888286 | -99762199 | 49971210 | 44635430 | 289733093 | 0.000000 | 0.000000
09-04-2025 19:32:25.000 | 10784698 | 107846980 | 107.847 | 72482158 | 15611094 | 39976953 | -99774918 | 49980686 | 43139111 | 279596954 | 0.000000 | 0.000000
09-04-2025 19:32:20.000 | 10784630 | 107846300 | 107.8463 | 70818833 | 15609188 | 39977578 | -99785088 | 49994701 | 41640386 | 269560944 | 0.000000 | 0.000000
09-04-2025 19:32:15.000 | 10805225 | 108052250 | 108.0523 | 67753311 | 15610122 | 40044736 | -99803986 | 50005550 | 40142214 | 259883636 | 0.000000 | 0.000000
09-04-2025 19:32:10.000 | 10763533 | 107635330 | 107.6353 | 70376021 | 15608751 | 39899810 | -99786934 | 50014950 | 38646001 | 250358078 | 0.000000 | 0.000000
09-04-2025 19:32:05.000 | 10722246 | 107222460 | 107.2225 | 67102031 | 15612671 | 39729678 | -99804749 | 50025661 | 37156003 | 240771698 | 0.000000 | 0.000000
09-04-2025 19:32:00.000 | 10758248 | 107582480 | 107.5825 | 67811245 | 15612339 | 39865527 | -99801941 | 50013954 | 35664927 | 231377670 | 0.000000 | 0.000000
09-04-2025 19:31:55.000 | 10725755 | 107257550 | 107.2575 | 70134766 | 15608841 | 39759490 | -99786896 | 50017765 | 34171677 | 221773972 | 0.000000 | 0.000000
09-04-2025 19:31:50.000 | 10684484 | 106844840 | 106.8448 | 68907656 | 15609216 | 39603394 | -99792679 | 50024410 | 32684370 | 212199661 | 0.000000 | 0.000000
09-04-2025 19:31:45.000 | 10662362 | 106623620 | 106.6236 | 67230366 | 15610148 | 39515693 | -99801804 | 50038425 | 31203774 | 202741394 | 0.000000 | 0.000000
09-04-2025 19:31:40.000 | 10630113 | 106301130 | 106.3011 | 66663232 | 15613950 | 39385620 | -99803940 | 50039906 | 29725452 | 193538010 | 0.000000 | 0.000000
09-04-2025 19:31:35.000 | 10618191 | 106181910 | 106.1819 | 67074468 | 15613834 | 39342920 | -99801079 | 50049793 | 28248367 | 184106659 | 0.000000 | 0.000000
09-04-2025 19:31:30.000 | 10709380 | 107093800 | 107.0938 | 65709658 | 15611626 | 39681609 | -99812294 | 50024914 | 26767441 | 174947418 | 0.000000 | 0.000000
09-04-2025 19:31:25.000 | 10739114 | 107391140 | 107.3911 | 67402886 | 15607811 | 39804998 | -99803612 | 50012203 | 25276628 | 165653015 | 0.000000 | 0.000000
09-04-2025 19:31:20.000 | 10670248 | 106702480 | 106.7025 | 65861792 | 15608758 | 39544856 | -99810043 | 50022987 | 23789553 | 156324402 | 0.000000 | 0.000000
09-04-2025 19:31:15.000 | 10614754 | 106147540 | 106.1475 | 66059282 | 15608797 | 39340493 | -99806908 | 50042175 | 22312854 | 147174271 | 0.000000 | 0.000000
09-04-2025 19:31:10.000 | 10542652 | 105426520 | 105.4265 | 65282813 | 15609793 | 39069832 | -99808830 | 50050423 | 20841011 | 138014755 | 0.000000 | 0.000000
09-04-2025 19:31:05.000 | 10501438 | 105014380 | 105.0144 | 64433442 | 15611193 | 38912278 | -99812294 | 50038193 | 19378135 | 129023926 | 0.000000 | 0.000000
09-04-2025 19:31:00.000 | 10438504 | 104385040 | 104.385 | 65947036 | 15612763 | 38679539 | -99801033 | 50032692 | 17921476 | 120028008 | 0.000000 | 0.000000
09-04-2025 19:30:55.000 | 10373577 | 103735770 | 103.7358 | 66322485 | 15620095 | 38423057 | -99796249 | 50055775 | 16476379 | 110755615 | 0.000000 | 0.000000
09-04-2025 19:30:50.000 | 10530799 | 105307990 | 105.308 | 70866748 | 15617782 | 39019612 | -99774338 | 50023792 | 15031259 | 101189423 | 0.000000 | 0.000000
09-04-2025 19:30:45.000 | 10694951 | 106949510 | 106.9495 | 72119512 | 15615388 | 39634058 | -99773407 | 49975990 | 13558866 | 91346184 | 0.000000 | 0.000000
09-04-2025 19:30:40.000 | 10758376 | 107583760 | 107.5838 | 74967832 | 15610913 | 39887153 | -99758095 | 49954884 | 12068032 | 81209030 | 0.000000 | 0.000000
09-04-2025 19:30:35.000 | 10732136 | 107321360 | 107.3214 | 75997324 | 15611892 | 39790005 | -99750214 | 49967915 | 10576305 | 70763062 | 0.000000 | 0.000000
09-04-2025 19:30:30.000 | 10716440 | 107164400 | 107.1644 | 73048218 | 15616252 | 39713728 | -99768486 | 49976452 | 908905823 | 60349865 | 0.000000 | 0.000000
09-04-2025 19:30:25.000 | 10809739 | 108097390 | 108.0974 | 74252788 | 15616095 | 40061279 | -99764908 | 49974545 | 759345581 | 50030888 | 0.000000 | 0.000000
09-04-2025 19:30:20.000 | 10914054 | 109140540 | 109.1405 | 74440176 | 15613251 | 40453635 | -99768204 | 49970913 | 608555908 | 39598591 | 0.000000 | 0.000000
09-04-2025 19:30:15.000 | 10966230 | 109662300 | 109.6623 | 73036523 | 15610986 | 40649314 | -99778946 | 49971870 | 456646759 | 29296669 | 0.000000 | 0.000000
09-04-2025 19:30:10.000 | 10991359 | 109913590 | 109.9136 | 70349595 | 15608141 | 40742236 | -99795799 | 49974926 | 304152679 | 19193121 | 0.000000 | 0.000000
09-04-2025 19:30:05.000 | 10971142 | 109711420 | 109.7114 | 69539727 | 15605049 | 40674167 | -99799728 | 49978611 | 151633743 | 9473030 | 0.000000 | 0.000000
09-04-2025 19:30:00.000 | 10849654 | 108496540 | 108.4965 | 65820962 | 15605160 | 40216304 | -99816483 | 50017307 | 29439377 | 18919933 | 0.000000 | 0.000000
09-04-2025 19:29:55.000 | 10751051 | 107510510 | 107.5105 | 61271943 | 15606454 | 39839033 | -99837990 | 50039871 | 29289248 | 18831547 | 0.000000 | 0.000000
09-04-2025 19:29:50.000 | 10622510 | 106225100 | 106.2251 | 62452354 | 15608325 | 39362627 | -99827621 | 50065151 | 29140557 | 18745757 | 0.000000 | 0.000000
09-04-2025 19:29:45.000 | 10493883 | 104938830 | 104.9388 | 60469502 | 15611679 | 38874653 | -99834389 | 50088814 | 28993908 | 18660585 | 0.000000 | 0.000000
09-04-2025 19:29:40.000 | 10523642 | 105236420 | 105.2364 | 60116543 | 15610795 | 38985791 | -99837234 | 50077785 | 28848469 | 18578284 | 0.000000 | 0.000000
09-04-2025 19:29:35.000 | 10500352 | 105003520 | 105.0035 | 60700415 | 15611051 | 38900356 | -99833328 | 50047966 | 28702516 | 18495587 | 0.000000 | 0.000000
09-04-2025 19:29:30.000 | 10442882 | 104428820 | 104.4288 | 63446758 | 15609499 | 38698198 | -99815948 | 50045776 | 28556816 | 18409880 | 0.000000 | 0.000000
09-04-2025 19:29:25.000 | 10314384 | 103143840 | 103.1438 | 63403433 | 15614488 | 38211558 | -99811600 | 50060955 | 28412645 | 18322844 | 0.000000 | 0.000000
09-04-2025 19:29:20.000 | 10328052 | 103280520 | 103.2805 | 64569575 | 15616852 | 38259429 | -99805145 | 50054684 | 28269037 | 18234517 | 0.000000 | 0.000000
09-04-2025 19:29:15.000 | 10424844 | 104248440 | 104.2484 | 66559351 | 15622200 | 38607288 | -99796799 | 50036926 | 28124883 | 18143218 | 0.000000 | 0.000000
09-04-2025 19:29:10.000 | 10634930 | 106349300 | 106.3493 | 71088774 | 15618197 | 39403188 | -99777336 | 49988483 | 27978916 | 18047273 | 0.000000 | 0.000000
09-04-2025 19:29:05.000 | 10761405 | 107614050 | 107.6141 | 71843384 | 15615387 | 39878479 | -99777893 | 49974312 | 27830428 | 17948187 | 0.000000 | 0.000000
09-04-2025 19:29:00.000 | 10877814 | 108778140 | 108.7781 | 70400303 | 15613570 | 40309382 | -99791229 | 49971123 | 27680375 | 17848640 | 0.000000 | 0.000000
09-04-2025 19:28:55.000 | 10999010 | 109990100 | 109.9901 | 68362490 | 15610852 | 40758723 | -99807404 | 49945629 | 27528291 | 17751766 | 0.000000 | 0.000000
09-04-2025 19:28:50.000 | 10955972 | 109559720 | 109.5597 | 70638936 | 15604494 | 40622214 | -99792793 | 49953812 | 27375463 | 17654329 | 0.000000 | 0.000000
09-04-2025 19:28:45.000 | 10860123 | 108601230 | 108.6012 | 68471890 | 15604892 | 40262021 | -99801834 | 49991421 | 27223867 | 17557655 | 0.000000 | 0.000000
09-04-2025 19:28:40.000 | 10683576 | 106835760 | 106.8358 | 65287227 | 15607896 | 39594854 | -99813797 | 50032280 | 27074195 | 17464418 | 0.000000 | 0.000000
09-04-2025 19:28:35.000 | 10653883 | 106538830 | 106.5388 | 60562344 | 15610025 | 39469639 | -99838821 | 50039761 | 26926248 | 17377043 | 0.000000 | 0.000000
09-04-2025 19:28:30.000 | 10612030 | 106120300 | 106.1203 | 59892100 | 15609767 | 39314673 | -99841118 | 50045998 | 26778334 | 17293157 | 0.000000 | 0.000000
09-04-2025 19:28:25.000 | 10509269 | 105092690 | 105.0927 | 62685723 | 15614323 | 38929370 | -99822578 | 50057678 | 26631484 | 17207699 | 0.000000 | 0.000000
09-04-2025 19:28:20.000 | 10522084 | 105220840 | 105.2208 | 61447378 | 15618103 | 38965347 | -99829918 | 50051647 | 26485656 | 17121196 | 0.000000 | 0.000000
09-04-2025 19:28:15.000 | 10623538 | 106235380 | 106.2354 | 63785933 | 15614359 | 39355161 | -99820236 | 50024761 | 26338988 | 17033452 | 0.000000 | 0.000000
09-04-2025 19:28:10.000 | 10637770 | 106377700 | 106.3777 | 67209785 | 15612675 | 39418298 | -99801010 | 50016319 | 26191354 | 16942573 | 0.000000 | 0.000000
09-04-2025 19:28:05.000 | 10583563 | 105835630 | 105.8356 | 68550317 | 15609830 | 39228660 | -99790894 | 50029884 | 26043877 | 16847537 | 0.000000 | 0.000000
09-04-2025 19:28:00.000 | 10559382 | 105593820 | 105.5938 | 66250562 | 15616147 | 39117861 | -99803757 | 50046532 | 25896955 | 16754180 | 0.000000 | 0.000000
09-04-2025 19:27:55.000 | 10660553 | 106605530 | 106.6055 | 66964819 | 15616429 | 39492092 | -99803291 | 50019714 | 25749816 | 16662820 | 0.000000 | 0.000000
09-04-2025 19:27:50.000 | 10680785 | 106807850 | 106.8079 | 66545322 | 15616301 | 39566897 | -99806473 | 50026463 | 25601686 | 16568893 | 0.000000 | 0.000000
09-04-2025 19:27:45.000 | 10804433 | 108044330 | 108.0443 | 65687866 | 15613281 | 40028137 | -99815697 | 50002998 | 25452648 | 16477565 | 0.000000 | 0.000000
09-04-2025 19:27:40.000 | 10889736 | 108897360 | 108.8974 | 64379170 | 15608822 | 40351614 | -99825706 | 49995880 | 25301840 | 16386654 | 0.000000 | 0.000000
09-04-2025 19:27:35.000 | 10817379 | 108173790 | 108.1738 | 65781118 | 15605879 | 40095125 | -99815613 | 50011276 | 25150813 | 16295907 | 0.000000 | 0.000000
09-04-2025 19:27:30.000 | 10672603 | 106726030 | 106.726 | 63460386 | 15610732 | 39543262 | -99823685 | 50049671 | 25001623 | 16205948 | 0.000000 | 0.000000
09-04-2025 19:27:25.000 | 10632757 | 106327570 | 106.3276 | 60622661 | 15609270 | 39393560 | -99837860 | 50053436 | 24853807 | 16118541 | 0.000000 | 0.000000
09-04-2025 19:27:20.000 | 10567680 | 105676800 | 105.6768 | 60737144 | 15608975 | 39154648 | -99835243 | 50057735 | 24706094 | 16034564 | 0.000000 | 0.000000
09-04-2025 19:27:15.000 | 10486813 | 104868130 | 104.8681 | 59239932 | 15613284 | 38842214 | -99840828 | 50072624 | 24559463 | 15950601 | 0.000000 | 0.000000
09-04-2025 19:27:10.000 | 10471416 | 104714160 | 104.7142 | 60147271 | 15612455 | 38788992 | -99835442 | 50069054 | 24413863 | 15866628 | 0.000000 | 0.000000
09-04-2025 19:27:05.000 | 10499674 | 104996740 | 104.9967 | 60927744 | 15614854 | 38888960 | -99832062 | 50052620 | 24268180 | 15782877 | 0.000000 | 0.000000
09-04-2025 19:27:00.000 | 10542448 | 105424480 | 105.4245 | 62220107 | 15614708 | 39049873 | -99826294 | 50040241 | 24122232 | 15697362 | 0.000000 | 0.000000
09-04-2025 19:26:55.000 | 10593302 | 105933020 | 105.933 | 65462959 | 15614649 | 39244915 | -99809601 | 50034313 | 23975514 | 15608740 | 0.000000 | 0.000000
09-04-2025 19:26:50.000 | 10683603 | 106836030 | 106.836 | 63050005 | 15615496 | 39571130 | -99826309 | 50010506 | 23827945 | 15519158 | 0.000000 | 0.000000
09-04-2025 19:26:45.000 | 10724988 | 107249880 | 107.2499 | 67546738 | 15612458 | 39741279 | -99802261 | 49998661 | 23679158 | 15427151 | 0.000000 | 0.000000
09-04-2025 19:26:40.000 | 10693051 | 106930510 | 106.9305 | 65432778 | 15614702 | 39612917 | -99813301 | 50019108 | 23530514 | 15333322 | 0.000000 | 0.000000
09-04-2025 19:26:35.000 | 10812823 | 108128230 | 108.1282 | 65037930 | 15613447 | 40057668 | -99819595 | 49991581 | 23381545 | 15243921 | 0.000000 | 0.000000
09-04-2025 19:26:30.000 | 10849441 | 108494410 | 108.4944 | 67946489 | 15607463 | 40214587 | -99804466 | 49987949 | 23230895 | 15151875 | 0.000000 | 0.000000
09-04-2025 19:26:25.000 | 10749818 | 107498180 | 107.4982 | 62543726 | 15610889 | 39825779 | -99831177 | 50018448 | 23080451 | 15059625 | 0.000000 | 0.000000
09-04-2025 19:26:20.000 | 10779867 | 107798670 | 107.7987 | 60932808 | 15607743 | 39941421 | -99840630 | 50023239 | 22931029 | 14974347 | 0.000000 | 0.000000
09-04-2025 19:26:15.000 | 10741374 | 107413740 | 107.4137 | 59708887 | 15608002 | 39795955 | -99845856 | 50034695 | 22781486 | 14890465 | 0.000000 | 0.000000
09-04-2025 19:26:10.000 | 10642297 | 106422970 | 106.423 | 61357222 | 15606791 | 39436563 | -99834213 | 50051510 | 22632900 | 14806694 | 0.000000 | 0.000000
09-04-2025 19:26:05.000 | 10539624 | 105396240 | 105.3962 | 59896392 | 15612637 | 39039634 | -99838913 | 50063946 | 22485904 | 14721929 | 0.000000 | 0.000000
09-04-2025 19:26:00.000 | 10571115 | 105711150 | 105.7112 | 62142114 | 15614154 | 39156946 | -99827667 | 50048962 | 22339541 | 14639338 | 0.000000 | 0.000000
09-04-2025 19:25:55.000 | 10560714 | 105607140 | 105.6071 | 60754697 | 15614388 | 39115259 | -99834930 | 50060555 | 22192766 | 14553130 | 0.000000 | 0.000000
09-04-2025 19:25:50.000 | 10569141 | 105691410 | 105.6914 | 60805068 | 15613855 | 39147605 | -99834923 | 50055786 | 22046070 | 14468207 | 0.000000 | 0.000000
09-04-2025 19:25:45.000 | 10627777 | 106277770 | 106.2778 | 62317549 | 15615379 | 39363450 | -99828529 | 50036591 | 21898814 | 14384199 | 0.000000 | 0.000000
09-04-2025 19:25:40.000 | 10620034 | 106200340 | 106.2003 | 63507046 | 15612106 | 39345955 | -99821678 | 50039448 | 21751141 | 14295651 | 0.000000 | 0.000000
09-04-2025 19:25:35.000 | 10660270 | 106602700 | 106.6027 | 61116982 | 15610581 | 39493120 | -99836060 | 50044090 | 21603486 | 14208175 | 0.000000 | 0.000000
09-04-2025 19:25:30.000 | 10630242 | 106302420 | 106.3024 | 62347012 | 15610725 | 39384905 | -99828445 | 50030552 | 21455525 | 14122218 | 0.000000 | 0.000000
09-04-2025 19:25:25.000 | 10547867 | 105478670 | 105.4787 | 65007148 | 15610019 | 39088030 | -99810623 | 50040852 | 21308273 | 14032695 | 0.000000 | 0.000000
09-04-2025 19:25:20.000 | 10444925 | 104449250 | 104.4493 | 63591919 | 15614356 | 38694204 | -99815178 | 50060509 | 21162691 | 13942634 | 0.000000 | 0.000000
09-04-2025 19:25:15.000 | 10496930 | 104969300 | 104.9693 | 62289712 | 15617864 | 38874209 | -99824394 | 50045135 | 21017871 | 13855144 | 0.000000 | 0.000000
09-04-2025 19:25:10.000 | 10638080 | 106380800 | 106.3808 | 66129829 | 15617170 | 39405713 | -99807343 | 50017349 | 20871379 | 13767528 | 0.000000 | 0.000000
09-04-2025 19:25:05.000 | 10688559 | 106885590 | 106.8856 | 67985708 | 15613035 | 39606960 | -99798325 | 50004681 | 20723318 | 13674213 | 0.000000 | 0.000000
09-04-2025 19:25:00.000 | 10724255 | 107242550 | 107.2425 | 66259155 | 15612663 | 39735393 | -99809677 | 49991276 | 20574563 | 13581687 | 0.000000 | 0.000000
09-04-2025 19:24:55.000 | 10681788 | 106817880 | 106.8179 | 68584341 | 15607918 | 39595933 | -99794510 | 49992577 | 20425639 | 13488230 | 0.000000 | 0.000000
09-04-2025 19:24:50.000 | 10588363 | 105883630 | 105.8836 | 65707070 | 15610220 | 39238372 | -99808006 | 50010769 | 20277766 | 13394717 | 0.000000 | 0.000000
09-04-2025 19:24:45.000 | 10516257 | 105162570 | 105.1626 | 65785991 | 15613275 | 38965291 | -99804909 | 50027794 | 20130834 | 13303242 | 0.000000 | 0.000000
09-04-2025 19:24:40.000 | 10516971 | 105169710 | 105.1697 | 67056880 | 15617792 | 38959268 | -99797348 | 50038315 | 19985078 | 13211104 | 0.000000 | 0.000000
09-04-2025 19:24:35.000 | 10695058 | 106950580 | 106.9506 | 65511128 | 15617962 | 39612600 | -99812927 | 49998428 | 19838275 | 13119502 | 0.000000 | 0.000000
09-04-2025 19:24:30.000 | 10888039 | 108880390 | 108.8804 | 67286558 | 15612920 | 40341416 | -99809593 | 49960621 | 19688373 | 13027411 | 0.000000 | 0.000000
09-04-2025 19:24:25.000 | 10879737 | 108797370 | 108.7974 | 64712939 | 15610340 | 40311523 | -99823570 | 49977245 | 19536977 | 12934604 | 0.000000 | 0.000000
09-04-2025 19:24:20.000 | 10828995 | 108289950 | 108.29 | 65823687 | 15607244 | 40134697 | -99815773 | 50007027 | 19386215 | 12843696 | 0.000000 | 0.000000
09-04-2025 19:24:15.000 | 10769543 | 107695430 | 107.6954 | 63518857 | 15611241 | 39899919 | -99826523 | 50018082 | 19236020 | 12754137 | 0.000000 | 0.000000
09-04-2025 19:24:10.000 | 10712341 | 107123410 | 107.1234 | 63133174 | 15607369 | 39697869 | -99826782 | 50025749 | 19086537 | 12665088 | 0.000000 | 0.000000
09-04-2025 19:24:05.000 | 10638013 | 106380130 | 106.3801 | 59992017 | 15609466 | 39411313 | -99841362 | 50035511 | 18938098 | 12579869 | 0.000000 | 0.000000
09-04-2025 19:24:00.000 | 10526777 | 105267770 | 105.2678 | 58459644 | 15613597 | 38986870 | -99846153 | 50048737 | 18790693 | 12497476 | 0.000000 | 0.000000
09-04-2025 19:23:55.000 | 10520920 | 105209200 | 105.2092 | 62377632 | 15618216 | 38962441 | -99824699 | 50065434 | 18644705 | 12413185 | 0.000000 | 0.000000
09-04-2025 19:23:50.000 | 10686112 | 106861120 | 106.8611 | 63402710 | 15621155 | 39567363 | -99824448 | 50038670 | 18497768 | 12326189 | 0.000000 | 0.000000
09-04-2025 19:23:45.000 | 10896735 | 108967350 | 108.9673 | 68533354 | 15611876 | 40379153 | -99802803 | 49997574 | 18348115 | 12234902 | 0.000000 | 0.000000
09-04-2025 19:23:40.000 | 10922431 | 109224310 | 109.2243 | 68024961 | 15608884 | 40480603 | -99806625 | 49990818 | 18196412 | 12140522 | 0.000000 | 0.000000
09-04-2025 19:23:35.000 | 10857252 | 108572520 | 108.5725 | 68579229 | 15610615 | 40236755 | -99801109 | 50021328 | 18044891 | 12045907 | 0.000000 | 0.000000
09-04-2025 19:23:30.000 | 10824297 | 108242970 | 108.243 | 69896211 | 15616634 | 40102600 | -99792160 | 50054569 | 17894365 | 11950129 | 0.000000 | 0.000000
09-04-2025 19:23:25.000 | 10926598 | 109265980 | 109.266 | 70943418 | 15621690 | 40469961 | -99789886 | 50060459 | 17743738 | 11853660 | 0.000000 | 0.000000
09-04-2025 19:23:20.000 | 11123823 | 111238230 | 111.2382 | 70029727 | 15620103 | 41198945 | -99802422 | 50042450 | 17590926 | 11755637 | 0.000000 | 0.000000
09-04-2025 19:23:15.000 | 11291911 | 112919110 | 112.9191 | 71768750 | 15616615 | 41832378 | -99798630 | 50019321 | 17435293 | 11656578 | 0.000000 | 0.000000
09-04-2025 19:23:10.000 | 11436173 | 114361730 | 114.3617 | 72331245 | 15614307 | 42372231 | -99800583 | 49995274 | 17277535 | 11556373 | 0.000000 | 0.000000
09-04-2025 19:23:05.000 | 11463805 | 114638050 | 114.6381 | 75598184 | 15612693 | 42486353 | -99783272 | 50015011 | 17118334 | 11451888 | 0.000000 | 0.000000
09-04-2025 19:23:00.000 | 11532338 | 115323380 | 115.3234 | 73214844 | 15612966 | 42735493 | -99799080 | 50008110 | 16958711 | 11348739 | 0.000000 | 0.000000
09-04-2025 19:22:55.000 | 11597983 | 115979830 | 115.9798 | 73147104 | 15609213 | 42985693 | -99801704 | 49995026 | 16797736 | 11247524 | 0.000000 | 0.000000
09-04-2025 19:22:50.000 | 11538961 | 115389610 | 115.3896 | 72961348 | 15611028 | 42761768 | -99800690 | 50033089 | 16636840 | 11145060 | 0.000000 | 0.000000
09-04-2025 19:22:45.000 | 11519305 | 115193050 | 115.193 | 71960928 | 15618868 | 42665767 | -99805443 | 50061001 | 16476703 | 11044551 | 0.000000 | 0.000000
09-04-2025 19:22:40.000 | 11685202 | 116852020 | 116.852 | 72382437 | 15616860 | 43284404 | -99808701 | 50042671 | 16315767 | 10944456 | 0.000000 | 0.000000
09-04-2025 19:22:35.000 | 11834144 | 118341440 | 118.3414 | 72644575 | 15612852 | 43845776 | -99812119 | 50036762 | 16152468 | 10843131 | 0.000000 | 0.000000
09-04-2025 19:22:30.000 | 11914006 | 119140060 | 119.1401 | 75059722 | 15610626 | 44152148 | -99802132 | 50017265 | 15987734 | 10740914 | 0.000000 | 0.000000
09-04-2025 19:22:25.000 | 11854739 | 118547390 | 118.5474 | 78197788 | 15613237 | 43933711 | -99783150 | 50050076 | 15822610 | 10634626 | 0.000000 | 0.000000
09-04-2025 19:22:20.000 | 11874107 | 118741070 | 118.7411 | 77130571 | 15620443 | 43982144 | -99789696 | 50076019 | 15658057 | 10526104 | 0.000000 | 0.000000
09-04-2025 19:22:15.000 | 12115820 | 121158200 | 121.1582 | 80482065 | 15616957 | 44892070 | -99780098 | 50048794 | 15491932 | 10416289 | 0.000000 | 0.000000
09-04-2025 19:22:10.000 | 12265589 | 122655890 | 122.6559 | 81777021 | 15612871 | 45459517 | -99778481 | 50026165 | 15322974 | 10304091 | 0.000000 | 0.000000
09-04-2025 19:22:05.000 | 12299973 | 122999730 | 122.9997 | 82275137 | 15611719 | 45590718 | -99777031 | 50020729 | 15152418 | 10191332 | 0.000000 | 0.000000
09-04-2025 19:22:00.000 | 12306275 | 123062750 | 123.0627 | 82909902 | 15611991 | 45614717 | -99773819 | 50027458 | 14981416 | 10077149 | 0.000000 | 0.000000
09-04-2025 19:21:55.000 | 12259457 | 122594570 | 122.5946 | 86269570 | 15617773 | 45434736 | -99753319 | 50059238 | 14810781 | 995985107 | 0.000000 | 0.000000
09-04-2025 19:21:50.000 | 12319555 | 123195550 | 123.1955 | 84769277 | 15621000 | 45642676 | -99764107 | 50087566 | 14640454 | 984085022 | 0.000000 | 0.000000
09-04-2025 19:21:45.000 | 12517923 | 125179230 | 125.1792 | 87410703 | 15623364 | 46373335 | -99757088 | 50064835 | 14468350 | 972181458 | 0.000000 | 0.000000
09-04-2025 19:21:40.000 | 12782230 | 127822300 | 127.8223 | 87728154 | 15617084 | 47367544 | -99765305 | 50009750 | 14292770 | 960043579 | 0.000000 | 0.000000
09-04-2025 19:21:35.000 | 12842066 | 128420660 | 128.4207 | 92553301 | 15610334 | 47621128 | -99741302 | 49984310 | 14114827 | 947451355 | 0.000000 | 0.000000
09-04-2025 19:21:30.000 | 12841641 | 128416410 | 128.4164 | 91199316 | 15612076 | 47610811 | -99748772 | 49994827 | 13936466 | 934697205 | 0.000000 | 0.000000
09-04-2025 19:21:25.000 | 12821608 | 128216080 | 128.2161 | 93900957 | 15615427 | 47533804 | -99732895 | 49973576 | 13758227 | 921987366 | 0.000000 | 0.000000
09-04-2025 19:21:20.000 | 12891446 | 128914460 | 128.9145 | 95992061 | 15608135 | 47819521 | -99723923 | 49988174 | 13579755 | 908812866 | 0.000000 | 0.000000
09-04-2025 19:21:15.000 | 12871800 | 128718000 | 128.718 | 92613994 | 15612402 | 47724707 | -99742149 | 50022163 | 13400665 | 895723083 | 0.000000 | 0.000000
09-04-2025 19:21:10.000 | 12867962 | 128679620 | 128.6796 | 87552500 | 15613810 | 47693179 | -99769333 | 50044468 | 13221666 | 883134155 | 0.000000 | 0.000000
09-04-2025 19:21:05.000 | 12878383 | 128783830 | 128.7838 | 87390176 | 15610779 | 47740737 | -99770554 | 50060635 | 13042744 | 870855103 | 0.000000 | 0.000000
09-04-2025 19:21:00.000 | 12877218 | 128772180 | 128.7722 | 85378691 | 15613017 | 47724355 | -99780922 | 50054035 | 12863646 | 858849182 | 0.000000 | 0.000000
09-04-2025 19:20:55.000 | 12904347 | 129043470 | 129.0435 | 86572715 | 15610009 | 47836523 | -99775719 | 50049911 | 12684682 | 846921570 | 0.000000 | 0.000000
09-04-2025 19:20:50.000 | 12851648 | 128516480 | 128.5165 | 87910156 | 15616278 | 47626465 | -99766861 | 50028019 | 12505835 | 834858337 | 0.000000 | 0.000000
09-04-2025 19:20:45.000 | 12905692 | 129056920 | 129.0569 | 92278389 | 15610711 | 47853945 | -99745346 | 50006821 | 12327229 | 822465698 | 0.000000 | 0.000000
09-04-2025 19:20:40.000 | 12901600 | 129016000 | 129.016 | 89576738 | 15612143 | 47827471 | -99759834 | 50047535 | 12147855 | 809748657 | 0.000000 | 0.000000
09-04-2025 19:20:35.000 | 12879781 | 128797810 | 128.7978 | 89262832 | 15609770 | 47753594 | -99760704 | 50047810 | 11968770 | 797293762 | 0.000000 | 0.000000
09-04-2025 19:20:30.000 | 12843802 | 128438020 | 128.438 | 86660928 | 15614104 | 47600874 | -99773148 | 50024651 | 11790182 | 785171265 | 0.000000 | 0.000000
09-04-2025 19:20:25.000 | 12913061 | 129130610 | 129.1306 | 85716201 | 15607658 | 47873838 | -99780411 | 50037563 | 11611454 | 773029419 | 0.000000 | 0.000000
09-04-2025 19:20:20.000 | 12869277 | 128692770 | 128.6928 | 83798262 | 15613860 | 47688594 | -99788673 | 50044575 | 11432250 | 761218262 | 0.000000 | 0.000000
09-04-2025 19:20:15.000 | 12861074 | 128610740 | 128.6107 | 85857871 | 15613223 | 47665215 | -99777908 | 50033604 | 11253387 | 749346741 | 0.000000 | 0.000000
09-04-2025 19:20:10.000 | 12854823 | 128548230 | 128.5482 | 86310508 | 15616206 | 47634380 | -99775352 | 50024063 | 11074513 | 737442871 | 0.000000 | 0.000000
09-04-2025 19:20:05.000 | 12871452 | 128714520 | 128.7145 | 90456377 | 15615925 | 47707070 | -99753967 | 50002338 | 10895896 | 725128479 | 0.000000 | 0.000000
09-04-2025 19:20:00.000 | 12897032 | 128970320 | 128.9703 | 91636943 | 15612496 | 47815098 | -99748528 | 50010811 | 10717144 | 712399780 | 0.000000 | 0.000000
09-04-2025 19:19:55.000 | 12899451 | 128994510 | 128.9945 | 90899902 | 15608871 | 47832954 | -99752632 | 50031860 | 10538124 | 699739014 | 0.000000 | 0.000000
09-04-2025 19:19:50.000 | 12886966 | 128869660 | 128.8697 | 86693477 | 15610013 | 47772852 | -99774490 | 50054520 | 10359126 | 687398132 | 0.000000 | 0.000000
09-04-2025 19:19:45.000 | 12815832 | 128158320 | 128.1583 | 89617754 | 15614849 | 47502949 | -99756401 | 50021450 | 10180623 | 675307983 | 0.000000 | 0.000000
09-04-2025 19:19:40.000 | 12842677 | 128426770 | 128.4268 | 91301172 | 15613050 | 47612012 | -99748253 | 50000706 | 10002603 | 662842468 | 0.000000 | 0.000000
09-04-2025 19:19:35.000 | 12865007 | 128650070 | 128.6501 | 89056553 | 15611899 | 47692656 | -99761261 | 50008858 | 98240508 | 650192871 | 0.000000 | 0.000000
09-04-2025 19:19:30.000 | 12860944 | 128609440 | 128.6094 | 88606426 | 15611957 | 47675688 | -99763512 | 50007240 | 96453359 | 637846008 | 0.000000 | 0.000000
09-04-2025 19:19:25.000 | 12855330 | 128553300 | 128.5533 | 89589746 | 15612197 | 47656689 | -99758041 | 50003448 | 94667021 | 625510559 | 0.000000 | 0.000000
09-04-2025 19:19:20.000 | 12881026 | 128810260 | 128.8103 | 89648984 | 15610400 | 47757070 | -99758682 | 50025253 | 92877158 | 612950684 | 0.000000 | 0.000000
09-04-2025 19:19:15.000 | 12885609 | 128856090 | 128.8561 | 90178818 | 15610166 | 47776074 | -99756004 | 50037937 | 91090117 | 600620850 | 0.000000 | 0.000000
09-04-2025 19:19:10.000 | 12861960 | 128619600 | 128.6196 | 86774160 | 15610627 | 47678867 | -99773193 | 50060143 | 89300586 | 588182678 | 0.000000 | 0.000000
09-04-2025 19:19:05.000 | 12847967 | 128479670 | 128.4797 | 86500996 | 15614849 | 47613677 | -99774124 | 50040344 | 87513652 | 576180481 | 0.000000 | 0.000000
09-04-2025 19:19:00.000 | 12910408 | 129104080 | 129.1041 | 90105195 | 15607606 | 47875400 | -99757332 | 50035255 | 85728350 | 563908752 | 0.000000 | 0.000000
09-04-2025 19:18:55.000 | 12850292 | 128502920 | 128.5029 | 89427686 | 15614071 | 47631899 | -99758720 | 50046032 | 83938027 | 551490479 | 0.000000 | 0.000000
09-04-2025 19:18:50.000 | 12824413 | 128244130 | 128.2441 | 91354805 | 15614587 | 47540137 | -99747238 | 50013939 | 82154688 | 538907104 | 0.000000 | 0.000000
09-04-2025 19:18:45.000 | 12862477 | 128624770 | 128.6248 | 91946523 | 15613135 | 47686323 | -99745476 | 49997551 | 80372266 | 526259216 | 0.000000 | 0.000000
09-04-2025 19:18:40.000 | 12921036 | 129210360 | 129.2104 | 90838564 | 15606241 | 47921401 | -99753784 | 50021172 | 78584561 | 513480286 | 0.000000 | 0.000000
09-04-2025 19:18:35.000 | 12888168 | 128881680 | 128.8817 | 87448760 | 15609889 | 47779668 | -99770599 | 50052647 | 76792788 | 501089081 | 0.000000 | 0.000000
09-04-2025 19:18:30.000 | 12848934 | 128489340 | 128.4893 | 87412100 | 15610798 | 47632607 | -99769394 | 50039944 | 75005107 | 488935272 | 0.000000 | 0.000000
09-04-2025 19:18:25.000 | 12839831 | 128398310 | 128.3983 | 87597031 | 15613601 | 47590034 | -99768089 | 50005611 | 73221416 | 476867676 | 0.000000 | 0.000000
09-04-2025 19:18:20.000 | 12806986 | 128069860 | 128.0699 | 90388389 | 15614087 | 47474668 | -99751869 | 49977020 | 71439126 | 464642914 | 0.000000 | 0.000000
09-04-2025 19:18:15.000 | 12865642 | 128656420 | 128.6564 | 90766885 | 15614248 | 47691592 | -99752060 | 49971127 | 69655088 | 452041656 | 0.000000 | 0.000000
09-04-2025 19:18:10.000 | 12876856 | 128768560 | 128.7686 | 89928379 | 15608835 | 47747285 | -99757027 | 49989990 | 67868843 | 439403442 | 0.000000 | 0.000000
09-04-2025 19:18:05.000 | 12855432 | 128554320 | 128.5543 | 90148193 | 15612998 | 47656011 | -99755028 | 50005062 | 66080396 | 427013245 | 0.000000 | 0.000000
09-04-2025 19:18:00.000 | 12876324 | 128763240 | 128.7632 | 88728828 | 15610446 | 47737207 | -99763420 | 50034267 | 64293540 | 414559082 | 0.000000 | 0.000000
09-04-2025 19:17:55.000 | 12829237 | 128292370 | 128.2924 | 89379717 | 15613447 | 47556050 | -99758194 | 50015560 | 62508496 | 402193604 | 0.000000 | 0.000000
09-04-2025 19:17:50.000 | 12873180 | 128731800 | 128.7318 | 90613408 | 15611906 | 47726807 | -99753181 | 49997681 | 60724141 | 389738556 | 0.000000 | 0.000000
09-04-2025 19:17:45.000 | 12855190 | 128551900 | 128.5519 | 89422314 | 15610942 | 47660063 | -99758934 | 50014553 | 58937637 | 377164063 | 0.000000 | 0.000000
09-04-2025 19:17:40.000 | 12836427 | 128364270 | 128.3643 | 86773525 | 15612291 | 47579878 | -99772293 | 50024948 | 57149595 | 364733765 | 0.000000 | 0.000000
09-04-2025 19:17:35.000 | 12833016 | 128330160 | 128.3302 | 90079609 | 15612505 | 47574609 | -99754547 | 50006721 | 55367197 | 352489227 | 0.000000 | 0.000000
09-04-2025 19:17:30.000 | 12804338 | 128043380 | 128.0434 | 89072168 | 15615096 | 47458379 | -99758919 | 49983120 | 53585508 | 340028046 | 0.000000 | 0.000000
09-04-2025 19:17:25.000 | 12848247 | 128482470 | 128.4825 | 90287520 | 15613369 | 47629146 | -99753998 | 49980556 | 51803779 | 327639526 | 0.000000 | 0.000000
09-04-2025 19:17:20.000 | 12835577 | 128355770 | 128.3558 | 88838467 | 15612479 | 47580938 | -99761337 | 49979000 | 50021187 | 315154510 | 0.000000 | 0.000000
09-04-2025 19:17:15.000 | 12834991 | 128349910 | 128.3499 | 88807295 | 15612828 | 47577656 | -99761482 | 49996014 | 48234912 | 302723022 | 0.000000 | 0.000000
09-04-2025 19:17:10.000 | 12900846 | 129008460 | 129.0085 | 87917451 | 15607239 | 47835630 | -99768593 | 50017532 | 46448398 | 290303436 | 0.000000 | 0.000000
09-04-2025 19:17:05.000 | 12851979 | 128519790 | 128.5198 | 83614424 | 15611161 | 47632681 | -99789032 | 50015049 | 44662500 | 278508728 | 0.000000 | 0.000000
09-04-2025 19:17:00.000 | 12863584 | 128635840 | 128.6358 | 82011260 | 15611570 | 47670391 | -99797386 | 50009941 | 42877407 | 267078491 | 0.000000 | 0.000000
09-04-2025 19:16:55.000 | 12820690 | 128206900 | 128.2069 | 84091504 | 15615843 | 47503916 | -99785583 | 50003510 | 41093130 | 255519150 | 0.000000 | 0.000000
09-04-2025 19:16:50.000 | 12838354 | 128383540 | 128.3835 | 86501396 | 15614611 | 47578799 | -99773788 | 49994289 | 39309006 | 243680649 | 0.000000 | 0.000000
09-04-2025 19:16:45.000 | 12889080 | 128890800 | 128.8908 | 85870527 | 15609060 | 47781509 | -99778809 | 50029373 | 37521191 | 231635529 | 0.000000 | 0.000000
09-04-2025 19:16:40.000 | 12845552 | 128455520 | 128.4555 | 82899502 | 15612045 | 47604824 | -99792404 | 50034843 | 35733362 | 219958481 | 0.000000 | 0.000000
09-04-2025 19:16:35.000 | 12878625 | 128786250 | 128.7862 | 84590313 | 15611181 | 47733159 | -99784981 | 50031155 | 33947537 | 208370789 | 0.000000 | 0.000000
09-04-2025 19:16:30.000 | 12894334 | 128943340 | 128.9433 | 83347832 | 15606905 | 47801182 | -99791740 | 50060169 | 32158560 | 196595734 | 0.000000 | 0.000000
09-04-2025 19:16:25.000 | 12830345 | 128303450 | 128.3034 | 80524434 | 15614523 | 47535605 | -99803635 | 50056145 | 30371079 | 185239670 | 0.000000 | 0.000000
09-04-2025 19:16:20.000 | 12819633 | 128196330 | 128.1963 | 85615645 | 15613364 | 47511333 | -99777733 | 50004944 | 28590710 | 173824860 | 0.000000 | 0.000000
09-04-2025 19:16:15.000 | 12822159 | 128221590 | 128.2216 | 83293467 | 15613691 | 47513970 | -99789673 | 49985332 | 26808064 | 162053833 | 0.000000 | 0.000000
09-04-2025 19:16:10.000 | 12835506 | 128355060 | 128.3551 | 83284434 | 15612889 | 47566001 | -99790154 | 49987488 | 25025500 | 150422272 | 0.000000 | 0.000000
09-04-2025 19:16:05.000 | 12871759 | 128717590 | 128.7176 | 82031279 | 15610643 | 47703472 | -99797546 | 50005379 | 23240225 | 138885574 | 0.000000 | 0.000000
09-04-2025 19:16:00.000 | 12857829 | 128578290 | 128.5783 | 82071191 | 15608052 | 47659976 | -99796906 | 50017872 | 21452539 | 127474648 | 0.000000 | 0.000000
09-04-2025 19:15:55.000 | 12855917 | 128559170 | 128.5592 | 79725415 | 15611837 | 47635801 | -99808266 | 50026581 | 19666205 | 116288475 | 0.000000 | 0.000000
09-04-2025 19:15:50.000 | 12875041 | 128750410 | 128.7504 | 77799478 | 15606730 | 47717803 | -99817932 | 50039833 | 17879694 | 105209328 | 0.000000 | 0.000000
09-04-2025 19:15:45.000 | 12849960 | 128499600 | 128.4996 | 75565762 | 15611288 | 47606387 | -99827538 | 50064087 | 16090089 | 94553429 | 0.000000 | 0.000000
09-04-2025 19:15:40.000 | 12898046 | 128980460 | 128.9805 | 74317603 | 15609344 | 47787026 | -99834412 | 50083092 | 14302452 | 84060608 | 0.000000 | 0.000000
09-04-2025 19:15:35.000 | 12889405 | 128894050 | 128.894 | 74664360 | 15609895 | 47754199 | -99832642 | 50092289 | 12513134 | 73760971 | 0.000000 | 0.000000
09-04-2025 19:15:30.000 | 12856572 | 128565720 | 128.5657 | 73270264 | 15614571 | 47616138 | -99837997 | 50091221 | 10727813 | 63451973 | 0.000000 | 0.000000
09-04-2025 19:15:25.000 | 12834741 | 128347410 | 128.3474 | 75636563 | 15612464 | 47547192 | -99826805 | 50066673 | 894219604 | 53133797 | 0.000000 | 0.000000
09-04-2025 19:15:20.000 | 12836179 | 128361790 | 128.3618 | 76312822 | 15616230 | 47541963 | -99823746 | 50049549 | 715606628 | 42669205 | 0.000000 | 0.000000
09-04-2025 19:15:15.000 | 12894525 | 128945250 | 128.9452 | 78018218 | 15609100 | 47783052 | -99817459 | 50060154 | 536946167 | 31876726 | 0.000000 | 0.000000
09-04-2025 19:15:10.000 | 12893942 | 128939420 | 128.9394 | 76738125 | 15609376 | 47777153 | -99823372 | 50097225 | 357661072 | 21151646 | 0.000000 | 0.000000
09-04-2025 19:15:05.000 | 12882727 | 128827270 | 128.8273 | 76094102 | 15610906 | 47729971 | -99826012 | 50111931 | 178673355 | 10586737 | 0.000000 | 0.000000
09-04-2025 19:15:00.000 | 12864984 | 128649840 | 128.6498 | 77874194 | 15613379 | 47660562 | -99817299 | 50082867 | 32086918 | 15821642 | 0.000000 | 0.000000
09-04-2025 19:14:55.000 | 12888891 | 128888910 | 128.8889 | 77733535 | 15612844 | 47750117 | -99818626 | 50062874 | 31908324 | 15714783 | 0.000000 | 0.000000
09-04-2025 19:14:50.000 | 12924459 | 129244590 | 129.2446 | 81279551 | 15610292 | 47897437 | -99802841 | 50087498 | 31729270 | 15606886 | 0.000000 | 0.000000
09-04-2025 19:14:45.000 | 12894488 | 128944880 | 128.9449 | 75982871 | 15610083 | 47775151 | -99826836 | 50098816 | 31550182 | 15496257 | 0.000000 | 0.000000
09-04-2025 19:14:40.000 | 12837715 | 128377150 | 128.3772 | 75882358 | 15614442 | 47552417 | -99825760 | 50070972 | 31371477 | 15390853 | 0.000000 | 0.000000
09-04-2025 19:14:35.000 | 12847601 | 128476010 | 128.476 | 76873979 | 15613524 | 47593975 | -99821465 | 50035343 | 31193064 | 15285275 | 0.000000 | 0.000000
09-04-2025 19:14:30.000 | 12825948 | 128259480 | 128.2595 | 79492319 | 15613810 | 47518721 | -99808487 | 50022030 | 31014541 | 15176447 | 0.000000 | 0.000000
09-04-2025 19:14:25.000 | 12854330 | 128543300 | 128.5433 | 79666758 | 15613354 | 47625190 | -99808495 | 50010948 | 30836217 | 15065826 | 0.000000 | 0.000000
09-04-2025 19:14:20.000 | 12889001 | 128890010 | 128.89 | 79644849 | 15609507 | 47764971 | -99809624 | 50029011 | 30657457 | 14953835 | 0.000000 | 0.000000
09-04-2025 19:14:15.000 | 12883259 | 128832590 | 128.8326 | 77957632 | 15611011 | 47735439 | -99817421 | 50061226 | 30478336 | 14843478 | 0.000000 | 0.000000
09-04-2025 19:14:10.000 | 12858100 | 128581000 | 128.581 | 75167788 | 15611140 | 47635859 | -99829559 | 50053047 | 30299781 | 14736426 | 0.000000 | 0.000000
09-04-2025 19:14:05.000 | 12857115 | 128571150 | 128.5711 | 75226987 | 15614052 | 47623823 | -99829269 | 50023315 | 30121322 | 14632684 | 0.000000 | 0.000000
09-04-2025 19:14:00.000 | 12891533 | 128915330 | 128.9153 | 76195933 | 15611712 | 47759814 | -99825783 | 50018772 | 29942854 | 14527915 | 0.000000 | 0.000000
09-04-2025 19:13:55.000 | 12862783 | 128627830 | 128.6278 | 73706187 | 15611105 | 47650127 | -99836227 | 50046898 | 29763881 | 14422347 | 0.000000 | 0.000000
09-04-2025 19:13:50.000 | 12844887 | 128448870 | 128.4489 | 72872705 | 15613990 | 47573955 | -99839455 | 50048248 | 29585025 | 14321194 | 0.000000 | 0.000000
09-04-2025 19:13:45.000 | 12866140 | 128661400 | 128.6614 | 72778506 | 15611365 | 47659819 | -99840401 | 50050938 | 29406414 | 14219724 | 0.000000 | 0.000000
09-04-2025 19:13:40.000 | 12897415 | 128974150 | 128.9742 | 71846899 | 15609641 | 47778706 | -99845200 | 50075443 | 29227293 | 14118737 | 0.000000 | 0.000000
09-04-2025 19:13:35.000 | 12825430 | 128254300 | 128.2543 | 71765332 | 15615881 | 47493726 | -99843819 | 50078072 | 29048424 | 14018422 | 0.000000 | 0.000000
09-04-2025 19:13:30.000 | 12869516 | 128695160 | 128.6952 | 72465581 | 15613188 | 47666274 | -99841850 | 50062233 | 28870039 | 13919156 | 0.000000 | 0.000000
09-04-2025 19:13:25.000 | 12896021 | 128960210 | 128.9602 | 72621636 | 15610777 | 47771680 | -99841820 | 50075249 | 28691223 | 13816898 | 0.000000 | 0.000000
09-04-2025 19:13:20.000 | 12849354 | 128493540 | 128.4935 | 71035293 | 15613810 | 47586743 | -99847534 | 50076843 | 28512338 | 13716611 | 0.000000 | 0.000000
09-04-2025 19:13:15.000 | 12870681 | 128706810 | 128.7068 | 72840947 | 15613281 | 47671084 | -99840240 | 50064217 | 28333752 | 13616995 | 0.000000 | 0.000000
09-04-2025 19:13:10.000 | 12844737 | 128447370 | 128.4474 | 72266636 | 15613315 | 47573901 | -99842110 | 50066772 | 28155133 | 13516062 | 0.000000 | 0.000000
09-04-2025 19:13:05.000 | 12867542 | 128675420 | 128.6754 | 71466509 | 15609973 | 47666548 | -99846123 | 50079552 | 27976236 | 13415474 | 0.000000 | 0.000000
09-04-2025 19:13:00.000 | 12817715 | 128177150 | 128.1772 | 69866846 | 15612924 | 47470674 | -99851776 | 50086872 | 27797506 | 13316936 | 0.000000 | 0.000000
09-04-2025 19:12:55.000 | 12876985 | 128769850 | 128.7698 | 68259780 | 15611125 | 47691597 | -99859795 | 50090996 | 27618871 | 13220565 | 0.000000 | 0.000000
09-04-2025 19:12:50.000 | 12897365 | 128973650 | 128.9736 | 68711313 | 15607896 | 47778618 | -99858391 | 50103184 | 27439980 | 13124813 | 0.000000 | 0.000000
09-04-2025 19:12:45.000 | 12860547 | 128605470 | 128.6055 | 64673789 | 15612866 | 47618628 | -99873795 | 50131973 | 27260764 | 13032217 | 0.000000 | 0.000000
09-04-2025 19:12:40.000 | 12860395 | 128603950 | 128.6039 | 66037915 | 15615327 | 47613066 | -99868423 | 50116184 | 27082436 | 12942134 | 0.000000 | 0.000000
09-04-2025 19:12:35.000 | 12918523 | 129185230 | 129.1852 | 67691055 | 15607523 | 47854893 | -99862999 | 50133514 | 26903580 | 12848000 | 0.000000 | 0.000000
09-04-2025 19:12:30.000 | 12896787 | 128967870 | 128.9679 | 64399365 | 15610274 | 47759888 | -99875557 | 50160641 | 26724223 | 12756401 | 0.000000 | 0.000000
09-04-2025 19:12:25.000 | 12873013 | 128730130 | 128.7301 | 63093325 | 15613754 | 47659019 | -99880104 | 50145054 | 26545443 | 12668274 | 0.000000 | 0.000000
09-04-2025 19:12:20.000 | 12865873 | 128658730 | 128.6587 | 64782461 | 15609727 | 47648159 | -99873474 | 50146271 | 26366580 | 12578441 | 0.000000 | 0.000000
09-04-2025 19:12:15.000 | 12870458 | 128704580 | 128.7046 | 63789053 | 15612423 | 47655103 | -99877403 | 50160713 | 26187518 | 12489832 | 0.000000 | 0.000000
09-04-2025 19:12:10.000 | 12889757 | 128897570 | 128.8976 | 63896245 | 15610839 | 47731284 | -99877357 | 50159447 | 26008725 | 12401666 | 0.000000 | 0.000000
09-04-2025 19:12:05.000 | 12853333 | 128533330 | 128.5333 | 63757896 | 15614321 | 47585835 | -99877197 | 50148808 | 25829961 | 12313955 | 0.000000 | 0.000000
09-04-2025 19:12:00.000 | 12868859 | 128688590 | 128.6886 | 64874937 | 15613545 | 47647495 | -99873169 | 50139206 | 25651332 | 12224572 | 0.000000 | 0.000000
09-04-2025 19:11:55.000 | 12901617 | 129016170 | 129.0162 | 64744189 | 15609021 | 47782148 | -99874321 | 50158154 | 25472254 | 12134139 | 0.000000 | 0.000000
09-04-2025 19:11:50.000 | 12876058 | 128760580 | 128.7606 | 63790229 | 15612845 | 47674302 | -99877502 | 50168430 | 25293188 | 12046049 | 0.000000 | 0.000000
09-04-2025 19:11:45.000 | 12908659 | 129086590 | 129.0866 | 66226890 | 15612174 | 47801411 | -99868652 | 50162800 | 25114516 | 11956727 | 0.000000 | 0.000000
09-04-2025 19:11:40.000 | 12886730 | 128867300 | 128.8673 | 65638730 | 15607699 | 47732866 | -99870529 | 50168987 | 24935506 | 11865166 | 0.000000 | 0.000000
09-04-2025 19:11:35.000 | 12861697 | 128616970 | 128.617 | 63899849 | 15611290 | 47626318 | -99876808 | 50161606 | 24756850 | 11775409 | 0.000000 | 0.000000
09-04-2025 19:11:30.000 | 12810329 | 128103290 | 128.1033 | 64885552 | 15615534 | 47425640 | -99871971 | 50123257 | 24578721 | 11686182 | 0.000000 | 0.000000
09-04-2025 19:11:25.000 | 12868704 | 128687040 | 128.687 | 67705508 | 15612023 | 47657090 | -99861885 | 50103912 | 24400416 | 11594880 | 0.000000 | 0.000000
09-04-2025 19:11:20.000 | 12881918 | 128819180 | 128.8192 | 67737085 | 15609161 | 47714688 | -99862038 | 50134785 | 24221396 | 11501234 | 0.000000 | 0.000000
09-04-2025 19:11:15.000 | 12873697 | 128736970 | 128.737 | 65088071 | 15611306 | 47672700 | -99872437 | 50175079 | 24042293 | 11408164 | 0.000000 | 0.000000
09-04-2025 19:11:10.000 | 12893588 | 128935880 | 128.9359 | 64102217 | 15611712 | 47743232 | -99876640 | 50178894 | 23863473 | 11318599 | 0.000000 | 0.000000
09-04-2025 19:11:05.000 | 12918020 | 129180200 | 129.1802 | 62788101 | 15609142 | 47838906 | -99882088 | 50182472 | 23684529 | 11230333 | 0.000000 | 0.000000
09-04-2025 19:11:00.000 | 12901044 | 129010440 | 129.0104 | 60814683 | 15611357 | 47765981 | -99889076 | 50193008 | 23505350 | 11144613 | 0.000000 | 0.000000
09-04-2025 19:10:55.000 | 12899903 | 128999030 | 128.999 | 60456206 | 15610081 | 47765078 | -99890358 | 50190701 | 23326313 | 11060742 | 0.000000 | 0.000000
09-04-2025 19:10:50.000 | 12888778 | 128887780 | 128.8878 | 59816255 | 15612488 | 47715610 | -99892479 | 50176224 | 23147529 | 10977915 | 0.000000 | 0.000000
09-04-2025 19:10:45.000 | 12858197 | 128581970 | 128.582 | 63317676 | 15613971 | 47604404 | -99878975 | 50163593 | 22968730 | 10892943 | 0.000000 | 0.000000
09-04-2025 19:10:40.000 | 12886901 | 128869010 | 128.869 | 62605815 | 15610141 | 47720552 | -99882202 | 50176815 | 22789811 | 10805006 | 0.000000 | 0.000000
09-04-2025 19:10:35.000 | 12881215 | 128812150 | 128.8122 | 63000264 | 15610441 | 47699331 | -99880615 | 50187561 | 22610750 | 10717753 | 0.000000 | 0.000000
09-04-2025 19:10:30.000 | 12888675 | 128886750 | 128.8868 | 61958896 | 15611468 | 47721797 | -99884651 | 50183178 | 22431676 | 10631573 | 0.000000 | 0.000000
09-04-2025 19:10:25.000 | 12908255 | 129082550 | 129.0825 | 61119976 | 15606674 | 47807783 | -99888092 | 50197922 | 22252535 | 10544955 | 0.000000 | 0.000000
09-04-2025 19:10:20.000 | 12856178 | 128561780 | 128.5618 | 60063843 | 15611535 | 47599297 | -99891045 | 50195351 | 22073371 | 10461472 | 0.000000 | 0.000000
09-04-2025 19:10:15.000 | 12869264 | 128692640 | 128.6926 | 61292891 | 15611768 | 47648394 | -99886772 | 50177040 | 21894678 | 10377328 | 0.000000 | 0.000000
09-04-2025 19:10:10.000 | 12856456 | 128564560 | 128.5646 | 61099297 | 15612913 | 47596821 | -99887260 | 50180428 | 21715805 | 10291941 | 0.000000 | 0.000000
09-04-2025 19:10:05.000 | 12905730 | 129057300 | 129.0573 | 60779102 | 15609561 | 47788779 | -99889290 | 50186474 | 21536979 | 10207517 | 0.000000 | 0.000000
09-04-2025 19:10:00.000 | 12874029 | 128740290 | 128.7403 | 58846538 | 15613011 | 47658110 | -99895699 | 50186733 | 21357926 | 10124222 | 0.000000 | 0.000000
09-04-2025 19:09:55.000 | 12897998 | 128979980 | 128.98 | 61213579 | 15609370 | 47761694 | -99887566 | 50168804 | 21179225 | 10041757 | 0.000000 | 0.000000
09-04-2025 19:09:50.000 | 12925126 | 129251260 | 129.2513 | 58078594 | 15605742 | 47867529 | -99899193 | 50218330 | 20999828 | 995887390 | 0.000000 | 0.000000
09-04-2025 19:09:45.000 | 12898151 | 128981510 | 128.9815 | 55097339 | 15612150 | 47743916 | -99908890 | 50227131 | 20820875 | 988159363 | 0.000000 | 0.000000
09-04-2025 19:09:40.000 | 12869519 | 128695190 | 128.6952 | 56959683 | 15613081 | 47637593 | -99902199 | 50202576 | 20642074 | 980508057 | 0.000000 | 0.000000
09-04-2025 19:09:35.000 | 12953587 | 129535870 | 129.5359 | 57572744 | 15607382 | 47967612 | -99901375 | 50220524 | 20463051 | 972494080 | 0.000000 | 0.000000
09-04-2025 19:09:30.000 | 12872882 | 128728820 | 128.7288 | 55806519 | 15610972 | 47654727 | -99906166 | 50229282 | 20283859 | 964690735 | 0.000000 | 0.000000
09-04-2025 19:09:25.000 | 12844725 | 128447250 | 128.4472 | 57876406 | 15613114 | 47547407 | -99898643 | 50216599 | 20105004 | 956894348 | 0.000000 | 0.000000
09-04-2025 19:09:20.000 | 12858473 | 128584730 | 128.5847 | 55858862 | 15611830 | 47599380 | -99905777 | 50213654 | 19926527 | 948957458 | 0.000000 | 0.000000
09-04-2025 19:09:15.000 | 12880600 | 128806000 | 128.806 | 57472671 | 15608001 | 47695186 | -99900604 | 50220085 | 19747527 | 941041931 | 0.000000 | 0.000000
09-04-2025 19:09:10.000 | 12892377 | 128923770 | 128.9238 | 56606323 | 15609999 | 47730825 | -99903748 | 50230145 | 19568506 | 933173645 | 0.000000 | 0.000000
09-04-2025 19:09:05.000 | 12851038 | 128510380 | 128.5104 | 56085015 | 15613059 | 47568130 | -99904900 | 50222542 | 19389721 | 925370544 | 0.000000 | 0.000000
09-04-2025 19:09:00.000 | 12831653 | 128316530 | 128.3165 | 60074150 | 15614661 | 47498110 | -99890587 | 50177261 | 19211355 | 917406921 | 0.000000 | 0.000000
09-04-2025 19:08:55.000 | 12840023 | 128400230 | 128.4002 | 62219883 | 15612352 | 47539824 | -99882797 | 50157139 | 19033180 | 908889648 | 0.000000 | 0.000000
09-04-2025 19:08:50.000 | 12862596 | 128625960 | 128.626 | 60417993 | 15611074 | 47624053 | -99889862 | 50159687 | 18854844 | 900390503 | 0.000000 | 0.000000
09-04-2025 19:08:45.000 | 12850021 | 128500210 | 128.5002 | 61216841 | 15611783 | 47577207 | -99886719 | 50175968 | 18676018 | 891991150 | 0.000000 | 0.000000
09-04-2025 19:08:40.000 | 12884170 | 128841700 | 128.8417 | 60128242 | 15612333 | 47699272 | -99891281 | 50188263 | 18497203 | 883483276 | 0.000000 | 0.000000
09-04-2025 19:08:35.000 | 12858717 | 128587170 | 128.5872 | 60254673 | 15612052 | 47606392 | -99890388 | 50188789 | 18318469 | 875093018 | 0.000000 | 0.000000
09-04-2025 19:08:30.000 | 12900863 | 129008630 | 129.0086 | 59459453 | 15609041 | 47769961 | -99893959 | 50210472 | 18139451 | 866830505 | 0.000000 | 0.000000
09-04-2025 19:08:25.000 | 12898230 | 128982300 | 128.9823 | 55590098 | 15611791 | 47745732 | -99907249 | 50236675 | 17960328 | 858908569 | 0.000000 | 0.000000
09-04-2025 19:08:20.000 | 12865236 | 128652360 | 128.6524 | 55856626 | 15609626 | 47630430 | -99905884 | 50227844 | 17781514 | 851143799 | 0.000000 | 0.000000
09-04-2025 19:08:15.000 | 12861050 | 128610500 | 128.6105 | 55642056 | 15613251 | 47604185 | -99906540 | 50211380 | 17602801 | 843513916 | 0.000000 | 0.000000
09-04-2025 19:08:10.000 | 12850345 | 128503450 | 128.5034 | 56742119 | 15612968 | 47566729 | -99902657 | 50200466 | 17424186 | 835670105 | 0.000000 | 0.000000
09-04-2025 19:08:05.000 | 12852220 | 128522200 | 128.5222 | 58365381 | 15611395 | 47582207 | -99897041 | 50203987 | 17245541 | 827690918 | 0.000000 | 0.000000
09-04-2025 19:08:00.000 | 12864550 | 128645500 | 128.6455 | 56796489 | 15611957 | 47624312 | -99902679 | 50216530 | 17066660 | 819739746 | 0.000000 | 0.000000
09-04-2025 19:07:55.000 | 12894288 | 128942880 | 128.9429 | 58364995 | 15610283 | 47740981 | -99897713 | 50215775 | 16887816 | 811762817 | 0.000000 | 0.000000
09-04-2025 19:07:50.000 | 12848687 | 128486870 | 128.4869 | 56036206 | 15613549 | 47557964 | -99905037 | 50222996 | 16708738 | 803771240 | 0.000000 | 0.000000
09-04-2025 19:07:45.000 | 12812142 | 128121420 | 128.1214 | 60218730 | 15613692 | 47429365 | -99889725 | 50174519 | 16530572 | 795723022 | 0.000000 | 0.000000
09-04-2025 19:07:40.000 | 12811893 | 128118930 | 128.1189 | 62267373 | 15612877 | 47434668 | -99882103 | 50158974 | 16352147 | 787248840 | 0.000000 | 0.000000
09-04-2025 19:07:35.000 | 12846805 | 128468050 | 128.4681 | 60978818 | 15611013 | 47566816 | -99887535 | 50152241 | 16173747 | 778568481 | 0.000000 | 0.000000
09-04-2025 19:07:30.000 | 12792784 | 127927840 | 127.9278 | 61842441 | 15614138 | 47359165 | -99883362 | 50109486 | 15995887 | 770080139 | 0.000000 | 0.000000
09-04-2025 19:07:25.000 | 12823821 | 128238210 | 128.2382 | 65345361 | 15612124 | 47486396 | -99870422 | 50096668 | 15817877 | 761276306 | 0.000000 | 0.000000
09-04-2025 19:07:20.000 | 12869030 | 128690300 | 128.6903 | 62751821 | 15608877 | 47658521 | -99881325 | 50134422 | 15639500 | 752298584 | 0.000000 | 0.000000
09-04-2025 19:07:15.000 | 12812802 | 128128020 | 128.128 | 61291689 | 15614001 | 47432773 | -99885780 | 50134766 | 15461336 | 743702271 | 0.000000 | 0.000000
09-04-2025 19:07:10.000 | 12898656 | 128986560 | 128.9866 | 60591992 | 15608204 | 47766318 | -99889847 | 50158833 | 15282762 | 735217041 | 0.000000 | 0.000000
09-04-2025 19:07:05.000 | 12846839 | 128468390 | 128.4684 | 56675898 | 15611207 | 47559092 | -99902824 | 50186523 | 15104062 | 727033997 | 0.000000 | 0.000000
09-04-2025 19:07:00.000 | 12863983 | 128639830 | 128.6398 | 56366968 | 15607853 | 47632173 | -99904137 | 50194302 | 14925472 | 719195496 | 0.000000 | 0.000000
09-04-2025 19:06:55.000 | 12842498 | 128424980 | 128.425 | 53972148 | 15612385 | 47535107 | -99911804 | 50189293 | 14746913 | 711598083 | 0.000000 | 0.000000
09-04-2025 19:06:50.000 | 12818927 | 128189270 | 128.1893 | 53721421 | 15610773 | 47452656 | -99912300 | 50167843 | 14568690 | 704091919 | 0.000000 | 0.000000
09-04-2025 19:06:45.000 | 12823780 | 128237800 | 128.2378 | 56137183 | 15613828 | 47465166 | -99904320 | 50162853 | 14390453 | 696551636 | 0.000000 | 0.000000
09-04-2025 19:06:40.000 | 12811607 | 128116070 | 128.1161 | 55637173 | 15612171 | 47424277 | -99905838 | 50154339 | 14212438 | 688725769 | 0.000000 | 0.000000
09-04-2025 19:06:35.000 | 12799700 | 127997000 | 127.997 | 58185630 | 15610307 | 47391523 | -99896835 | 50161510 | 14034160 | 680800415 | 0.000000 | 0.000000
09-04-2025 19:06:30.000 | 12823532 | 128235320 | 128.2353 | 56178335 | 15611337 | 47472144 | -99904175 | 50179527 | 13855924 | 672835632 | 0.000000 | 0.000000
09-04-2025 19:06:25.000 | 12847037 | 128470370 | 128.4704 | 55792358 | 15608589 | 47566279 | -99905830 | 50191147 | 13677622 | 665099304 | 0.000000 | 0.000000
09-04-2025 19:06:20.000 | 12818846 | 128188460 | 128.1885 | 53535415 | 15611280 | 47450776 | -99912903 | 50213459 | 13499117 | 657462402 | 0.000000 | 0.000000
09-04-2025 19:06:15.000 | 12781645 | 127816450 | 127.8165 | 51568350 | 15615362 | 47298071 | -99918709 | 50184822 | 13321144 | 650161316 | 0.000000 | 0.000000
09-04-2025 19:06:10.000 | 12833011 | 128330110 | 128.3301 | 52480635 | 15611545 | 47500454 | -99916481 | 50162178 | 13143330 | 642903992 | 0.000000 | 0.000000
09-04-2025 19:06:05.000 | 12817222 | 128172220 | 128.1722 | 53737402 | 15613110 | 47439233 | -99912224 | 50169216 | 12965042 | 635513245 | 0.000000 | 0.000000
09-04-2025 19:06:00.000 | 12795363 | 127953630 | 127.9536 | 52865488 | 15612390 | 47360811 | -99914757 | 50187801 | 12786695 | 627915405 | 0.000000 | 0.000000
09-04-2025 19:05:55.000 | 12798830 | 127988300 | 127.9883 | 54142544 | 15613216 | 47371992 | -99910645 | 50177578 | 12608675 | 620478088 | 0.000000 | 0.000000
09-04-2025 19:05:50.000 | 12767463 | 127674630 | 127.6746 | 53548828 | 15614092 | 47252959 | -99912163 | 50172222 | 12430601 | 612925110 | 0.000000 | 0.000000
09-04-2025 19:05:45.000 | 12809201 | 128092010 | 128.092 | 53169761 | 15611867 | 47413081 | -99913963 | 50172173 | 12252878 | 605519775 | 0.000000 | 0.000000
09-04-2025 19:05:40.000 | 12823876 | 128238760 | 128.2388 | 53252930 | 15610427 | 47471211 | -99913887 | 50171989 | 12074897 | 598154663 | 0.000000 | 0.000000
09-04-2025 19:05:35.000 | 12801039 | 128010390 | 128.0104 | 52657471 | 15613367 | 47376997 | -99915504 | 50177483 | 11896957 | 590827576 | 0.000000 | 0.000000
09-04-2025 19:05:30.000 | 12836863 | 128368630 | 128.3686 | 52424956 | 15609697 | 47520317 | -99916710 | 50194332 | 11719005 | 583450439 | 0.000000 | 0.000000
09-04-2025 19:05:25.000 | 12825421 | 128254210 | 128.2542 | 52393604 | 15611164 | 47473340 | -99916664 | 50219746 | 11540559 | 576192139 | 0.000000 | 0.000000
09-04-2025 19:05:20.000 | 12866913 | 128669130 | 128.6691 | 52689653 | 15610627 | 47629272 | -99916260 | 50221401 | 11362554 | 568906799 | 0.000000 | 0.000000
09-04-2025 19:05:15.000 | 12824966 | 128249660 | 128.2497 | 52485122 | 15611045 | 47472236 | -99916367 | 50218086 | 11184418 | 561588440 | 0.000000 | 0.000000
09-04-2025 19:05:10.000 | 12831353 | 128313530 | 128.3135 | 49638657 | 15609814 | 47495420 | -99925255 | 50228737 | 11006171 | 554425110 | 0.000000 | 0.000000
09-04-2025 19:05:05.000 | 12831109 | 128311090 | 128.3111 | 48806475 | 15609672 | 47494165 | -99927734 | 50232548 | 10828072 | 547628967 | 0.000000 | 0.000000
09-04-2025 19:05:00.000 | 12806633 | 128066330 | 128.0663 | 49336504 | 15613093 | 47393804 | -99925880 | 50216454 | 10650219 | 540804626 | 0.000000 | 0.000000
09-04-2025 19:04:55.000 | 12784502 | 127845020 | 127.845 | 49859023 | 15610927 | 47319556 | -99924042 | 50201168 | 10472399 | 533857361 | 0.000000 | 0.000000
09-04-2025 19:04:50.000 | 12791622 | 127916220 | 127.9162 | 50863291 | 15615473 | 47333501 | -99921036 | 50170616 | 10294838 | 526933777 | 0.000000 | 0.000000
09-04-2025 19:04:45.000 | 12835830 | 128358300 | 128.3583 | 56286729 | 15605408 | 47535845 | -99903992 | 50184319 | 10117163 | 519526855 | 0.000000 | 0.000000
09-04-2025 19:04:40.000 | 12767976 | 127679760 | 127.6798 | 52992212 | 15610320 | 47264766 | -99913979 | 50215637 | 99390000 | 511910919 | 0.000000 | 0.000000
09-04-2025 19:04:35.000 | 12752203 | 127522030 | 127.522 | 50809331 | 15615922 | 47185981 | -99920715 | 50195919 | 97616924 | 504689514 | 0.000000 | 0.000000
09-04-2025 19:04:30.000 | 12753860 | 127538600 | 127.5386 | 55308047 | 15616087 | 47198452 | -99906105 | 50165928 | 95845049 | 497347382 | 0.000000 | 0.000000
09-04-2025 19:04:25.000 | 12840223 | 128402230 | 128.4022 | 56951680 | 15609922 | 47539023 | -99901779 | 50190472 | 94068467 | 489539795 | 0.000000 | 0.000000
09-04-2025 19:04:20.000 | 12834172 | 128341720 | 128.3417 | 52386831 | 15611368 | 47505352 | -99916794 | 50219246 | 92286328 | 481925781 | 0.000000 | 0.000000
09-04-2025 19:04:15.000 | 12770171 | 127701710 | 127.7017 | 53831211 | 15614576 | 47261792 | -99911270 | 50207508 | 90505576 | 474651520 | 0.000000 | 0.000000
09-04-2025 19:04:10.000 | 12816992 | 128169920 | 128.1699 | 54093804 | 15610495 | 47446890 | -99911057 | 50208359 | 88726709 | 467100464 | 0.000000 | 0.000000
09-04-2025 19:04:05.000 | 12737754 | 127377540 | 127.3775 | 52901899 | 15617283 | 47131826 | -99913864 | 50196438 | 86947324 | 459625885 | 0.000000 | 0.000000
09-04-2025 19:04:00.000 | 12775585 | 127755850 | 127.7558 | 57165234 | 15615612 | 47283364 | -99900040 | 50146248 | 85175059 | 452017853 | 0.000000 | 0.000000
09-04-2025 19:03:55.000 | 12806763 | 128067630 | 128.0676 | 58948071 | 15610287 | 47418560 | -99894234 | 50141430 | 83399189 | 443998657 | 0.000000 | 0.000000
09-04-2025 19:03:50.000 | 12822093 | 128220930 | 128.2209 | 56437261 | 15610532 | 47469360 | -99903275 | 50176773 | 81617197 | 435995148 | 0.000000 | 0.000000
09-04-2025 19:03:45.000 | 12798302 | 127983020 | 127.983 | 54137988 | 15610113 | 47378896 | -99910652 | 50191853 | 79838398 | 428246887 | 0.000000 | 0.000000
09-04-2025 19:03:40.000 | 12799225 | 127992250 | 127.9922 | 55502119 | 15612450 | 47377695 | -99906113 | 50192997 | 78060132 | 420742310 | 0.000000 | 0.000000
09-04-2025 19:03:35.000 | 12804577 | 128045770 | 128.0458 | 55257476 | 15612457 | 47397002 | -99907013 | 50199459 | 76280054 | 413113007 | 0.000000 | 0.000000
09-04-2025 19:03:30.000 | 12813408 | 128134080 | 128.1341 | 53420142 | 15611777 | 47428350 | -99913208 | 50184231 | 74503887 | 405477936 | 0.000000 | 0.000000
09-04-2025 19:03:25.000 | 12810046 | 128100460 | 128.1005 | 56277603 | 15611892 | 47420107 | -99903633 | 50167908 | 72725249 | 397925751 | 0.000000 | 0.000000
09-04-2025 19:03:20.000 | 12793700 | 127937000 | 127.937 | 56794448 | 15611588 | 47361523 | -99901611 | 50197128 | 70944780 | 389995758 | 0.000000 | 0.000000
09-04-2025 19:03:15.000 | 12780330 | 127803300 | 127.8033 | 57677261 | 15613024 | 47310356 | -99898323 | 50184860 | 69170093 | 382128784 | 0.000000 | 0.000000
09-04-2025 19:03:10.000 | 12754535 | 127545350 | 127.5453 | 60160947 | 15612755 | 47219063 | -99888947 | 50167332 | 67395029 | 373935394 | 0.000000 | 0.000000
09-04-2025 19:03:05.000 | 12791139 | 127911390 | 127.9114 | 60967593 | 15609247 | 47366460 | -99886604 | 50152157 | 65623223 | 365583618 | 0.000000 | 0.000000
09-04-2025 19:03:00.000 | 12746852 | 127468520 | 127.4685 | 61101924 | 15615320 | 47184795 | -99885307 | 50139870 | 63851094 | 357196198 | 0.000000 | 0.000000
09-04-2025 19:02:55.000 | 12759454 | 127594540 | 127.5945 | 62108599 | 15616334 | 47230518 | -99881737 | 50128639 | 62079883 | 348601074 | 0.000000 | 0.000000
09-04-2025 19:02:50.000 | 12841071 | 128410710 | 128.4107 | 62577456 | 15607111 | 47561284 | -99881470 | 50160725 | 60304380 | 339695435 | 0.000000 | 0.000000
09-04-2025 19:02:45.000 | 12747564 | 127475640 | 127.4756 | 61131260 | 15616772 | 47183550 | -99885216 | 50157974 | 58528164 | 331175598 | 0.000000 | 0.000000
09-04-2025 19:02:40.000 | 12828296 | 128282960 | 128.283 | 66357197 | 15609222 | 47514604 | -99866486 | 50155052 | 56754102 | 322315186 | 0.000000 | 0.000000
09-04-2025 19:02:35.000 | 12746923 | 127469230 | 127.4692 | 62935220 | 15613051 | 47194941 | -99878342 | 50170792 | 54976489 | 313268250 | 0.000000 | 0.000000
09-04-2025 19:02:30.000 | 12759977 | 127599770 | 127.5998 | 65801968 | 15615586 | 47240835 | -99867294 | 50149406 | 53203721 | 304315155 | 0.000000 | 0.000000
09-04-2025 19:02:25.000 | 12809291 | 128092910 | 128.0929 | 71965234 | 15612438 | 47444863 | -99842552 | 50143105 | 51429478 | 294854156 | 0.000000 | 0.000000
09-04-2025 19:02:20.000 | 12783647 | 127836470 | 127.8365 | 72441792 | 15611523 | 47353936 | -99839828 | 50166283 | 49651558 | 284728333 | 0.000000 | 0.000000
09-04-2025 19:02:15.000 | 12795933 | 127959330 | 127.9593 | 73405693 | 15611074 | 47403032 | -99835861 | 50144897 | 47879336 | 274682251 | 0.000000 | 0.000000
09-04-2025 19:02:10.000 | 12764152 | 127641520 | 127.6415 | 71907256 | 15612001 | 47279351 | -99841690 | 50162395 | 46100830 | 264494995 | 0.000000 | 0.000000
09-04-2025 19:02:05.000 | 12760127 | 127601270 | 127.6013 | 75282773 | 15613529 | 47267148 | -99826408 | 50138054 | 44329648 | 254368118 | 0.000000 | 0.000000
09-04-2025 19:02:00.000 | 12806631 | 128066310 | 128.0663 | 74031011 | 15608411 | 47451768 | -99833336 | 50135174 | 42556714 | 243969681 | 0.000000 | 0.000000
09-04-2025 19:01:55.000 | 12789711 | 127897110 | 127.8971 | 72271235 | 15610146 | 47380649 | -99840729 | 50151821 | 40779902 | 233835907 | 0.000000 | 0.000000
09-04-2025 19:01:50.000 | 12796515 | 127965150 | 127.9651 | 71376567 | 15610220 | 47403076 | -99844803 | 50162487 | 39001870 | 223836395 | 0.000000 | 0.000000
09-04-2025 19:01:45.000 | 12796371 | 127963710 | 127.9637 | 72349790 | 15611110 | 47401914 | -99840546 | 50151989 | 37226758 | 213870148 | 0.000000 | 0.000000
09-04-2025 19:01:40.000 | 12749134 | 127491340 | 127.4913 | 73141250 | 15613792 | 47221187 | -99835838 | 50119972 | 35453396 | 203897675 | 0.000000 | 0.000000
09-04-2025 19:01:35.000 | 12777348 | 127773480 | 127.7735 | 71823193 | 15614067 | 47321816 | -99842384 | 50097305 | 33680281 | 193838913 | 0.000000 | 0.000000
09-04-2025 19:01:30.000 | 12771098 | 127710980 | 127.711 | 72945864 | 15613049 | 47303945 | -99837273 | 50082150 | 31908086 | 183828903 | 0.000000 | 0.000000
09-04-2025 19:01:25.000 | 12779423 | 127794230 | 127.7942 | 74115708 | 15612359 | 47339219 | -99832245 | 50081451 | 30134526 | 173620667 | 0.000000 | 0.000000
09-04-2025 19:01:20.000 | 12795611 | 127956110 | 127.9561 | 72850103 | 15609719 | 47404937 | -99838318 | 50094246 | 28357871 | 163307999 | 0.000000 | 0.000000
09-04-2025 19:01:15.000 | 12784609 | 127846090 | 127.8461 | 73408848 | 15610691 | 47362393 | -99835556 | 50097996 | 26581768 | 153246872 | 0.000000 | 0.000000
09-04-2025 19:01:10.000 | 12781306 | 127813060 | 127.8131 | 72498804 | 15611706 | 47344785 | -99839516 | 50093334 | 24805896 | 143111771 | 0.000000 | 0.000000
09-04-2025 19:01:05.000 | 12774799 | 127747990 | 127.748 | 74414702 | 15611949 | 47324102 | -99830772 | 50079006 | 23032979 | 133000443 | 0.000000 | 0.000000
09-04-2025 19:01:00.000 | 12737423 | 127374230 | 127.3742 | 74338945 | 15615318 | 47175669 | -99830124 | 50074757 | 21258354 | 122648956 | 0.000000 | 0.000000
09-04-2025 19:00:55.000 | 12770152 | 127701520 | 127.7015 | 74396108 | 15611785 | 47307422 | -99830734 | 50062927 | 19486278 | 112235977 | 0.000000 | 0.000000
09-04-2025 19:00:50.000 | 12736681 | 127366810 | 127.3668 | 75857744 | 15613012 | 47184326 | -99823112 | 50040302 | 17716521 | 101814629 | 0.000000 | 0.000000
09-04-2025 19:00:45.000 | 12763595 | 127635950 | 127.6359 | 77607441 | 15612664 | 47287939 | -99815659 | 50039761 | 15945714 | 91175652 | 0.000000 | 0.000000
09-04-2025 19:00:40.000 | 12811333 | 128113330 | 128.1133 | 74742622 | 15609595 | 47466836 | -99830246 | 50066261 | 14171404 | 80542496 | 0.000000 | 0.000000
09-04-2025 19:00:35.000 | 12805985 | 128059850 | 128.0599 | 73831216 | 15606412 | 47454829 | -99834213 | 50090874 | 12395673 | 70201614 | 0.000000 | 0.000000
09-04-2025 19:00:30.000 | 12753525 | 127535250 | 127.5353 | 69855376 | 15610826 | 47240342 | -99850334 | 50098549 | 10618116 | 60206562 | 0.000000 | 0.000000
09-04-2025 19:00:25.000 | 12769699 | 127696990 | 127.697 | 70922236 | 15612569 | 47296099 | -99846123 | 50093666 | 884529114 | 50443329 | 0.000000 | 0.000000
09-04-2025 19:00:20.000 | 12736123 | 127361230 | 127.3612 | 74769688 | 15611198 | 47184409 | -99828117 | 50056122 | 707727600 | 40339710 | 0.000000 | 0.000000
09-04-2025 19:00:15.000 | 12719927 | 127199270 | 127.1993 | 75129453 | 15611218 | 47125273 | -99826027 | 50051201 | 530690063 | 29905060 | 0.000000 | 0.000000
09-04-2025 19:00:10.000 | 12770230 | 127702300 | 127.7023 | 72390918 | 15610275 | 47308823 | -99839714 | 50046051 | 353829895 | 19607738 | 0.000000 | 0.000000
09-04-2025 19:00:05.000 | 12737473 | 127374730 | 127.3747 | 71103457 | 15607984 | 47191597 | -99844559 | 50046753 | 176799561 | 9529167 | 0.000000 | 0.000000
09-04-2025 19:00:00.000 | 12691616 | 126916160 | 126.9162 | 65442822 | 15609943 | 47004927 | -99867325 | 50038765 | 31657164 | 15215214 | 0.000000 | 0.000000
09-04-2025 18:59:55.000 | 12683998 | 126839980 | 126.84 | 48646816 | 15612506 | 46941299 | -99926537 | 49999310 | 31481141 | 15133755 | 0.000000 | 0.000000
09-04-2025 18:59:50.000 | 12693977 | 126939770 | 126.9398 | 49650947 | 15615999 | 46969004 | -99923592 | 49985405 | 31304719 | 15066151 | 0.000000 | 0.000000
09-04-2025 18:59:45.000 | 12761767 | 127617670 | 127.6177 | 50437788 | 15609273 | 47240938 | -99921989 | 49997993 | 31128234 | 14996080 | 0.000000 | 0.000000
09-04-2025 18:59:40.000 | 12735970 | 127359700 | 127.3597 | 49488740 | 15608509 | 47146528 | -99924591 | 50021458 | 30951367 | 14926237 | 0.000000 | 0.000000
09-04-2025 18:59:35.000 | 12706135 | 127061350 | 127.0614 | 47245283 | 15615302 | 47012822 | -99930946 | 50025219 | 30774436 | 14860112 | 0.000000 | 0.000000
09-04-2025 18:59:30.000 | 12736128 | 127361280 | 127.3613 | 49917437 | 15613091 | 47134072 | -99923279 | 50014111 | 30597904 | 14793376 | 0.000000 | 0.000000
09-04-2025 18:59:25.000 | 12777687 | 127776870 | 127.7769 | 50295376 | 15607730 | 47304385 | -99922623 | 50042969 | 30420846 | 14722037 | 0.000000 | 0.000000
09-04-2025 18:59:20.000 | 12721333 | 127213330 | 127.2133 | 46234268 | 15614261 | 47070498 | -99934021 | 50060734 | 30243570 | 14654844 | 0.000000 | 0.000000
09-04-2025 18:59:15.000 | 12726323 | 127263230 | 127.2632 | 48999468 | 15613697 | 47094858 | -99925957 | 50042164 | 30066859 | 14588805 | 0.000000 | 0.000000
09-04-2025 18:59:10.000 | 12738213 | 127382130 | 127.3821 | 50474033 | 15610292 | 47150884 | -99921585 | 50045292 | 29889746 | 14519413 | 0.000000 | 0.000000
09-04-2025 18:59:05.000 | 12747688 | 127476880 | 127.4769 | 48322500 | 15613204 | 47174023 | -99928230 | 50056072 | 29712652 | 14451704 | 0.000000 | 0.000000
09-04-2025 18:59:00.000 | 12756495 | 127564950 | 127.5649 | 48597002 | 15607158 | 47225098 | -99927513 | 50075382 | 29535477 | 14383040 | 0.000000 | 0.000000
09-04-2025 18:58:55.000 | 12711726 | 127117260 | 127.1173 | 47264238 | 15613550 | 47038677 | -99930946 | 50065529 | 29358494 | 14317345 | 0.000000 | 0.000000
09-04-2025 18:58:50.000 | 12691668 | 126916680 | 126.9167 | 52140518 | 15613642 | 46972241 | -99915718 | 50018101 | 29182254 | 14249271 | 0.000000 | 0.000000
09-04-2025 18:58:45.000 | 12761816 | 127618160 | 127.6182 | 50064468 | 15607282 | 47246704 | -99923141 | 50032936 | 29005473 | 14176826 | 0.000000 | 0.000000
09-04-2025 18:58:40.000 | 12703099 | 127030990 | 127.031 | 47449980 | 15613925 | 47005757 | -99930313 | 50026913 | 28828551 | 14109872 | 0.000000 | 0.000000
09-04-2025 18:58:35.000 | 12694502 | 126945020 | 126.945 | 49059858 | 15612327 | 46981128 | -99925407 | 50014149 | 28651891 | 14042510 | 0.000000 | 0.000000
09-04-2025 18:58:30.000 | 12711495 | 127114950 | 127.1149 | 49530928 | 15611630 | 47046743 | -99924171 | 50004807 | 28475400 | 13974231 | 0.000000 | 0.000000
09-04-2025 18:58:25.000 | 12691741 | 126917410 | 126.9174 | 51381260 | 15614217 | 46968813 | -99918152 | 49983925 | 28299109 | 13904692 | 0.000000 | 0.000000
09-04-2025 18:58:20.000 | 12700212 | 127002120 | 127.0021 | 54353223 | 15612553 | 47009707 | -99908546 | 49971096 | 28122885 | 13832119 | 0.000000 | 0.000000
09-04-2025 18:58:15.000 | 12740623 | 127406230 | 127.4062 | 50192026 | 15609679 | 47161484 | -99922493 | 50022228 | 27945943 | 13758583 | 0.000000 | 0.000000
09-04-2025 18:58:10.000 | 12694488 | 126944880 | 126.9449 | 46736182 | 15613235 | 46975952 | -99932297 | 50044201 | 27769141 | 13691613 | 0.000000 | 0.000000
09-04-2025 18:58:05.000 | 12716574 | 127165740 | 127.1657 | 48766021 | 15610132 | 47068887 | -99926552 | 50036522 | 27592588 | 13626122 | 0.000000 | 0.000000
09-04-2025 18:58:00.000 | 12732207 | 127322070 | 127.3221 | 47234990 | 15610458 | 47123511 | -99931252 | 50053131 | 27415838 | 13558750 | 0.000000 | 0.000000
09-04-2025 18:57:55.000 | 12674216 | 126742160 | 126.7422 | 47169292 | 15615420 | 46894341 | -99930817 | 50033688 | 27239498 | 13493683 | 0.000000 | 0.000000
09-04-2025 18:57:50.000 | 12697567 | 126975670 | 126.9757 | 49297852 | 15613991 | 46987954 | -99924721 | 50013832 | 27063254 | 13426638 | 0.000000 | 0.000000
09-04-2025 18:57:45.000 | 12723674 | 127236740 | 127.2367 | 49288169 | 15610481 | 47094814 | -99925056 | 50009567 | 26886973 | 13357870 | 0.000000 | 0.000000
09-04-2025 18:57:40.000 | 12740546 | 127405460 | 127.4055 | 48666616 | 15606830 | 47167544 | -99927124 | 50047409 | 26710127 | 13289792 | 0.000000 | 0.000000
09-04-2025 18:57:35.000 | 12698060 | 126980600 | 126.9806 | 46339326 | 15612598 | 46989810 | -99933479 | 50070129 | 26533451 | 13224385 | 0.000000 | 0.000000
09-04-2025 18:57:30.000 | 12692009 | 126920090 | 126.9201 | 46931528 | 15613957 | 46964058 | -99931702 | 50060314 | 26357162 | 13159344 | 0.000000 | 0.000000
09-04-2025 18:57:25.000 | 12684128 | 126841280 | 126.8413 | 46861597 | 15614813 | 46932134 | -99931824 | 50025024 | 26180895 | 13094331 | 0.000000 | 0.000000
09-04-2025 18:57:20.000 | 12711709 | 127117090 | 127.1171 | 48275205 | 15609660 | 47051650 | -99927963 | 50008461 | 26004631 | 13028296 | 0.000000 | 0.000000
09-04-2025 18:57:15.000 | 12671977 | 126719770 | 126.7198 | 46629536 | 15613316 | 46891597 | -99932365 | 50014801 | 25828059 | 12961370 | 0.000000 | 0.000000
09-04-2025 18:57:10.000 | 12706198 | 127061980 | 127.062 | 47109946 | 15610132 | 47028306 | -99931335 | 49994930 | 25652143 | 12896185 | 0.000000 | 0.000000
09-04-2025 18:57:05.000 | 12709288 | 127092880 | 127.0929 | 48777041 | 15610601 | 47040820 | -99926437 | 49996841 | 25475934 | 12828960 | 0.000000 | 0.000000
09-04-2025 18:57:00.000 | 12711655 | 127116550 | 127.1166 | 47411772 | 15609433 | 47051064 | -99930519 | 50008522 | 25299477 | 12761927 | 0.000000 | 0.000000
09-04-2025 18:56:55.000 | 12702513 | 127025130 | 127.0251 | 46662173 | 15611586 | 47009736 | -99932594 | 50028072 | 25123018 | 12696146 | 0.000000 | 0.000000
09-04-2025 18:56:50.000 | 12746555 | 127465550 | 127.4655 | 44216382 | 15611048 | 47170737 | -99939888 | 50055275 | 24946311 | 12632108 | 0.000000 | 0.000000
09-04-2025 18:56:45.000 | 12754345 | 127543450 | 127.5435 | 42799233 | 15604504 | 47217852 | -99943748 | 50076904 | 24769420 | 12570863 | 0.000000 | 0.000000
09-04-2025 18:56:40.000 | 12686367 | 126863670 | 126.8637 | 40182229 | 15614895 | 46931787 | -99949875 | 50073006 | 24592646 | 12514169 | 0.000000 | 0.000000
09-04-2025 18:56:35.000 | 12688126 | 126881260 | 126.8813 | 46187085 | 15615181 | 46945210 | -99933807 | 50043259 | 24416680 | 12455640 | 0.000000 | 0.000000
09-04-2025 18:56:30.000 | 12720616 | 127206160 | 127.2062 | 46474868 | 15610133 | 47080591 | -99933327 | 50063675 | 24240275 | 12391018 | 0.000000 | 0.000000
09-04-2025 18:56:25.000 | 12690304 | 126903040 | 126.903 | 45182974 | 15610857 | 46964619 | -99936676 | 50068863 | 24063730 | 12327305 | 0.000000 | 0.000000
09-04-2025 18:56:20.000 | 12700021 | 127000210 | 127.0002 | 45466519 | 15612598 | 46996079 | -99935982 | 50058353 | 23887428 | 12264237 | 0.000000 | 0.000000
09-04-2025 18:56:15.000 | 12680741 | 126807410 | 126.8074 | 49244546 | 15613341 | 46927466 | -99924683 | 50044788 | 23711094 | 12199712 | 0.000000 | 0.000000
09-04-2025 18:56:10.000 | 12703400 | 127034000 | 127.034 | 47978301 | 15610934 | 47016782 | -99928757 | 50047585 | 23534904 | 12131724 | 0.000000 | 0.000000
09-04-2025 18:56:05.000 | 12657946 | 126579460 | 126.5795 | 47582510 | 15614781 | 46836606 | -99929420 | 50023235 | 23358875 | 12065283 | 0.000000 | 0.000000
09-04-2025 18:56:00.000 | 12651894 | 126518940 | 126.5189 | 51400713 | 15614356 | 46821157 | -99917572 | 49999229 | 23183105 | 11997401 | 0.000000 | 0.000000
09-04-2025 18:55:55.000 | 12703748 | 127037480 | 127.0375 | 50781162 | 15609895 | 47025146 | -99920204 | 50008991 | 23007066 | 11925493 | 0.000000 | 0.000000
09-04-2025 18:55:50.000 | 12631388 | 126313880 | 126.3139 | 48562959 | 15613982 | 46742432 | -99926178 | 50011738 | 22830871 | 11856815 | 0.000000 | 0.000000
09-04-2025 18:55:45.000 | 12653805 | 126538050 | 126.538 | 48946523 | 15611531 | 46833389 | -99925270 | 50001999 | 22655150 | 11789409 | 0.000000 | 0.000000
09-04-2025 18:55:40.000 | 12615412 | 126154120 | 126.1541 | 47880728 | 15614124 | 46681797 | -99928055 | 49990158 | 22479420 | 11720321 | 0.000000 | 0.000000
09-04-2025 18:55:35.000 | 12669384 | 126693840 | 126.6938 | 49501626 | 15610746 | 46893711 | -99923759 | 49982750 | 22303828 | 11652542 | 0.000000 | 0.000000
09-04-2025 18:55:30.000 | 12727641 | 127276410 | 127.2764 | 49281191 | 15607127 | 47119878 | -99925125 | 50022774 | 22127670 | 11584126 | 0.000000 | 0.000000
09-04-2025 18:55:25.000 | 12650625 | 126506250 | 126.5062 | 46733198 | 15612404 | 46815830 | -99931839 | 50046753 | 21951307 | 11517618 | 0.000000 | 0.000000
09-04-2025 18:55:20.000 | 12697766 | 126977660 | 126.9777 | 48352173 | 15608141 | 47004888 | -99927574 | 50057281 | 21775320 | 11452614 | 0.000000 | 0.000000
09-04-2025 18:55:15.000 | 12631998 | 126319980 | 126.32 | 44951753 | 15612586 | 46743657 | -99936745 | 50055660 | 21599576 | 11387491 | 0.000000 | 0.000000
09-04-2025 18:55:10.000 | 12660468 | 126604680 | 126.6047 | 46576460 | 15611634 | 46854272 | -99932396 | 50032928 | 21424053 | 11325095 | 0.000000 | 0.000000
09-04-2025 18:55:05.000 | 12693820 | 126938200 | 126.9382 | 45314619 | 15609927 | 46981299 | -99936340 | 50040649 | 21248314 | 11260643 | 0.000000 | 0.000000
09-04-2025 18:55:00.000 | 12664096 | 126640960 | 126.641 | 42338481 | 15609967 | 46867271 | -99944160 | 50053101 | 21072096 | 11199362 | 0.000000 | 0.000000
09-04-2025 18:54:55.000 | 12650484 | 126504840 | 126.5048 | 40399277 | 15612116 | 46807705 | -99949043 | 50046131 | 20896268 | 11142407 | 0.000000 | 0.000000
09-04-2025 18:54:50.000 | 12627198 | 126271980 | 126.272 | 44694951 | 15613303 | 46724111 | -99937416 | 50025124 | 20720816 | 11082946 | 0.000000 | 0.000000
09-04-2025 18:54:45.000 | 12579856 | 125798560 | 125.7986 | 47073823 | 15618806 | 46535698 | -99930061 | 49990490 | 20545537 | 11019758 | 0.000000 | 0.000000
09-04-2025 18:54:40.000 | 12591673 | 125916730 | 125.9167 | 56432002 | 15616221 | 46600908 | -99899727 | 49961876 | 20370396 | 10947789 | 0.000000 | 0.000000
09-04-2025 18:54:35.000 | 12692745 | 126927450 | 126.9274 | 55068262 | 15608202 | 46996719 | -99906013 | 49997173 | 20194850 | 10869559 | 0.000000 | 0.000000
09-04-2025 18:54:30.000 | 12681037 | 126810370 | 126.8104 | 52026235 | 15606181 | 46954380 | -99915947 | 50048557 | 20018480 | 10795273 | 0.000000 | 0.000000
09-04-2025 18:54:25.000 | 12642005 | 126420050 | 126.4201 | 48223442 | 15614224 | 46780400 | -99927322 | 50053402 | 19842477 | 10725118 | 0.000000 | 0.000000
09-04-2025 18:54:20.000 | 12668081 | 126680810 | 126.6808 | 52667583 | 15610327 | 46894937 | -99913689 | 50007088 | 19667121 | 10656769 | 0.000000 | 0.000000
09-04-2025 18:54:15.000 | 12606689 | 126066890 | 126.0669 | 53935552 | 15614462 | 46657681 | -99908607 | 49980438 | 19491582 | 10583101 | 0.000000 | 0.000000
09-04-2025 18:54:10.000 | 12616536 | 126165360 | 126.1654 | 54614644 | 15612771 | 46700098 | -99906441 | 49989094 | 19316113 | 10507815 | 0.000000 | 0.000000
09-04-2025 18:54:05.000 | 12665192 | 126651920 | 126.6519 | 54938174 | 15607442 | 46896738 | -99906052 | 50002659 | 19140793 | 10431719 | 0.000000 | 0.000000
09-04-2025 18:54:00.000 | 12652373 | 126523730 | 126.5237 | 50468159 | 15612240 | 46827910 | -99920540 | 50021828 | 18964816 | 10357786 | 0.000000 | 0.000000
09-04-2025 18:53:55.000 | 12653628 | 126536280 | 126.5363 | 50509204 | 15613145 | 46829878 | -99920425 | 50005436 | 18789373 | 10288314 | 0.000000 | 0.000000
09-04-2025 18:53:50.000 | 12633762 | 126337620 | 126.3376 | 53164565 | 15611198 | 46766265 | -99911575 | 49994034 | 18614078 | 10216809 | 0.000000 | 0.000000
09-04-2025 18:53:45.000 | 12634538 | 126345380 | 126.3454 | 51823403 | 15612842 | 46762192 | -99915985 | 50000690 | 18438473 | 10143471 | 0.000000 | 0.000000
09-04-2025 18:53:40.000 | 12632089 | 126320890 | 126.3209 | 54219673 | 15615015 | 46750215 | -99908012 | 49982830 | 18263117 | 10071250 | 0.000000 | 0.000000
09-04-2025 18:53:35.000 | 12656580 | 126565800 | 126.5658 | 55427559 | 15608355 | 46862681 | -99904243 | 50000416 | 18087531 | 999370789 | 0.000000 | 0.000000
09-04-2025 18:53:30.000 | 12673713 | 126737130 | 126.7371 | 52963931 | 15609929 | 46917441 | -99912796 | 50035999 | 17911658 | 991925720 | 0.000000 | 0.000000
09-04-2025 18:53:25.000 | 12685986 | 126859860 | 126.8599 | 52894263 | 15606479 | 46973101 | -99913193 | 50076847 | 17735680 | 984593750 | 0.000000 | 0.000000
09-04-2025 18:53:20.000 | 12579915 | 125799150 | 125.7991 | 50175469 | 15613617 | 46555610 | -99920555 | 50061672 | 17560197 | 977421753 | 0.000000 | 0.000000
09-04-2025 18:53:15.000 | 12591323 | 125913230 | 125.9132 | 52768809 | 15614100 | 46600615 | -99912300 | 50010551 | 17385387 | 970328552 | 0.000000 | 0.000000
09-04-2025 18:53:10.000 | 12581858 | 125818580 | 125.8186 | 56325313 | 15611909 | 46577412 | -99899948 | 49996552 | 17210332 | 962773132 | 0.000000 | 0.000000
09-04-2025 18:53:05.000 | 12640131 | 126401310 | 126.4013 | 55056826 | 15612356 | 46789526 | -99905273 | 50020206 | 17035117 | 954985107 | 0.000000 | 0.000000
09-04-2025 18:53:00.000 | 12600863 | 126008630 | 126.0086 | 68841626 | 15612525 | 46668926 | -99851097 | 50007179 | 16859881 | 946733398 | 0.000000 | 0.000000
09-04-2025 18:52:55.000 | 12621836 | 126218360 | 126.2184 | 70312813 | 15612905 | 46748154 | -99845192 | 50004894 | 16684670 | 937078613 | 0.000000 | 0.000000
09-04-2025 18:52:50.000 | 12633905 | 126339050 | 126.3391 | 70490723 | 15609664 | 46802876 | -99844711 | 50016716 | 16509256 | 927285217 | 0.000000 | 0.000000
09-04-2025 18:52:45.000 | 12554354 | 125543540 | 125.5435 | 67202144 | 15617418 | 46479312 | -99857040 | 50012257 | 16333934 | 917661133 | 0.000000 | 0.000000
09-04-2025 18:52:40.000 | 12566217 | 125662170 | 125.6622 | 70598203 | 15614980 | 46537271 | -99842560 | 49971390 | 16159542 | 908122437 | 0.000000 | 0.000000
09-04-2025 18:52:35.000 | 12613052 | 126130520 | 126.1305 | 71734077 | 15609163 | 46730161 | -99838661 | 49976467 | 15984693 | 898193115 | 0.000000 | 0.000000
09-04-2025 18:52:30.000 | 12588196 | 125881960 | 125.882 | 70116104 | 15612369 | 46625142 | -99845238 | 49999420 | 15809382 | 888314514 | 0.000000 | 0.000000
09-04-2025 18:52:25.000 | 12607623 | 126076230 | 126.0762 | 68735596 | 15611201 | 46697720 | -99851715 | 50002850 | 15634605 | 878670776 | 0.000000 | 0.000000
09-04-2025 18:52:20.000 | 12612070 | 126120700 | 126.1207 | 68438745 | 15611028 | 46714185 | -99853096 | 50006416 | 15459622 | 869143433 | 0.000000 | 0.000000
09-04-2025 18:52:15.000 | 12593675 | 125936750 | 125.9368 | 66851802 | 15611138 | 46642612 | -99859406 | 50006290 | 15284424 | 859775391 | 0.000000 | 0.000000
09-04-2025 18:52:10.000 | 12572839 | 125728390 | 125.7284 | 67920215 | 15616380 | 46552021 | -99854401 | 49998466 | 15109482 | 850430542 | 0.000000 | 0.000000
09-04-2025 18:52:05.000 | 12614323 | 126143230 | 126.1432 | 69043271 | 15613523 | 46716733 | -99850548 | 50003204 | 14934453 | 840875854 | 0.000000 | 0.000000
09-04-2025 18:52:00.000 | 12629914 | 126299140 | 126.2991 | 69335503 | 15610817 | 46782319 | -99849648 | 50013382 | 14759495 | 831237061 | 0.000000 | 0.000000
09-04-2025 18:51:55.000 | 12634020 | 126340200 | 126.3402 | 69815962 | 15606519 | 46811670 | -99847664 | 50036991 | 14584283 | 821584961 | 0.000000 | 0.000000
09-04-2025 18:51:50.000 | 12601027 | 126010270 | 126.0103 | 65524565 | 15610981 | 46667490 | -99865074 | 50081581 | 14408423 | 812070984 | 0.000000 | 0.000000
09-04-2025 18:51:45.000 | 12606868 | 126068680 | 126.0687 | 66822168 | 15612206 | 46688071 | -99859818 | 50064644 | 14233419 | 802890381 | 0.000000 | 0.000000
09-04-2025 18:51:40.000 | 12557263 | 125572630 | 125.5726 | 69151685 | 15613049 | 46506934 | -99848717 | 50023872 | 14058801 | 793440186 | 0.000000 | 0.000000
09-04-2025 18:51:35.000 | 12545587 | 125455870 | 125.4559 | 71587041 | 15614750 | 46463896 | -99837593 | 49993752 | 13884254 | 783680786 | 0.000000 | 0.000000
09-04-2025 18:51:30.000 | 12563480 | 125634800 | 125.6348 | 74478223 | 15614742 | 46536064 | -99824745 | 49940552 | 13710159 | 773667175 | 0.000000 | 0.000000
09-04-2025 18:51:25.000 | 12597857 | 125978570 | 125.9786 | 75041636 | 15609429 | 46680303 | -99823059 | 49941509 | 13535422 | 763236267 | 0.000000 | 0.000000
09-04-2025 18:51:20.000 | 12580371 | 125803710 | 125.8037 | 71815518 | 15611238 | 46603198 | -99837463 | 49967022 | 13360688 | 752986877 | 0.000000 | 0.000000
09-04-2025 18:51:15.000 | 12608272 | 126082720 | 126.0827 | 71033594 | 15610208 | 46707876 | -99841675 | 49980129 | 13185786 | 743025146 | 0.000000 | 0.000000
09-04-2025 18:51:10.000 | 12584983 | 125849830 | 125.8498 | 71325127 | 15612505 | 46615356 | -99839783 | 49994240 | 13010565 | 733123352 | 0.000000 | 0.000000
09-04-2025 18:51:05.000 | 12600007 | 126000070 | 126.0001 | 71366069 | 15614603 | 46664683 | -99839981 | 49985970 | 12835691 | 723225708 | 0.000000 | 0.000000
09-04-2025 18:51:00.000 | 12597620 | 125976200 | 125.9762 | 73446758 | 15613414 | 46663940 | -99830475 | 49970039 | 12660874 | 713057861 | 0.000000 | 0.000000
09-04-2025 18:50:55.000 | 12648480 | 126484800 | 126.4848 | 74018979 | 15610704 | 46860991 | -99829208 | 50006340 | 12485397 | 702633118 | 0.000000 | 0.000000
09-04-2025 18:50:50.000 | 12645756 | 126457560 | 126.4576 | 71290117 | 15611646 | 46842739 | -99841469 | 50028767 | 12309927 | 692571655 | 0.000000 | 0.000000
09-04-2025 18:50:45.000 | 12606169 | 126061690 | 126.0617 | 69947817 | 15610390 | 46697612 | -99846413 | 50041210 | 12134440 | 682629517 | 0.000000 | 0.000000
09-04-2025 18:50:40.000 | 12660194 | 126601940 | 126.6019 | 68440161 | 15606352 | 46905767 | -99854202 | 50066380 | 11958907 | 672985413 | 0.000000 | 0.000000
09-04-2025 18:50:35.000 | 12641092 | 126410920 | 126.4109 | 64581821 | 15609310 | 46818672 | -99869751 | 50063251 | 11783186 | 663684814 | 0.000000 | 0.000000
09-04-2025 18:50:30.000 | 12560936 | 125609360 | 125.6094 | 67764424 | 15615879 | 46509346 | -99854797 | 50010792 | 11608304 | 654665588 | 0.000000 | 0.000000
09-04-2025 18:50:25.000 | 12559393 | 125593930 | 125.5939 | 72924878 | 15618482 | 46506558 | -99831856 | 49970947 | 11433839 | 645084473 | 0.000000 | 0.000000
09-04-2025 18:50:20.000 | 12602945 | 126029450 | 126.0294 | 75643960 | 15612633 | 46690923 | -99820358 | 49956497 | 11259180 | 634756775 | 0.000000 | 0.000000
09-04-2025 18:50:15.000 | 12642744 | 126427440 | 126.4274 | 72520732 | 15610894 | 46836416 | -99835884 | 49990238 | 11083903 | 624360718 | 0.000000 | 0.000000
09-04-2025 18:50:10.000 | 12631145 | 126311450 | 126.3114 | 70830278 | 15608365 | 46797290 | -99843147 | 50026310 | 10908239 | 614277161 | 0.000000 | 0.000000
09-04-2025 18:50:05.000 | 12645106 | 126451060 | 126.4511 | 68428242 | 15612385 | 46831729 | -99853905 | 50028111 | 10732656 | 604621399 | 0.000000 | 0.000000
09-04-2025 18:50:00.000 | 12626528 | 126265280 | 126.2653 | 69179380 | 15611712 | 46766782 | -99850243 | 50014938 | 10557232 | 594950378 | 0.000000 | 0.000000
09-04-2025 18:49:55.000 | 12640887 | 126408870 | 126.4089 | 70363633 | 15611653 | 46822842 | -99845436 | 50010517 | 10381793 | 585273254 | 0.000000 | 0.000000
09-04-2025 18:49:50.000 | 12654108 | 126541080 | 126.5411 | 69584746 | 15612493 | 46867080 | -99849152 | 50016315 | 10206092 | 575590088 | 0.000000 | 0.000000
09-04-2025 18:49:45.000 | 12685513 | 126855130 | 126.8551 | 70565610 | 15607282 | 47000962 | -99845642 | 50033234 | 10030294 | 565856628 | 0.000000 | 0.000000
09-04-2025 18:49:40.000 | 12659514 | 126595140 | 126.5951 | 68432393 | 15610296 | 46891387 | -99854218 | 50048889 | 98543740 | 556249451 | 0.000000 | 0.000000
09-04-2025 18:49:35.000 | 12656419 | 126564190 | 126.5642 | 68900859 | 15610515 | 46880645 | -99852142 | 50048836 | 96785156 | 546620239 | 0.000000 | 0.000000
09-04-2025 18:49:30.000 | 12605316 | 126053160 | 126.0532 | 69036484 | 15614547 | 46679756 | -99850365 | 50030460 | 95028584 | 537069397 | 0.000000 | 0.000000
09-04-2025 18:49:25.000 | 12588126 | 125881260 | 125.8813 | 71212876 | 15616055 | 46616094 | -99840370 | 49993694 | 93278311 | 527301514 | 0.000000 | 0.000000
09-04-2025 18:49:20.000 | 12655678 | 126556780 | 126.5568 | 73856943 | 15609002 | 46892666 | -99830147 | 50002815 | 91525635 | 517129883 | 0.000000 | 0.000000
09-04-2025 18:49:15.000 | 12644217 | 126442170 | 126.4422 | 69499443 | 15607703 | 46844858 | -99849281 | 50048176 | 89766826 | 506985809 | 0.000000 | 0.000000
09-04-2025 18:49:10.000 | 12610128 | 126101280 | 126.1013 | 68912031 | 15615454 | 46694419 | -99851013 | 50025703 | 88014404 | 497508942 | 0.000000 | 0.000000
09-04-2025 18:49:05.000 | 12609891 | 126098910 | 126.0989 | 73934351 | 15613790 | 46709043 | -99828560 | 49989708 | 86266816 | 487614044 | 0.000000 | 0.000000
09-04-2025 18:49:00.000 | 12640093 | 126400930 | 126.4009 | 73602974 | 15610932 | 46828452 | -99830894 | 50006542 | 84513154 | 477309570 | 0.000000 | 0.000000
09-04-2025 18:48:55.000 | 12650295 | 126502950 | 126.5029 | 71568374 | 15610938 | 46861919 | -99840347 | 50025501 | 82757852 | 467237610 | 0.000000 | 0.000000
09-04-2025 18:48:50.000 | 12628702 | 126287020 | 126.287 | 70028008 | 15610482 | 46780103 | -99846611 | 50036556 | 81003496 | 457356598 | 0.000000 | 0.000000
09-04-2025 18:48:45.000 | 12624848 | 126248480 | 126.2485 | 68718423 | 15611395 | 46760518 | -99852188 | 50038620 | 79248945 | 447692017 | 0.000000 | 0.000000
09-04-2025 18:48:40.000 | 12644883 | 126448830 | 126.4488 | 68242637 | 15613461 | 46827407 | -99854691 | 50033321 | 77494746 | 438254669 | 0.000000 | 0.000000
09-04-2025 18:48:35.000 | 12652641 | 126526410 | 126.5264 | 70414639 | 15612656 | 46862896 | -99845497 | 50042099 | 75740205 | 428631317 | 0.000000 | 0.000000
09-04-2025 18:48:30.000 | 12682505 | 126825050 | 126.8251 | 69309106 | 15606412 | 46989707 | -99851006 | 50074902 | 73978999 | 418840393 | 0.000000 | 0.000000
09-04-2025 18:48:25.000 | 12684421 | 126844210 | 126.8442 | 67602007 | 15610456 | 46981904 | -99858284 | 50086624 | 72219712 | 409525085 | 0.000000 | 0.000000
09-04-2025 18:48:20.000 | 12607236 | 126072360 | 126.0724 | 68955063 | 15614888 | 46685557 | -99850761 | 50080555 | 70461738 | 400043488 | 0.000000 | 0.000000
09-04-2025 18:48:15.000 | 12608134 | 126081340 | 126.0813 | 68855635 | 15615799 | 46686167 | -99851212 | 50054600 | 68709146 | 390449341 | 0.000000 | 0.000000
09-04-2025 18:48:10.000 | 12608604 | 126086040 | 126.086 | 72317583 | 15610385 | 46712876 | -99835922 | 50029343 | 66957388 | 380584930 | 0.000000 | 0.000000
09-04-2025 18:48:05.000 | 12635746 | 126357460 | 126.3575 | 68458604 | 15612809 | 46796606 | -99853554 | 50031033 | 65204136 | 370703522 | 0.000000 | 0.000000
09-04-2025 18:48:00.000 | 12643842 | 126438420 | 126.4384 | 68164219 | 15611574 | 46829121 | -99854996 | 50012745 | 63451367 | 361293793 | 0.000000 | 0.000000
09-04-2025 18:47:55.000 | 12594377 | 125943770 | 125.9438 | 69051191 | 15614249 | 46641016 | -99850037 | 50001930 | 61698643 | 351714233 | 0.000000 | 0.000000
09-04-2025 18:47:50.000 | 12624630 | 126246300 | 126.2463 | 73404722 | 15611354 | 46770303 | -99831390 | 49977905 | 59947344 | 341925903 | 0.000000 | 0.000000
09-04-2025 18:47:45.000 | 12576819 | 125768190 | 125.7682 | 71734922 | 15616964 | 46572715 | -99837730 | 49977470 | 58195654 | 331719055 | 0.000000 | 0.000000
09-04-2025 18:47:40.000 | 12610217 | 126102170 | 126.1022 | 75416255 | 15611801 | 46719668 | -99821640 | 49959240 | 56445801 | 321442230 | 0.000000 | 0.000000
09-04-2025 18:47:35.000 | 12699896 | 126998960 | 126.999 | 74086616 | 15606450 | 47063701 | -99830276 | 49993351 | 54688047 | 310957123 | 0.000000 | 0.000000
09-04-2025 18:47:30.000 | 12653756 | 126537560 | 126.5376 | 70283125 | 15609541 | 46876230 | -99846100 | 50030338 | 52927061 | 300764282 | 0.000000 | 0.000000
09-04-2025 18:47:25.000 | 12655710 | 126557100 | 126.5571 | 71404609 | 15612662 | 46876162 | -99841217 | 50019249 | 51169307 | 291004456 | 0.000000 | 0.000000
09-04-2025 18:47:20.000 | 12654384 | 126543840 | 126.5438 | 70513579 | 15612802 | 46869053 | -99845108 | 50001560 | 49412393 | 281179871 | 0.000000 | 0.000000
09-04-2025 18:47:15.000 | 12629357 | 126293570 | 126.2936 | 72119443 | 15612969 | 46779561 | -99837349 | 49987492 | 47655884 | 271273071 | 0.000000 | 0.000000
09-04-2025 18:47:10.000 | 12659405 | 126594050 | 126.594 | 70652837 | 15610553 | 46894761 | -99844620 | 49990368 | 45900073 | 261314301 | 0.000000 | 0.000000
09-04-2025 18:47:05.000 | 12679588 | 126795880 | 126.7959 | 70600640 | 15611986 | 46965283 | -99845345 | 49989193 | 44141401 | 251422150 | 0.000000 | 0.000000
09-04-2025 18:47:00.000 | 12686816 | 126868160 | 126.8682 | 70998457 | 15608743 | 47002896 | -99843781 | 49981194 | 42380767 | 241631439 | 0.000000 | 0.000000
09-04-2025 18:46:55.000 | 12642197 | 126421970 | 126.422 | 72362842 | 15616558 | 46816641 | -99836586 | 49965546 | 40623035 | 231834183 | 0.000000 | 0.000000
09-04-2025 18:46:50.000 | 12680128 | 126801280 | 126.8013 | 75097070 | 15612643 | 46974321 | -99825081 | 49958904 | 38864751 | 221580658 | 0.000000 | 0.000000
09-04-2025 18:46:45.000 | 12726482 | 127264820 | 127.2648 | 72943105 | 15610106 | 47148789 | -99836151 | 50001949 | 37097683 | 211228546 | 0.000000 | 0.000000
09-04-2025 18:46:40.000 | 12737270 | 127372700 | 127.3727 | 69185889 | 15612084 | 47174482 | -99852806 | 50028381 | 35329585 | 201223297 | 0.000000 | 0.000000
09-04-2025 18:46:35.000 | 12716979 | 127169790 | 127.1698 | 70172188 | 15613711 | 47097188 | -99848106 | 50031086 | 33562661 | 191606644 | 0.000000 | 0.000000
09-04-2025 18:46:30.000 | 12742702 | 127427020 | 127.427 | 70419707 | 15610020 | 47203901 | -99847649 | 50040722 | 31795854 | 181848572 | 0.000000 | 0.000000
09-04-2025 18:46:25.000 | 12739553 | 127395530 | 127.3955 | 70575713 | 15609672 | 47193086 | -99846901 | 50052364 | 30027415 | 172072815 | 0.000000 | 0.000000
09-04-2025 18:46:20.000 | 12732109 | 127321090 | 127.3211 | 69261899 | 15611095 | 47158828 | -99852364 | 50042686 | 28260134 | 162422363 | 0.000000 | 0.000000
09-04-2025 18:46:15.000 | 12704256 | 127042560 | 127.0426 | 69869292 | 15610203 | 47059663 | -99849113 | 50044014 | 26493301 | 152810959 | 0.000000 | 0.000000
09-04-2025 18:46:10.000 | 12691198 | 126911980 | 126.912 | 69063950 | 15613046 | 47002046 | -99852257 | 50030350 | 24729814 | 143141724 | 0.000000 | 0.000000
09-04-2025 18:46:05.000 | 12675251 | 126752510 | 126.7525 | 74044346 | 15614708 | 46948135 | -99829811 | 49987762 | 22971189 | 133373169 | 0.000000 | 0.000000
09-04-2025 18:46:00.000 | 12682648 | 126826480 | 126.8265 | 73574521 | 15614063 | 46976431 | -99832153 | 49974911 | 21208364 | 123047615 | 0.000000 | 0.000000
09-04-2025 18:45:55.000 | 12664743 | 126647430 | 126.6474 | 77810015 | 15614396 | 46918354 | -99811798 | 49945374 | 19450894 | 112586769 | 0.000000 | 0.000000
09-04-2025 18:45:50.000 | 12693044 | 126930440 | 126.9304 | 77539331 | 15613511 | 47024854 | -99813934 | 49948978 | 17688494 | 101731934 | 0.000000 | 0.000000
09-04-2025 18:45:45.000 | 12782127 | 127821270 | 127.8213 | 77887378 | 15606206 | 47377642 | -99814865 | 49984138 | 15921704 | 90842186 | 0.000000 | 0.000000
09-04-2025 18:45:40.000 | 12740504 | 127405040 | 127.405 | 73712163 | 15610700 | 47200254 | -99833054 | 50018147 | 14150677 | 80333946 | 0.000000 | 0.000000
09-04-2025 18:45:35.000 | 12701488 | 127014880 | 127.0149 | 71893770 | 15612705 | 47046138 | -99840195 | 50009686 | 12382626 | 70282669 | 0.000000 | 0.000000
09-04-2025 18:45:30.000 | 12712611 | 127126110 | 127.1261 | 73758970 | 15612680 | 47091245 | -99832108 | 49993382 | 10617133 | 60165459 | 0.000000 | 0.000000
09-04-2025 18:45:25.000 | 12734050 | 127340500 | 127.3405 | 72112188 | 15611890 | 47169243 | -99840042 | 49984894 | 885057983 | 50012207 | 0.000000 | 0.000000
09-04-2025 18:45:20.000 | 12727286 | 127272860 | 127.2729 | 72518232 | 15610669 | 47148867 | -99838066 | 49983196 | 708174927 | 39948921 | 0.000000 | 0.000000
09-04-2025 18:45:15.000 | 12735412 | 127354120 | 127.3541 | 72790913 | 15611419 | 47177788 | -99837059 | 49975281 | 531287292 | 29854652 | 0.000000 | 0.000000
09-04-2025 18:45:10.000 | 12767930 | 127679300 | 127.6793 | 71487471 | 15610901 | 47295942 | -99843628 | 49983913 | 354221924 | 19869982 | 0.000000 | 0.000000
09-04-2025 18:45:05.000 | 12788533 | 127885330 | 127.8853 | 71999468 | 15608903 | 47379336 | -99841888 | 49999699 | 177200836 | 9810257 | 0.000000 | 0.000000
09-04-2025 18:45:00.000 | 12756923 | 127569230 | 127.5692 | 72060391 | 15609634 | 47260591 | -99840843 | 50004066 | 31820957 | 16780322 | 0.000000 | 0.000000
09-04-2025 18:44:55.000 | 12746098 | 127460980 | 127.461 | 72343218 | 15609844 | 47220483 | -99839317 | 49997639 | 31644096 | 16681248 | 0.000000 | 0.000000
09-04-2025 18:44:50.000 | 12750540 | 127505400 | 127.5054 | 71661143 | 15611294 | 47231245 | -99842438 | 50007626 | 31467086 | 16581227 | 0.000000 | 0.000000
09-04-2025 18:44:45.000 | 12747330 | 127473300 | 127.4733 | 72383833 | 15613965 | 47212617 | -99839172 | 50004532 | 31290072 | 16482466 | 0.000000 | 0.000000
09-04-2025 18:44:40.000 | 12771233 | 127712330 | 127.7123 | 74026167 | 15609064 | 47319214 | -99832436 | 50006062 | 31113143 | 16381185 | 0.000000 | 0.000000
09-04-2025 18:44:35.000 | 12683465 | 126834650 | 126.8346 | 73480571 | 15615443 | 46975317 | -99832603 | 49989094 | 30936281 | 16279816 | 0.000000 | 0.000000
09-04-2025 18:44:30.000 | 12751871 | 127518710 | 127.5187 | 75911226 | 15609602 | 47250352 | -99823280 | 49989342 | 30759365 | 16174343 | 0.000000 | 0.000000
09-04-2025 18:44:25.000 | 12756538 | 127565380 | 127.5654 | 72474966 | 15610340 | 47257798 | -99838997 | 50017647 | 30582104 | 16070225 | 0.000000 | 0.000000
09-04-2025 18:44:20.000 | 12744913 | 127449130 | 127.4491 | 69536831 | 15612846 | 47201118 | -99851486 | 50048813 | 30404443 | 15970309 | 0.000000 | 0.000000
09-04-2025 18:44:15.000 | 12730908 | 127309080 | 127.3091 | 70103418 | 15614183 | 47146689 | -99848732 | 50020264 | 30227559 | 15873594 | 0.000000 | 0.000000
09-04-2025 18:44:10.000 | 12722423 | 127224230 | 127.2242 | 71475791 | 15611145 | 47128613 | -99842560 | 50002319 | 30050875 | 15774141 | 0.000000 | 0.000000
09-04-2025 18:44:05.000 | 12735375 | 127353750 | 127.3538 | 73052202 | 15616979 | 47161836 | -99835884 | 49973965 | 29874107 | 15674795 | 0.000000 | 0.000000
09-04-2025 18:44:00.000 | 12739602 | 127396020 | 127.396 | 76498203 | 15613615 | 47195220 | -99820198 | 49946815 | 29697578 | 15571022 | 0.000000 | 0.000000
09-04-2025 18:43:55.000 | 12750921 | 127509210 | 127.5092 | 77391543 | 15610581 | 47247646 | -99816315 | 49962143 | 29520746 | 15463798 | 0.000000 | 0.000000
09-04-2025 18:43:50.000 | 12743255 | 127432550 | 127.4326 | 74972866 | 15610915 | 47213057 | -99827377 | 49996826 | 29343418 | 15357617 | 0.000000 | 0.000000
09-04-2025 18:43:45.000 | 12743048 | 127430480 | 127.4305 | 73571191 | 15611649 | 47208364 | -99833755 | 49995747 | 29166477 | 15254451 | 0.000000 | 0.000000
09-04-2025 18:43:40.000 | 12760126 | 127601260 | 127.6013 | 73103799 | 15611594 | 47269209 | -99836288 | 50003670 | 28989258 | 15152098 | 0.000000 | 0.000000
09-04-2025 18:43:35.000 | 12780570 | 127805700 | 127.8057 | 70635723 | 15608247 | 47349321 | -99847618 | 50026409 | 28811957 | 15052025 | 0.000000 | 0.000000
09-04-2025 18:43:30.000 | 12748605 | 127486050 | 127.4861 | 68850444 | 15609529 | 47224297 | -99854485 | 50036022 | 28634904 | 14953760 | 0.000000 | 0.000000
09-04-2025 18:43:25.000 | 12711508 | 127115080 | 127.1151 | 68665376 | 15616628 | 47065820 | -99854424 | 49988487 | 28458273 | 14859661 | 0.000000 | 0.000000
09-04-2025 18:43:20.000 | 12734221 | 127342210 | 127.3422 | 71869658 | 15613152 | 47167422 | -99841118 | 49967697 | 28281779 | 14760239 | 0.000000 | 0.000000
09-04-2025 18:43:15.000 | 12706367 | 127063670 | 127.0637 | 72644199 | 15611526 | 47070479 | -99836967 | 49952480 | 28105094 | 14659292 | 0.000000 | 0.000000
09-04-2025 18:43:10.000 | 12675409 | 126754090 | 126.7541 | 74571128 | 15613845 | 46953369 | -99827393 | 49947834 | 27928289 | 14556577 | 0.000000 | 0.000000
09-04-2025 18:43:05.000 | 12698917 | 126989170 | 126.9892 | 76952681 | 15613139 | 47046470 | -99816902 | 49928535 | 27751906 | 14450453 | 0.000000 | 0.000000
09-04-2025 18:43:00.000 | 12642479 | 126424790 | 126.4248 | 79469893 | 15617807 | 46830439 | -99803017 | 49894379 | 27575783 | 14342788 | 0.000000 | 0.000000
09-04-2025 18:42:55.000 | 12744611 | 127446110 | 127.4461 | 81316406 | 15606869 | 47244180 | -99797066 | 49918709 | 27399229 | 14229509 | 0.000000 | 0.000000
09-04-2025 18:42:50.000 | 12790684 | 127906840 | 127.9068 | 76209863 | 15605542 | 47407822 | -99822968 | 49975304 | 27222064 | 14119435 | 0.000000 | 0.000000
09-04-2025 18:42:45.000 | 12750730 | 127507300 | 127.5073 | 71664150 | 15609840 | 47238042 | -99842430 | 50002434 | 27044813 | 14017007 | 0.000000 | 0.000000
09-04-2025 18:42:40.000 | 12710733 | 127107330 | 127.1073 | 68251558 | 15611635 | 47076494 | -99856148 | 50004379 | 26867811 | 13919705 | 0.000000 | 0.000000
09-04-2025 18:42:35.000 | 12691916 | 126919160 | 126.9192 | 69409146 | 15614751 | 47000210 | -99850800 | 49987003 | 26691205 | 13824602 | 0.000000 | 0.000000
09-04-2025 18:42:30.000 | 12707738 | 127077380 | 127.0774 | 73253613 | 15612517 | 47073408 | -99834267 | 49961693 | 26514912 | 13726002 | 0.000000 | 0.000000
09-04-2025 18:42:25.000 | 12699952 | 126999520 | 126.9995 | 73767969 | 15615106 | 47038018 | -99831734 | 49954769 | 26338652 | 13624354 | 0.000000 | 0.000000
09-04-2025 18:42:20.000 | 12745851 | 127458510 | 127.4585 | 76381235 | 15606610 | 47238296 | -99820923 | 49968590 | 26162195 | 13519666 | 0.000000 | 0.000000
09-04-2025 18:42:15.000 | 12718523 | 127185230 | 127.1852 | 71110815 | 15609437 | 47117437 | -99844063 | 50012634 | 25985189 | 13417067 | 0.000000 | 0.000000
09-04-2025 18:42:10.000 | 12726664 | 127266640 | 127.2666 | 69934976 | 15608962 | 47146899 | -99849358 | 50017696 | 25808555 | 13319846 | 0.000000 | 0.000000
09-04-2025 18:42:05.000 | 12717702 | 127177020 | 127.177 | 68496040 | 15612445 | 47100869 | -99855278 | 50008545 | 25631867 | 13224219 | 0.000000 | 0.000000
09-04-2025 18:42:00.000 | 12689848 | 126898480 | 126.8985 | 69073022 | 15614815 | 46991699 | -99852188 | 49980553 | 25455457 | 13128718 | 0.000000 | 0.000000
09-04-2025 18:41:55.000 | 12733971 | 127339710 | 127.3397 | 74006826 | 15610033 | 47179146 | -99831543 | 49965778 | 25279213 | 13030634 | 0.000000 | 0.000000
09-04-2025 18:41:50.000 | 12703542 | 127035420 | 127.0354 | 72836948 | 15612592 | 47056406 | -99836037 | 49992851 | 25102391 | 12928032 | 0.000000 | 0.000000
09-04-2025 18:41:45.000 | 12667187 | 126671870 | 126.6719 | 75536924 | 15613809 | 46924097 | -99822678 | 49956772 | 24926236 | 12826278 | 0.000000 | 0.000000
09-04-2025 18:41:40.000 | 12717986 | 127179860 | 127.1799 | 76640112 | 15611565 | 47121147 | -99818924 | 49949799 | 24750025 | 12720406 | 0.000000 | 0.000000
09-04-2025 18:41:35.000 | 12697984 | 126979840 | 126.9798 | 75309834 | 15612160 | 47042314 | -99824585 | 49967381 | 24573465 | 12615319 | 0.000000 | 0.000000
09-04-2025 18:41:30.000 | 12721088 | 127210880 | 127.2109 | 72597554 | 15609961 | 47128306 | -99837555 | 49974159 | 24396961 | 12511581 | 0.000000 | 0.000000
09-04-2025 18:41:25.000 | 12702312 | 127023120 | 127.0231 | 76201914 | 15610396 | 47065459 | -99820541 | 49962158 | 24220400 | 12409753 | 0.000000 | 0.000000
09-04-2025 18:41:20.000 | 12660902 | 126609020 | 126.609 | 74195181 | 15614683 | 46896172 | -99828735 | 49947083 | 24044020 | 12305635 | 0.000000 | 0.000000
09-04-2025 18:41:15.000 | 12672988 | 126729880 | 126.7299 | 74764922 | 15611505 | 46951094 | -99826431 | 49918766 | 23868070 | 12201676 | 0.000000 | 0.000000
09-04-2025 18:41:10.000 | 12686655 | 126866550 | 126.8666 | 73923369 | 15614308 | 46991479 | -99830673 | 49920391 | 23691621 | 12097826 | 0.000000 | 0.000000
09-04-2025 18:41:05.000 | 12731357 | 127313570 | 127.3136 | 74039395 | 15610107 | 47169092 | -99831329 | 49930912 | 23515236 | 11994519 | 0.000000 | 0.000000
09-04-2025 18:41:00.000 | 12671574 | 126715740 | 126.7157 | 74581079 | 15612307 | 46943208 | -99827240 | 49950878 | 23338525 | 11890962 | 0.000000 | 0.000000
09-04-2025 18:40:55.000 | 12718581 | 127185810 | 127.1858 | 74323442 | 15610772 | 47121069 | -99829689 | 49962044 | 23162098 | 11786630 | 0.000000 | 0.000000
09-04-2025 18:40:50.000 | 12703766 | 127037660 | 127.0377 | 74744014 | 15612203 | 47063438 | -99827362 | 49965664 | 22985656 | 11684026 | 0.000000 | 0.000000
09-04-2025 18:40:45.000 | 12780623 | 127806230 | 127.8062 | 77312866 | 15607493 | 47367080 | -99817535 | 49993755 | 22808842 | 11578544 | 0.000000 | 0.000000
09-04-2025 18:40:40.000 | 12775615 | 127756150 | 127.7562 | 72325288 | 15607643 | 47336694 | -99840141 | 50045216 | 22631465 | 11474374 | 0.000000 | 0.000000
09-04-2025 18:40:35.000 | 12697588 | 126975880 | 126.9759 | 68012856 | 15612397 | 47025132 | -99856857 | 50033543 | 22454613 | 11376309 | 0.000000 | 0.000000
09-04-2025 18:40:30.000 | 12715446 | 127154460 | 127.1545 | 68875781 | 15612520 | 47092783 | -99853622 | 50008923 | 22278283 | 11282036 | 0.000000 | 0.000000
09-04-2025 18:40:25.000 | 12717268 | 127172680 | 127.1727 | 68915146 | 15614917 | 47093008 | -99853493 | 49999069 | 22101781 | 11186414 | 0.000000 | 0.000000
09-04-2025 18:40:20.000 | 12673577 | 126735770 | 126.7358 | 73074341 | 15613197 | 46945957 | -99834183 | 49973537 | 21925805 | 11086302 | 0.000000 | 0.000000
09-04-2025 18:40:15.000 | 12667888 | 126678880 | 126.6789 | 75548496 | 15614476 | 46925781 | -99822639 | 49945477 | 21749621 | 10983225 | 0.000000 | 0.000000
09-04-2025 18:40:10.000 | 12635156 | 126351560 | 126.3516 | 77636621 | 15616897 | 46801470 | -99811760 | 49924042 | 21573707 | 10876727 | 0.000000 | 0.000000
09-04-2025 18:40:05.000 | 12664728 | 126647280 | 126.6473 | 81129053 | 15607917 | 46945845 | -99795448 | 49913376 | 21398027 | 10765848 | 0.000000 | 0.000000
09-04-2025 18:40:00.000 | 12616348 | 126163480 | 126.1635 | 77076040 | 15615574 | 46735581 | -99813911 | 49919025 | 21222047 | 10656252 | 0.000000 | 0.000000
09-04-2025 18:39:55.000 | 12701063 | 127010630 | 127.0106 | 78536577 | 15610168 | 47067280 | -99809372 | 49896351 | 21046307 | 10548480 | 0.000000 | 0.000000
09-04-2025 18:39:50.000 | 12717549 | 127175490 | 127.1755 | 77175361 | 15610952 | 47123135 | -99816376 | 49901630 | 20870111 | 10440096 | 0.000000 | 0.000000
09-04-2025 18:39:45.000 | 12708453 | 127084530 | 127.0845 | 72247031 | 15614023 | 47069507 | -99838799 | 49911800 | 20693615 | 10335221 | 0.000000 | 0.000000
09-04-2025 18:39:40.000 | 12714677 | 127146770 | 127.1468 | 74277422 | 15611195 | 47105874 | -99829796 | 49924763 | 20517150 | 10233119 | 0.000000 | 0.000000
09-04-2025 18:39:35.000 | 12761220 | 127612200 | 127.6122 | 71154219 | 15608906 | 47278237 | -99844910 | 49978752 | 20340250 | 10131483 | 0.000000 | 0.000000
09-04-2025 18:39:30.000 | 12764849 | 127648490 | 127.6485 | 70451748 | 15608708 | 47289629 | -99848038 | 50002159 | 20163328 | 10034965 | 0.000000 | 0.000000
09-04-2025 18:39:25.000 | 12762076 | 127620760 | 127.6208 | 68450137 | 15610832 | 47269922 | -99856468 | 50018528 | 19986107 | 993834656 | 0.000000 | 0.000000
09-04-2025 18:39:20.000 | 12728695 | 127286950 | 127.287 | 68072329 | 15612753 | 47139009 | -99857300 | 50005447 | 19809234 | 984411743 | 0.000000 | 0.000000
09-04-2025 18:39:15.000 | 12719913 | 127199130 | 127.1991 | 69964854 | 15614320 | 47105400 | -99849068 | 49990387 | 19632508 | 974865295 | 0.000000 | 0.000000
09-04-2025 18:39:10.000 | 12737191 | 127371910 | 127.3719 | 71066841 | 15608631 | 47190210 | -99844711 | 49990757 | 19455791 | 965035217 | 0.000000 | 0.000000
09-04-2025 18:39:05.000 | 12741020 | 127410200 | 127.4102 | 69830786 | 15610269 | 47196689 | -99850143 | 50010334 | 19278480 | 955282654 | 0.000000 | 0.000000
09-04-2025 18:39:00.000 | 12758344 | 127583440 | 127.5834 | 70026167 | 15609131 | 47263599 | -99849716 | 50020573 | 19101406 | 945572449 | 0.000000 | 0.000000
09-04-2025 18:38:55.000 | 12727523 | 127275230 | 127.2752 | 70128066 | 15611777 | 47142236 | -99848549 | 50014339 | 18924461 | 935849121 | 0.000000 | 0.000000
09-04-2025 18:38:50.000 | 12731045 | 127310450 | 127.3105 | 71915552 | 15615965 | 47147212 | -99840836 | 49989666 | 18747758 | 926113525 | 0.000000 | 0.000000
09-04-2025 18:38:45.000 | 12752734 | 127527340 | 127.5273 | 73573652 | 15609481 | 47250161 | -99833992 | 49975990 | 18571166 | 916014771 | 0.000000 | 0.000000
09-04-2025 18:38:40.000 | 12773066 | 127730660 | 127.7307 | 70461113 | 15606793 | 47326372 | -99848190 | 49998280 | 18394125 | 905972717 | 0.000000 | 0.000000
09-04-2025 18:38:35.000 | 12719934 | 127199340 | 127.1993 | 66572529 | 15615725 | 47095894 | -99863319 | 49984425 | 18217098 | 896524780 | 0.000000 | 0.000000
09-04-2025 18:38:30.000 | 12708191 | 127081910 | 127.0819 | 73549028 | 15616018 | 47065869 | -99832939 | 49924896 | 18040941 | 886807739 | 0.000000 | 0.000000
09-04-2025 18:38:25.000 | 12699592 | 126995920 | 126.9959 | 75006753 | 15615463 | 47038013 | -99826035 | 49916203 | 17864561 | 876400757 | 0.000000 | 0.000000
09-04-2025 18:38:20.000 | 12737686 | 127376860 | 127.3769 | 76132598 | 15611327 | 47193149 | -99821854 | 49908260 | 17688008 | 865916931 | 0.000000 | 0.000000
09-04-2025 18:38:15.000 | 12720603 | 127206030 | 127.206 | 75868125 | 15611693 | 47128960 | -99822617 | 49933819 | 17511063 | 855285400 | 0.000000 | 0.000000
09-04-2025 18:38:10.000 | 12722844 | 127228440 | 127.2284 | 74053687 | 15609860 | 47138203 | -99831039 | 49954632 | 17334045 | 844721497 | 0.000000 | 0.000000
09-04-2025 18:38:05.000 | 12733843 | 127338430 | 127.3384 | 71601431 | 15611291 | 47169521 | -99842285 | 49934250 | 17157357 | 834630371 | 0.000000 | 0.000000
09-04-2025 18:38:00.000 | 12715166 | 127151660 | 127.1517 | 71060801 | 15611206 | 47100054 | -99844200 | 49912128 | 16980789 | 824803528 | 0.000000 | 0.000000
09-04-2025 18:37:55.000 | 12713991 | 127139910 | 127.1399 | 70744971 | 15616617 | 47078799 | -99845551 | 49913486 | 16803967 | 815086731 | 0.000000 | 0.000000
09-04-2025 18:37:50.000 | 12764488 | 127644880 | 127.6449 | 73371128 | 15608511 | 47294829 | -99835205 | 49941380 | 16626945 | 804985901 | 0.000000 | 0.000000
09-04-2025 18:37:45.000 | 12735934 | 127359340 | 127.3593 | 70216021 | 15614554 | 47165366 | -99848366 | 49964489 | 16449834 | 795026733 | 0.000000 | 0.000000
09-04-2025 18:37:40.000 | 12739532 | 127395320 | 127.3953 | 72601997 | 15611294 | 47194414 | -99838005 | 49945274 | 16273186 | 785121033 | 0.000000 | 0.000000
09-04-2025 18:37:35.000 | 12735012 | 127350120 | 127.3501 | 74553955 | 15612978 | 47178101 | -99829079 | 49932213 | 16096521 | 774976257 | 0.000000 | 0.000000
09-04-2025 18:37:30.000 | 12729141 | 127291410 | 127.2914 | 72903345 | 15608653 | 47163755 | -99836395 | 49915962 | 15920139 | 764706909 | 0.000000 | 0.000000
09-04-2025 18:37:25.000 | 12724709 | 127247090 | 127.2471 | 71905942 | 15613264 | 47131006 | -99840721 | 49917278 | 15743152 | 754625061 | 0.000000 | 0.000000
09-04-2025 18:37:20.000 | 12699898 | 126998980 | 126.999 | 75204766 | 15612558 | 47049492 | -99825127 | 49909637 | 15566538 | 744433838 | 0.000000 | 0.000000
09-04-2025 18:37:15.000 | 12707955 | 127079550 | 127.0795 | 75990908 | 15613354 | 47078359 | -99821686 | 49886967 | 15390194 | 733969116 | 0.000000 | 0.000000
09-04-2025 18:37:10.000 | 12737191 | 127371910 | 127.3719 | 75930967 | 15609906 | 47196099 | -99822784 | 49900005 | 15213190 | 723335815 | 0.000000 | 0.000000
09-04-2025 18:37:05.000 | 12730189 | 127301890 | 127.3019 | 74136240 | 15607187 | 47174707 | -99830856 | 49916458 | 15036372 | 712859436 | 0.000000 | 0.000000
09-04-2025 18:37:00.000 | 12686820 | 126868200 | 126.8682 | 73804365 | 15614702 | 46990425 | -99831215 | 49894264 | 14860050 | 702767090 | 0.000000 | 0.000000
09-04-2025 18:36:55.000 | 12717130 | 127171300 | 127.1713 | 73254209 | 15611592 | 47110547 | -99834511 | 49875999 | 14683488 | 692579651 | 0.000000 | 0.000000
09-04-2025 18:36:50.000 | 12694748 | 126947480 | 126.9475 | 70485698 | 15611594 | 47022349 | -99846214 | 49869080 | 14507093 | 682599365 | 0.000000 | 0.000000
09-04-2025 18:36:45.000 | 12622052 | 126220520 | 126.2205 | 68943833 | 15620229 | 46725000 | -99851158 | 49833805 | 14330924 | 672914612 | 0.000000 | 0.000000
09-04-2025 18:36:40.000 | 12747198 | 127471980 | 127.472 | 73849463 | 15614511 | 47216250 | -99832603 | 49824768 | 14154746 | 663224548 | 0.000000 | 0.000000
09-04-2025 18:36:35.000 | 12979098 | 129790980 | 129.791 | 65904810 | 15593624 | 48119053 | -99871330 | 50007893 | 13976252 | 652968628 | 0.000000 | 0.000000
09-04-2025 18:36:30.000 | 12794823 | 127948230 | 127.9482 | 61055645 | 15612522 | 47371167 | -99886337 | 50053711 | 13798136 | 644416260 | 0.000000 | 0.000000
09-04-2025 18:36:25.000 | 12763188 | 127631880 | 127.6319 | 61665967 | 15612436 | 47254946 | -99883484 | 50065186 | 13620308 | 635850037 | 0.000000 | 0.000000
09-04-2025 18:36:20.000 | 12785334 | 127853340 | 127.8533 | 61512690 | 15610540 | 47342881 | -99884460 | 50069843 | 13442870 | 627282288 | 0.000000 | 0.000000
09-04-2025 18:36:15.000 | 12790199 | 127901990 | 127.902 | 60722334 | 15610020 | 47360435 | -99887497 | 50076679 | 13265388 | 618776855 | 0.000000 | 0.000000
09-04-2025 18:36:10.000 | 12770076 | 127700760 | 127.7008 | 60487954 | 15611511 | 47282021 | -99888008 | 50079681 | 13088034 | 610338562 | 0.000000 | 0.000000
09-04-2025 18:36:05.000 | 12774421 | 127744210 | 127.7442 | 60775947 | 15606677 | 47313105 | -99887016 | 50079311 | 12910481 | 601915833 | 0.000000 | 0.000000
09-04-2025 18:36:00.000 | 12715320 | 127153200 | 127.1532 | 54977520 | 15615034 | 47060420 | -99906654 | 50096584 | 12732771 | 593777466 | 0.000000 | 0.000000
09-04-2025 18:35:55.000 | 12747815 | 127478150 | 127.4781 | 62502046 | 15615565 | 47190732 | -99880020 | 50026222 | 12556298 | 585773254 | 0.000000 | 0.000000
09-04-2025 18:35:50.000 | 12794494 | 127944940 | 127.9449 | 64776133 | 15611122 | 47380239 | -99872086 | 50022064 | 12379238 | 576893066 | 0.000000 | 0.000000
09-04-2025 18:35:45.000 | 12762998 | 127629980 | 127.63 | 63512090 | 15612965 | 47256621 | -99876411 | 50031776 | 12201727 | 567926147 | 0.000000 | 0.000000
09-04-2025 18:35:40.000 | 12766338 | 127663380 | 127.6634 | 62640908 | 15608242 | 47281187 | -99879837 | 50045204 | 12024498 | 559041443 | 0.000000 | 0.000000
09-04-2025 18:35:35.000 | 12743452 | 127434520 | 127.4345 | 59837544 | 15610762 | 47184839 | -99889938 | 50056831 | 11847120 | 550569580 | 0.000000 | 0.000000
09-04-2025 18:35:30.000 | 12747560 | 127475600 | 127.4756 | 58833354 | 15614313 | 47187280 | -99893669 | 50045650 | 11669917 | 542342896 | 0.000000 | 0.000000
09-04-2025 18:35:25.000 | 12782047 | 127820470 | 127.8205 | 62562397 | 15615002 | 47318789 | -99880432 | 50020763 | 11492966 | 534026489 | 0.000000 | 0.000000
09-04-2025 18:35:20.000 | 12779587 | 127795870 | 127.7959 | 60640767 | 15612143 | 47316309 | -99887611 | 50056583 | 11315435 | 525248169 | 0.000000 | 0.000000
09-04-2025 18:35:15.000 | 12789452 | 127894520 | 127.8945 | 60157124 | 15609783 | 47357954 | -99889565 | 50072495 | 11137960 | 516845032 | 0.000000 | 0.000000
09-04-2025 18:35:10.000 | 12773548 | 127735480 | 127.7355 | 59187085 | 15611898 | 47291743 | -99892822 | 50069050 | 10960539 | 508622070 | 0.000000 | 0.000000
09-04-2025 18:35:05.000 | 12768739 | 127687390 | 127.6874 | 60165825 | 15609880 | 47281401 | -99889168 | 50065495 | 10783180 | 500337433 | 0.000000 | 0.000000
09-04-2025 18:35:00.000 | 12758542 | 127585420 | 127.5854 | 58455200 | 15613438 | 47229517 | -99895210 | 50067978 | 10605459 | 492099304 | 0.000000 | 0.000000
09-04-2025 18:34:55.000 | 12765854 | 127658540 | 127.6585 | 60600630 | 15612366 | 47264297 | -99887512 | 50041698 | 10428335 | 483885071 | 0.000000 | 0.000000
09-04-2025 18:34:50.000 | 12816198 | 128161980 | 128.162 | 60622671 | 15608712 | 47462427 | -99888313 | 50074360 | 10250763 | 475340790 | 0.000000 | 0.000000
09-04-2025 18:34:45.000 | 12742637 | 127426370 | 127.4264 | 59648472 | 15613904 | 47172197 | -99890617 | 50075623 | 10073180 | 466979614 | 0.000000 | 0.000000
09-04-2025 18:34:40.000 | 12744800 | 127448000 | 127.448 | 63207441 | 15614636 | 47183706 | -99877243 | 50037872 | 98962393 | 458579773 | 0.000000 | 0.000000
09-04-2025 18:34:35.000 | 12774805 | 127748050 | 127.7481 | 63171514 | 15608977 | 47311089 | -99877960 | 50052368 | 97189727 | 449677368 | 0.000000 | 0.000000
09-04-2025 18:34:30.000 | 12799746 | 127997460 | 127.9975 | 58826255 | 15607298 | 47401665 | -99894554 | 50106987 | 95411563 | 441144836 | 0.000000 | 0.000000
09-04-2025 18:34:25.000 | 12776622 | 127766220 | 127.7662 | 58472964 | 15611539 | 47302412 | -99895439 | 50107666 | 93636777 | 433104950 | 0.000000 | 0.000000
09-04-2025 18:34:20.000 | 12717352 | 127173520 | 127.1735 | 59705273 | 15615179 | 47074575 | -99889977 | 50068523 | 91868838 | 425015076 | 0.000000 | 0.000000
09-04-2025 18:34:15.000 | 12730570 | 127305700 | 127.3057 | 61261533 | 15613515 | 47130889 | -99884415 | 50053753 | 90100459 | 416498322 | 0.000000 | 0.000000
09-04-2025 18:34:10.000 | 12697264 | 126972640 | 126.9726 | 64873364 | 15613177 | 47015532 | -99869736 | 50009758 | 88335840 | 407879181 | 0.000000 | 0.000000
09-04-2025 18:34:05.000 | 12748099 | 127480990 | 127.481 | 64057178 | 15608030 | 47217510 | -99873993 | 50015381 | 86568564 | 398813385 | 0.000000 | 0.000000
09-04-2025 18:34:00.000 | 12727028 | 127270280 | 127.2703 | 63320859 | 15610974 | 47128833 | -99876457 | 50034229 | 84795771 | 390030701 | 0.000000 | 0.000000
09-04-2025 18:33:55.000 | 12787720 | 127877200 | 127.8772 | 62823228 | 15607899 | 47362588 | -99879539 | 50048943 | 83027861 | 381334747 | 0.000000 | 0.000000
09-04-2025 18:33:50.000 | 12760014 | 127600140 | 127.6001 | 60040503 | 15610282 | 47247056 | -99889481 | 50069145 | 81255122 | 372752502 | 0.000000 | 0.000000
09-04-2025 18:33:45.000 | 12696875 | 126968750 | 126.9688 | 59147500 | 15616604 | 46994204 | -99891670 | 50046932 | 79486636 | 364547882 | 0.000000 | 0.000000
09-04-2025 18:33:40.000 | 12736661 | 127366610 | 127.3666 | 62541895 | 15614992 | 47151045 | -99879662 | 50020939 | 77722544 | 356208893 | 0.000000 | 0.000000
09-04-2025 18:33:35.000 | 12757170 | 127571700 | 127.5717 | 62253960 | 15611306 | 47237446 | -99881142 | 50049736 | 75950942 | 347421692 | 0.000000 | 0.000000
09-04-2025 18:33:30.000 | 12732985 | 127329850 | 127.3298 | 61136821 | 15609495 | 47152104 | -99884926 | 50072926 | 74177642 | 338763672 | 0.000000 | 0.000000
09-04-2025 18:33:25.000 | 12717323 | 127173230 | 127.1732 | 60076670 | 15612730 | 47082080 | -99888603 | 50070004 | 72409478 | 330262543 | 0.000000 | 0.000000
09-04-2025 18:33:20.000 | 12722241 | 127222410 | 127.2224 | 63343306 | 15612106 | 47108584 | -99876282 | 50028091 | 70645884 | 321880157 | 0.000000 | 0.000000
09-04-2025 18:33:15.000 | 12756722 | 127567220 | 127.5672 | 62386685 | 15610123 | 47240439 | -99880630 | 50035061 | 68878369 | 313142548 | 0.000000 | 0.000000
09-04-2025 18:33:10.000 | 12758132 | 127581320 | 127.5813 | 59649370 | 15608091 | 47246265 | -99890884 | 50037598 | 67112368 | 304596130 | 0.000000 | 0.000000
09-04-2025 18:33:05.000 | 12666004 | 126660040 | 126.66 | 58417544 | 15612667 | 46890479 | -99893806 | 50034702 | 65343633 | 296377136 | 0.000000 | 0.000000
09-04-2025 18:33:00.000 | 12686722 | 126867220 | 126.8672 | 59446309 | 15610829 | 46974043 | -99890404 | 50018391 | 63579976 | 288231873 | 0.000000 | 0.000000
09-04-2025 18:32:55.000 | 12670501 | 126705010 | 126.705 | 61590029 | 15615321 | 46903906 | -99882065 | 49990162 | 61818291 | 279969177 | 0.000000 | 0.000000
09-04-2025 18:32:50.000 | 12703959 | 127039590 | 127.0396 | 64619961 | 15612379 | 47041899 | -99870880 | 49968479 | 60056587 | 271295013 | 0.000000 | 0.000000
09-04-2025 18:32:45.000 | 12742505 | 127425050 | 127.425 | 60510552 | 15609877 | 47184595 | -99887436 | 49998798 | 58290605 | 262548401 | 0.000000 | 0.000000
09-04-2025 18:32:40.000 | 12716223 | 127162230 | 127.1622 | 59477349 | 15610778 | 47083369 | -99890793 | 50020817 | 56523208 | 254229279 | 0.000000 | 0.000000
09-04-2025 18:32:35.000 | 12693488 | 126934880 | 126.9349 | 55915571 | 15610339 | 46994961 | -99903122 | 50049339 | 54755098 | 246047379 | 0.000000 | 0.000000
09-04-2025 18:32:30.000 | 12699419 | 126994190 | 126.9942 | 56876440 | 15612132 | 47012944 | -99899857 | 50037258 | 52989541 | 238301407 | 0.000000 | 0.000000
09-04-2025 18:32:25.000 | 12683039 | 126830390 | 126.8304 | 57589341 | 15614116 | 46948140 | -99897072 | 50017471 | 51225864 | 230423126 | 0.000000 | 0.000000
09-04-2025 18:32:20.000 | 12738506 | 127385060 | 127.3851 | 59644941 | 15611455 | 47163677 | -99890564 | 50026295 | 49460278 | 222298782 | 0.000000 | 0.000000
09-04-2025 18:32:15.000 | 12770205 | 127702050 | 127.702 | 58501606 | 15609794 | 47283521 | -99895233 | 50061115 | 47689980 | 214102554 | 0.000000 | 0.000000
09-04-2025 18:32:10.000 | 12730837 | 127308370 | 127.3084 | 51862139 | 15607579 | 47134155 | -99917130 | 50086254 | 45919888 | 206135315 | 0.000000 | 0.000000
09-04-2025 18:32:05.000 | 12632366 | 126323660 | 126.3237 | 51533076 | 15616610 | 46742871 | -99916893 | 50040749 | 44156577 | 199017181 | 0.000000 | 0.000000
09-04-2025 18:32:00.000 | 12647855 | 126478550 | 126.4785 | 58537246 | 15616939 | 46810679 | -99893066 | 49974049 | 42399136 | 191580673 | 0.000000 | 0.000000
09-04-2025 18:31:55.000 | 12749048 | 127490480 | 127.4905 | 60085039 | 15610949 | 47205591 | -99889130 | 49963253 | 40638521 | 183375092 | 0.000000 | 0.000000
09-04-2025 18:31:50.000 | 12751890 | 127518900 | 127.5189 | 57758745 | 15608768 | 47217896 | -99897575 | 50019379 | 38866948 | 175149033 | 0.000000 | 0.000000
09-04-2025 18:31:45.000 | 12733629 | 127336290 | 127.3363 | 54175205 | 15609539 | 47142695 | -99909622 | 50062653 | 37095586 | 167304642 | 0.000000 | 0.000000
09-04-2025 18:31:40.000 | 12710397 | 127103970 | 127.104 | 52052598 | 15611692 | 47047485 | -99916252 | 50075142 | 35326245 | 159911423 | 0.000000 | 0.000000
09-04-2025 18:31:35.000 | 12714003 | 127140030 | 127.14 | 53310371 | 15613017 | 47057910 | -99912209 | 50042938 | 33561052 | 152632599 | 0.000000 | 0.000000
09-04-2025 18:31:30.000 | 12721137 | 127211370 | 127.2114 | 55086343 | 15612403 | 47089609 | -99906372 | 50037434 | 31795737 | 145155807 | 0.000000 | 0.000000
09-04-2025 18:31:25.000 | 12682731 | 126827310 | 126.8273 | 53681636 | 15612418 | 46945083 | -99910545 | 50052494 | 30031138 | 137476028 | 0.000000 | 0.000000
09-04-2025 18:31:20.000 | 12680709 | 126807090 | 126.8071 | 55355840 | 15615307 | 46931475 | -99904854 | 50035461 | 28266221 | 130014328 | 0.000000 | 0.000000
09-04-2025 18:31:15.000 | 12728769 | 127287690 | 127.2877 | 56317886 | 15610361 | 47126177 | -99902267 | 50039291 | 26499678 | 122204414 | 0.000000 | 0.000000
09-04-2025 18:31:10.000 | 12747341 | 127473410 | 127.4734 | 53453442 | 15611475 | 47185615 | -99912193 | 50080814 | 24726992 | 114514290 | 0.000000 | 0.000000
09-04-2025 18:31:05.000 | 12769527 | 127695270 | 127.6953 | 52267412 | 15610873 | 47267739 | -99916336 | 50117256 | 22954109 | 107149185 | 0.000000 | 0.000000
09-04-2025 18:31:00.000 | 12773841 | 127738410 | 127.7384 | 53869590 | 15608321 | 47294458 | -99911194 | 50126415 | 21182292 | 99880135 | 0.000000 | 0.000000
09-04-2025 18:30:55.000 | 12749187 | 127491870 | 127.4919 | 52322480 | 15611357 | 47191890 | -99915894 | 50153561 | 19407323 | 92454964 | 0.000000 | 0.000000
09-04-2025 18:30:50.000 | 12731527 | 127315270 | 127.3153 | 54135933 | 15614019 | 47121519 | -99909721 | 50132973 | 17638350 | 85168144 | 0.000000 | 0.000000
09-04-2025 18:30:45.000 | 12694112 | 126941120 | 126.9411 | 58546938 | 15615427 | 46986011 | -99893814 | 50077866 | 15875587 | 77486694 | 0.000000 | 0.000000
09-04-2025 18:30:40.000 | 12750187 | 127501870 | 127.5019 | 62464233 | 15606720 | 47226743 | -99880211 | 50089058 | 14106761 | 69024529 | 0.000000 | 0.000000
09-04-2025 18:30:35.000 | 12728897 | 127288970 | 127.289 | 58979448 | 15612472 | 47124893 | -99892822 | 50112823 | 12335857 | 60658730 | 0.000000 | 0.000000
09-04-2025 18:30:30.000 | 12714168 | 127141680 | 127.1417 | 60767212 | 15611071 | 47077461 | -99885979 | 50097439 | 10571710 | 52386719 | 0.000000 | 0.000000
09-04-2025 18:30:25.000 | 12677589 | 126775890 | 126.7759 | 61996328 | 15614681 | 46933379 | -99880646 | 50074959 | 880946899 | 43904457 | 0.000000 | 0.000000
09-04-2025 18:30:20.000 | 12630357 | 126303570 | 126.3036 | 63688774 | 15616232 | 46757295 | -99873108 | 50043972 | 705056274 | 35286526 | 0.000000 | 0.000000
09-04-2025 18:30:15.000 | 12672951 | 126729510 | 126.7295 | 65316675 | 15609319 | 46938354 | -99867447 | 50045708 | 528906250 | 26331993 | 0.000000 | 0.000000
09-04-2025 18:30:10.000 | 12709574 | 127095740 | 127.0957 | 61715679 | 15611680 | 47060122 | -99882309 | 50082977 | 352349487 | 17461578 | 0.000000 | 0.000000
09-04-2025 18:30:05.000 | 12672539 | 126725390 | 126.7254 | 63467754 | 15617113 | 46909795 | -99874817 | 50060341 | 176322815 | 8941641 | 0.000000 | 0.000000
09-04-2025 18:30:00.000 | 12706482 | 127064820 | 127.0648 | 63181870 | 15608117 | 47062017 | -99876602 | 50081745 | 31541770 | 13911138 | 0.000000 | 0.000000
09-04-2025 18:29:55.000 | 12721327 | 127213270 | 127.2133 | 58453877 | 15609444 | 47104214 | -99894600 | 50127857 | 31364893 | 13826030 | 0.000000 | 0.000000
09-04-2025 18:29:50.000 | 12691300 | 126913000 | 126.913 | 58928486 | 15613365 | 46981782 | -99892380 | 50105320 | 31188691 | 13745984 | 0.000000 | 0.000000
09-04-2025 18:29:45.000 | 12708214 | 127082140 | 127.0821 | 59789497 | 15612818 | 47048164 | -99889511 | 50098316 | 31012508 | 13663392 | 0.000000 | 0.000000
09-04-2025 18:29:40.000 | 12753120 | 127531200 | 127.5312 | 60817197 | 15609908 | 47226084 | -99886482 | 50105835 | 30836111 | 13580565 | 0.000000 | 0.000000
09-04-2025 18:29:35.000 | 12752734 | 127527340 | 127.5273 | 55618921 | 15608910 | 47217837 | -99905029 | 50147568 | 30659119 | 13498145 | 0.000000 | 0.000000
09-04-2025 18:29:30.000 | 12707263 | 127072630 | 127.0726 | 53996865 | 15610425 | 47041899 | -99909843 | 50155853 | 30482232 | 13422236 | 0.000000 | 0.000000
09-04-2025 18:29:25.000 | 12674062 | 126740620 | 126.7406 | 54636143 | 15612511 | 46914331 | -99907211 | 50140106 | 30305941 | 13347683 | 0.000000 | 0.000000
09-04-2025 18:29:20.000 | 12721009 | 127210090 | 127.2101 | 57611299 | 15610025 | 47099580 | -99897606 | 50130360 | 30129621 | 13270774 | 0.000000 | 0.000000
09-04-2025 18:29:15.000 | 12716347 | 127163470 | 127.1635 | 58306880 | 15609298 | 47087031 | -99895042 | 50134811 | 29953344 | 13190804 | 0.000000 | 0.000000
09-04-2025 18:29:10.000 | 12670945 | 126709450 | 126.7095 | 57368037 | 15612478 | 46907983 | -99897667 | 50140266 | 29777277 | 13111077 | 0.000000 | 0.000000
09-04-2025 18:29:05.000 | 12645000 | 126450000 | 126.45 | 59353306 | 15612528 | 46814956 | -99890022 | 50110664 | 29601695 | 13030836 | 0.000000 | 0.000000
09-04-2025 18:29:00.000 | 12638377 | 126383770 | 126.3838 | 61084092 | 15613569 | 46791157 | -99883408 | 50093449 | 29425934 | 12947997 | 0.000000 | 0.000000
09-04-2025 18:28:55.000 | 12635186 | 126351860 | 126.3519 | 59807705 | 15612895 | 46777925 | -99888161 | 50082962 | 29250609 | 12863849 | 0.000000 | 0.000000
09-04-2025 18:28:50.000 | 12681034 | 126810340 | 126.8103 | 61105547 | 15607665 | 46964878 | -99884102 | 50083496 | 29074980 | 12779410 | 0.000000 | 0.000000
09-04-2025 18:28:45.000 | 12686501 | 126865010 | 126.865 | 60434355 | 15610421 | 46976035 | -99886726 | 50099010 | 28898992 | 12694805 | 0.000000 | 0.000000
09-04-2025 18:28:40.000 | 12674110 | 126741100 | 126.7411 | 58325156 | 15611877 | 46921841 | -99894279 | 50096291 | 28723193 | 12613165 | 0.000000 | 0.000000
09-04-2025 18:28:35.000 | 12654957 | 126549570 | 126.5496 | 58886343 | 15613124 | 46848667 | -99891914 | 50098816 | 28547232 | 12531420 | 0.000000 | 0.000000
09-04-2025 18:28:30.000 | 12682196 | 126821960 | 126.822 | 58957495 | 15611719 | 46953618 | -99892113 | 50112484 | 28371160 | 12448707 | 0.000000 | 0.000000
09-04-2025 18:28:25.000 | 12701465 | 127014650 | 127.0147 | 55332012 | 15608018 | 47029893 | -99905243 | 50151054 | 28195002 | 12367822 | 0.000000 | 0.000000
09-04-2025 18:28:20.000 | 12691183 | 126911830 | 126.9118 | 52013511 | 15612065 | 46974766 | -99916122 | 50165325 | 28018482 | 12294041 | 0.000000 | 0.000000
09-04-2025 18:28:15.000 | 12652800 | 126528000 | 126.528 | 52898115 | 15611271 | 46836704 | -99912720 | 50130989 | 27842705 | 12222152 | 0.000000 | 0.000000
09-04-2025 18:28:10.000 | 12595980 | 125959800 | 125.9598 | 52718335 | 15616534 | 46611685 | -99912529 | 50108807 | 27666945 | 12148622 | 0.000000 | 0.000000
09-04-2025 18:28:05.000 | 12658553 | 126585530 | 126.5855 | 59013735 | 15615341 | 46855654 | -99891510 | 50082718 | 27491641 | 12072167 | 0.000000 | 0.000000
09-04-2025 18:28:00.000 | 12706593 | 127065930 | 127.0659 | 58666904 | 15609206 | 47050591 | -99893585 | 50112713 | 27315629 | 11989614 | 0.000000 | 0.000000
09-04-2025 18:27:55.000 | 12714380 | 127143800 | 127.1438 | 53534009 | 15610241 | 47068257 | -99911476 | 50162849 | 27138879 | 11909774 | 0.000000 | 0.000000
09-04-2025 18:27:50.000 | 12678155 | 126781550 | 126.7815 | 52466914 | 15612034 | 46927168 | -99914482 | 50165531 | 26962557 | 11836226 | 0.000000 | 0.000000
09-04-2025 18:27:45.000 | 12711941 | 127119410 | 127.1194 | 55700288 | 15608694 | 47067500 | -99904137 | 50162273 | 26786328 | 11761538 | 0.000000 | 0.000000
09-04-2025 18:27:40.000 | 12666865 | 126668650 | 126.6686 | 52574878 | 15612756 | 46883701 | -99913971 | 50166317 | 26610270 | 11687155 | 0.000000 | 0.000000
09-04-2025 18:27:35.000 | 12609572 | 126095720 | 126.0957 | 55588188 | 15615494 | 46668652 | -99902969 | 50132153 | 26434795 | 11613221 | 0.000000 | 0.000000
09-04-2025 18:27:30.000 | 12684914 | 126849140 | 126.8491 | 58015776 | 15609253 | 46969893 | -99895576 | 50135693 | 26259016 | 11534296 | 0.000000 | 0.000000
09-04-2025 18:27:25.000 | 12674625 | 126746250 | 126.7463 | 56044277 | 15614250 | 46913989 | -99902382 | 50136311 | 26082898 | 11455510 | 0.000000 | 0.000000
09-04-2025 18:27:20.000 | 12657820 | 126578200 | 126.5782 | 58210850 | 15611705 | 46862485 | -99894424 | 50113991 | 25907201 | 11375839 | 0.000000 | 0.000000
09-04-2025 18:27:15.000 | 12611100 | 126111000 | 126.111 | 57880928 | 15613031 | 46687036 | -99894844 | 50115940 | 25731439 | 11294840 | 0.000000 | 0.000000
09-04-2025 18:27:10.000 | 12632829 | 126328290 | 126.3283 | 57253350 | 15613558 | 46763989 | -99897461 | 50109985 | 25555867 | 11214060 | 0.000000 | 0.000000
09-04-2025 18:27:05.000 | 12677390 | 126773900 | 126.7739 | 60044380 | 15606710 | 46952886 | -99888023 | 50104641 | 25380295 | 11132866 | 0.000000 | 0.000000
09-04-2025 18:27:00.000 | 12641214 | 126412140 | 126.4121 | 55081841 | 15612151 | 46795127 | -99905205 | 50129536 | 25204402 | 11052510 | 0.000000 | 0.000000
09-04-2025 18:26:55.000 | 12653668 | 126536680 | 126.5367 | 54836963 | 15610761 | 46844844 | -99906227 | 50121189 | 25028906 | 10976519 | 0.000000 | 0.000000
09-04-2025 18:26:50.000 | 12637305 | 126373050 | 126.3731 | 54770181 | 15611539 | 46782124 | -99906212 | 50130505 | 24853121 | 10900914 | 0.000000 | 0.000000
09-04-2025 18:26:45.000 | 12647159 | 126471590 | 126.4716 | 52768057 | 15609948 | 46819897 | -99913071 | 50143078 | 24677443 | 10825034 | 0.000000 | 0.000000
09-04-2025 18:26:40.000 | 12617430 | 126174300 | 126.1743 | 53359844 | 15613590 | 46700386 | -99910698 | 50134090 | 24501748 | 10752034 | 0.000000 | 0.000000
09-04-2025 18:26:35.000 | 12635609 | 126356090 | 126.3561 | 53797295 | 15609444 | 46780386 | -99909485 | 50146347 | 24326127 | 10676903 | 0.000000 | 0.000000
09-04-2025 18:26:30.000 | 12625473 | 126254730 | 126.2547 | 52730322 | 15613635 | 46729194 | -99912895 | 50145592 | 24150629 | 10603335 | 0.000000 | 0.000000
09-04-2025 18:26:25.000 | 12615094 | 126150940 | 126.1509 | 53865806 | 15614560 | 46689019 | -99908958 | 50140228 | 23975074 | 10529542 | 0.000000 | 0.000000
09-04-2025 18:26:20.000 | 12649873 | 126498730 | 126.4987 | 55360967 | 15612583 | 46825776 | -99904373 | 50127708 | 23799666 | 10453500 | 0.000000 | 0.000000
09-04-2025 18:26:15.000 | 12626825 | 126268250 | 126.2682 | 55276040 | 15608168 | 46754019 | -99904320 | 50134884 | 23624156 | 10376306 | 0.000000 | 0.000000
09-04-2025 18:26:10.000 | 12581079 | 125810790 | 125.8108 | 53799775 | 15615846 | 46559829 | -99908691 | 50121746 | 23448969 | 10301296 | 0.000000 | 0.000000
09-04-2025 18:26:05.000 | 12635402 | 126354020 | 126.354 | 57329263 | 15614116 | 46771436 | -99897224 | 50100151 | 23273898 | 10225038 | 0.000000 | 0.000000
09-04-2025 18:26:00.000 | 12661749 | 126617490 | 126.6175 | 57083428 | 15608278 | 46885146 | -99898529 | 50116043 | 23098494 | 10144784 | 0.000000 | 0.000000
09-04-2025 18:25:55.000 | 12615704 | 126157040 | 126.157 | 54469888 | 15612717 | 46697974 | -99906921 | 50126431 | 22922646 | 10067013 | 0.000000 | 0.000000
09-04-2025 18:25:50.000 | 12607546 | 126075460 | 126.0755 | 55027095 | 15612337 | 46669751 | -99904884 | 50109646 | 22747348 | 999130493 | 0.000000 | 0.000000
09-04-2025 18:25:45.000 | 12618261 | 126182610 | 126.1826 | 55483755 | 15610811 | 46714639 | -99903465 | 50103718 | 22572100 | 991452209 | 0.000000 | 0.000000
09-04-2025 18:25:40.000 | 12666819 | 126668190 | 126.6682 | 55461748 | 15608222 | 46901084 | -99904282 | 50118420 | 22396684 | 983780884 | 0.000000 | 0.000000
09-04-2025 18:25:35.000 | 12653793 | 126537930 | 126.5379 | 50166030 | 15611396 | 46835591 | -99921509 | 50153278 | 22220820 | 976374695 | 0.000000 | 0.000000
09-04-2025 18:25:30.000 | 12616613 | 126166130 | 126.1661 | 51270122 | 15614699 | 46690913 | -99917534 | 50126175 | 22045656 | 969405884 | 0.000000 | 0.000000
09-04-2025 18:25:25.000 | 12688110 | 126881100 | 126.8811 | 52776021 | 15606276 | 46982485 | -99913605 | 50155266 | 21869695 | 961976563 | 0.000000 | 0.000000
09-04-2025 18:25:20.000 | 12635248 | 126352480 | 126.3525 | 49924038 | 15614106 | 46758647 | -99922035 | 50169945 | 21693463 | 954857666 | 0.000000 | 0.000000
09-04-2025 18:25:15.000 | 12626213 | 126262130 | 126.2621 | 51820898 | 15612496 | 46734229 | -99915886 | 50145725 | 21517922 | 947673096 | 0.000000 | 0.000000
09-04-2025 18:25:10.000 | 12605799 | 126057990 | 126.058 | 54120894 | 15617618 | 46646475 | -99907967 | 50120304 | 21342355 | 940367065 | 0.000000 | 0.000000
09-04-2025 18:25:05.000 | 12717581 | 127175810 | 127.1758 | 56455879 | 15606725 | 47096104 | -99901611 | 50136978 | 21166590 | 932605774 | 0.000000 | 0.000000
09-04-2025 18:25:00.000 | 12667590 | 126675900 | 126.6759 | 53325972 | 15611172 | 46893779 | -99911514 | 50149364 | 20990584 | 925056702 | 0.000000 | 0.000000
09-04-2025 18:24:55.000 | 12636455 | 126364550 | 126.3645 | 53220000 | 15612678 | 46772598 | -99911430 | 50124905 | 20815004 | 917686829 | 0.000000 | 0.000000
09-04-2025 18:24:50.000 | 12625388 | 126253880 | 126.2539 | 54760894 | 15614636 | 46728306 | -99906067 | 50103596 | 20639662 | 910309753 | 0.000000 | 0.000000
09-04-2025 18:24:45.000 | 12618073 | 126180730 | 126.1807 | 54855537 | 15612350 | 46709429 | -99905632 | 50112000 | 20464162 | 902640381 | 0.000000 | 0.000000
09-04-2025 18:24:40.000 | 12646109 | 126461090 | 126.4611 | 53939932 | 15610073 | 46817104 | -99909157 | 50126034 | 20288641 | 895023865 | 0.000000 | 0.000000
09-04-2025 18:24:35.000 | 12663182 | 126631820 | 126.6318 | 52258379 | 15609960 | 46878237 | -99914955 | 50146835 | 20112873 | 887630127 | 0.000000 | 0.000000
09-04-2025 18:24:30.000 | 12688079 | 126880790 | 126.8808 | 51489829 | 15612240 | 46962319 | -99917763 | 50152309 | 19937068 | 880494446 | 0.000000 | 0.000000
09-04-2025 18:24:25.000 | 12675811 | 126758110 | 126.7581 | 51805264 | 15608748 | 46927446 | -99916588 | 50140316 | 19761496 | 873353516 | 0.000000 | 0.000000
09-04-2025 18:24:20.000 | 12632534 | 126325340 | 126.3253 | 50776353 | 15612106 | 46755767 | -99919319 | 50149326 | 19585586 | 866248596 | 0.000000 | 0.000000
09-04-2025 18:24:15.000 | 12615211 | 126152110 | 126.1521 | 52886987 | 15612764 | 46693687 | -99912239 | 50132549 | 19410219 | 859071106 | 0.000000 | 0.000000
09-04-2025 18:24:10.000 | 12621444 | 126214440 | 126.2144 | 53650601 | 15610967 | 46723218 | -99909775 | 50141777 | 19234721 | 851646606 | 0.000000 | 0.000000
09-04-2025 18:24:05.000 | 12618052 | 126180520 | 126.1805 | 52787002 | 15615399 | 46697061 | -99912605 | 50119621 | 19059512 | 844277100 | 0.000000 | 0.000000
09-04-2025 18:24:00.000 | 12597322 | 125973220 | 125.9732 | 56024814 | 15612878 | 46631255 | -99901253 | 50092323 | 18884480 | 836666809 | 0.000000 | 0.000000
09-04-2025 18:23:55.000 | 12593281 | 125932810 | 125.9328 | 55497456 | 15612356 | 46618003 | -99903038 | 50087231 | 18709309 | 828846130 | 0.000000 | 0.000000
09-04-2025 18:23:50.000 | 12640384 | 126403840 | 126.4038 | 57193955 | 15611096 | 46798169 | -99897789 | 50088940 | 18534084 | 821080261 | 0.000000 | 0.000000
09-04-2025 18:23:45.000 | 12652223 | 126522230 | 126.5222 | 52090498 | 15609967 | 46837993 | -99915352 | 50110153 | 18358547 | 813386047 | 0.000000 | 0.000000
09-04-2025 18:23:40.000 | 12581768 | 125817680 | 125.8177 | 53367979 | 15614896 | 46565156 | -99910164 | 50096870 | 18183059 | 806134949 | 0.000000 | 0.000000
09-04-2025 18:23:35.000 | 12606843 | 126068430 | 126.0684 | 55271519 | 15610392 | 46673755 | -99904030 | 50081779 | 18007992 | 798599976 | 0.000000 | 0.000000
09-04-2025 18:23:30.000 | 12590381 | 125903810 | 125.9038 | 53769023 | 15615250 | 46595898 | -99908936 | 50093548 | 17832523 | 790956482 | 0.000000 | 0.000000
09-04-2025 18:23:25.000 | 12629209 | 126292090 | 126.2921 | 56065791 | 15613423 | 46748140 | -99901604 | 50081188 | 17657309 | 783327148 | 0.000000 | 0.000000
09-04-2025 18:23:20.000 | 12661948 | 126619480 | 126.6195 | 54386626 | 15609470 | 46878262 | -99907883 | 50100269 | 17481779 | 775574829 | 0.000000 | 0.000000
09-04-2025 18:23:15.000 | 12619259 | 126192590 | 126.1926 | 52044756 | 15611974 | 46709214 | -99915062 | 50113899 | 17306037 | 768171326 | 0.000000 | 0.000000
09-04-2025 18:23:10.000 | 12631245 | 126312450 | 126.3124 | 52845464 | 15611367 | 46756533 | -99912598 | 50104965 | 17130920 | 760853516 | 0.000000 | 0.000000
09-04-2025 18:23:05.000 | 12601805 | 126018050 | 126.0181 | 53983652 | 15614952 | 46639102 | -99908371 | 50085598 | 16955689 | 753548950 | 0.000000 | 0.000000
09-04-2025 18:23:00.000 | 12640820 | 126408200 | 126.4082 | 58326953 | 15607546 | 46812339 | -99893715 | 50083237 | 16780545 | 745755737 | 0.000000 | 0.000000
09-04-2025 18:22:55.000 | 12636988 | 126369880 | 126.3699 | 56040254 | 15607593 | 46794795 | -99901817 | 50098671 | 16605029 | 737877930 | 0.000000 | 0.000000
09-04-2025 18:22:50.000 | 12610166 | 126101660 | 126.1017 | 53298066 | 15614340 | 46670542 | -99910797 | 50099609 | 16429586 | 730318359 | 0.000000 | 0.000000
09-04-2025 18:22:45.000 | 12645107 | 126451070 | 126.4511 | 56546689 | 15610853 | 46816831 | -99900162 | 50084282 | 16254599 | 722686890 | 0.000000 | 0.000000
09-04-2025 18:22:40.000 | 12592453 | 125924530 | 125.9245 | 55441694 | 15614151 | 46610391 | -99903221 | 50074650 | 16079457 | 714979553 | 0.000000 | 0.000000
09-04-2025 18:22:35.000 | 12626299 | 126262990 | 126.263 | 57686924 | 15611231 | 46746152 | -99895790 | 50060459 | 15904674 | 707149597 | 0.000000 | 0.000000
09-04-2025 18:22:30.000 | 12572558 | 125725580 | 125.7256 | 57967334 | 15611830 | 46548145 | -99893883 | 50063251 | 15729622 | 699120056 | 0.000000 | 0.000000
09-04-2025 18:22:25.000 | 12616293 | 126162930 | 126.1629 | 58318989 | 15609760 | 46715679 | -99893333 | 50065617 | 15554649 | 691106140 | 0.000000 | 0.000000
09-04-2025 18:22:20.000 | 12617188 | 126171880 | 126.1719 | 56314258 | 15610853 | 46712827 | -99900543 | 50070072 | 15379758 | 683168579 | 0.000000 | 0.000000
09-04-2025 18:22:15.000 | 12573999 | 125739990 | 125.74 | 55276040 | 15616874 | 46532896 | -99903511 | 50058941 | 15204972 | 675485718 | 0.000000 | 0.000000
09-04-2025 18:22:10.000 | 12614770 | 126147700 | 126.1477 | 57792915 | 15612958 | 46699941 | -99895218 | 50058243 | 15030270 | 667562622 | 0.000000 | 0.000000
09-04-2025 18:22:05.000 | 12556666 | 125566660 | 125.5667 | 57255078 | 15610675 | 46490361 | -99896202 | 50065727 | 14855437 | 659471375 | 0.000000 | 0.000000
09-04-2025 18:22:00.000 | 12583345 | 125833450 | 125.8334 | 55566880 | 15609855 | 46588037 | -99902641 | 50086212 | 14680674 | 651592834 | 0.000000 | 0.000000
09-04-2025 18:21:55.000 | 12555989 | 125559890 | 125.5599 | 55537241 | 15614009 | 46475249 | -99902321 | 50082741 | 14505891 | 643882507 | 0.000000 | 0.000000
09-04-2025 18:21:50.000 | 12601413 | 126014130 | 126.0141 | 57136753 | 15611668 | 46653066 | -99897362 | 50061657 | 14331417 | 636056152 | 0.000000 | 0.000000
09-04-2025 18:21:45.000 | 12576927 | 125769270 | 125.7693 | 57243521 | 15613548 | 46556270 | -99896584 | 50060257 | 14156398 | 628059326 | 0.000000 | 0.000000
09-04-2025 18:21:40.000 | 12529944 | 125299440 | 125.2994 | 59225283 | 15614516 | 46384238 | -99888481 | 50028522 | 13981830 | 620105103 | 0.000000 | 0.000000
09-04-2025 18:21:35.000 | 12594087 | 125940870 | 125.9409 | 60190732 | 15611331 | 46631953 | -99885986 | 50021740 | 13807440 | 611752747 | 0.000000 | 0.000000
09-04-2025 18:21:30.000 | 12611815 | 126118150 | 126.1181 | 59630571 | 15611924 | 46695889 | -99888412 | 50029484 | 13632618 | 603461792 | 0.000000 | 0.000000
09-04-2025 18:21:25.000 | 12633980 | 126339800 | 126.3398 | 58653301 | 15607605 | 46790195 | -99892410 | 50055077 | 13457558 | 595141968 | 0.000000 | 0.000000
09-04-2025 18:21:20.000 | 12534732 | 125347320 | 125.3473 | 55438311 | 15615488 | 46392603 | -99902336 | 50056458 | 13282758 | 587181946 | 0.000000 | 0.000000
09-04-2025 18:21:15.000 | 12586721 | 125867210 | 125.8672 | 56107207 | 15609861 | 46601523 | -99900795 | 50059708 | 13108084 | 579326477 | 0.000000 | 0.000000
09-04-2025 18:21:10.000 | 12607845 | 126078450 | 126.0785 | 54838745 | 15607895 | 46685317 | -99905540 | 50089077 | 12933104 | 571596985 | 0.000000 | 0.000000
09-04-2025 18:21:05.000 | 12566347 | 125663470 | 125.6635 | 51241172 | 15614364 | 46505308 | -99916969 | 50086479 | 12758143 | 564229492 | 0.000000 | 0.000000
09-04-2025 18:21:00.000 | 12555918 | 125559180 | 125.5592 | 53013105 | 15614990 | 46468696 | -99910988 | 50054588 | 12583768 | 556995667 | 0.000000 | 0.000000
09-04-2025 18:20:55.000 | 12616064 | 126160640 | 126.1606 | 54337456 | 15611985 | 46701426 | -99907379 | 50047291 | 12409032 | 549606934 | 0.000000 | 0.000000
09-04-2025 18:20:50.000 | 12617776 | 126177760 | 126.1778 | 55714478 | 15610852 | 46712832 | -99902657 | 50069260 | 12233956 | 541932007 | 0.000000 | 0.000000
09-04-2025 18:20:45.000 | 12604254 | 126042540 | 126.0425 | 55384048 | 15611173 | 46661377 | -99903603 | 50084343 | 12058720 | 534261841 | 0.000000 | 0.000000
09-04-2025 18:20:40.000 | 12615941 | 126159410 | 126.1594 | 54461016 | 15610589 | 46704731 | -99906952 | 50100010 | 11883594 | 526659729 | 0.000000 | 0.000000
09-04-2025 18:20:35.000 | 12603105 | 126031050 | 126.031 | 52218589 | 15608956 | 46658809 | -99914276 | 50131012 | 11708271 | 519125488 | 0.000000 | 0.000000
09-04-2025 18:20:30.000 | 12592211 | 125922110 | 125.9221 | 51539932 | 15611172 | 46610649 | -99916344 | 50124561 | 11533363 | 512052856 | 0.000000 | 0.000000
09-04-2025 18:20:25.000 | 12594610 | 125946100 | 125.9461 | 54380059 | 15612227 | 46621187 | -99906914 | 50111778 | 11358669 | 504745941 | 0.000000 | 0.000000
09-04-2025 18:20:20.000 | 12571044 | 125710440 | 125.7104 | 54965273 | 15610668 | 46539258 | -99904549 | 50083763 | 11184431 | 497114075 | 0.000000 | 0.000000
09-04-2025 18:20:15.000 | 12566238 | 125662380 | 125.6624 | 55125195 | 15613646 | 46513257 | -99903923 | 50047646 | 11010078 | 489592377 | 0.000000 | 0.000000
09-04-2025 18:20:10.000 | 12560452 | 125604520 | 125.6045 | 57416494 | 15610308 | 46505776 | -99895683 | 50041294 | 10835486 | 481741791 | 0.000000 | 0.000000
09-04-2025 18:20:05.000 | 12534818 | 125348180 | 125.3482 | 57869580 | 15614120 | 46400376 | -99893600 | 50017925 | 10661383 | 473869171 | 0.000000 | 0.000000
09-04-2025 18:20:00.000 | 12610376 | 126103760 | 126.1038 | 60028066 | 15609320 | 46697407 | -99886894 | 50015320 | 10486935 | 465711273 | 0.000000 | 0.000000
09-04-2025 18:19:55.000 | 12629977 | 126299770 | 126.2998 | 58019019 | 15609060 | 46767119 | -99894653 | 50053452 | 10311832 | 457538269 | 0.000000 | 0.000000
09-04-2025 18:19:50.000 | 12606599 | 126065990 | 126.066 | 55553306 | 15610026 | 46673452 | -99903046 | 50076210 | 10136782 | 449595032 | 0.000000 | 0.000000
09-04-2025 18:19:45.000 | 12582347 | 125823470 | 125.8235 | 54006533 | 15613684 | 46571201 | -99908012 | 50085365 | 99616230 | 441937012 | 0.000000 | 0.000000
09-04-2025 18:19:40.000 | 12648062 | 126480620 | 126.4806 | 56848955 | 15609162 | 46831699 | -99899139 | 50082184 | 97867031 | 434309723 | 0.000000 | 0.000000
09-04-2025 18:19:35.000 | 12625013 | 126250130 | 126.2501 | 56771411 | 15609476 | 46745869 | -99899048 | 50098675 | 96113730 | 426521759 | 0.000000 | 0.000000
09-04-2025 18:19:30.000 | 12581464 | 125814640 | 125.8146 | 53224136 | 15612730 | 46569868 | -99910637 | 50100826 | 94361748 | 418891571 | 0.000000 | 0.000000
09-04-2025 18:19:25.000 | 12548676 | 125486760 | 125.4868 | 56070757 | 15612978 | 46451982 | -99900322 | 50071930 | 92613809 | 411292725 | 0.000000 | 0.000000
09-04-2025 18:19:20.000 | 12573120 | 125731200 | 125.7312 | 56425146 | 15612472 | 46544810 | -99899452 | 50061432 | 90868457 | 403473663 | 0.000000 | 0.000000
09-04-2025 18:19:15.000 | 12584564 | 125845640 | 125.8456 | 55972715 | 15615656 | 46578403 | -99901237 | 50059853 | 89119912 | 395608948 | 0.000000 | 0.000000
09-04-2025 18:19:10.000 | 12627341 | 126273410 | 126.2734 | 60330596 | 15610407 | 46757324 | -99886063 | 50045803 | 87370000 | 387649445 | 0.000000 | 0.000000
09-04-2025 18:19:05.000 | 12637863 | 126378630 | 126.3786 | 57283306 | 15610593 | 46790684 | -99897430 | 50074219 | 85616396 | 379508759 | 0.000000 | 0.000000
09-04-2025 18:19:00.000 | 12585923 | 125859230 | 125.8592 | 56999102 | 15611840 | 46594443 | -99897606 | 50067440 | 83864277 | 371555847 | 0.000000 | 0.000000
09-04-2025 18:18:55.000 | 12606650 | 126066500 | 126.0665 | 58534390 | 15611238 | 46675630 | -99892380 | 50049324 | 82115762 | 363512939 | 0.000000 | 0.000000
09-04-2025 18:18:50.000 | 12595741 | 125957410 | 125.9574 | 58434775 | 15610281 | 46637451 | -99892563 | 50054420 | 80365273 | 355328369 | 0.000000 | 0.000000
09-04-2025 18:18:45.000 | 12575452 | 125754520 | 125.7545 | 59097720 | 15613889 | 46553135 | -99889755 | 50030930 | 78616860 | 347172180 | 0.000000 | 0.000000
09-04-2025 18:18:40.000 | 12619569 | 126195690 | 126.1957 | 61013398 | 15609062 | 46734629 | -99883324 | 50026203 | 76870889 | 338807861 | 0.000000 | 0.000000
09-04-2025 18:18:35.000 | 12608995 | 126089950 | 126.09 | 57262412 | 15609373 | 46687842 | -99897041 | 50057137 | 75117451 | 330530182 | 0.000000 | 0.000000
09-04-2025 18:18:30.000 | 12584530 | 125845300 | 125.8453 | 53946626 | 15612739 | 46581377 | -99908249 | 50071312 | 73367339 | 322795563 | 0.000000 | 0.000000
09-04-2025 18:18:25.000 | 12613092 | 126130920 | 126.1309 | 56716416 | 15614687 | 46685459 | -99899055 | 50056332 | 71618511 | 315275116 | 0.000000 | 0.000000
09-04-2025 18:18:20.000 | 12681676 | 126816760 | 126.8168 | 57063833 | 15607189 | 46961958 | -99898918 | 50073967 | 69864912 | 307294067 | 0.000000 | 0.000000
09-04-2025 18:18:15.000 | 12619298 | 126192980 | 126.193 | 54578647 | 15611065 | 46716089 | -99906601 | 50111485 | 68105771 | 299602234 | 0.000000 | 0.000000
09-04-2025 18:18:10.000 | 12595604 | 125956040 | 125.956 | 56297114 | 15611394 | 46630610 | -99900261 | 50113777 | 66352524 | 291859344 | 0.000000 | 0.000000
09-04-2025 18:18:05.000 | 12588994 | 125889940 | 125.8899 | 52964868 | 15611983 | 46599033 | -99911613 | 50108887 | 64601304 | 284144867 | 0.000000 | 0.000000
09-04-2025 18:18:00.000 | 12512295 | 125122950 | 125.123 | 55435659 | 15618002 | 46301108 | -99902000 | 50062904 | 62854082 | 276637482 | 0.000000 | 0.000000
09-04-2025 18:17:55.000 | 12551598 | 125515980 | 125.516 | 61025503 | 15615286 | 46465063 | -99882019 | 49993977 | 61117085 | 268635010 | 0.000000 | 0.000000
09-04-2025 18:17:50.000 | 12566825 | 125668250 | 125.6683 | 64649541 | 15612650 | 46535635 | -99867935 | 49978489 | 59373828 | 259912659 | 0.000000 | 0.000000
09-04-2025 18:17:45.000 | 12595794 | 125957940 | 125.9579 | 59581465 | 15608950 | 46643760 | -99888313 | 50014805 | 57625112 | 251050613 | 0.000000 | 0.000000
09-04-2025 18:17:40.000 | 12579075 | 125790750 | 125.7908 | 59490840 | 15610563 | 46576875 | -99888351 | 50023464 | 55876670 | 242795883 | 0.000000 | 0.000000
09-04-2025 18:17:35.000 | 12589483 | 125894830 | 125.8948 | 58418076 | 15610545 | 46613672 | -99892517 | 50041691 | 54130029 | 234559418 | 0.000000 | 0.000000
09-04-2025 18:17:30.000 | 12549189 | 125491890 | 125.4919 | 56915806 | 15613092 | 46454814 | -99897308 | 50055111 | 52383315 | 226606461 | 0.000000 | 0.000000
09-04-2025 18:17:25.000 | 12589623 | 125896230 | 125.8962 | 56257212 | 15608128 | 46617397 | -99900307 | 50073959 | 50635034 | 218737686 | 0.000000 | 0.000000
09-04-2025 18:17:20.000 | 12612845 | 126128450 | 126.1285 | 53609097 | 15609882 | 46694746 | -99909798 | 50085842 | 48888447 | 211132416 | 0.000000 | 0.000000
09-04-2025 18:17:15.000 | 12562132 | 125621320 | 125.6213 | 54539795 | 15615998 | 46490654 | -99905884 | 50059055 | 47141733 | 203721924 | 0.000000 | 0.000000
09-04-2025 18:17:10.000 | 12590658 | 125906580 | 125.9066 | 54535107 | 15612412 | 46606748 | -99906326 | 50059803 | 45392876 | 195981430 | 0.000000 | 0.000000
09-04-2025 18:17:05.000 | 12598651 | 125986510 | 125.9865 | 56395542 | 15609509 | 46647295 | -99899963 | 50068268 | 43646040 | 188273361 | 0.000000 | 0.000000
09-04-2025 18:17:00.000 | 12544162 | 125441620 | 125.4416 | 50702480 | 15613292 | 46425713 | -99918411 | 50099125 | 41895093 | 180701050 | 0.000000 | 0.000000
09-04-2025 18:16:55.000 | 12564320 | 125643200 | 125.6432 | 53202793 | 15613630 | 46503833 | -99910469 | 50072926 | 40148828 | 173508896 | 0.000000 | 0.000000
09-04-2025 18:16:50.000 | 12590770 | 125907700 | 125.9077 | 53884824 | 15611506 | 46608301 | -99908546 | 50071526 | 38401348 | 166092422 | 0.000000 | 0.000000
09-04-2025 18:16:45.000 | 12613956 | 126139560 | 126.1396 | 54904810 | 15610039 | 46700332 | -99905403 | 50085068 | 36651482 | 158546265 | 0.000000 | 0.000000
09-04-2025 18:16:40.000 | 12578642 | 125786420 | 125.7864 | 53686001 | 15610702 | 46565000 | -99909042 | 50083988 | 34901506 | 151028625 | 0.000000 | 0.000000
09-04-2025 18:16:35.000 | 12542999 | 125429990 | 125.43 | 54928032 | 15612596 | 46430171 | -99904251 | 50071716 | 33154412 | 143487900 | 0.000000 | 0.000000
09-04-2025 18:16:30.000 | 12552934 | 125529340 | 125.5293 | 57593438 | 15614248 | 46466191 | -99894913 | 50053753 | 31411323 | 135800247 | 0.000000 | 0.000000
09-04-2025 18:16:25.000 | 12567332 | 125673320 | 125.6733 | 57189341 | 15612186 | 46524546 | -99896622 | 50054848 | 29668276 | 127783554 | 0.000000 | 0.000000
09-04-2025 18:16:20.000 | 12554128 | 125541280 | 125.5413 | 55652080 | 15612086 | 46473477 | -99901886 | 50053097 | 27923503 | 119861923 | 0.000000 | 0.000000
09-04-2025 18:16:15.000 | 12548070 | 125480700 | 125.4807 | 56438462 | 15612104 | 46452739 | -99899002 | 50052341 | 26178435 | 112007637 | 0.000000 | 0.000000
09-04-2025 18:16:10.000 | 12563661 | 125636610 | 125.6366 | 55552705 | 15612593 | 46507002 | -99902390 | 50040089 | 24436086 | 104208504 | 0.000000 | 0.000000
09-04-2025 18:16:05.000 | 12585324 | 125853240 | 125.8532 | 55176680 | 15607345 | 46602710 | -99904030 | 50049980 | 22690681 | 96412926 | 0.000000 | 0.000000
09-04-2025 18:16:00.000 | 12546015 | 125460150 | 125.4601 | 54240059 | 15611392 | 46443765 | -99906677 | 50059296 | 20943242 | 88843849 | 0.000000 | 0.000000
09-04-2025 18:15:55.000 | 12592010 | 125920100 | 125.9201 | 52932402 | 15611252 | 46611538 | -99911766 | 50071762 | 19199473 | 81326157 | 0.000000 | 0.000000
09-04-2025 18:15:50.000 | 12606449 | 126064490 | 126.0645 | 52242163 | 15610521 | 46667026 | -99914246 | 50081146 | 17450842 | 74038986 | 0.000000 | 0.000000
09-04-2025 18:15:45.000 | 12583365 | 125833650 | 125.8337 | 50366260 | 15609797 | 46580737 | -99919991 | 50101868 | 15701857 | 66854683 | 0.000000 | 0.000000
09-04-2025 18:15:40.000 | 12503195 | 125031950 | 125.0319 | 50462192 | 15614915 | 46269741 | -99918655 | 50082870 | 13957094 | 59919170 | 0.000000 | 0.000000
09-04-2025 18:15:35.000 | 12576012 | 125760120 | 125.7601 | 52362803 | 15611996 | 46550010 | -99913429 | 50085106 | 12213235 | 52742290 | 0.000000 | 0.000000
09-04-2025 18:15:30.000 | 12558334 | 125583340 | 125.5833 | 52062002 | 15609987 | 46490586 | -99914177 | 50099518 | 10465540 | 45403198 | 0.000000 | 0.000000
09-04-2025 18:15:25.000 | 12548732 | 125487320 | 125.4873 | 51703232 | 15614276 | 46441777 | -99915230 | 50096504 | 872003662 | 38181614 | 0.000000 | 0.000000
09-04-2025 18:15:20.000 | 12553991 | 125539910 | 125.5399 | 54177837 | 15611525 | 46472910 | -99907005 | 50076889 | 697870056 | 30765314 | 0.000000 | 0.000000
09-04-2025 18:15:15.000 | 12528201 | 125282010 | 125.282 | 54351523 | 15614094 | 46369722 | -99906029 | 50084686 | 523396423 | 23131199 | 0.000000 | 0.000000
09-04-2025 18:15:10.000 | 12567193 | 125671930 | 125.6719 | 55170435 | 15610350 | 46526372 | -99903778 | 50071301 | 349302185 | 15493147 | 0.000000 | 0.000000
09-04-2025 18:15:05.000 | 12540077 | 125400770 | 125.4008 | 55348960 | 15610719 | 46425352 | -99902733 | 50087200 | 174541412 | 7726775 | 0.000000 | 0.000000
09-04-2025 18:15:00.000 | 12561302 | 125613020 | 125.613 | 55555088 | 15612716 | 46498628 | -99902344 | 50092632 | 32916602 | 18326522 | 0.000000 | 0.000000
09-04-2025 18:14:55.000 | 12496816 | 124968160 | 124.9682 | 59056621 | 15614813 | 46259775 | -99888527 | 50050442 | 32742707 | 18248267 | 0.000000 | 0.000000
09-04-2025 18:14:50.000 | 12522020 | 125220200 | 125.2202 | 61018506 | 15613424 | 46360439 | -99881485 | 50035751 | 32568684 | 18164557 | 0.000000 | 0.000000
09-04-2025 18:14:45.000 | 12520615 | 125206150 | 125.2061 | 61961367 | 15614481 | 46354380 | -99877777 | 50016960 | 32394773 | 18080171 | 0.000000 | 0.000000
09-04-2025 18:14:40.000 | 12608991 | 126089910 | 126.0899 | 60856743 | 15604625 | 46707705 | -99883728 | 50058765 | 32220283 | 17993699 | 0.000000 | 0.000000
09-04-2025 18:14:35.000 | 12593155 | 125931550 | 125.9316 | 55719761 | 15608851 | 46628730 | -99902260 | 50100761 | 32045316 | 17912512 | 0.000000 | 0.000000
09-04-2025 18:14:30.000 | 12518247 | 125182470 | 125.1825 | 55980142 | 15614540 | 46334614 | -99900162 | 50068066 | 31871361 | 17835031 | 0.000000 | 0.000000
09-04-2025 18:14:25.000 | 12527109 | 125271090 | 125.2711 | 55647778 | 15615035 | 46365396 | -99901482 | 50053467 | 31697018 | 17757356 | 0.000000 | 0.000000
09-04-2025 18:14:20.000 | 12544606 | 125446060 | 125.4461 | 57344336 | 15614028 | 46435928 | -99895683 | 50033588 | 31522877 | 17679385 | 0.000000 | 0.000000
09-04-2025 18:14:15.000 | 12596963 | 125969630 | 125.9696 | 57348999 | 15607902 | 46647520 | -99896530 | 50059803 | 31348271 | 17599414 | 0.000000 | 0.000000
09-04-2025 18:14:10.000 | 12581323 | 125813230 | 125.8132 | 57123745 | 15612450 | 46575854 | -99897087 | 50077164 | 31173537 | 17521749 | 0.000000 | 0.000000
09-04-2025 18:14:05.000 | 12586229 | 125862290 | 125.8623 | 57439590 | 15612447 | 46594775 | -99896027 | 50082020 | 30998996 | 17442419 | 0.000000 | 0.000000
09-04-2025 18:14:00.000 | 12573234 | 125732340 | 125.7323 | 58561768 | 15609535 | 46557700 | -99891708 | 50086357 | 30824387 | 17362983 | 0.000000 | 0.000000
09-04-2025 18:13:55.000 | 12555987 | 125559870 | 125.5599 | 59187744 | 15610961 | 46490337 | -99889084 | 50109871 | 30649605 | 17282358 | 0.000000 | 0.000000
09-04-2025 18:13:50.000 | 12581334 | 125813340 | 125.8133 | 57129526 | 15612524 | 46575356 | -99897064 | 50121372 | 30475008 | 17201857 | 0.000000 | 0.000000
09-04-2025 18:13:45.000 | 12534384 | 125343840 | 125.3438 | 61025400 | 15612670 | 46408721 | -99881691 | 50103916 | 30300615 | 17119896 | 0.000000 | 0.000000
09-04-2025 18:13:40.000 | 12561749 | 125617490 | 125.6175 | 60755366 | 15612090 | 46511729 | -99883247 | 50097218 | 30126432 | 17035809 | 0.000000 | 0.000000
09-04-2025 18:13:35.000 | 12532377 | 125323770 | 125.3238 | 62423013 | 15612896 | 46403677 | -99876183 | 50078945 | 29952148 | 16949910 | 0.000000 | 0.000000
09-04-2025 18:13:30.000 | 12505567 | 125055670 | 125.0557 | 63388179 | 15614694 | 46300571 | -99871780 | 50053913 | 29777932 | 16861951 | 0.000000 | 0.000000
09-04-2025 18:13:25.000 | 12497333 | 124973330 | 124.9733 | 66435645 | 15614959 | 46275332 | -99859001 | 50031601 | 29604303 | 16772040 | 0.000000 | 0.000000
09-04-2025 18:13:20.000 | 12512877 | 125128770 | 125.1288 | 67004917 | 15614627 | 46334639 | -99856934 | 50004677 | 29430746 | 16679919 | 0.000000 | 0.000000
09-04-2025 18:13:15.000 | 12561687 | 125616870 | 125.6169 | 67134512 | 15607665 | 46536187 | -99857491 | 50014484 | 29256590 | 16585835 | 0.000000 | 0.000000
09-04-2025 18:13:10.000 | 12551457 | 125514570 | 125.5146 | 64578892 | 15610897 | 46483208 | -99867897 | 50028610 | 29082197 | 16494932 | 0.000000 | 0.000000
09-04-2025 18:13:05.000 | 12574405 | 125744050 | 125.7441 | 64808638 | 15612031 | 46566191 | -99867447 | 50027142 | 28907857 | 16406005 | 0.000000 | 0.000000
09-04-2025 18:13:00.000 | 12600888 | 126008880 | 126.0089 | 63142246 | 15609184 | 46669268 | -99874687 | 50054729 | 28733301 | 16316724 | 0.000000 | 0.000000
09-04-2025 18:12:55.000 | 12589577 | 125895770 | 125.8958 | 60988081 | 15608656 | 46624438 | -99882866 | 50089340 | 28558453 | 16230664 | 0.000000 | 0.000000
09-04-2025 18:12:50.000 | 12496845 | 124968450 | 124.9685 | 57439595 | 15615374 | 46256484 | -99894539 | 50089771 | 28384018 | 16148398 | 0.000000 | 0.000000
09-04-2025 18:12:45.000 | 12573745 | 125737450 | 125.7374 | 60144712 | 15608962 | 46563770 | -99885796 | 50073231 | 28210201 | 16066517 | 0.000000 | 0.000000
09-04-2025 18:12:40.000 | 12580580 | 125805800 | 125.8058 | 58486743 | 15609848 | 46583633 | -99892113 | 50108772 | 28035475 | 15984465 | 0.000000 | 0.000000
09-04-2025 18:12:35.000 | 12518905 | 125189050 | 125.189 | 57341279 | 15614246 | 46340991 | -99895264 | 50111538 | 27861107 | 15904321 | 0.000000 | 0.000000
09-04-2025 18:12:30.000 | 12529851 | 125298510 | 125.2985 | 59033711 | 15615498 | 46380605 | -99889198 | 50092846 | 27686916 | 15823467 | 0.000000 | 0.000000
09-04-2025 18:12:25.000 | 12548938 | 125489380 | 125.4894 | 61084614 | 15612112 | 46464077 | -99881737 | 50092892 | 27512635 | 15739078 | 0.000000 | 0.000000
09-04-2025 18:12:20.000 | 12591955 | 125919550 | 125.9196 | 61593784 | 15611293 | 46626782 | -99880577 | 50101250 | 27338078 | 15654021 | 0.000000 | 0.000000
09-04-2025 18:12:15.000 | 12548097 | 125480970 | 125.481 | 60289263 | 15612863 | 46457314 | -99884773 | 50090744 | 27163443 | 15569570 | 0.000000 | 0.000000
09-04-2025 18:12:10.000 | 12530502 | 125305020 | 125.305 | 62912119 | 15616175 | 46387817 | -99874199 | 50055653 | 26989266 | 15484270 | 0.000000 | 0.000000
09-04-2025 18:12:05.000 | 12554277 | 125542770 | 125.5428 | 67979883 | 15610194 | 46502827 | -99853714 | 50043114 | 26815066 | 15393064 | 0.000000 | 0.000000
09-04-2025 18:12:00.000 | 12572448 | 125724480 | 125.7245 | 64671274 | 15608712 | 46567285 | -99867966 | 50079296 | 26640174 | 15299839 | 0.000000 | 0.000000
09-04-2025 18:11:55.000 | 12539228 | 125392280 | 125.3923 | 62517300 | 15615753 | 46419766 | -99875946 | 50061527 | 26465863 | 15211851 | 0.000000 | 0.000000
09-04-2025 18:11:50.000 | 12525819 | 125258190 | 125.2582 | 67743555 | 15615139 | 46383364 | -99854073 | 50019516 | 26291855 | 15122609 | 0.000000 | 0.000000
09-04-2025 18:11:45.000 | 12585644 | 125856440 | 125.8564 | 66708545 | 15607518 | 46623770 | -99859825 | 50051056 | 26117482 | 15027126 | 0.000000 | 0.000000
09-04-2025 18:11:40.000 | 12570059 | 125700590 | 125.7006 | 66751655 | 15610795 | 46557061 | -99859299 | 50066380 | 25942875 | 14935493 | 0.000000 | 0.000000
09-04-2025 18:11:35.000 | 12556203 | 125562030 | 125.562 | 64553438 | 15614558 | 46489951 | -99868103 | 50074444 | 25768387 | 14844003 | 0.000000 | 0.000000
09-04-2025 18:11:30.000 | 12538387 | 125383870 | 125.3839 | 67373413 | 15610620 | 46442290 | -99855949 | 50043755 | 25594406 | 14752500 | 0.000000 | 0.000000
09-04-2025 18:11:25.000 | 12575636 | 125756360 | 125.7564 | 68118936 | 15609011 | 46585005 | -99853615 | 50070103 | 25419891 | 14657618 | 0.000000 | 0.000000
09-04-2025 18:11:20.000 | 12490730 | 124907300 | 124.9073 | 65591074 | 15615838 | 46246411 | -99862411 | 50057640 | 25245869 | 14565016 | 0.000000 | 0.000000
09-04-2025 18:11:15.000 | 12498596 | 124985960 | 124.986 | 68662080 | 15616413 | 46280596 | -99849442 | 50032177 | 25072193 | 14472212 | 0.000000 | 0.000000
09-04-2025 18:11:10.000 | 12554178 | 125541780 | 125.5418 | 69721143 | 15607446 | 46514917 | -99846146 | 50056168 | 24898227 | 14374175 | 0.000000 | 0.000000
09-04-2025 18:11:05.000 | 12545214 | 125452140 | 125.4521 | 63996719 | 15613842 | 46450664 | -99870140 | 50078854 | 24723760 | 14280068 | 0.000000 | 0.000000
09-04-2025 18:11:00.000 | 12530224 | 125302240 | 125.3022 | 65505571 | 15613985 | 46398418 | -99863632 | 50058270 | 24549793 | 14190579 | 0.000000 | 0.000000
09-04-2025 18:10:55.000 | 12513023 | 125130230 | 125.1302 | 65388330 | 15614895 | 46331304 | -99863747 | 50047520 | 24375764 | 14098790 | 0.000000 | 0.000000
09-04-2025 18:10:50.000 | 12576051 | 125760510 | 125.7605 | 69987031 | 15610298 | 46586479 | -99845505 | 50055050 | 24201717 | 14005557 | 0.000000 | 0.000000
09-04-2025 18:10:45.000 | 12602020 | 126020200 | 126.0202 | 68039839 | 15602843 | 46700806 | -99854568 | 50109409 | 24026945 | 13908331 | 0.000000 | 0.000000
09-04-2025 18:10:40.000 | 12477506 | 124775060 | 124.7751 | 63873809 | 15621573 | 46177510 | -99869232 | 50108646 | 23852561 | 13818387 | 0.000000 | 0.000000
09-04-2025 18:10:35.000 | 12508866 | 125088660 | 125.0887 | 71504248 | 15610226 | 46342397 | -99837021 | 50045933 | 23679289 | 13724601 | 0.000000 | 0.000000
09-04-2025 18:10:30.000 | 12521140 | 125211400 | 125.2114 | 69823633 | 15608781 | 46388828 | -99844879 | 50068462 | 23505195 | 13626223 | 0.000000 | 0.000000
09-04-2025 18:10:25.000 | 12539965 | 125399650 | 125.3996 | 68006665 | 15610789 | 46448296 | -99853271 | 50065369 | 23331352 | 13530656 | 0.000000 | 0.000000
09-04-2025 18:10:20.000 | 12482069 | 124820690 | 124.8207 | 67048853 | 15615525 | 46218213 | -99856041 | 50059761 | 23157445 | 13437004 | 0.000000 | 0.000000
09-04-2025 18:10:15.000 | 12499964 | 124999640 | 124.9996 | 70274951 | 15609943 | 46308149 | -99842339 | 50047672 | 22984195 | 13342318 | 0.000000 | 0.000000
09-04-2025 18:10:10.000 | 12477773 | 124777730 | 124.7777 | 66760244 | 15608192 | 46224229 | -99857178 | 50084343 | 22810264 | 13245856 | 0.000000 | 0.000000
09-04-2025 18:10:05.000 | 12439330 | 124393300 | 124.3933 | 64288486 | 15615686 | 46055835 | -99866714 | 50075584 | 22636709 | 13155708 | 0.000000 | 0.000000
09-04-2025 18:10:00.000 | 12464498 | 124644980 | 124.645 | 66290029 | 15612803 | 46160664 | -99858879 | 50049404 | 22463986 | 13064637 | 0.000000 | 0.000000
09-04-2025 18:09:55.000 | 12440673 | 124406730 | 124.4067 | 65827358 | 15615096 | 46064414 | -99860306 | 50054787 | 22290861 | 12972002 | 0.000000 | 0.000000
09-04-2025 18:09:50.000 | 12449366 | 124493660 | 124.4937 | 68243398 | 15610329 | 46116118 | -99850098 | 50059967 | 22118047 | 12878646 | 0.000000 | 0.000000
09-04-2025 18:09:45.000 | 12430975 | 124309750 | 124.3097 | 68243042 | 15615647 | 46031885 | -99849655 | 50063953 | 21945092 | 12783527 | 0.000000 | 0.000000
09-04-2025 18:09:40.000 | 12509368 | 125093680 | 125.0937 | 69630469 | 15619094 | 46313696 | -99845444 | 50055347 | 21772164 | 12688948 | 0.000000 | 0.000000
09-04-2025 18:09:35.000 | 12679170 | 126791700 | 126.7917 | 72266626 | 15610669 | 46971216 | -99837967 | 50066795 | 21597635 | 12590334 | 0.000000 | 0.000000
09-04-2025 18:09:30.000 | 12733913 | 127339130 | 127.3391 | 67340918 | 15615021 | 47150215 | -99860458 | 50088081 | 21421314 | 12494343 | 0.000000 | 0.000000
09-04-2025 18:09:25.000 | 12817094 | 128170940 | 128.1709 | 71066118 | 15614380 | 47467026 | -99846642 | 50063980 | 21244500 | 12400072 | 0.000000 | 0.000000
09-04-2025 18:09:20.000 | 12924119 | 129241190 | 129.2412 | 70020400 | 15614509 | 47859956 | -99853561 | 50073181 | 21065754 | 12301632 | 0.000000 | 0.000000
09-04-2025 18:09:15.000 | 13000180 | 130001800 | 130.0018 | 74495239 | 15620541 | 48130703 | -99836220 | 50052967 | 20885988 | 12203304 | 0.000000 | 0.000000
09-04-2025 18:09:10.000 | 13099033 | 130990330 | 130.9903 | 78730078 | 15612906 | 48528472 | -99819862 | 50035694 | 20705080 | 12095858 | 0.000000 | 0.000000
09-04-2025 18:09:05.000 | 13226902 | 132269020 | 132.269 | 75047451 | 15613442 | 48990435 | -99839424 | 50065742 | 20522168 | 11989885 | 0.000000 | 0.000000
09-04-2025 18:09:00.000 | 13285763 | 132857630 | 132.8576 | 72140586 | 15616060 | 49194546 | -99852905 | 50062107 | 20338189 | 11887615 | 0.000000 | 0.000000
09-04-2025 18:08:55.000 | 13375334 | 133753340 | 133.7533 | 73991069 | 15615689 | 49529629 | -99847343 | 50055511 | 20152930 | 11785959 | 0.000000 | 0.000000
09-04-2025 18:08:50.000 | 13495567 | 134955670 | 134.9557 | 74295474 | 15614423 | 49978447 | -99848808 | 50072388 | 19966494 | 11682760 | 0.000000 | 0.000000
09-04-2025 18:08:45.000 | 13563619 | 135636190 | 135.6362 | 74210474 | 15613487 | 50231733 | -99850662 | 50053055 | 19779150 | 11579189 | 0.000000 | 0.000000
09-04-2025 18:08:40.000 | 13580061 | 135800610 | 135.8006 | 74549038 | 15615329 | 50287427 | -99849663 | 50028767 | 19590395 | 11475476 | 0.000000 | 0.000000
09-04-2025 18:08:35.000 | 13673019 | 136730190 | 136.7302 | 74164814 | 15611215 | 50644233 | -99853218 | 50029671 | 19401238 | 11369846 | 0.000000 | 0.000000
09-04-2025 18:08:30.000 | 13639800 | 136398000 | 136.398 | 68734658 | 15607616 | 50522969 | -99873268 | 50054638 | 19211766 | 11268345 | 0.000000 | 0.000000
09-04-2025 18:08:25.000 | 13646173 | 136461730 | 136.4617 | 70999849 | 15609656 | 50542715 | -99864922 | 50049725 | 19022586 | 11173462 | 0.000000 | 0.000000
09-04-2025 18:08:20.000 | 13586242 | 135862420 | 135.8624 | 70934199 | 15612824 | 50312236 | -99863983 | 50083675 | 18833662 | 11073268 | 0.000000 | 0.000000
09-04-2025 18:08:15.000 | 13606147 | 136061470 | 136.0615 | 68163184 | 15613132 | 50378691 | -99874748 | 50067451 | 18645129 | 10976725 | 0.000000 | 0.000000
09-04-2025 18:08:10.000 | 13615431 | 136154310 | 136.1543 | 71933784 | 15610866 | 50427144 | -99860725 | 50032272 | 18455988 | 10880385 | 0.000000 | 0.000000
09-04-2025 18:08:05.000 | 13659856 | 136598560 | 136.5986 | 70088545 | 15606283 | 50603667 | -99868622 | 50048409 | 18266469 | 10781431 | 0.000000 | 0.000000
09-04-2025 18:08:00.000 | 13579992 | 135799920 | 135.7999 | 71017852 | 15616352 | 50277183 | -99863533 | 50032082 | 18077221 | 10685293 | 0.000000 | 0.000000
09-04-2025 18:07:55.000 | 13629853 | 136298530 | 136.2985 | 74024355 | 15608155 | 50493335 | -99852844 | 50008091 | 17888688 | 10584193 | 0.000000 | 0.000000
09-04-2025 18:07:50.000 | 13621903 | 136219030 | 136.219 | 71045679 | 15613135 | 50442632 | -99864265 | 50005714 | 17699775 | 10484841 | 0.000000 | 0.000000
09-04-2025 18:07:45.000 | 13628034 | 136280340 | 136.2803 | 72552778 | 15608102 | 50484722 | -99858589 | 50009090 | 17510572 | 10383409 | 0.000000 | 0.000000
09-04-2025 18:07:40.000 | 13619013 | 136190130 | 136.1901 | 68800874 | 15613269 | 50427061 | -99872643 | 50021149 | 17320982 | 10285836 | 0.000000 | 0.000000
09-04-2025 18:07:35.000 | 13643939 | 136439390 | 136.4394 | 70915015 | 15610009 | 50533745 | -99865204 | 50017735 | 17131680 | 10188289 | 0.000000 | 0.000000
09-04-2025 18:07:30.000 | 13637491 | 136374910 | 136.3749 | 70677520 | 15609992 | 50509023 | -99865974 | 50035126 | 16942002 | 10089926 | 0.000000 | 0.000000
09-04-2025 18:07:25.000 | 13660441 | 136604410 | 136.6044 | 69007588 | 15609694 | 50592236 | -99872650 | 50045444 | 16752260 | 999253418 | 0.000000 | 0.000000
09-04-2025 18:07:20.000 | 13608911 | 136089110 | 136.0891 | 71336494 | 15616346 | 50385439 | -99862892 | 50015285 | 16563035 | 989557373 | 0.000000 | 0.000000
09-04-2025 18:07:15.000 | 13613138 | 136131380 | 136.1314 | 74077993 | 15613818 | 50413462 | -99852272 | 49986923 | 16374059 | 979393127 | 0.000000 | 0.000000
09-04-2025 18:07:10.000 | 13593934 | 135939340 | 135.9393 | 75911245 | 15613674 | 50347197 | -99844444 | 49956806 | 16185234 | 969037354 | 0.000000 | 0.000000
09-04-2025 18:07:05.000 | 13594402 | 135944020 | 135.944 | 78204683 | 15611305 | 50360894 | -99834938 | 49944977 | 15996515 | 958300171 | 0.000000 | 0.000000
09-04-2025 18:07:00.000 | 13620084 | 136200840 | 136.2008 | 79061543 | 15609350 | 50464507 | -99831947 | 49949760 | 15807704 | 947439209 | 0.000000 | 0.000000
09-04-2025 18:06:55.000 | 13583420 | 135834200 | 135.8342 | 73361250 | 15610356 | 50313657 | -99854477 | 49980438 | 15618358 | 936778503 | 0.000000 | 0.000000
09-04-2025 18:06:50.000 | 13566503 | 135665030 | 135.665 | 71702603 | 15612739 | 50240581 | -99860619 | 49972065 | 15429751 | 926717957 | 0.000000 | 0.000000
09-04-2025 18:06:45.000 | 13562461 | 135624610 | 135.6246 | 76547905 | 15613216 | 50233535 | -99841103 | 49957237 | 15241043 | 916517517 | 0.000000 | 0.000000
09-04-2025 18:06:40.000 | 13612319 | 136123190 | 136.1232 | 77465986 | 15609241 | 50432158 | -99838463 | 49963657 | 15052023 | 905828979 | 0.000000 | 0.000000
09-04-2025 18:06:35.000 | 13624703 | 136247030 | 136.247 | 75972256 | 15611678 | 50467231 | -99844902 | 49957180 | 14863072 | 895259399 | 0.000000 | 0.000000
09-04-2025 18:06:30.000 | 13568989 | 135689890 | 135.6899 | 76390527 | 15612836 | 50258433 | -99841904 | 49936138 | 14674083 | 884657166 | 0.000000 | 0.000000
09-04-2025 18:06:25.000 | 13573352 | 135733520 | 135.7335 | 76675381 | 15612117 | 50277456 | -99840828 | 49927082 | 14485156 | 873987000 | 0.000000 | 0.000000
09-04-2025 18:06:20.000 | 13602991 | 136029910 | 136.0299 | 75006201 | 15609251 | 50394082 | -99848328 | 49944592 | 14296132 | 863335327 | 0.000000 | 0.000000
09-04-2025 18:06:15.000 | 13618302 | 136183020 | 136.183 | 71583276 | 15610817 | 50436729 | -99862137 | 49957226 | 14106945 | 853226379 | 0.000000 | 0.000000
09-04-2025 18:06:10.000 | 13610545 | 136105450 | 136.1054 | 74524561 | 15614667 | 50402178 | -99850433 | 49959572 | 13917916 | 843301941 | 0.000000 | 0.000000
09-04-2025 18:06:05.000 | 13657822 | 136578220 | 136.5782 | 75965630 | 15606632 | 50605933 | -99845673 | 49966858 | 13728968 | 832890198 | 0.000000 | 0.000000
09-04-2025 18:06:00.000 | 13598523 | 135985230 | 135.9852 | 74025547 | 15610425 | 50370630 | -99852165 | 49991611 | 13539636 | 822422058 | 0.000000 | 0.000000
09-04-2025 18:05:55.000 | 13489125 | 134891250 | 134.8913 | 80329248 | 15619118 | 49951694 | -99823151 | 49881710 | 13352189 | 811959839 | 0.000000 | 0.000000
09-04-2025 18:05:50.000 | 13517333 | 135173330 | 135.1733 | 84440654 | 15615396 | 50077554 | -99805450 | 49833988 | 13164642 | 800469849 | 0.000000 | 0.000000
09-04-2025 18:05:45.000 | 13554989 | 135549890 | 135.5499 | 85669199 | 15609448 | 50238311 | -99800873 | 49829468 | 12976452 | 788525391 | 0.000000 | 0.000000
09-04-2025 18:05:40.000 | 13573166 | 135731660 | 135.7317 | 82126084 | 15608385 | 50300474 | -99817451 | 49860291 | 12787918 | 776828430 | 0.000000 | 0.000000
09-04-2025 18:05:35.000 | 13513998 | 135139980 | 135.14 | 82952461 | 15613305 | 50068062 | -99812141 | 49856529 | 12599623 | 765521057 | 0.000000 | 0.000000
09-04-2025 18:05:30.000 | 13533902 | 135339020 | 135.339 | 85564941 | 15610525 | 50156274 | -99800743 | 49837414 | 12411867 | 753901672 | 0.000000 | 0.000000
09-04-2025 18:05:25.000 | 13543064 | 135430640 | 135.4306 | 84412549 | 15610057 | 50188667 | -99806320 | 49846554 | 12223859 | 742100281 | 0.000000 | 0.000000
09-04-2025 18:05:20.000 | 13520216 | 135202160 | 135.2022 | 84819619 | 15616541 | 50085229 | -99803795 | 49813992 | 12035902 | 730409363 | 0.000000 | 0.000000
09-04-2025 18:05:15.000 | 13563313 | 135633130 | 135.6331 | 87075234 | 15612611 | 50261895 | -99794556 | 49799248 | 11847950 | 718494934 | 0.000000 | 0.000000
09-04-2025 18:05:10.000 | 13588670 | 135886700 | 135.8867 | 86612109 | 15605790 | 50376445 | -99797485 | 49824001 | 11659629 | 706410278 | 0.000000 | 0.000000
09-04-2025 18:05:05.000 | 13539341 | 135393410 | 135.3934 | 82119746 | 15611175 | 50166636 | -99816566 | 49848507 | 11470989 | 694649963 | 0.000000 | 0.000000
09-04-2025 18:05:00.000 | 13542073 | 135420730 | 135.4207 | 82277607 | 15613358 | 50171011 | -99815941 | 49849762 | 11282748 | 683202576 | 0.000000 | 0.000000
09-04-2025 18:04:55.000 | 13497188 | 134971880 | 134.9719 | 85469990 | 15611920 | 50018618 | -99800102 | 49827393 | 11095021 | 671602539 | 0.000000 | 0.000000
09-04-2025 18:04:50.000 | 13507659 | 135076590 | 135.0766 | 86639277 | 15609410 | 50065762 | -99794930 | 49845856 | 10907121 | 659659302 | 0.000000 | 0.000000
09-04-2025 18:04:45.000 | 13493616 | 134936160 | 134.9362 | 84299561 | 15615079 | 49990923 | -99805420 | 49822906 | 10719516 | 647878845 | 0.000000 | 0.000000
09-04-2025 18:04:40.000 | 13520863 | 135208630 | 135.2086 | 87963984 | 15613183 | 50106074 | -99789040 | 49779846 | 10532129 | 635963074 | 0.000000 | 0.000000
09-04-2025 18:04:35.000 | 13564314 | 135643140 | 135.6431 | 87712266 | 15608115 | 50282686 | -99791580 | 49797142 | 10344104 | 623634094 | 0.000000 | 0.000000
09-04-2025 18:04:30.000 | 13547411 | 135474110 | 135.4741 | 86471865 | 15613296 | 50199897 | -99796913 | 49797279 | 10156105 | 611638611 | 0.000000 | 0.000000
09-04-2025 18:04:25.000 | 13503620 | 135036200 | 135.0362 | 86398408 | 15615939 | 50028955 | -99795944 | 49801353 | 99680488 | 599500854 | 0.000000 | 0.000000
09-04-2025 18:04:20.000 | 13567072 | 135670720 | 135.6707 | 87725996 | 15610801 | 50282847 | -99791603 | 49807468 | 97799346 | 587225525 | 0.000000 | 0.000000
09-04-2025 18:04:15.000 | 13561153 | 135611530 | 135.6115 | 86747373 | 15611274 | 50257402 | -99796036 | 49811943 | 95916689 | 575149170 | 0.000000 | 0.000000
09-04-2025 18:04:10.000 | 13557059 | 135570590 | 135.5706 | 86654307 | 15609929 | 50246060 | -99796349 | 49822849 | 94032930 | 563012085 | 0.000000 | 0.000000
09-04-2025 18:04:05.000 | 13508083 | 135080830 | 135.0808 | 83944443 | 15610323 | 50058789 | -99807465 | 49837814 | 92148555 | 551101501 | 0.000000 | 0.000000
09-04-2025 18:04:00.000 | 13483338 | 134833380 | 134.8334 | 81990410 | 15616384 | 49943140 | -99815628 | 49829800 | 90268936 | 539475159 | 0.000000 | 0.000000
09-04-2025 18:03:55.000 | 13556423 | 135564230 | 135.5642 | 85519863 | 15610854 | 50238984 | -99801613 | 49816753 | 88389990 | 527773560 | 0.000000 | 0.000000
09-04-2025 18:03:50.000 | 13600741 | 136007410 | 136.0074 | 83832773 | 15608449 | 50405967 | -99810577 | 49846382 | 86503525 | 515897156 | 0.000000 | 0.000000
09-04-2025 18:03:45.000 | 13537348 | 135373480 | 135.3735 | 83432832 | 15613142 | 50156528 | -99810616 | 49835022 | 84621133 | 504371613 | 0.000000 | 0.000000
09-04-2025 18:03:40.000 | 13569698 | 135696980 | 135.697 | 83065176 | 15611997 | 50278823 | -99813171 | 49825722 | 82740244 | 492873779 | 0.000000 | 0.000000
09-04-2025 18:03:35.000 | 13612558 | 136125580 | 136.1256 | 86070869 | 15608403 | 50454868 | -99800705 | 49830753 | 80857290 | 481226501 | 0.000000 | 0.000000
09-04-2025 18:03:30.000 | 13599569 | 135995690 | 135.9957 | 81046289 | 15606793 | 50400557 | -99822891 | 49869968 | 78968408 | 469513824 | 0.000000 | 0.000000
09-04-2025 18:03:25.000 | 13517230 | 135172300 | 135.1723 | 80592261 | 15613818 | 50072622 | -99822731 | 49866425 | 77082773 | 458287933 | 0.000000 | 0.000000
09-04-2025 18:03:20.000 | 13492747 | 134927470 | 134.9275 | 83822139 | 15615525 | 49984038 | -99807587 | 49818764 | 75203979 | 446909363 | 0.000000 | 0.000000
09-04-2025 18:03:15.000 | 13524886 | 135248860 | 135.2489 | 87192656 | 15612582 | 50120615 | -99792839 | 49790733 | 73327734 | 435074982 | 0.000000 | 0.000000
09-04-2025 18:03:10.000 | 13553650 | 135536500 | 135.5365 | 86610459 | 15611490 | 50228403 | -99796448 | 49798332 | 71447778 | 422899353 | 0.000000 | 0.000000
09-04-2025 18:03:05.000 | 13589163 | 135891630 | 135.8916 | 85612529 | 15606396 | 50373750 | -99802132 | 49820343 | 69565767 | 410907990 | 0.000000 | 0.000000
09-04-2025 18:03:00.000 | 13528278 | 135282780 | 135.2828 | 82982070 | 15613306 | 50121440 | -99812401 | 49831375 | 67682563 | 399139130 | 0.000000 | 0.000000
09-04-2025 18:02:55.000 | 13501303 | 135013030 | 135.013 | 83239473 | 15613697 | 50020732 | -99810486 | 49822792 | 65805186 | 387505249 | 0.000000 | 0.000000
09-04-2025 18:02:50.000 | 13518581 | 135185810 | 135.1858 | 85674160 | 15613519 | 50091416 | -99799782 | 49806561 | 63928838 | 375844604 | 0.000000 | 0.000000
09-04-2025 18:02:45.000 | 13529586 | 135295860 | 135.2959 | 84912910 | 15611412 | 50135942 | -99803635 | 49822742 | 62049893 | 363941376 | 0.000000 | 0.000000
09-04-2025 18:02:40.000 | 13589911 | 135899110 | 135.8991 | 82740498 | 15609104 | 50361270 | -99815170 | 49841347 | 60164634 | 352273407 | 0.000000 | 0.000000
09-04-2025 18:02:35.000 | 13567989 | 135679890 | 135.6799 | 80569727 | 15610737 | 50270112 | -99824150 | 49846062 | 58281753 | 340973938 | 0.000000 | 0.000000
09-04-2025 18:02:30.000 | 13513411 | 135134110 | 135.1341 | 83077451 | 15614954 | 50061338 | -99811562 | 49823921 | 56401660 | 329694794 | 0.000000 | 0.000000
09-04-2025 18:02:25.000 | 13574594 | 135745940 | 135.7459 | 82647725 | 15607510 | 50310762 | -99815170 | 49842300 | 54521172 | 318074341 | 0.000000 | 0.000000
09-04-2025 18:02:20.000 | 13494739 | 134947390 | 134.9474 | 84198174 | 15612963 | 50001851 | -99805923 | 49827312 | 52644902 | 306624084 | 0.000000 | 0.000000
09-04-2025 18:02:15.000 | 13507795 | 135077950 | 135.0779 | 85732002 | 15608609 | 50067354 | -99799194 | 49818764 | 50768384 | 294862183 | 0.000000 | 0.000000
09-04-2025 18:02:10.000 | 13530586 | 135305860 | 135.3059 | 83097998 | 15611928 | 50134375 | -99811943 | 49802265 | 48895967 | 283264038 | 0.000000 | 0.000000
09-04-2025 18:02:05.000 | 13500558 | 135005580 | 135.0056 | 85077051 | 15610321 | 50033135 | -99802032 | 49788616 | 47022095 | 271630585 | 0.000000 | 0.000000
09-04-2025 18:02:00.000 | 13486213 | 134862130 | 134.8621 | 82214170 | 15614806 | 49959165 | -99814697 | 49795712 | 45145034 | 260018524 | 0.000000 | 0.000000
09-04-2025 18:01:55.000 | 13559703 | 135597030 | 135.597 | 82716689 | 15609582 | 50248159 | -99814453 | 49809540 | 43265654 | 248607910 | 0.000000 | 0.000000
09-04-2025 18:01:50.000 | 13521269 | 135212690 | 135.2127 | 79911455 | 15610699 | 50096714 | -99825813 | 49831165 | 41382769 | 237211792 | 0.000000 | 0.000000
09-04-2025 18:01:45.000 | 13549542 | 135495420 | 135.4954 | 78900547 | 15611675 | 50195283 | -99830887 | 49843628 | 39500754 | 226214920 | 0.000000 | 0.000000
09-04-2025 18:01:40.000 | 13549684 | 135496840 | 135.4968 | 78984385 | 15611133 | 50197876 | -99830528 | 49838676 | 37620830 | 215271988 | 0.000000 | 0.000000
09-04-2025 18:01:35.000 | 13540444 | 135404440 | 135.4044 | 79377822 | 15612472 | 50160415 | -99828613 | 49827274 | 35741921 | 204344925 | 0.000000 | 0.000000
09-04-2025 18:01:30.000 | 13503495 | 135034950 | 135.035 | 78860815 | 15610999 | 50028174 | -99829903 | 49846825 | 33860752 | 193270050 | 0.000000 | 0.000000
09-04-2025 18:01:25.000 | 13550359 | 135503590 | 135.5036 | 77833877 | 15609096 | 50205586 | -99835434 | 49871323 | 31982788 | 182300766 | 0.000000 | 0.000000
09-04-2025 18:01:20.000 | 13481673 | 134816730 | 134.8167 | 76132471 | 15609335 | 49947085 | -99840935 | 49881943 | 30102061 | 171560974 | 0.000000 | 0.000000
09-04-2025 18:01:15.000 | 13445866 | 134458660 | 134.4587 | 75091318 | 15618066 | 49784141 | -99844421 | 49854191 | 28228042 | 161094666 | 0.000000 | 0.000000
09-04-2025 18:01:10.000 | 13509777 | 135097770 | 135.0978 | 81008687 | 15611850 | 50053281 | -99820702 | 49823265 | 26355706 | 150312408 | 0.000000 | 0.000000
09-04-2025 18:01:05.000 | 13527698 | 135276980 | 135.277 | 79811978 | 15611483 | 50117363 | -99826408 | 49842995 | 24476987 | 139078094 | 0.000000 | 0.000000
09-04-2025 18:01:00.000 | 13499370 | 134993700 | 134.9937 | 81009814 | 15614849 | 50004473 | -99820427 | 49833851 | 22601628 | 127964027 | 0.000000 | 0.000000
09-04-2025 18:00:55.000 | 13576916 | 135769160 | 135.7692 | 83462441 | 15605439 | 50326816 | -99811584 | 49848663 | 20722869 | 116448532 | 0.000000 | 0.000000
09-04-2025 18:00:50.000 | 13438223 | 134382230 | 134.3822 | 79463379 | 15615864 | 49774189 | -99825623 | 49854740 | 18843000 | 105104538 | 0.000000 | 0.000000
09-04-2025 18:00:45.000 | 13499523 | 134995230 | 134.9952 | 82752637 | 15617520 | 50001064 | -99812637 | 49803253 | 16973085 | 93970459 | 0.000000 | 0.000000
09-04-2025 18:00:40.000 | 13533211 | 135332110 | 135.3321 | 83367393 | 15612120 | 50143755 | -99810799 | 49793461 | 15096365 | 82321808 | 0.000000 | 0.000000
09-04-2025 18:00:35.000 | 13623738 | 136237380 | 136.2374 | 81887388 | 15604047 | 50501055 | -99819847 | 49853317 | 13213064 | 70788734 | 0.000000 | 0.000000
09-04-2025 18:00:30.000 | 13597566 | 135975660 | 135.9757 | 73350117 | 15609262 | 50369268 | -99854820 | 49922375 | 11321161 | 60037029 | 0.000000 | 0.000000
09-04-2025 18:00:25.000 | 13541616 | 135416160 | 135.4162 | 72034712 | 15615912 | 50138296 | -99858810 | 49916893 | 943515625 | 49912086 | 0.000000 | 0.000000
09-04-2025 18:00:20.000 | 13606866 | 136068660 | 136.0687 | 74772520 | 15609814 | 50404517 | -99849358 | 49917545 | 755067810 | 39724903 | 0.000000 | 0.000000
09-04-2025 18:00:15.000 | 13595661 | 135956610 | 135.9566 | 70966499 | 15607419 | 50363286 | -99864044 | 49960766 | 565981934 | 29495684 | 0.000000 | 0.000000
09-04-2025 18:00:10.000 | 13558166 | 135581660 | 135.5817 | 68827725 | 15616979 | 50191597 | -99871399 | 49953430 | 377194397 | 19844067 | 0.000000 | 0.000000
09-04-2025 18:00:05.000 | 13587427 | 135874270 | 135.8743 | 72299126 | 15614753 | 50312310 | -99858734 | 49923904 | 188808502 | 10068660 | 0.000000 | 0.000000
09-04-2025 18:00:00.000 | 13616744 | 136167440 | 136.1674 | 70300850 | 15607697 | 50438740 | -99866989 | 49940041 | 34054742 | 14420588 | 0.000000 | 0.000000
09-04-2025 17:59:55.000 | 13570402 | 135704020 | 135.704 | 71319771 | 15614542 | 50248096 | -99862183 | 49940815 | 33866027 | 14323445 | 0.000000 | 0.000000
09-04-2025 17:59:50.000 | 13662136 | 136621360 | 136.6214 | 69300879 | 15604195 | 50616470 | -99871597 | 49970058 | 33677309 | 14224583 | 0.000000 | 0.000000
09-04-2025 17:59:45.000 | 13561245 | 135612450 | 135.6124 | 67421401 | 15614128 | 50208267 | -99876640 | 49980988 | 33488336 | 14130592 | 0.000000 | 0.000000
09-04-2025 17:59:40.000 | 13561617 | 135616170 | 135.6162 | 67405552 | 15613115 | 50212559 | -99876709 | 49971088 | 33299789 | 14036255 | 0.000000 | 0.000000
09-04-2025 17:59:35.000 | 13565328 | 135653280 | 135.6533 | 69158696 | 15612244 | 50232998 | -99870293 | 49944386 | 33111418 | 13942537 | 0.000000 | 0.000000
09-04-2025 17:59:30.000 | 13571563 | 135715630 | 135.7156 | 69508804 | 15611225 | 50259277 | -99869102 | 49940796 | 32922813 | 13846229 | 0.000000 | 0.000000
09-04-2025 17:59:25.000 | 13599252 | 135992520 | 135.9925 | 68242275 | 15611579 | 50358076 | -99874329 | 49928886 | 32734340 | 13750691 | 0.000000 | 0.000000
09-04-2025 17:59:20.000 | 13589363 | 135893630 | 135.8936 | 72338506 | 15609101 | 50337026 | -99858620 | 49931404 | 32545789 | 13653353 | 0.000000 | 0.000000
09-04-2025 17:59:15.000 | 13541066 | 135410660 | 135.4107 | 68628584 | 15613511 | 50137173 | -99871811 | 49950325 | 32357059 | 13554713 | 0.000000 | 0.000000
09-04-2025 17:59:10.000 | 13581583 | 135815830 | 135.8158 | 69135571 | 15610427 | 50298159 | -99870689 | 49940815 | 32168891 | 13458799 | 0.000000 | 0.000000
09-04-2025 17:59:05.000 | 13574130 | 135741300 | 135.7413 | 69953223 | 15612385 | 50265767 | -99867477 | 49945141 | 31980143 | 13362543 | 0.000000 | 0.000000
09-04-2025 17:59:00.000 | 13594572 | 135945720 | 135.9457 | 69312573 | 15611854 | 50342715 | -99870277 | 49950024 | 31791473 | 13266522 | 0.000000 | 0.000000
09-04-2025 17:58:55.000 | 13630331 | 136303310 | 136.3033 | 69221704 | 15607390 | 50487852 | -99871292 | 49961685 | 31602682 | 13170452 | 0.000000 | 0.000000
09-04-2025 17:58:50.000 | 13559555 | 135595550 | 135.5956 | 69700850 | 15613635 | 50207510 | -99868149 | 49952419 | 31413955 | 13075316 | 0.000000 | 0.000000
09-04-2025 17:58:45.000 | 13562138 | 135621380 | 135.6214 | 69755532 | 15611713 | 50224023 | -99867989 | 49945000 | 31225379 | 12978256 | 0.000000 | 0.000000
09-04-2025 17:58:40.000 | 13581033 | 135810330 | 135.8103 | 67986938 | 15608085 | 50302212 | -99874931 | 49957809 | 31036637 | 12881527 | 0.000000 | 0.000000
09-04-2025 17:58:35.000 | 13548569 | 135485690 | 135.4857 | 67030508 | 15614254 | 50160415 | -99877838 | 49951557 | 30847791 | 12787067 | 0.000000 | 0.000000
09-04-2025 17:58:30.000 | 13570217 | 135702170 | 135.7022 | 67976802 | 15612339 | 50248389 | -99874771 | 49930378 | 30659646 | 12692706 | 0.000000 | 0.000000
09-04-2025 17:58:25.000 | 13557986 | 135579860 | 135.5799 | 70804629 | 15613351 | 50204565 | -99863914 | 49925072 | 30471287 | 12596841 | 0.000000 | 0.000000
09-04-2025 17:58:20.000 | 13642027 | 136420270 | 136.4203 | 68661118 | 15607011 | 50531895 | -99873581 | 49961460 | 30282482 | 12499218 | 0.000000 | 0.000000
09-04-2025 17:58:15.000 | 13597923 | 135979230 | 135.9792 | 65045400 | 15609584 | 50353628 | -99885788 | 50008255 | 30093121 | 12405962 | 0.000000 | 0.000000
09-04-2025 17:58:10.000 | 13564509 | 135645090 | 135.6451 | 63171245 | 15611854 | 50222349 | -99891731 | 50017391 | 29904119 | 12316423 | 0.000000 | 0.000000
09-04-2025 17:58:05.000 | 13588434 | 135884340 | 135.8843 | 63603892 | 15611219 | 50310581 | -99890633 | 49996155 | 29715406 | 12228497 | 0.000000 | 0.000000
09-04-2025 17:58:00.000 | 13559495 | 135594950 | 135.595 | 66546489 | 15610531 | 50212080 | -99879791 | 49974491 | 29526861 | 12138278 | 0.000000 | 0.000000
09-04-2025 17:57:55.000 | 13520197 | 135201970 | 135.202 | 65904419 | 15614411 | 50052983 | -99881409 | 49973743 | 29338379 | 12045514 | 0.000000 | 0.000000
09-04-2025 17:57:50.000 | 13579791 | 135797910 | 135.7979 | 67584136 | 15611515 | 50285063 | -99876389 | 49958241 | 29150129 | 11952959 | 0.000000 | 0.000000
09-04-2025 17:57:45.000 | 13544030 | 135440300 | 135.4403 | 68746636 | 15611959 | 50154092 | -99871429 | 49963711 | 28962010 | 11857874 | 0.000000 | 0.000000
09-04-2025 17:57:40.000 | 13540916 | 135409160 | 135.4092 | 68589185 | 15611002 | 50144922 | -99871956 | 49968956 | 28773994 | 11763125 | 0.000000 | 0.000000
09-04-2025 17:57:35.000 | 13528181 | 135281810 | 135.2818 | 68139331 | 15612991 | 50091753 | -99873390 | 49978050 | 28585627 | 11667921 | 0.000000 | 0.000000
09-04-2025 17:57:30.000 | 13529764 | 135297640 | 135.2976 | 68507607 | 15612223 | 50099717 | -99872055 | 49978466 | 28397521 | 11572251 | 0.000000 | 0.000000
09-04-2025 17:57:25.000 | 13576341 | 135763410 | 135.7634 | 66634282 | 15611631 | 50270454 | -99879768 | 49987659 | 28209205 | 11477361 | 0.000000 | 0.000000
09-04-2025 17:57:20.000 | 13543734 | 135437340 | 135.4373 | 67034678 | 15610691 | 50153677 | -99877739 | 49980968 | 28021145 | 11384381 | 0.000000 | 0.000000
09-04-2025 17:57:15.000 | 13523659 | 135236590 | 135.2366 | 65992466 | 15614029 | 50067148 | -99881149 | 49999725 | 27832629 | 11291219 | 0.000000 | 0.000000
09-04-2025 17:57:10.000 | 13598856 | 135988560 | 135.9886 | 64208633 | 15611381 | 50349648 | -99888718 | 50009808 | 27644035 | 11199719 | 0.000000 | 0.000000
09-04-2025 17:57:05.000 | 13619408 | 136194080 | 136.1941 | 65609453 | 15608900 | 50436665 | -99884171 | 50009022 | 27455410 | 11109532 | 0.000000 | 0.000000
09-04-2025 17:57:00.000 | 13595425 | 135954250 | 135.9543 | 62184839 | 15608707 | 50342192 | -99895561 | 50039806 | 27266361 | 11019473 | 0.000000 | 0.000000
09-04-2025 17:56:55.000 | 13540645 | 135406450 | 135.4065 | 63229971 | 15611038 | 50134746 | -99891151 | 50025757 | 27077848 | 10933380 | 0.000000 | 0.000000
09-04-2025 17:56:50.000 | 13572503 | 135725030 | 135.725 | 61847075 | 15608790 | 50257227 | -99896339 | 50044563 | 26889332 | 10846471 | 0.000000 | 0.000000
09-04-2025 17:56:45.000 | 13500095 | 135000950 | 135.0009 | 61680156 | 15616878 | 49964268 | -99895790 | 50023998 | 26701006 | 10761392 | 0.000000 | 0.000000
09-04-2025 17:56:40.000 | 13599836 | 135998360 | 135.9984 | 63535591 | 15609287 | 50359722 | -99891052 | 49998489 | 26513184 | 10674066 | 0.000000 | 0.000000
09-04-2025 17:56:35.000 | 13546022 | 135460220 | 135.4602 | 65860581 | 15613146 | 50152285 | -99882011 | 49979118 | 26324752 | 10585908 | 0.000000 | 0.000000
09-04-2025 17:56:30.000 | 13556069 | 135560690 | 135.5607 | 66258979 | 15610687 | 50198062 | -99880760 | 49981102 | 26136344 | 10494109 | 0.000000 | 0.000000
09-04-2025 17:56:25.000 | 13542931 | 135429310 | 135.4293 | 67317397 | 15611691 | 50147803 | -99876694 | 49976360 | 25948166 | 10402003 | 0.000000 | 0.000000
09-04-2025 17:56:20.000 | 13574844 | 135748440 | 135.7484 | 67071543 | 15608544 | 50275581 | -99878159 | 49988983 | 25759701 | 10308140 | 0.000000 | 0.000000
09-04-2025 17:56:15.000 | 13556102 | 135561020 | 135.561 | 67243643 | 15613017 | 50192275 | -99877197 | 49969349 | 25571158 | 10216346 | 0.000000 | 0.000000
09-04-2025 17:56:10.000 | 13589098 | 135890980 | 135.891 | 67709731 | 15611706 | 50319199 | -99876099 | 49955513 | 25382869 | 10122635 | 0.000000 | 0.000000
09-04-2025 17:56:05.000 | 13554220 | 135542200 | 135.5422 | 68527212 | 15612952 | 50187900 | -99872437 | 49941185 | 25194795 | 10028737 | 0.000000 | 0.000000
09-04-2025 17:56:00.000 | 13640238 | 136402380 | 136.4024 | 68978667 | 15609478 | 50518247 | -99872375 | 49963715 | 25006326 | 993271667 | 0.000000 | 0.000000
09-04-2025 17:55:55.000 | 13592591 | 135925910 | 135.9259 | 65736704 | 15610368 | 50333071 | -99883263 | 49990021 | 24817152 | 983853760 | 0.000000 | 0.000000
09-04-2025 17:55:50.000 | 13607611 | 136076110 | 136.0761 | 65621440 | 15608995 | 50393540 | -99883926 | 50007626 | 24627990 | 974780823 | 0.000000 | 0.000000
09-04-2025 17:55:45.000 | 13604814 | 136048140 | 136.0481 | 61853989 | 15612795 | 50363604 | -99896805 | 50021118 | 24438951 | 965888306 | 0.000000 | 0.000000
09-04-2025 17:55:40.000 | 13609900 | 136099000 | 136.099 | 61764463 | 15614309 | 50377036 | -99897179 | 50007652 | 24249850 | 957300476 | 0.000000 | 0.000000
09-04-2025 17:55:35.000 | 13669567 | 136695670 | 136.6957 | 64133311 | 15610062 | 50615239 | -99890121 | 50001324 | 24060691 | 948575378 | 0.000000 | 0.000000
09-04-2025 17:55:30.000 | 13667338 | 136673380 | 136.6734 | 62883545 | 15608474 | 50610332 | -99894318 | 50031059 | 23871244 | 939686523 | 0.000000 | 0.000000
09-04-2025 17:55:25.000 | 13629863 | 136298630 | 136.2986 | 60365635 | 15610466 | 50461426 | -99902069 | 50070091 | 23680998 | 930999023 | 0.000000 | 0.000000
09-04-2025 17:55:20.000 | 13637723 | 136377230 | 136.3772 | 61135649 | 15613497 | 50481431 | -99899673 | 50045948 | 23491516 | 922627869 | 0.000000 | 0.000000
09-04-2025 17:55:15.000 | 13632067 | 136320670 | 136.3207 | 66118599 | 15612720 | 50471919 | -99882584 | 50003567 | 23302498 | 913953247 | 0.000000 | 0.000000
09-04-2025 17:55:10.000 | 13636680 | 136366800 | 136.3668 | 67965317 | 15611006 | 50497720 | -99876030 | 50005226 | 23113145 | 904637451 | 0.000000 | 0.000000
09-04-2025 17:55:05.000 | 13652602 | 136526020 | 136.526 | 65457607 | 15612026 | 50548501 | -99885262 | 50009937 | 22923760 | 895488037 | 0.000000 | 0.000000
09-04-2025 17:55:00.000 | 13647916 | 136479160 | 136.4792 | 64904619 | 15609802 | 50537876 | -99887108 | 50021790 | 22734182 | 886394043 | 0.000000 | 0.000000
09-04-2025 17:54:55.000 | 13628269 | 136282690 | 136.2827 | 64718999 | 15612762 | 50455278 | -99887428 | 50020897 | 22544662 | 877433777 | 0.000000 | 0.000000
09-04-2025 17:54:50.000 | 13654414 | 136544140 | 136.5441 | 65828853 | 15610725 | 50560596 | -99883987 | 50018337 | 22355334 | 868453796 | 0.000000 | 0.000000
09-04-2025 17:54:45.000 | 13603788 | 136037880 | 136.0379 | 65981011 | 15616155 | 50356499 | -99882584 | 50024086 | 22166000 | 859404297 | 0.000000 | 0.000000
09-04-2025 17:54:40.000 | 13701258 | 137012580 | 137.0126 | 65464390 | 15609307 | 50736992 | -99886047 | 50064201 | 21976318 | 850159607 | 0.000000 | 0.000000
09-04-2025 17:54:35.000 | 13689172 | 136891720 | 136.8917 | 62395879 | 15608674 | 50689575 | -99896286 | 50084007 | 21786352 | 841269043 | 0.000000 | 0.000000
09-04-2025 17:54:30.000 | 13653370 | 136533700 | 136.5337 | 61538130 | 15612889 | 50542310 | -99898582 | 50089577 | 21596318 | 832664368 | 0.000000 | 0.000000
09-04-2025 17:54:25.000 | 13631575 | 136315750 | 136.3158 | 62857085 | 15615065 | 50456597 | -99893860 | 50072872 | 21406600 | 824092590 | 0.000000 | 0.000000
09-04-2025 17:54:20.000 | 13661822 | 136618220 | 136.6182 | 63869561 | 15606379 | 50599321 | -99890900 | 50054474 | 21217186 | 815199829 | 0.000000 | 0.000000
09-04-2025 17:54:15.000 | 13589244 | 135892440 | 135.8924 | 63819443 | 15615398 | 50301279 | -99889908 | 50045757 | 21027338 | 806255249 | 0.000000 | 0.000000
09-04-2025 17:54:10.000 | 13622714 | 136227140 | 136.2271 | 67846162 | 15611990 | 50442676 | -99876213 | 50005295 | 20838162 | 797192932 | 0.000000 | 0.000000
09-04-2025 17:54:05.000 | 13653961 | 136539610 | 136.5396 | 68855205 | 15616235 | 50546362 | -99873093 | 49996559 | 20648822 | 787846863 | 0.000000 | 0.000000
09-04-2025 17:54:00.000 | 13671364 | 136713640 | 136.7136 | 69565728 | 15607203 | 50640952 | -99870789 | 50015976 | 20459045 | 778132019 | 0.000000 | 0.000000
09-04-2025 17:53:55.000 | 13636548 | 136365480 | 136.3655 | 66839912 | 15613277 | 50487446 | -99880089 | 50016262 | 20269396 | 768724609 | 0.000000 | 0.000000
09-04-2025 17:53:50.000 | 13614136 | 136141360 | 136.1414 | 68021250 | 15614797 | 50402036 | -99875412 | 49983154 | 20080100 | 759409485 | 0.000000 | 0.000000
09-04-2025 17:53:45.000 | 13659111 | 136591110 | 136.5911 | 68616377 | 15611046 | 50581768 | -99874062 | 49970509 | 19890697 | 749945923 | 0.000000 | 0.000000
09-04-2025 17:53:40.000 | 13659031 | 136590310 | 136.5903 | 69858960 | 15613476 | 50575981 | -99869469 | 49980598 | 19701133 | 740449036 | 0.000000 | 0.000000
09-04-2025 17:53:35.000 | 13683744 | 136837440 | 136.8374 | 67706270 | 15608622 | 50678608 | -99877815 | 50013622 | 19511287 | 730818726 | 0.000000 | 0.000000
09-04-2025 17:53:30.000 | 13645327 | 136453270 | 136.4533 | 65917695 | 15612704 | 50520210 | -99883522 | 50020493 | 19321764 | 721670349 | 0.000000 | 0.000000
09-04-2025 17:53:25.000 | 13649430 | 136494300 | 136.4943 | 66419458 | 15612259 | 50537461 | -99881813 | 50019527 | 19132197 | 712432312 | 0.000000 | 0.000000
09-04-2025 17:53:20.000 | 13673728 | 136737280 | 136.7373 | 65756045 | 15611177 | 50630308 | -99884567 | 50019699 | 18942348 | 703278442 | 0.000000 | 0.000000
09-04-2025 17:53:15.000 | 13673178 | 136731780 | 136.7318 | 64360371 | 15611907 | 50622939 | -99889404 | 50024986 | 18752756 | 694234436 | 0.000000 | 0.000000
09-04-2025 17:53:10.000 | 13595645 | 135956450 | 135.9564 | 64081812 | 15614601 | 50327744 | -99889107 | 50023701 | 18562988 | 685220398 | 0.000000 | 0.000000
09-04-2025 17:53:05.000 | 13666370 | 136663700 | 136.6637 | 67337002 | 15609399 | 50611211 | -99878838 | 50006840 | 18373791 | 676199463 | 0.000000 | 0.000000
09-04-2025 17:53:00.000 | 13674094 | 136740940 | 136.7409 | 62620576 | 15606998 | 50639390 | -99895302 | 50050961 | 18183645 | 667069214 | 0.000000 | 0.000000
09-04-2025 17:52:55.000 | 13635630 | 136356300 | 136.3563 | 61011968 | 15610302 | 50483960 | -99900047 | 50053360 | 17993824 | 658587952 | 0.000000 | 0.000000
09-04-2025 17:52:50.000 | 13635873 | 136358730 | 136.3587 | 61766475 | 15611571 | 50482051 | -99897568 | 50040802 | 17804506 | 650121826 | 0.000000 | 0.000000
09-04-2025 17:52:45.000 | 13653664 | 136536640 | 136.5366 | 62481401 | 15608178 | 50559639 | -99895454 | 50042316 | 17615258 | 641496399 | 0.000000 | 0.000000
09-04-2025 17:52:40.000 | 13652753 | 136527530 | 136.5275 | 59844399 | 15611184 | 50542109 | -99904068 | 50066219 | 17425350 | 633004517 | 0.000000 | 0.000000
09-04-2025 17:52:35.000 | 13681317 | 136813170 | 136.8132 | 60172046 | 15613353 | 50644453 | -99903419 | 50057720 | 17235768 | 624722168 | 0.000000 | 0.000000
09-04-2025 17:52:30.000 | 13632156 | 136321560 | 136.3216 | 60774023 | 15612432 | 50463638 | -99900772 | 50059410 | 17046201 | 616275085 | 0.000000 | 0.000000
09-04-2025 17:52:25.000 | 13635586 | 136355860 | 136.3559 | 59969575 | 15611673 | 50477388 | -99903427 | 50051964 | 16856795 | 607873718 | 0.000000 | 0.000000
09-04-2025 17:52:20.000 | 13657169 | 136571690 | 136.5717 | 62734619 | 15611741 | 50561226 | -99894661 | 50033077 | 16667555 | 599444458 | 0.000000 | 0.000000
09-04-2025 17:52:15.000 | 13585125 | 135851250 | 135.8512 | 62442949 | 15614708 | 50285161 | -99894531 | 50038204 | 16478031 | 590702271 | 0.000000 | 0.000000
09-04-2025 17:52:10.000 | 13665778 | 136657780 | 136.6578 | 61464087 | 15609319 | 50598901 | -99899010 | 50060562 | 16288524 | 581951416 | 0.000000 | 0.000000
09-04-2025 17:52:05.000 | 13651445 | 136514450 | 136.5145 | 58491245 | 15611377 | 50536450 | -99908333 | 50073135 | 16098819 | 573550476 | 0.000000 | 0.000000
09-04-2025 17:52:00.000 | 13623158 | 136231580 | 136.2316 | 60038418 | 15609170 | 50439980 | -99903030 | 50072990 | 15909261 | 565251526 | 0.000000 | 0.000000
09-04-2025 17:51:55.000 | 13596106 | 135961060 | 135.9611 | 61113306 | 15613401 | 50327451 | -99899132 | 50064548 | 15719868 | 556953918 | 0.000000 | 0.000000
09-04-2025 17:51:50.000 | 13622500 | 136225000 | 136.225 | 60469951 | 15612113 | 50429072 | -99901627 | 50063545 | 15531033 | 548412476 | 0.000000 | 0.000000
09-04-2025 17:51:45.000 | 13604927 | 136049270 | 136.0493 | 62302827 | 15614811 | 50358037 | -99895309 | 50038685 | 15342191 | 539983337 | 0.000000 | 0.000000
09-04-2025 17:51:40.000 | 13636266 | 136362660 | 136.3627 | 60640044 | 15609123 | 50489258 | -99901268 | 50052391 | 15153068 | 531370728 | 0.000000 | 0.000000
09-04-2025 17:51:35.000 | 13593892 | 135938920 | 135.9389 | 58486792 | 15611124 | 50323447 | -99907578 | 50069683 | 14963803 | 523014954 | 0.000000 | 0.000000
09-04-2025 17:51:30.000 | 13605272 | 136052720 | 136.0527 | 58417612 | 15613805 | 50356445 | -99907944 | 50061550 | 14774824 | 514945435 | 0.000000 | 0.000000
09-04-2025 17:51:25.000 | 13614902 | 136149020 | 136.149 | 59672241 | 15615746 | 50386958 | -99904091 | 50040813 | 14585641 | 506770355 | 0.000000 | 0.000000
09-04-2025 17:51:20.000 | 13648066 | 136480660 | 136.4807 | 62230449 | 15610918 | 50530132 | -99896210 | 50035660 | 14396503 | 498236267 | 0.000000 | 0.000000
09-04-2025 17:51:15.000 | 13664583 | 136645830 | 136.6458 | 59832251 | 15610121 | 50590015 | -99904274 | 50064594 | 14206787 | 489701019 | 0.000000 | 0.000000
09-04-2025 17:51:10.000 | 13655759 | 136557590 | 136.5576 | 58327656 | 15611937 | 50548833 | -99908905 | 50060211 | 14017279 | 481470337 | 0.000000 | 0.000000
09-04-2025 17:51:05.000 | 13641830 | 136418300 | 136.4183 | 57887524 | 15604219 | 50521396 | -99910088 | 50067883 | 13827649 | 473321930 | 0.000000 | 0.000000
09-04-2025 17:51:00.000 | 13601177 | 136011770 | 136.0118 | 52853291 | 15613112 | 50335850 | -99924583 | 50085957 | 13638071 | 465728912 | 0.000000 | 0.000000
09-04-2025 17:50:55.000 | 13619759 | 136197590 | 136.1976 | 53231680 | 15613556 | 50403506 | -99923706 | 50055973 | 13449337 | 458437775 | 0.000000 | 0.000000
09-04-2025 17:50:50.000 | 13629431 | 136294310 | 136.2943 | 55374102 | 15613961 | 50440342 | -99917572 | 50043423 | 13260149 | 451026520 | 0.000000 | 0.000000
09-04-2025 17:50:45.000 | 13681748 | 136817480 | 136.8175 | 53714766 | 15607003 | 50653442 | -99923019 | 50070961 | 13070356 | 443389832 | 0.000000 | 0.000000
09-04-2025 17:50:40.000 | 13646072 | 136460720 | 136.4607 | 49101416 | 15613346 | 50494473 | -99935326 | 50087463 | 12880449 | 436217438 | 0.000000 | 0.000000
09-04-2025 17:50:35.000 | 13631623 | 136316230 | 136.3162 | 50627588 | 15616345 | 50434146 | -99931107 | 50059139 | 12691017 | 429310242 | 0.000000 | 0.000000
09-04-2025 17:50:30.000 | 13664717 | 136647170 | 136.6472 | 51728594 | 15608396 | 50583198 | -99928421 | 50062119 | 12501620 | 422126373 | 0.000000 | 0.000000
09-04-2025 17:50:25.000 | 13673816 | 136738160 | 136.7382 | 51115400 | 15608824 | 50615449 | -99930206 | 50079006 | 12311938 | 414910614 | 0.000000 | 0.000000
09-04-2025 17:50:20.000 | 13641320 | 136413200 | 136.4132 | 51386641 | 15613151 | 50481123 | -99929123 | 50054966 | 12122274 | 407877350 | 0.000000 | 0.000000
09-04-2025 17:50:15.000 | 13595995 | 135959950 | 135.9599 | 53745591 | 15614641 | 50311948 | -99921959 | 50026905 | 11932950 | 400703522 | 0.000000 | 0.000000
09-04-2025 17:50:10.000 | 13616620 | 136166200 | 136.1662 | 54607104 | 15612197 | 50397734 | -99919685 | 50029846 | 11743840 | 393086914 | 0.000000 | 0.000000
09-04-2025 17:50:05.000 | 13641244 | 136412440 | 136.4124 | 53277876 | 15613950 | 50482686 | -99923820 | 50036255 | 11554693 | 385575867 | 0.000000 | 0.000000
09-04-2025 17:50:00.000 | 13632089 | 136320890 | 136.3209 | 55251309 | 15612852 | 50453511 | -99917969 | 50025967 | 11365729 | 378048340 | 0.000000 | 0.000000
09-04-2025 17:49:55.000 | 13644745 | 136447450 | 136.4475 | 53516372 | 15614249 | 50493730 | -99923172 | 50019482 | 11176371 | 370524902 | 0.000000 | 0.000000
09-04-2025 17:49:50.000 | 13674181 | 136741810 | 136.7418 | 51788872 | 15606376 | 50625703 | -99928360 | 50042267 | 10986547 | 363042572 | 0.000000 | 0.000000
09-04-2025 17:49:45.000 | 13621664 | 136216640 | 136.2166 | 48918193 | 15612982 | 50406074 | -99935577 | 50044506 | 10796829 | 355982025 | 0.000000 | 0.000000
09-04-2025 17:49:40.000 | 13645036 | 136450360 | 136.4504 | 52058179 | 15614030 | 50493833 | -99927299 | 50019638 | 10607499 | 349079041 | 0.000000 | 0.000000
09-04-2025 17:49:35.000 | 13698139 | 136981390 | 136.9814 | 50615991 | 15606927 | 50710542 | -99931801 | 50052105 | 10417652 | 341919983 | 0.000000 | 0.000000
09-04-2025 17:49:30.000 | 13678777 | 136787770 | 136.7878 | 45940259 | 15609371 | 50625640 | -99943649 | 50081676 | 10227939 | 335243958 | 0.000000 | 0.000000
09-04-2025 17:49:25.000 | 13622223 | 136222230 | 136.2222 | 44661729 | 15612059 | 50405313 | -99946297 | 50088837 | 10038265 | 328935272 | 0.000000 | 0.000000
09-04-2025 17:49:20.000 | 13613286 | 136132860 | 136.1329 | 45467930 | 15612666 | 50371553 | -99944267 | 50067474 | 98489141 | 322703033 | 0.000000 | 0.000000
09-04-2025 17:49:15.000 | 13598542 | 135985420 | 135.9854 | 48086523 | 15614481 | 50314702 | -99937538 | 50043808 | 96595332 | 316290222 | 0.000000 | 0.000000
09-04-2025 17:49:10.000 | 13744514 | 137445140 | 137.4451 | 47916309 | 15606378 | 50880298 | -99939285 | 50086956 | 94694717 | 309479980 | 0.000000 | 0.000000
09-04-2025 17:49:05.000 | 13711948 | 137119480 | 137.1195 | 44673418 | 15608545 | 50748184 | -99946968 | 50114372 | 92792744 | 303164795 | 0.000000 | 0.000000
09-04-2025 17:49:00.000 | 13678644 | 136786440 | 136.7864 | 44052637 | 15611994 | 50614082 | -99948181 | 50114204 | 90892314 | 297034027 | 0.000000 | 0.000000
09-04-2025 17:48:55.000 | 13653459 | 136534590 | 136.5346 | 42609097 | 15611642 | 50519717 | -99951340 | 50095352 | 88993848 | 291024292 | 0.000000 | 0.000000
09-04-2025 17:48:50.000 | 13620313 | 136203130 | 136.2031 | 46387617 | 15613044 | 50397319 | -99942055 | 50090919 | 87098682 | 284942383 | 0.000000 | 0.000000
09-04-2025 17:48:45.000 | 13648089 | 136480890 | 136.4809 | 47008521 | 15609005 | 50514224 | -99940735 | 50108120 | 85203018 | 278416473 | 0.000000 | 0.000000
09-04-2025 17:48:40.000 | 13635947 | 136359470 | 136.3595 | 45604092 | 15613725 | 50452690 | -99944122 | 50099583 | 83305430 | 272179535 | 0.000000 | 0.000000
09-04-2025 17:48:35.000 | 13665695 | 136656950 | 136.6569 | 46017754 | 15612478 | 50566255 | -99943352 | 50089806 | 81410142 | 265860107 | 0.000000 | 0.000000
09-04-2025 17:48:30.000 | 13699009 | 136990090 | 136.9901 | 45883276 | 15608146 | 50703940 | -99943954 | 50105827 | 79510142 | 259455811 | 0.000000 | 0.000000
09-04-2025 17:48:25.000 | 13679275 | 136792750 | 136.7928 | 43582051 | 15610599 | 50619932 | -99949287 | 50116562 | 77610503 | 253274338 | 0.000000 | 0.000000
09-04-2025 17:48:20.000 | 13672975 | 136729750 | 136.7297 | 43992524 | 15610172 | 50598794 | -99948280 | 50098042 | 75714282 | 247186981 | 0.000000 | 0.000000
09-04-2025 17:48:15.000 | 13639247 | 136392470 | 136.3925 | 45066626 | 15612577 | 50468140 | -99945457 | 50098934 | 73816182 | 241006180 | 0.000000 | 0.000000
09-04-2025 17:48:10.000 | 13638469 | 136384690 | 136.3847 | 46906904 | 15614857 | 50458887 | -99940910 | 50077614 | 71923389 | 234712097 | 0.000000 | 0.000000
09-04-2025 17:48:05.000 | 13636498 | 136364980 | 136.365 | 47921045 | 15612773 | 50460054 | -99938309 | 50078861 | 70029404 | 228099640 | 0.000000 | 0.000000
09-04-2025 17:48:00.000 | 13725691 | 137256910 | 137.2569 | 47169023 | 15606633 | 50808540 | -99941002 | 50105938 | 68133623 | 221443436 | 0.000000 | 0.000000
09-04-2025 17:47:55.000 | 13634161 | 136341610 | 136.3416 | 44132231 | 15612919 | 50445771 | -99947655 | 50114388 | 66235625 | 215119812 | 0.000000 | 0.000000
09-04-2025 17:47:50.000 | 13633502 | 136335020 | 136.335 | 44925483 | 15613388 | 50442832 | -99945755 | 50103970 | 64339463 | 208927460 | 0.000000 | 0.000000
09-04-2025 17:47:45.000 | 13640895 | 136408950 | 136.409 | 45269043 | 15610667 | 50479155 | -99944977 | 50092514 | 62444702 | 202632721 | 0.000000 | 0.000000
09-04-2025 17:47:40.000 | 13650848 | 136508480 | 136.5085 | 45747925 | 15611539 | 50514043 | -99943893 | 50084618 | 60549839 | 196373581 | 0.000000 | 0.000000
09-04-2025 17:47:35.000 | 13632803 | 136328030 | 136.328 | 47050972 | 15612017 | 50447349 | -99940498 | 50078808 | 58654429 | 189999069 | 0.000000 | 0.000000
09-04-2025 17:47:30.000 | 13682208 | 136822080 | 136.8221 | 45377275 | 15609981 | 50634365 | -99945045 | 50093430 | 56758496 | 183571915 | 0.000000 | 0.000000
09-04-2025 17:47:25.000 | 13668931 | 136689310 | 136.6893 | 45659624 | 15608417 | 50590786 | -99944252 | 50092751 | 54861978 | 177339417 | 0.000000 | 0.000000
09-04-2025 17:47:20.000 | 13646872 | 136468720 | 136.4687 | 43953696 | 15612633 | 50493521 | -99948174 | 50103168 | 52964575 | 171084244 | 0.000000 | 0.000000
09-04-2025 17:47:15.000 | 13583438 | 135834380 | 135.8344 | 44201924 | 15617074 | 50245337 | -99947098 | 50076187 | 51072061 | 164990616 | 0.000000 | 0.000000
09-04-2025 17:47:10.000 | 13624447 | 136244470 | 136.2445 | 48293638 | 15609368 | 50427334 | -99937241 | 50057732 | 49185234 | 158547211 | 0.000000 | 0.000000
09-04-2025 17:47:05.000 | 13643913 | 136439130 | 136.4391 | 46158794 | 15610412 | 50492368 | -99942825 | 50064835 | 47293452 | 152100601 | 0.000000 | 0.000000
09-04-2025 17:47:00.000 | 13618470 | 136184700 | 136.1847 | 46587031 | 15609200 | 50403330 | -99941536 | 50059597 | 45402734 | 145650238 | 0.000000 | 0.000000
09-04-2025 17:46:55.000 | 13616853 | 136168530 | 136.1685 | 45989546 | 15610452 | 50392515 | -99943016 | 50063396 | 43510918 | 139207596 | 0.000000 | 0.000000
09-04-2025 17:46:50.000 | 13549808 | 135498080 | 135.4981 | 45066138 | 15617005 | 50122578 | -99944733 | 50054283 | 41623242 | 132860336 | 0.000000 | 0.000000
09-04-2025 17:46:45.000 | 13587781 | 135877810 | 135.8778 | 46737305 | 15612029 | 50281001 | -99940895 | 50043636 | 39738394 | 126461044 | 0.000000 | 0.000000
09-04-2025 17:46:40.000 | 13604539 | 136045390 | 136.0454 | 44868301 | 15610941 | 50343442 | -99945656 | 50063049 | 37845884 | 120010612 | 0.000000 | 0.000000
09-04-2025 17:46:35.000 | 13596103 | 135961030 | 135.961 | 44965552 | 15613325 | 50305181 | -99945358 | 50070213 | 35954316 | 113816856 | 0.000000 | 0.000000
09-04-2025 17:46:30.000 | 13630848 | 136308480 | 136.3085 | 42882788 | 15612965 | 50431997 | -99950546 | 50073368 | 34067620 | 107686264 | 0.000000 | 0.000000
09-04-2025 17:46:25.000 | 13627350 | 136273500 | 136.2735 | 44814619 | 15610599 | 50428955 | -99945969 | 50075699 | 32174670 | 101632996 | 0.000000 | 0.000000
09-04-2025 17:46:20.000 | 13636772 | 136367720 | 136.3677 | 43082710 | 15607134 | 50473091 | -99950134 | 50107422 | 30278542 | 95431778 | 0.000000 | 0.000000
09-04-2025 17:46:15.000 | 13616448 | 136164480 | 136.1645 | 40481284 | 15611555 | 50382529 | -99955833 | 50118984 | 28385242 | 89627441 | 0.000000 | 0.000000
09-04-2025 17:46:10.000 | 13574613 | 135746130 | 135.7461 | 44580825 | 15612230 | 50229590 | -99946114 | 50105186 | 26494072 | 83797279 | 0.000000 | 0.000000
09-04-2025 17:46:05.000 | 13628264 | 136282640 | 136.2826 | 43013491 | 15613078 | 50422881 | -99950226 | 50110462 | 24604233 | 77790962 | 0.000000 | 0.000000
09-04-2025 17:46:00.000 | 13658569 | 136585690 | 136.5857 | 41304355 | 15607737 | 50549258 | -99954308 | 50123932 | 22709971 | 71852562 | 0.000000 | 0.000000
09-04-2025 17:45:55.000 | 13600548 | 136005480 | 136.0055 | 41351353 | 15615636 | 50309658 | -99953812 | 50100212 | 20816423 | 66196007 | 0.000000 | 0.000000
09-04-2025 17:45:50.000 | 13633639 | 136336390 | 136.3364 | 43234805 | 15613461 | 50441577 | -99949753 | 50078274 | 18925247 | 60433041 | 0.000000 | 0.000000
09-04-2025 17:45:45.000 | 13624850 | 136248500 | 136.2485 | 43304868 | 15610481 | 50418784 | -99949532 | 50099983 | 17029939 | 54376377 | 0.000000 | 0.000000
09-04-2025 17:45:40.000 | 13630678 | 136306780 | 136.3068 | 41883413 | 15610221 | 50439126 | -99952827 | 50117294 | 15136674 | 48465988 | 0.000000 | 0.000000
09-04-2025 17:45:35.000 | 13625269 | 136252690 | 136.2527 | 41811885 | 15610259 | 50419131 | -99952950 | 50123001 | 13243530 | 42693363 | 0.000000 | 0.000000
09-04-2025 17:45:30.000 | 13628408 | 136284080 | 136.2841 | 42108179 | 15611770 | 50425850 | -99952301 | 50120682 | 11349718 | 36879082 | 0.000000 | 0.000000
09-04-2025 17:45:25.000 | 13588969 | 135889690 | 135.8897 | 43649146 | 15615167 | 50271333 | -99948448 | 50116611 | 945641602 | 30973782 | 0.000000 | 0.000000
09-04-2025 17:45:20.000 | 13572255 | 135722550 | 135.7226 | 43554839 | 15614397 | 50212090 | -99948547 | 50101009 | 756917480 | 24891012 | 0.000000 | 0.000000
09-04-2025 17:45:15.000 | 13630761 | 136307610 | 136.3076 | 45420635 | 15613448 | 50433086 | -99944527 | 50091599 | 567960022 | 18830700 | 0.000000 | 0.000000
09-04-2025 17:45:10.000 | 13651150 | 136511500 | 136.5115 | 45894697 | 15609303 | 50522886 | -99943535 | 50110992 | 378591919 | 12502616 | 0.000000 | 0.000000
09-04-2025 17:45:05.000 | 13639002 | 136390020 | 136.39 | 44941846 | 15610047 | 50474546 | -99945755 | 50104580 | 189314041 | 6270689 | 0.000000 | 0.000000
09-04-2025 17:45:00.000 | 13614497 | 136144970 | 136.145 | 45293223 | 15612742 | 50374795 | -99944710 | 50096558 | 34012578 | 12441923 | 0.000000 | 0.000000
09-04-2025 17:44:55.000 | 13620864 | 136208640 | 136.2086 | 47376831 | 15610991 | 50406758 | -99939560 | 50068764 | 33823879 | 12378508 | 0.000000 | 0.000000
09-04-2025 17:44:50.000 | 13550389 | 135503890 | 135.5039 | 50253848 | 15618541 | 50126440 | -99931297 | 50040264 | 33635070 | 12312041 | 0.000000 | 0.000000
09-04-2025 17:44:45.000 | 13626384 | 136263840 | 136.2638 | 56253296 | 15608754 | 50446934 | -99914894 | 50040817 | 33446180 | 12236990 | 0.000000 | 0.000000
09-04-2025 17:44:40.000 | 13616648 | 136166480 | 136.1665 | 52123057 | 15609102 | 50403682 | -99926819 | 50069180 | 33256832 | 12160867 | 0.000000 | 0.000000
09-04-2025 17:44:35.000 | 13579013 | 135790130 | 135.7901 | 51330332 | 15612198 | 50253755 | -99928627 | 50059982 | 33067973 | 12088534 | 0.000000 | 0.000000
09-04-2025 17:44:30.000 | 13570263 | 135702630 | 135.7026 | 54028452 | 15609629 | 50234243 | -99920837 | 50035011 | 32879414 | 12016262 | 0.000000 | 0.000000
09-04-2025 17:44:25.000 | 13601158 | 136011580 | 136.0116 | 51343564 | 15609155 | 50345654 | -99928825 | 50036106 | 32690777 | 11942611 | 0.000000 | 0.000000
09-04-2025 17:44:20.000 | 13538009 | 135380090 | 135.3801 | 50156821 | 15613499 | 50097002 | -99931442 | 50014423 | 32502279 | 11871949 | 0.000000 | 0.000000
09-04-2025 17:44:15.000 | 13550250 | 135502500 | 135.5025 | 53063867 | 15613077 | 50147788 | -99923409 | 49990292 | 32313947 | 11800638 | 0.000000 | 0.000000
09-04-2025 17:44:10.000 | 13579694 | 135796940 | 135.7969 | 55238711 | 15614956 | 50253926 | -99917374 | 49964405 | 32125824 | 11726384 | 0.000000 | 0.000000
09-04-2025 17:44:05.000 | 13532272 | 135322720 | 135.3227 | 55193423 | 15614208 | 50080601 | -99916924 | 49965618 | 31937518 | 11649583 | 0.000000 | 0.000000
09-04-2025 17:44:00.000 | 13575178 | 135751780 | 135.7518 | 55814106 | 15606612 | 50264517 | -99915588 | 49967331 | 31749471 | 11572090 | 0.000000 | 0.000000
09-04-2025 17:43:55.000 | 13515014 | 135150140 | 135.1501 | 53198091 | 15610198 | 50025957 | -99922623 | 49982494 | 31560992 | 11496018 | 0.000000 | 0.000000
09-04-2025 17:43:50.000 | 13545309 | 135453090 | 135.4531 | 55448618 | 15613615 | 50130547 | -99916321 | 49958523 | 31372947 | 11422098 | 0.000000 | 0.000000
09-04-2025 17:43:45.000 | 13588788 | 135887880 | 135.8879 | 54035029 | 15607539 | 50308315 | -99921036 | 49981552 | 31184537 | 11344724 | 0.000000 | 0.000000
09-04-2025 17:43:40.000 | 13565706 | 135657060 | 135.6571 | 54348652 | 15613408 | 50204824 | -99919846 | 49999683 | 30996219 | 11269948 | 0.000000 | 0.000000
09-04-2025 17:43:35.000 | 13611097 | 136110970 | 136.111 | 51450146 | 15606902 | 50389043 | -99928635 | 50056492 | 30807438 | 11194430 | 0.000000 | 0.000000
09-04-2025 17:43:30.000 | 13546383 | 135463830 | 135.4638 | 47963491 | 15612707 | 50126841 | -99937378 | 50081665 | 30618629 | 11125122 | 0.000000 | 0.000000
09-04-2025 17:43:25.000 | 13528105 | 135281050 | 135.281 | 47980391 | 15616015 | 50049639 | -99937164 | 50045803 | 30430377 | 11059880 | 0.000000 | 0.000000
09-04-2025 17:43:20.000 | 13573531 | 135735310 | 135.7353 | 49421699 | 15612570 | 50229375 | -99933777 | 50009892 | 30242256 | 10991934 | 0.000000 | 0.000000
09-04-2025 17:43:15.000 | 13605739 | 136057390 | 136.0574 | 51427412 | 15610772 | 50357192 | -99928642 | 50011177 | 30053813 | 10922899 | 0.000000 | 0.000000
09-04-2025 17:43:10.000 | 13623241 | 136232410 | 136.2324 | 47441919 | 15606909 | 50429409 | -99939415 | 50064453 | 29864471 | 10852783 | 0.000000 | 0.000000
09-04-2025 17:43:05.000 | 13563919 | 135639190 | 135.6392 | 45007236 | 15612851 | 50187871 | -99944992 | 50078228 | 29675479 | 10789078 | 0.000000 | 0.000000
09-04-2025 17:43:00.000 | 13568170 | 135681700 | 135.6817 | 45945444 | 15615271 | 50196802 | -99942719 | 50059811 | 29486900 | 10726588 | 0.000000 | 0.000000
09-04-2025 17:42:55.000 | 13578630 | 135786300 | 135.7863 | 49482290 | 15611023 | 50253135 | -99933670 | 50044044 | 29298527 | 10660775 | 0.000000 | 0.000000
09-04-2025 17:42:50.000 | 13626559 | 136265590 | 136.2656 | 46015059 | 15609145 | 50433154 | -99943031 | 50064037 | 29110137 | 10594602 | 0.000000 | 0.000000
09-04-2025 17:42:45.000 | 13608908 | 136089080 | 136.0891 | 45761772 | 15609408 | 50365737 | -99943512 | 50087971 | 28921324 | 10531565 | 0.000000 | 0.000000
09-04-2025 17:42:40.000 | 13588778 | 135887780 | 135.8878 | 44381299 | 15610961 | 50285010 | -99946709 | 50107319 | 28732461 | 10469874 | 0.000000 | 0.000000
09-04-2025 17:42:35.000 | 13589392 | 135893920 | 135.8939 | 43429111 | 15611578 | 50284316 | -99948975 | 50104691 | 28543840 | 10409349 | 0.000000 | 0.000000
09-04-2025 17:42:30.000 | 13561058 | 135610580 | 135.6106 | 44791680 | 15614566 | 50171509 | -99945496 | 50087559 | 28355102 | 10347811 | 0.000000 | 0.000000
09-04-2025 17:42:25.000 | 13595169 | 135951690 | 135.9517 | 45041812 | 15611325 | 50307642 | -99945160 | 50071220 | 28166398 | 10285117 | 0.000000 | 0.000000
09-04-2025 17:42:20.000 | 13610189 | 136101890 | 136.1019 | 44183418 | 15612981 | 50357520 | -99947350 | 50056042 | 27977711 | 10222498 | 0.000000 | 0.000000
09-04-2025 17:42:15.000 | 13592350 | 135923500 | 135.9235 | 47974487 | 15610714 | 50304106 | -99937767 | 50028187 | 27789203 | 10159557 | 0.000000 | 0.000000
09-04-2025 17:42:10.000 | 13592742 | 135927420 | 135.9274 | 45656362 | 15609260 | 50306187 | -99943634 | 50055893 | 27600115 | 10093607 | 0.000000 | 0.000000
09-04-2025 17:42:05.000 | 13554500 | 135545000 | 135.545 | 44743486 | 15614388 | 50147236 | -99945564 | 50056999 | 27411469 | 10030605 | 0.000000 | 0.000000
09-04-2025 17:42:00.000 | 13582977 | 135829770 | 135.8298 | 46336606 | 15612091 | 50262393 | -99941864 | 50032425 | 27223334 | 996801941 | 0.000000 | 0.000000
09-04-2025 17:41:55.000 | 13613813 | 136138130 | 136.1381 | 44808525 | 15607673 | 50389419 | -99945877 | 50046268 | 27034777 | 990397156 | 0.000000 | 0.000000
09-04-2025 17:41:50.000 | 13524131 | 135241310 | 135.2413 | 45335757 | 15613399 | 50039141 | -99943863 | 50040066 | 26846295 | 984265076 | 0.000000 | 0.000000
09-04-2025 17:41:45.000 | 13583848 | 135838480 | 135.8385 | 45126553 | 15608264 | 50276040 | -99944862 | 50045998 | 26658012 | 977938965 | 0.000000 | 0.000000
09-04-2025 17:41:40.000 | 13548189 | 135481890 | 135.4819 | 44334175 | 15617879 | 50112900 | -99946503 | 50021351 | 26469670 | 971867065 | 0.000000 | 0.000000
09-04-2025 17:41:35.000 | 13608356 | 136083560 | 136.0836 | 48627422 | 15609110 | 50369814 | -99936218 | 50022110 | 26281309 | 965317627 | 0.000000 | 0.000000
09-04-2025 17:41:30.000 | 13628077 | 136280770 | 136.2808 | 46633730 | 15607462 | 50444380 | -99941505 | 50060001 | 26092414 | 958712341 | 0.000000 | 0.000000
09-04-2025 17:41:25.000 | 13590897 | 135908970 | 135.909 | 42684302 | 15610993 | 50290010 | -99950722 | 50073494 | 25903455 | 952487793 | 0.000000 | 0.000000
09-04-2025 17:41:20.000 | 13571911 | 135719110 | 135.7191 | 44660908 | 15612685 | 50218823 | -99945900 | 50058960 | 25714738 | 946502197 | 0.000000 | 0.000000
09-04-2025 17:41:15.000 | 13633241 | 136332410 | 136.3324 | 45003438 | 15608889 | 50456440 | -99945564 | 50058479 | 25525959 | 940303467 | 0.000000 | 0.000000
09-04-2025 17:41:10.000 | 13572955 | 135729550 | 135.7295 | 43465557 | 15614129 | 50215156 | -99948761 | 50060268 | 25337273 | 934194153 | 0.000000 | 0.000000
09-04-2025 17:41:05.000 | 13562952 | 135629520 | 135.6295 | 46555400 | 15615425 | 50178062 | -99941139 | 50024887 | 25148930 | 928078369 | 0.000000 | 0.000000
09-04-2025 17:41:00.000 | 13602363 | 136023630 | 136.0236 | 49684639 | 15612299 | 50337676 | -99933357 | 50015038 | 24960760 | 921479675 | 0.000000 | 0.000000
09-04-2025 17:40:55.000 | 13610861 | 136108610 | 136.1086 | 45342017 | 15606907 | 50382134 | -99944557 | 50064629 | 24771596 | 914662170 | 0.000000 | 0.000000
09-04-2025 17:40:50.000 | 13589930 | 135899300 | 135.8993 | 43566694 | 15612715 | 50282114 | -99948654 | 50076538 | 24582389 | 908523865 | 0.000000 | 0.000000
09-04-2025 17:40:45.000 | 13604073 | 136040730 | 136.0407 | 45279849 | 15610507 | 50343955 | -99944656 | 50056248 | 24393824 | 902408447 | 0.000000 | 0.000000
09-04-2025 17:40:40.000 | 13604373 | 136043730 | 136.0437 | 45754658 | 15610819 | 50344341 | -99943489 | 50065567 | 24204889 | 896148560 | 0.000000 | 0.000000
09-04-2025 17:40:35.000 | 13632178 | 136321780 | 136.3218 | 46543271 | 15611405 | 50446616 | -99941765 | 50075161 | 24016002 | 889769775 | 0.000000 | 0.000000
09-04-2025 17:40:30.000 | 13598670 | 135986700 | 135.9867 | 45795317 | 15613161 | 50316187 | -99943344 | 50074680 | 23827100 | 883345398 | 0.000000 | 0.000000
09-04-2025 17:40:25.000 | 13536842 | 135368420 | 135.3684 | 49032109 | 15612839 | 50093154 | -99934464 | 50051018 | 23638574 | 876822021 | 0.000000 | 0.000000
09-04-2025 17:40:20.000 | 13540006 | 135400060 | 135.4001 | 50532817 | 15612505 | 50108452 | -99930428 | 50033531 | 23450348 | 869979858 | 0.000000 | 0.000000
09-04-2025 17:40:15.000 | 13481220 | 134812200 | 134.8122 | 50726831 | 15613383 | 49887593 | -99929283 | 50014900 | 23262379 | 862899902 | 0.000000 | 0.000000
09-04-2025 17:40:10.000 | 13533261 | 135332610 | 135.3326 | 52555996 | 15612014 | 50086816 | -99924675 | 49995525 | 23074549 | 855707581 | 0.000000 | 0.000000
09-04-2025 17:40:05.000 | 13617531 | 136175310 | 136.1753 | 52146294 | 15609481 | 50407192 | -99926758 | 49994064 | 22886426 | 848472473 | 0.000000 | 0.000000
09-04-2025 17:40:00.000 | 13590597 | 135905970 | 135.906 | 50558242 | 15611188 | 50298833 | -99930878 | 50011349 | 22697584 | 841301636 | 0.000000 | 0.000000
09-04-2025 17:39:55.000 | 13611911 | 136119110 | 136.1191 | 50851387 | 15611754 | 50376152 | -99930290 | 50010437 | 22508674 | 834328796 | 0.000000 | 0.000000
09-04-2025 17:39:50.000 | 13639389 | 136393890 | 136.3939 | 48027495 | 15610547 | 50478682 | -99938065 | 50037693 | 22319422 | 827326965 | 0.000000 | 0.000000
09-04-2025 17:39:45.000 | 13594425 | 135944250 | 135.9443 | 47978364 | 15609163 | 50316367 | -99937782 | 50037224 | 22130328 | 820759094 | 0.000000 | 0.000000
09-04-2025 17:39:40.000 | 13608883 | 136088830 | 136.0888 | 47071592 | 15613657 | 50353145 | -99940231 | 50037548 | 21941188 | 814229736 | 0.000000 | 0.000000
09-04-2025 17:39:35.000 | 13593539 | 135935390 | 135.9354 | 48179185 | 15613743 | 50298608 | -99937248 | 50024601 | 21752447 | 807687561 | 0.000000 | 0.000000
09-04-2025 17:39:30.000 | 13617058 | 136170580 | 136.1706 | 47081934 | 15608051 | 50402246 | -99940277 | 50068096 | 21563133 | 800987610 | 0.000000 | 0.000000
09-04-2025 17:39:25.000 | 13626898 | 136268980 | 136.269 | 45156641 | 15607798 | 50437710 | -99945137 | 50105724 | 21373646 | 794613586 | 0.000000 | 0.000000
09-04-2025 17:39:20.000 | 13638758 | 136387580 | 136.3876 | 41981187 | 15611199 | 50466460 | -99952660 | 50112835 | 21184070 | 788532654 | 0.000000 | 0.000000
09-04-2025 17:39:15.000 | 13606564 | 136065640 | 136.0656 | 44799536 | 15615233 | 50337520 | -99945839 | 50085243 | 20994814 | 782624268 | 0.000000 | 0.000000
09-04-2025 17:39:10.000 | 13692766 | 136927660 | 136.9277 | 44145874 | 15607310 | 50680503 | -99948067 | 50118969 | 20805135 | 776322327 | 0.000000 | 0.000000
09-04-2025 17:39:05.000 | 13627397 | 136273970 | 136.274 | 41806182 | 15612716 | 50418960 | -99952972 | 50132931 | 20615523 | 770284851 | 0.000000 | 0.000000
09-04-2025 17:39:00.000 | 13611856 | 136118560 | 136.1186 | 44656094 | 15613552 | 50362686 | -99946228 | 50098770 | 20426248 | 764323303 | 0.000000 | 0.000000
09-04-2025 17:38:55.000 | 13594381 | 135943810 | 135.9438 | 46365894 | 15615337 | 50294243 | -99941887 | 50059437 | 20237193 | 758052490 | 0.000000 | 0.000000
09-04-2025 17:38:50.000 | 13631802 | 136318020 | 136.318 | 51416519 | 15613146 | 50445840 | -99928940 | 50040073 | 20048105 | 751316528 | 0.000000 | 0.000000
09-04-2025 17:38:45.000 | 13675488 | 136754880 | 136.7549 | 49027153 | 15605181 | 50629385 | -99935799 | 50067741 | 19858516 | 744247009 | 0.000000 | 0.000000
09-04-2025 17:38:40.000 | 13621597 | 136215970 | 136.216 | 45835698 | 15611067 | 50407090 | -99943436 | 50084915 | 19668744 | 737584412 | 0.000000 | 0.000000
09-04-2025 17:38:35.000 | 13604161 | 136041610 | 136.0416 | 48265103 | 15615292 | 50333228 | -99937126 | 50041115 | 19479680 | 731162720 | 0.000000 | 0.000000
09-04-2025 17:38:30.000 | 13672547 | 136725470 | 136.7255 | 48407686 | 15606771 | 50612988 | -99937386 | 50041870 | 19290645 | 724327209 | 0.000000 | 0.000000
09-04-2025 17:38:25.000 | 13605183 | 136051830 | 136.0518 | 45801860 | 15611945 | 50343696 | -99943382 | 50069782 | 19101023 | 717754395 | 0.000000 | 0.000000
09-04-2025 17:38:20.000 | 13587589 | 135875890 | 135.8759 | 45424917 | 15616080 | 50264834 | -99944168 | 50067665 | 18912070 | 711483215 | 0.000000 | 0.000000
09-04-2025 17:38:15.000 | 13696928 | 136969280 | 136.9693 | 44491069 | 15611053 | 50684111 | -99947289 | 50085041 | 18722855 | 705222168 | 0.000000 | 0.000000
09-04-2025 17:38:10.000 | 13675355 | 136753550 | 136.7535 | 43680884 | 15609274 | 50609199 | -99949028 | 50114254 | 18532816 | 699058411 | 0.000000 | 0.000000
09-04-2025 17:38:05.000 | 13642231 | 136422310 | 136.4223 | 43864063 | 15611285 | 50481372 | -99948349 | 50125443 | 18342867 | 693071350 | 0.000000 | 0.000000
09-04-2025 17:38:00.000 | 13592970 | 135929700 | 135.9297 | 41604077 | 15613623 | 50288262 | -99953194 | 50123283 | 18153453 | 687098511 | 0.000000 | 0.000000
09-04-2025 17:37:55.000 | 13618230 | 136182300 | 136.1823 | 44817798 | 15614393 | 50382939 | -99945892 | 50105267 | 17964182 | 681163757 | 0.000000 | 0.000000
09-04-2025 17:37:50.000 | 13723178 | 137231780 | 137.2318 | 44725552 | 15607823 | 50791875 | -99946930 | 50136219 | 17774309 | 674785645 | 0.000000 | 0.000000
09-04-2025 17:37:45.000 | 13649733 | 136497330 | 136.4973 | 43896099 | 15611877 | 50507974 | -99948334 | 50144447 | 17584344 | 668604675 | 0.000000 | 0.000000
09-04-2025 17:37:40.000 | 13593119 | 135931190 | 135.9312 | 45106519 | 15615840 | 50286689 | -99944992 | 50122772 | 17395037 | 662473755 | 0.000000 | 0.000000
09-04-2025 17:37:35.000 | 13640092 | 136400920 | 136.4009 | 46410405 | 15607638 | 50487456 | -99942162 | 50114006 | 17205674 | 656094055 | 0.000000 | 0.000000
09-04-2025 17:37:30.000 | 13549231 | 135492310 | 135.4923 | 45793682 | 15616183 | 50124116 | -99942932 | 50097717 | 17016443 | 649629456 | 0.000000 | 0.000000
09-04-2025 17:37:25.000 | 13576764 | 135767640 | 135.7676 | 55487090 | 15615021 | 50241782 | -99916588 | 49998611 | 16828574 | 642990417 | 0.000000 | 0.000000
09-04-2025 17:37:20.000 | 13606306 | 136063060 | 136.0631 | 56062676 | 15611638 | 50363315 | -99915222 | 49994640 | 16639855 | 635169861 | 0.000000 | 0.000000
09-04-2025 17:37:15.000 | 13578188 | 135781880 | 135.7819 | 53923438 | 15613818 | 50249199 | -99921234 | 49995804 | 16451078 | 627532043 | 0.000000 | 0.000000
09-04-2025 17:37:10.000 | 13616205 | 136162050 | 136.162 | 55018501 | 15608665 | 50407378 | -99918465 | 50002186 | 16262186 | 619932983 | 0.000000 | 0.000000
09-04-2025 17:37:05.000 | 13608764 | 136087640 | 136.0876 | 51049502 | 15610508 | 50368457 | -99929718 | 50032791 | 16072896 | 612514404 | 0.000000 | 0.000000
09-04-2025 17:37:00.000 | 13648281 | 136482810 | 136.4828 | 51398970 | 15608545 | 50522388 | -99929161 | 50030323 | 15883833 | 605471985 | 0.000000 | 0.000000
09-04-2025 17:36:55.000 | 13639692 | 136396920 | 136.3969 | 49868384 | 15610886 | 50480630 | -99933228 | 50031738 | 15694835 | 598462036 | 0.000000 | 0.000000
09-04-2025 17:36:50.000 | 13632536 | 136325360 | 136.3254 | 52022163 | 15610753 | 50457959 | -99927269 | 50022926 | 15505961 | 591479309 | 0.000000 | 0.000000
09-04-2025 17:36:45.000 | 13598003 | 135980030 | 135.98 | 52523906 | 15610167 | 50332729 | -99925484 | 50017445 | 15317216 | 584345337 | 0.000000 | 0.000000
09-04-2025 17:36:40.000 | 13660352 | 136603520 | 136.6035 | 50626099 | 15607438 | 50568452 | -99931396 | 50066479 | 15127947 | 577154846 | 0.000000 | 0.000000
09-04-2025 17:36:35.000 | 13596302 | 135963020 | 135.963 | 47272202 | 15610949 | 50316592 | -99939613 | 50095501 | 14938312 | 570322876 | 0.000000 | 0.000000
09-04-2025 17:36:30.000 | 13634066 | 136340660 | 136.3407 | 48154419 | 15607278 | 50468638 | -99937683 | 50105698 | 14749225 | 563727051 | 0.000000 | 0.000000
09-04-2025 17:36:25.000 | 13565964 | 135659640 | 135.6596 | 47031128 | 15611990 | 50200010 | -99939957 | 50093613 | 14560185 | 557179016 | 0.000000 | 0.000000
09-04-2025 17:36:20.000 | 13544356 | 135443560 | 135.4436 | 49087935 | 15613510 | 50118833 | -99934387 | 50069336 | 14371426 | 550484192 | 0.000000 | 0.000000
09-04-2025 17:36:15.000 | 13591288 | 135912880 | 135.9129 | 50591230 | 15614477 | 50290977 | -99930794 | 50055290 | 14183282 | 543629333 | 0.000000 | 0.000000
09-04-2025 17:36:10.000 | 13618420 | 136184200 | 136.1842 | 54050811 | 15609063 | 50412949 | -99921333 | 50056835 | 13994726 | 536314209 | 0.000000 | 0.000000
09-04-2025 17:36:05.000 | 13617905 | 136179050 | 136.179 | 52479458 | 15609910 | 50406445 | -99925827 | 50089569 | 13805632 | 528984131 | 0.000000 | 0.000000
09-04-2025 17:36:00.000 | 13579159 | 135791590 | 135.7916 | 49339565 | 15611257 | 50254448 | -99934052 | 50078163 | 13616647 | 521885559 | 0.000000 | 0.000000
09-04-2025 17:35:55.000 | 13531047 | 135310470 | 135.3105 | 50938110 | 15619597 | 50051729 | -99929214 | 50024323 | 13428296 | 515023315 | 0.000000 | 0.000000
09-04-2025 17:35:50.000 | 13637895 | 136378950 | 136.379 | 56727031 | 15608461 | 50491479 | -99913605 | 50011646 | 13239830 | 507508118 | 0.000000 | 0.000000
09-04-2025 17:35:45.000 | 13641523 | 136415230 | 136.4152 | 53380278 | 15610622 | 50492676 | -99923531 | 50046963 | 13050599 | 499852417 | 0.000000 | 0.000000
09-04-2025 17:35:40.000 | 13618108 | 136181080 | 136.1811 | 51767090 | 15609636 | 50406411 | -99927826 | 50063606 | 12861464 | 492421631 | 0.000000 | 0.000000
09-04-2025 17:35:35.000 | 13624772 | 136247720 | 136.2477 | 50511343 | 15611581 | 50423794 | -99931351 | 50071522 | 12672222 | 485278015 | 0.000000 | 0.000000
09-04-2025 17:35:30.000 | 13583727 | 135837270 | 135.8373 | 52167627 | 15617549 | 50254766 | -99926338 | 50048702 | 12483508 | 478162109 | 0.000000 | 0.000000
09-04-2025 17:35:25.000 | 13640994 | 136409940 | 136.4099 | 54305508 | 15609684 | 50495850 | -99920853 | 50051514 | 12294602 | 470599518 | 0.000000 | 0.000000
09-04-2025 17:35:20.000 | 13661772 | 136617720 | 136.6177 | 51855430 | 15607790 | 50574663 | -99928040 | 50079315 | 12105027 | 463118286 | 0.000000 | 0.000000
09-04-2025 17:35:15.000 | 13590300 | 135903000 | 135.903 | 51552471 | 15615193 | 50287114 | -99928131 | 50062752 | 11915866 | 456027679 | 0.000000 | 0.000000
09-04-2025 17:35:10.000 | 13632031 | 136320310 | 136.3203 | 54751318 | 15610085 | 50460913 | -99919441 | 50041775 | 11726850 | 448739288 | 0.000000 | 0.000000
09-04-2025 17:35:05.000 | 13586375 | 135863750 | 135.8638 | 52268623 | 15609075 | 50293110 | -99926079 | 50053879 | 11537641 | 441254150 | 0.000000 | 0.000000
09-04-2025 17:35:00.000 | 13566205 | 135662050 | 135.662 | 52978184 | 15614796 | 50201074 | -99923836 | 50044453 | 11348673 | 433955933 | 0.000000 | 0.000000
09-04-2025 17:34:55.000 | 13587780 | 135877800 | 135.8778 | 55737764 | 15610731 | 50297114 | -99915970 | 50031815 | 11160306 | 426414886 | 0.000000 | 0.000000
09-04-2025 17:34:50.000 | 13636963 | 136369630 | 136.3696 | 54435669 | 15609250 | 50482002 | -99920425 | 50073349 | 10971219 | 418754028 | 0.000000 | 0.000000
09-04-2025 17:34:45.000 | 13610213 | 136102130 | 136.1021 | 53315356 | 15612719 | 50370073 | -99923363 | 50059792 | 10782140 | 411365753 | 0.000000 | 0.000000
09-04-2025 17:34:40.000 | 13604602 | 136046020 | 136.046 | 55122808 | 15615079 | 50344854 | -99918015 | 50037563 | 10593355 | 403852966 | 0.000000 | 0.000000
09-04-2025 17:34:35.000 | 13607656 | 136076560 | 136.0766 | 56890815 | 15611997 | 50368022 | -99912720 | 50029476 | 10404591 | 396055298 | 0.000000 | 0.000000
09-04-2025 17:34:30.000 | 13628717 | 136287170 | 136.2872 | 55485083 | 15611831 | 50444165 | -99917229 | 50041683 | 10215359 | 388168365 | 0.000000 | 0.000000
09-04-2025 17:34:25.000 | 13611647 | 136116470 | 136.1165 | 56980229 | 15610328 | 50389683 | -99912498 | 50030582 | 10026344 | 380410187 | 0.000000 | 0.000000
09-04-2025 17:34:20.000 | 13614656 | 136146560 | 136.1466 | 54015537 | 15609058 | 50398706 | -99921387 | 50043194 | 98371641 | 372696411 | 0.000000 | 0.000000
09-04-2025 17:34:15.000 | 13586341 | 135863410 | 135.8634 | 55141489 | 15614094 | 50280000 | -99917740 | 50037601 | 96481680 | 365175629 | 0.000000 | 0.000000
09-04-2025 17:34:10.000 | 13648342 | 136483420 | 136.4834 | 55567285 | 15610147 | 50523091 | -99917221 | 50031967 | 94591699 | 357588501 | 0.000000 | 0.000000
09-04-2025 17:34:05.000 | 13638195 | 136381950 | 136.3819 | 53378794 | 15608281 | 50488569 | -99923492 | 50074848 | 92694512 | 350005798 | 0.000000 | 0.000000
09-04-2025 17:34:00.000 | 13626111 | 136261110 | 136.2611 | 51424185 | 15614477 | 50420996 | -99928864 | 50096245 | 90800957 | 342718872 | 0.000000 | 0.000000
09-04-2025 17:33:55.000 | 13687172 | 136871720 | 136.8717 | 53318301 | 15610438 | 50662485 | -99924210 | 50078117 | 88910439 | 335447052 | 0.000000 | 0.000000
09-04-2025 17:33:50.000 | 13662745 | 136627450 | 136.6275 | 55853047 | 15610984 | 50573755 | -99916550 | 50077019 | 87015947 | 327905060 | 0.000000 | 0.000000
09-04-2025 17:33:45.000 | 13626745 | 136267450 | 136.2674 | 54256787 | 15609920 | 50441543 | -99920830 | 50076221 | 85121611 | 320298248 | 0.000000 | 0.000000
09-04-2025 17:33:40.000 | 13616236 | 136162360 | 136.1624 | 53513877 | 15608695 | 50406099 | -99922859 | 50085922 | 83230625 | 312791351 | 0.000000 | 0.000000
09-04-2025 17:33:35.000 | 13578927 | 135789270 | 135.7893 | 53009219 | 15614727 | 50248970 | -99923889 | 50068684 | 81342007 | 305472809 | 0.000000 | 0.000000
09-04-2025 17:33:30.000 | 13618423 | 136184230 | 136.1842 | 57540850 | 15613594 | 50404727 | -99910858 | 50025608 | 79456060 | 297933716 | 0.000000 | 0.000000
09-04-2025 17:33:25.000 | 13688319 | 136883190 | 136.8832 | 55785571 | 15604614 | 50689810 | -99917061 | 50072746 | 77561816 | 289911224 | 0.000000 | 0.000000
09-04-2025 17:33:20.000 | 13620759 | 136207590 | 136.2076 | 51899473 | 15611129 | 50412813 | -99927483 | 50097790 | 75663706 | 282327759 | 0.000000 | 0.000000
09-04-2025 17:33:15.000 | 13589219 | 135892190 | 135.8922 | 51934790 | 15614506 | 50284927 | -99927048 | 50082577 | 73771924 | 275098663 | 0.000000 | 0.000000
09-04-2025 17:33:10.000 | 13578170 | 135781700 | 135.7817 | 52111240 | 15611357 | 50254722 | -99926437 | 50072449 | 71883701 | 267756073 | 0.000000 | 0.000000
09-04-2025 17:33:05.000 | 13636508 | 136365080 | 136.3651 | 51996797 | 15606632 | 50485552 | -99927383 | 50098122 | 69992114 | 260514282 | 0.000000 | 0.000000
09-04-2025 17:33:00.000 | 13639030 | 136390300 | 136.3903 | 51080161 | 15611532 | 50478188 | -99929939 | 50087090 | 68105400 | 253600281 | 0.000000 | 0.000000
09-04-2025 17:32:55.000 | 13628445 | 136284450 | 136.2844 | 50245747 | 15609832 | 50443691 | -99932106 | 50091221 | 66215474 | 246584106 | 0.000000 | 0.000000
09-04-2025 17:32:50.000 | 13645536 | 136455360 | 136.4554 | 49452529 | 15610411 | 50502861 | -99934395 | 50130257 | 64319331 | 239689285 | 0.000000 | 0.000000
09-04-2025 17:32:45.000 | 13629858 | 136298580 | 136.2986 | 49510942 | 15609634 | 50447412 | -99934090 | 50130646 | 62428530 | 232886032 | 0.000000 | 0.000000
09-04-2025 17:32:40.000 | 13597756 | 135977560 | 135.9776 | 48420547 | 15610971 | 50323838 | -99936661 | 50124641 | 60534971 | 226134033 | 0.000000 | 0.000000
09-04-2025 17:32:35.000 | 13629936 | 136299360 | 136.2994 | 50230757 | 15611858 | 50442334 | -99932159 | 50113335 | 58641401 | 219354355 | 0.000000 | 0.000000
09-04-2025 17:32:30.000 | 13656238 | 136562380 | 136.5624 | 49961631 | 15609868 | 50544722 | -99933144 | 50118931 | 56746821 | 212358994 | 0.000000 | 0.000000
09-04-2025 17:32:25.000 | 13641502 | 136415020 | 136.415 | 50315996 | 15609467 | 50492192 | -99932045 | 50123383 | 54852295 | 205458237 | 0.000000 | 0.000000
09-04-2025 17:32:20.000 | 13675780 | 136757800 | 136.7578 | 48454272 | 15606570 | 50625659 | -99937294 | 50144520 | 52956514 | 198520981 | 0.000000 | 0.000000
09-04-2025 17:32:15.000 | 13605670 | 136056700 | 136.0567 | 48186870 | 15611724 | 50349771 | -99937340 | 50141449 | 51062188 | 191814575 | 0.000000 | 0.000000
09-04-2025 17:32:10.000 | 13541545 | 135415450 | 135.4154 | 51789980 | 15615834 | 50104790 | -99926949 | 50099049 | 49174351 | 185064072 | 0.000000 | 0.000000
09-04-2025 17:32:05.000 | 13580569 | 135805690 | 135.8057 | 53906641 | 15613964 | 50257788 | -99921310 | 50091972 | 47287690 | 177819183 | 0.000000 | 0.000000
09-04-2025 17:32:00.000 | 13645480 | 136454800 | 136.4548 | 51354688 | 15606667 | 50518159 | -99929253 | 50113552 | 45400620 | 170387085 | 0.000000 | 0.000000
09-04-2025 17:31:55.000 | 13581591 | 135815910 | 135.8159 | 54168633 | 15614354 | 50261138 | -99920555 | 50092766 | 43511333 | 163289047 | 0.000000 | 0.000000
09-04-2025 17:31:50.000 | 13594100 | 135941000 | 135.941 | 52624019 | 15612392 | 50310962 | -99925156 | 50100994 | 41619883 | 155884933 | 0.000000 | 0.000000
09-04-2025 17:31:45.000 | 13600272 | 136002720 | 136.0027 | 52218413 | 15610010 | 50340664 | -99926369 | 50107574 | 39728777 | 148526001 | 0.000000 | 0.000000
09-04-2025 17:31:40.000 | 13572189 | 135721890 | 135.7219 | 51695425 | 15616053 | 50215894 | -99927536 | 50092602 | 37838320 | 141405762 | 0.000000 | 0.000000
09-04-2025 17:31:35.000 | 13678970 | 136789700 | 136.7897 | 53647798 | 15608405 | 50638857 | -99923180 | 50105278 | 35947454 | 134141312 | 0.000000 | 0.000000
09-04-2025 17:31:30.000 | 13705333 | 137053330 | 137.0533 | 49938276 | 15606688 | 50736895 | -99933685 | 50161823 | 34048384 | 126796967 | 0.000000 | 0.000000
09-04-2025 17:31:25.000 | 13625086 | 136250860 | 136.2509 | 47566050 | 15614295 | 50412749 | -99939117 | 50161633 | 32151150 | 120088684 | 0.000000 | 0.000000
09-04-2025 17:31:20.000 | 13620709 | 136207090 | 136.2071 | 49895703 | 15612630 | 50404351 | -99932968 | 50147720 | 30260852 | 113322105 | 0.000000 | 0.000000
09-04-2025 17:31:15.000 | 13642417 | 136424170 | 136.4242 | 48693574 | 15609589 | 50493672 | -99936363 | 50150562 | 28365610 | 106446274 | 0.000000 | 0.000000
09-04-2025 17:31:10.000 | 13587828 | 135878280 | 135.8783 | 48702129 | 15613492 | 50279185 | -99935829 | 50133556 | 26470588 | 99709831 | 0.000000 | 0.000000
09-04-2025 17:31:05.000 | 13601552 | 136015520 | 136.0155 | 51291626 | 15612118 | 50337437 | -99928970 | 50106709 | 24581658 | 92790062 | 0.000000 | 0.000000
09-04-2025 17:31:00.000 | 13637334 | 136373340 | 136.3733 | 51937471 | 15609439 | 50479390 | -99927559 | 50120087 | 22688943 | 85634026 | 0.000000 | 0.000000
09-04-2025 17:30:55.000 | 13674708 | 136747080 | 136.7471 | 50328467 | 15605714 | 50627207 | -99932343 | 50144321 | 20793679 | 78563995 | 0.000000 | 0.000000
09-04-2025 17:30:50.000 | 13588416 | 135884160 | 135.8842 | 49691758 | 15614248 | 50279409 | -99933205 | 50153114 | 18901329 | 71711739 | 0.000000 | 0.000000
09-04-2025 17:30:45.000 | 13588628 | 135886280 | 135.8863 | 52054585 | 15611771 | 50291782 | -99926704 | 50103363 | 17018848 | 64802223 | 0.000000 | 0.000000
09-04-2025 17:30:40.000 | 13590294 | 135902940 | 135.9029 | 53223105 | 15614049 | 50292290 | -99923401 | 50083347 | 15134731 | 57534950 | 0.000000 | 0.000000
09-04-2025 17:30:35.000 | 13596278 | 135962780 | 135.9628 | 54652231 | 15610026 | 50329082 | -99919312 | 50083771 | 13246783 | 49969574 | 0.000000 | 0.000000
09-04-2025 17:30:30.000 | 13598206 | 135982060 | 135.9821 | 51801631 | 15614104 | 50318740 | -99927521 | 50107090 | 11356674 | 42531052 | 0.000000 | 0.000000
09-04-2025 17:30:25.000 | 13640733 | 136407330 | 136.4073 | 52808057 | 15612931 | 50481509 | -99925148 | 50111359 | 946615479 | 35209885 | 0.000000 | 0.000000
09-04-2025 17:30:20.000 | 13652198 | 136521980 | 136.522 | 52441816 | 15607588 | 50540542 | -99926308 | 50132893 | 757155334 | 27840208 | 0.000000 | 0.000000
09-04-2025 17:30:15.000 | 13610273 | 136102730 | 136.1027 | 47888276 | 15613183 | 50361191 | -99938156 | 50160694 | 567260620 | 20741718 | 0.000000 | 0.000000
09-04-2025 17:30:10.000 | 13658052 | 136580520 | 136.5805 | 51368545 | 15610569 | 50550908 | -99929344 | 50125656 | 378524414 | 14069225 | 0.000000 | 0.000000
09-04-2025 17:30:05.000 | 13624995 | 136249950 | 136.25 | 50705405 | 15610232 | 50429238 | -99930824 | 50130478 | 189243774 | 7011151 | 0.000000 | 0.000000
09-04-2025 17:30:00.000 | 13615897 | 136158970 | 136.159 | 50284321 | 15611759 | 50390425 | -99931877 | 50138741 | 33941191 | 10173383 | 0.000000 | 0.000000
09-04-2025 17:29:55.000 | 13601361 | 136013610 | 136.0136 | 48917993 | 15612724 | 50331567 | -99935387 | 50142757 | 33751973 | 10103264 | 0.000000 | 0.000000
09-04-2025 17:29:50.000 | 13603094 | 136030940 | 136.0309 | 47339644 | 15613940 | 50331816 | -99939499 | 50130478 | 33562938 | 10035217 | 0.000000 | 0.000000
09-04-2025 17:29:45.000 | 13691706 | 136917060 | 136.9171 | 45760679 | 15604946 | 50686230 | -99944191 | 50158726 | 33373621 | 996998596 | 0.000000 | 0.000000
09-04-2025 17:29:40.000 | 13624464 | 136244640 | 136.2446 | 42786963 | 15608020 | 50425034 | -99950722 | 50200039 | 33183676 | 990803528 | 0.000000 | 0.000000
09-04-2025 17:29:35.000 | 13616419 | 136164190 | 136.1642 | 44599956 | 15613228 | 50380078 | -99946404 | 50181538 | 32994281 | 984921265 | 0.000000 | 0.000000
09-04-2025 17:29:30.000 | 13590369 | 135903690 | 135.9037 | 44202578 | 15615362 | 50277305 | -99947151 | 50161640 | 32805324 | 978562073 | 0.000000 | 0.000000
09-04-2025 17:29:25.000 | 13649480 | 136494800 | 136.4948 | 48320566 | 15612125 | 50510435 | -99937401 | 50143696 | 32616193 | 972153015 | 0.000000 | 0.000000
09-04-2025 17:29:20.000 | 13630963 | 136309630 | 136.3096 | 48911870 | 15612989 | 50440518 | -99935684 | 50140053 | 32426893 | 965451416 | 0.000000 | 0.000000
09-04-2025 17:29:15.000 | 13671772 | 136717720 | 136.7177 | 48613911 | 15609251 | 50604287 | -99936844 | 50147434 | 32237629 | 958613098 | 0.000000 | 0.000000
09-04-2025 17:29:10.000 | 13603600 | 136036000 | 136.036 | 48106792 | 15611717 | 50342383 | -99937531 | 50153290 | 32048047 | 951913025 | 0.000000 | 0.000000
09-04-2025 17:29:05.000 | 13649938 | 136499380 | 136.4994 | 47129922 | 15607503 | 50526211 | -99940445 | 50161572 | 31858652 | 945270813 | 0.000000 | 0.000000
09-04-2025 17:29:00.000 | 13535295 | 135352950 | 135.3529 | 46626172 | 15614609 | 50077822 | -99940720 | 50172993 | 31669109 | 938702515 | 0.000000 | 0.000000
09-04-2025 17:28:55.000 | 13599208 | 135992080 | 135.9921 | 47369639 | 15614429 | 50316357 | -99939392 | 50141087 | 31480234 | 932111267 | 0.000000 | 0.000000
09-04-2025 17:28:50.000 | 13654719 | 136547190 | 136.5472 | 43525322 | 15600558 | 50561138 | -99949234 | 50125324 | 31291160 | 925610107 | 0.000000 | 0.000000
09-04-2025 17:28:45.000 | 13628141 | 136281410 | 136.2814 | 31577793 | 15613510 | 50408833 | -99973167 | 50110836 | 31101896 | 920783020 | 0.000000 | 0.000000
09-04-2025 17:28:40.000 | 13639348 | 136393480 | 136.3935 | 33133630 | 15610661 | 50460640 | -99970505 | 50120121 | 30912426 | 916252136 | 0.000000 | 0.000000
09-04-2025 17:28:35.000 | 13664330 | 136643300 | 136.6433 | 29354924 | 15607891 | 50558989 | -99976929 | 50158772 | 30722686 | 911736389 | 0.000000 | 0.000000
09-04-2025 17:28:30.000 | 13641188 | 136411880 | 136.4119 | 28562822 | 15612073 | 50458667 | -99978088 | 50159859 | 30533010 | 907745728 | 0.000000 | 0.000000
09-04-2025 17:28:25.000 | 13641398 | 136413980 | 136.414 | 29502256 | 15612669 | 50458945 | -99976624 | 50149994 | 30343826 | 903739685 | 0.000000 | 0.000000
09-04-2025 17:28:20.000 | 13571853 | 135718530 | 135.7185 | 30159678 | 15616222 | 50191567 | -99975319 | 50122513 | 30154963 | 899536133 | 0.000000 | 0.000000
09-04-2025 17:28:15.000 | 13589716 | 135897160 | 135.8972 | 33126326 | 15613968 | 50267617 | -99970306 | 50123363 | 29966027 | 895020813 | 0.000000 | 0.000000
09-04-2025 17:28:10.000 | 13636508 | 136365080 | 136.3651 | 33440381 | 15609060 | 50456895 | -99969948 | 50127930 | 29776955 | 890381165 | 0.000000 | 0.000000
09-04-2025 17:28:05.000 | 13639514 | 136395140 | 136.3951 | 30758137 | 15611349 | 50456929 | -99974586 | 50156570 | 29587352 | 885914307 | 0.000000 | 0.000000
09-04-2025 17:28:00.000 | 13651536 | 136515360 | 136.5154 | 30236802 | 15610069 | 50507461 | -99975479 | 50156139 | 29397762 | 881607605 | 0.000000 | 0.000000
09-04-2025 17:27:55.000 | 13633741 | 136337410 | 136.3374 | 28316001 | 15609990 | 50438574 | -99978439 | 50142361 | 29208547 | 877500977 | 0.000000 | 0.000000
09-04-2025 17:27:50.000 | 13626852 | 136268520 | 136.2685 | 30600168 | 15613122 | 50405015 | -99974800 | 50129837 | 29019479 | 873436157 | 0.000000 | 0.000000
09-04-2025 17:27:45.000 | 13597628 | 135976280 | 135.9763 | 27294421 | 15616357 | 50284219 | -99979858 | 50145813 | 28829949 | 869234314 | 0.000000 | 0.000000
09-04-2025 17:27:40.000 | 13691341 | 136913410 | 136.9134 | 29232002 | 15608003 | 50659331 | -99977219 | 50155853 | 28640707 | 865215881 | 0.000000 | 0.000000
09-04-2025 17:27:35.000 | 13630033 | 136300330 | 136.3003 | 27711011 | 15613198 | 50415547 | -99979340 | 50172535 | 28451068 | 861161987 | 0.000000 | 0.000000
09-04-2025 17:27:30.000 | 13609122 | 136091220 | 136.0912 | 27512217 | 15613993 | 50334419 | -99979568 | 50148632 | 28261990 | 857425720 | 0.000000 | 0.000000
09-04-2025 17:27:25.000 | 13581741 | 135817410 | 135.8174 | 32510945 | 15614025 | 50236304 | -99971359 | 50124130 | 28073334 | 853330750 | 0.000000 | 0.000000
09-04-2025 17:27:20.000 | 13579270 | 135792700 | 135.7927 | 31158069 | 15610984 | 50236616 | -99973686 | 50152050 | 27884092 | 848708679 | 0.000000 | 0.000000
09-04-2025 17:27:15.000 | 13552755 | 135527550 | 135.5275 | 30797913 | 15612667 | 50134790 | -99974190 | 50140900 | 27695277 | 844355896 | 0.000000 | 0.000000
09-04-2025 17:27:10.000 | 13545848 | 135458480 | 135.4585 | 31879097 | 15615586 | 50098511 | -99972321 | 50122540 | 27506893 | 840013611 | 0.000000 | 0.000000
09-04-2025 17:27:05.000 | 13592913 | 135929130 | 135.9291 | 31333828 | 15611731 | 50285498 | -99973442 | 50118168 | 27318326 | 835504028 | 0.000000 | 0.000000
09-04-2025 17:27:00.000 | 13584811 | 135848110 | 135.8481 | 34020361 | 15613447 | 50250708 | -99968658 | 50067822 | 27130035 | 831095947 | 0.000000 | 0.000000
09-04-2025 17:26:55.000 | 13566559 | 135665590 | 135.6656 | 37565068 | 15612046 | 50191792 | -99961685 | 50058628 | 26941652 | 826198547 | 0.000000 | 0.000000
09-04-2025 17:26:50.000 | 13605467 | 136054670 | 136.0547 | 34901938 | 15608814 | 50343423 | -99967110 | 50084023 | 26752914 | 821124390 | 0.000000 | 0.000000
09-04-2025 17:26:45.000 | 13497858 | 134978580 | 134.9786 | 35090369 | 15611494 | 49937798 | -99966225 | 50063000 | 26564748 | 816300293 | 0.000000 | 0.000000
09-04-2025 17:26:40.000 | 13491022 | 134910220 | 134.9102 | 36291243 | 15613423 | 49907124 | -99963837 | 50035175 | 26376965 | 811422729 | 0.000000 | 0.000000
09-04-2025 17:26:35.000 | 13500786 | 135007860 | 135.0079 | 39199819 | 15613132 | 49948018 | -99957878 | 50000664 | 26189525 | 806355774 | 0.000000 | 0.000000
09-04-2025 17:26:30.000 | 13565520 | 135655200 | 135.6552 | 39736296 | 15611874 | 50191416 | -99957123 | 49973564 | 26002068 | 801002197 | 0.000000 | 0.000000
09-04-2025 17:26:25.000 | 13594020 | 135940200 | 135.9402 | 40088477 | 15607749 | 50310566 | -99956543 | 50000061 | 25813768 | 795453674 | 0.000000 | 0.000000
09-04-2025 17:26:20.000 | 13570566 | 135705660 | 135.7057 | 39376836 | 15613182 | 50204683 | -99957932 | 50004864 | 25625393 | 790048523 | 0.000000 | 0.000000
09-04-2025 17:26:15.000 | 13631934 | 136319340 | 136.3193 | 37860291 | 15602475 | 50465791 | -99961456 | 50047714 | 25436650 | 784605835 | 0.000000 | 0.000000
09-04-2025 17:26:10.000 | 13529358 | 135293580 | 135.2936 | 36087651 | 15614513 | 50044717 | -99964447 | 50051994 | 25247908 | 779576233 | 0.000000 | 0.000000
09-04-2025 17:26:05.000 | 13579981 | 135799810 | 135.7998 | 39231675 | 15610229 | 50249238 | -99958298 | 50038162 | 25059676 | 774353394 | 0.000000 | 0.000000
09-04-2025 17:26:00.000 | 13530433 | 135304330 | 135.3043 | 37713679 | 15613332 | 50055410 | -99961174 | 50052887 | 24870967 | 768903076 | 0.000000 | 0.000000
09-04-2025 17:25:55.000 | 13537291 | 135372910 | 135.3729 | 37893040 | 15614977 | 50074023 | -99960846 | 50042160 | 24682832 | 763623596 | 0.000000 | 0.000000
09-04-2025 17:25:50.000 | 13587191 | 135871910 | 135.8719 | 42254551 | 15613414 | 50269629 | -99951675 | 50008522 | 24495016 | 758195923 | 0.000000 | 0.000000
09-04-2025 17:25:45.000 | 13573411 | 135734110 | 135.7341 | 42035234 | 15611479 | 50224160 | -99952080 | 50015549 | 24306525 | 752262939 | 0.000000 | 0.000000
09-04-2025 17:25:40.000 | 13613689 | 136136890 | 136.1369 | 43549199 | 15609276 | 50381621 | -99948875 | 50021759 | 24117697 | 746419922 | 0.000000 | 0.000000
09-04-2025 17:25:35.000 | 13620588 | 136205880 | 136.2059 | 42788726 | 15609902 | 50403560 | -99950691 | 50038284 | 23928656 | 740566956 | 0.000000 | 0.000000
09-04-2025 17:25:30.000 | 13575377 | 135753770 | 135.7538 | 39684485 | 15614633 | 50219458 | -99957298 | 50060162 | 23739430 | 734799561 | 0.000000 | 0.000000
09-04-2025 17:25:25.000 | 13641438 | 136414380 | 136.4144 | 42079429 | 15610889 | 50478516 | -99952461 | 50068558 | 23550289 | 729161621 | 0.000000 | 0.000000
09-04-2025 17:25:20.000 | 13641830 | 136418300 | 136.4183 | 41286030 | 15608691 | 50484688 | -99954231 | 50074738 | 23361148 | 723383728 | 0.000000 | 0.000000
09-04-2025 17:25:15.000 | 13608639 | 136086390 | 136.0864 | 39674959 | 15614176 | 50342886 | -99957527 | 50086956 | 23171770 | 717761841 | 0.000000 | 0.000000
09-04-2025 17:25:10.000 | 13536364 | 135363640 | 135.3636 | 42319873 | 15613635 | 50079697 | -99951164 | 50062176 | 22983064 | 712002136 | 0.000000 | 0.000000
09-04-2025 17:25:05.000 | 13591027 | 135910270 | 135.9103 | 44296494 | 15606823 | 50307471 | -99946930 | 50045948 | 22794828 | 705903259 | 0.000000 | 0.000000
09-04-2025 17:25:00.000 | 13551728 | 135517280 | 135.5173 | 43518115 | 15610573 | 50148604 | -99948479 | 50044109 | 22606047 | 699845581 | 0.000000 | 0.000000
09-04-2025 17:24:55.000 | 13533214 | 135332140 | 135.3321 | 45317051 | 15613918 | 50071357 | -99943985 | 50017845 | 22417846 | 693714172 | 0.000000 | 0.000000
09-04-2025 17:24:50.000 | 13541494 | 135414940 | 135.4149 | 45456211 | 15615994 | 50094648 | -99943710 | 50010571 | 22229668 | 687415955 | 0.000000 | 0.000000
09-04-2025 17:24:45.000 | 13618670 | 136186700 | 136.1867 | 47644673 | 15608911 | 50406353 | -99938858 | 50018719 | 22041400 | 681006897 | 0.000000 | 0.000000
09-04-2025 17:24:40.000 | 13612472 | 136124720 | 136.1247 | 44797920 | 15608963 | 50380078 | -99945892 | 50053078 | 21852408 | 674707458 | 0.000000 | 0.000000
09-04-2025 17:24:35.000 | 13578895 | 135788950 | 135.7889 | 41469507 | 15611647 | 50243481 | -99953400 | 50076752 | 21663244 | 668682373 | 0.000000 | 0.000000
09-04-2025 17:24:30.000 | 13561448 | 135614480 | 135.6145 | 42421167 | 15612575 | 50175972 | -99951111 | 50044777 | 21474961 | 662943909 | 0.000000 | 0.000000
09-04-2025 17:24:25.000 | 13536591 | 135365910 | 135.3659 | 46182822 | 15609586 | 50100391 | -99941849 | 50029861 | 21286793 | 656873535 | 0.000000 | 0.000000
09-04-2025 17:24:20.000 | 13589094 | 135890940 | 135.8909 | 40223242 | 15609499 | 50286025 | -99956223 | 50084255 | 21097846 | 650637085 | 0.000000 | 0.000000
09-04-2025 17:24:15.000 | 13564506 | 135645060 | 135.6451 | 37988066 | 15616885 | 50171465 | -99960808 | 50079094 | 20909004 | 645239014 | 0.000000 | 0.000000
09-04-2025 17:24:10.000 | 13608994 | 136089940 | 136.0899 | 42284951 | 15609256 | 50362778 | -99951767 | 50047291 | 20720650 | 639507751 | 0.000000 | 0.000000
09-04-2025 17:24:05.000 | 13670122 | 136701220 | 136.7012 | 45259131 | 15602828 | 50613027 | -99945236 | 50061024 | 20531699 | 633571350 | 0.000000 | 0.000000
09-04-2025 17:24:00.000 | 13615178 | 136151780 | 136.1518 | 41522227 | 15609323 | 50384585 | -99953529 | 50093094 | 20342572 | 627646484 | 0.000000 | 0.000000
09-04-2025 17:23:55.000 | 13534514 | 135345140 | 135.3451 | 42284575 | 15614703 | 50069370 | -99951233 | 50068645 | 20154078 | 621801819 | 0.000000 | 0.000000
09-04-2025 17:23:50.000 | 13577417 | 135774170 | 135.7742 | 44816519 | 15614422 | 50232148 | -99945564 | 50056522 | 19965402 | 615753357 | 0.000000 | 0.000000
09-04-2025 17:23:45.000 | 13586798 | 135867980 | 135.868 | 45151807 | 15611217 | 50277515 | -99944824 | 50047642 | 19776816 | 609458374 | 0.000000 | 0.000000
09-04-2025 17:23:40.000 | 13567209 | 135672090 | 135.6721 | 40759370 | 15605929 | 50217119 | -99954903 | 50052517 | 19587838 | 603308838 | 0.000000 | 0.000000
09-04-2025 17:23:35.000 | 13608364 | 136083640 | 136.0836 | 32898557 | 15608469 | 50354917 | -99970787 | 50051422 | 19398980 | 598394653 | 0.000000 | 0.000000
09-04-2025 17:23:30.000 | 13601289 | 136012890 | 136.0129 | 31379802 | 15607791 | 50329043 | -99973396 | 50073814 | 19209850 | 593824463 | 0.000000 | 0.000000
09-04-2025 17:23:25.000 | 13583622 | 135836220 | 135.8362 | 33816602 | 15615027 | 50242109 | -99969025 | 50045471 | 19021195 | 589524170 | 0.000000 | 0.000000
09-04-2025 17:23:20.000 | 13594591 | 135945910 | 135.9459 | 36984070 | 15609061 | 50304175 | -99963013 | 50035316 | 18832684 | 584409241 | 0.000000 | 0.000000
09-04-2025 17:23:15.000 | 13543875 | 135438750 | 135.4387 | 38495771 | 15610591 | 50114248 | -99959633 | 50014698 | 18644307 | 579244812 | 0.000000 | 0.000000
09-04-2025 17:23:10.000 | 13500678 | 135006780 | 135.0068 | 34322354 | 15616284 | 49932324 | -99967697 | 49994831 | 18456363 | 573973145 | 0.000000 | 0.000000
09-04-2025 17:23:05.000 | 13563675 | 135636750 | 135.6368 | 36776814 | 15608752 | 50190825 | -99963264 | 49977184 | 18268840 | 569081238 | 0.000000 | 0.000000
09-04-2025 17:23:00.000 | 13578456 | 135784560 | 135.7846 | 36987791 | 15608881 | 50244810 | -99962921 | 50004776 | 18080256 | 564031067 | 0.000000 | 0.000000
09-04-2025 17:22:55.000 | 13597980 | 135979800 | 135.9798 | 32780339 | 15610269 | 50308745 | -99970955 | 50034733 | 17891676 | 559155396 | 0.000000 | 0.000000
09-04-2025 17:22:50.000 | 13575789 | 135757890 | 135.7579 | 31439048 | 15613448 | 50215894 | -99973198 | 50037296 | 17703092 | 554819153 | 0.000000 | 0.000000
09-04-2025 17:22:45.000 | 13658934 | 136589340 | 136.5893 | 32459434 | 15603237 | 50556260 | -99971771 | 50050495 | 17514186 | 550364929 | 0.000000 | 0.000000
09-04-2025 17:22:40.000 | 13635670 | 136356700 | 136.3567 | 26877747 | 15607861 | 50451470 | -99980576 | 50084106 | 17324910 | 546288025 | 0.000000 | 0.000000
09-04-2025 17:22:35.000 | 13559727 | 135597270 | 135.5973 | 28206943 | 15612686 | 50155513 | -99978371 | 50075012 | 17135969 | 542514221 | 0.000000 | 0.000000
09-04-2025 17:22:30.000 | 13628536 | 136285360 | 136.2854 | 25164187 | 15610479 | 50414995 | -99982956 | 50092937 | 16946951 | 538608826 | 0.000000 | 0.000000
09-04-2025 17:22:25.000 | 13614538 | 136145380 | 136.1454 | 27521868 | 15612426 | 50358848 | -99979576 | 50064163 | 16758145 | 535167786 | 0.000000 | 0.000000
09-04-2025 17:22:20.000 | 13618630 | 136186300 | 136.1863 | 33167632 | 15611593 | 50380962 | -99970352 | 50086124 | 16568893 | 531117310 | 0.000000 | 0.000000
09-04-2025 17:22:15.000 | 13656116 | 136561160 | 136.5612 | 32306909 | 15611024 | 50520410 | -99972031 | 50115997 | 16379305 | 526618713 | 0.000000 | 0.000000
09-04-2025 17:22:10.000 | 13607736 | 136077360 | 136.0774 | 32266531 | 15610307 | 50344077 | -99971901 | 50132549 | 16189604 | 522057312 | 0.000000 | 0.000000
09-04-2025 17:22:05.000 | 13606866 | 136068660 | 136.0687 | 36072683 | 15617168 | 50322129 | -99964874 | 50085384 | 16000550 | 517474243 | 0.000000 | 0.000000
09-04-2025 17:22:00.000 | 13646273 | 136462730 | 136.4627 | 38636450 | 15608625 | 50497900 | -99959946 | 50083534 | 15811477 | 512126282 | 0.000000 | 0.000000
09-04-2025 17:21:55.000 | 13583331 | 135833310 | 135.8333 | 37478391 | 15613537 | 50248296 | -99961960 | 50078506 | 15622120 | 506863129 | 0.000000 | 0.000000
09-04-2025 17:21:50.000 | 13608245 | 136082450 | 136.0824 | 39216763 | 15607899 | 50360181 | -99958504 | 50063812 | 15433389 | 501490234 | 0.000000 | 0.000000
09-04-2025 17:21:45.000 | 13595767 | 135957670 | 135.9577 | 36882612 | 15610763 | 50302529 | -99963226 | 50064098 | 15244737 | 496200806 | 0.000000 | 0.000000
09-04-2025 17:21:40.000 | 13574241 | 135742410 | 135.7424 | 36702007 | 15610500 | 50223896 | -99963470 | 50061279 | 15055896 | 491084076 | 0.000000 | 0.000000
09-04-2025 17:21:35.000 | 13605511 | 136055110 | 136.0551 | 34657424 | 15610369 | 50338423 | -99967575 | 50084564 | 14867050 | 486076965 | 0.000000 | 0.000000
09-04-2025 17:21:30.000 | 13600358 | 136003580 | 136.0036 | 35538792 | 15611992 | 50314185 | -99965874 | 50074406 | 14678158 | 481213531 | 0.000000 | 0.000000
09-04-2025 17:21:25.000 | 13665342 | 136653420 | 136.6534 | 35156748 | 15608623 | 50565386 | -99966919 | 50093365 | 14488786 | 476297241 | 0.000000 | 0.000000
09-04-2025 17:21:20.000 | 13671603 | 136716030 | 136.716 | 32136104 | 15607850 | 50587817 | -99972389 | 50134998 | 14298917 | 471536407 | 0.000000 | 0.000000
09-04-2025 17:21:15.000 | 13611866 | 136118660 | 136.1187 | 31294575 | 15613525 | 50348149 | -99973579 | 50125530 | 14109406 | 467178131 | 0.000000 | 0.000000
09-04-2025 17:21:10.000 | 13620425 | 136204250 | 136.2043 | 31493755 | 15615112 | 50375137 | -99973282 | 50110771 | 13920105 | 462774719 | 0.000000 | 0.000000
09-04-2025 17:21:05.000 | 13655361 | 136553610 | 136.5536 | 34508691 | 15614343 | 50509033 | -99968086 | 50106274 | 13730850 | 458255402 | 0.000000 | 0.000000
09-04-2025 17:21:00.000 | 13668556 | 136685560 | 136.6856 | 32303787 | 15606085 | 50582510 | -99972084 | 50140884 | 13541009 | 453509735 | 0.000000 | 0.000000
09-04-2025 17:20:55.000 | 13597775 | 135977750 | 135.9777 | 32060789 | 15612232 | 50300879 | -99972214 | 50135075 | 13351559 | 449127136 | 0.000000 | 0.000000
09-04-2025 17:20:50.000 | 13613363 | 136133630 | 136.1336 | 34026753 | 15613481 | 50355977 | -99968781 | 50114254 | 13162384 | 444620361 | 0.000000 | 0.000000
09-04-2025 17:20:45.000 | 13591738 | 135917380 | 135.9174 | 36349458 | 15613664 | 50278828 | -99964256 | 50094418 | 12973408 | 439795135 | 0.000000 | 0.000000
09-04-2025 17:20:40.000 | 13610281 | 136102810 | 136.1028 | 37638389 | 15610935 | 50356787 | -99961784 | 50088802 | 12784349 | 434544861 | 0.000000 | 0.000000
09-04-2025 17:20:35.000 | 13543333 | 135433330 | 135.4333 | 38103853 | 15618392 | 50086411 | -99960442 | 50056114 | 12595582 | 429291168 | 0.000000 | 0.000000
09-04-2025 17:20:30.000 | 13570919 | 135709190 | 135.7092 | 45142080 | 15612594 | 50214536 | -99944725 | 49999371 | 12407450 | 423521393 | 0.000000 | 0.000000
09-04-2025 17:20:25.000 | 13562550 | 135625500 | 135.6255 | 44764248 | 15609995 | 50191157 | -99945572 | 49987988 | 12218958 | 417281586 | 0.000000 | 0.000000
09-04-2025 17:20:20.000 | 13531836 | 135318360 | 135.3184 | 44707651 | 15613364 | 50067070 | -99945465 | 49969257 | 12030808 | 411053589 | 0.000000 | 0.000000
09-04-2025 17:20:15.000 | 13527850 | 135278500 | 135.2785 | 45073379 | 15616008 | 50043853 | -99944542 | 49958683 | 11842896 | 404749298 | 0.000000 | 0.000000
09-04-2025 17:20:10.000 | 13590228 | 135902280 | 135.9023 | 45724375 | 15608707 | 50298784 | -99943451 | 49970562 | 11654561 | 398329346 | 0.000000 | 0.000000
09-04-2025 17:20:05.000 | 13584494 | 135844940 | 135.8449 | 42886411 | 15610592 | 50268384 | -99950203 | 49996506 | 11466024 | 392137299 | 0.000000 | 0.000000
09-04-2025 17:20:00.000 | 13605578 | 136055780 | 136.0558 | 40951252 | 15610744 | 50343374 | -99954735 | 50037991 | 11276696 | 386161987 | 0.000000 | 0.000000
09-04-2025 17:19:55.000 | 13597950 | 135979500 | 135.9795 | 39988059 | 15610553 | 50314868 | -99956787 | 50048195 | 11087495 | 380551727 | 0.000000 | 0.000000
09-04-2025 17:19:50.000 | 13610409 | 136104090 | 136.1041 | 38911794 | 15609449 | 50363931 | -99959160 | 50053360 | 10898644 | 375043335 | 0.000000 | 0.000000
09-04-2025 17:19:45.000 | 13571550 | 135715500 | 135.7155 | 38836880 | 15613994 | 50205054 | -99959084 | 50046993 | 10709508 | 369608459 | 0.000000 | 0.000000
09-04-2025 17:19:40.000 | 13600561 | 136005610 | 136.0056 | 41253652 | 15612250 | 50321479 | -99954033 | 50031330 | 10521137 | 364062836 | 0.000000 | 0.000000
09-04-2025 17:19:35.000 | 13576850 | 135768500 | 135.7685 | 39722229 | 15613527 | 50227002 | -99957230 | 50022625 | 10332388 | 358308044 | 0.000000 | 0.000000
09-04-2025 17:19:30.000 | 13541058 | 135410580 | 135.4106 | 42344536 | 15615221 | 50092051 | -99951141 | 49975990 | 10143992 | 352614777 | 0.000000 | 0.000000
09-04-2025 17:19:25.000 | 13582528 | 135825280 | 135.8253 | 45895146 | 15606801 | 50277275 | -99942963 | 49968296 | 99556641 | 346450867 | 0.000000 | 0.000000
09-04-2025 17:19:20.000 | 13522722 | 135227220 | 135.2272 | 43618364 | 15613625 | 50031582 | -99948021 | 49974609 | 97670283 | 340262360 | 0.000000 | 0.000000
09-04-2025 17:19:15.000 | 13520164 | 135201640 | 135.2016 | 46351895 | 15613196 | 50025801 | -99941284 | 49948837 | 95789375 | 333967743 | 0.000000 | 0.000000
09-04-2025 17:19:10.000 | 13529511 | 135295110 | 135.2951 | 45314756 | 15609261 | 50071924 | -99943954 | 49949322 | 93906807 | 327511932 | 0.000000 | 0.000000
09-04-2025 17:19:05.000 | 13507694 | 135076940 | 135.0769 | 43147148 | 15616864 | 49964414 | -99949020 | 49934750 | 92027969 | 321345062 | 0.000000 | 0.000000
09-04-2025 17:19:00.000 | 13506364 | 135063640 | 135.0636 | 46759302 | 15614394 | 49972119 | -99940125 | 49910175 | 90151035 | 315085571 | 0.000000 | 0.000000
09-04-2025 17:18:55.000 | 13563197 | 135631970 | 135.632 | 43949243 | 15608289 | 50198765 | -99947540 | 49946697 | 88271953 | 308614929 | 0.000000 | 0.000000
09-04-2025 17:18:50.000 | 13519241 | 135192410 | 135.1924 | 42524185 | 15613663 | 50017212 | -99950569 | 49937397 | 86395117 | 302722290 | 0.000000 | 0.000000
09-04-2025 17:18:45.000 | 13550617 | 135506170 | 135.5062 | 42940693 | 15614749 | 50129409 | -99949829 | 49933784 | 84515898 | 296798157 | 0.000000 | 0.000000
09-04-2025 17:18:40.000 | 13584438 | 135844380 | 135.8444 | 42508916 | 15605845 | 50283389 | -99951073 | 49980808 | 82633105 | 290642334 | 0.000000 | 0.000000
09-04-2025 17:18:35.000 | 13521348 | 135213480 | 135.2135 | 39232495 | 15609257 | 50035615 | -99957932 | 50027756 | 80746958 | 284883240 | 0.000000 | 0.000000
09-04-2025 17:18:30.000 | 13471728 | 134717280 | 134.7173 | 39286709 | 15614617 | 49834561 | -99957504 | 49996155 | 78870347 | 279556396 | 0.000000 | 0.000000
09-04-2025 17:18:25.000 | 13504775 | 135047750 | 135.0478 | 42216660 | 15616604 | 49953521 | -99951172 | 49961201 | 76998433 | 273932922 | 0.000000 | 0.000000
09-04-2025 17:18:20.000 | 13551692 | 135516920 | 135.5169 | 46000015 | 15606707 | 50162983 | -99942436 | 49963188 | 75119521 | 267759827 | 0.000000 | 0.000000
09-04-2025 17:18:15.000 | 13519464 | 135194640 | 135.1946 | 43545942 | 15614064 | 50017437 | -99948166 | 49981667 | 73236187 | 261739838 | 0.000000 | 0.000000
09-04-2025 17:18:10.000 | 13566359 | 135663590 | 135.6636 | 41878701 | 15609833 | 50202280 | -99952385 | 50002998 | 71352808 | 255655167 | 0.000000 | 0.000000
09-04-2025 17:18:05.000 | 13526634 | 135266340 | 135.2663 | 41565742 | 15613948 | 50043350 | -99952820 | 50016850 | 69467461 | 249772018 | 0.000000 | 0.000000
09-04-2025 17:18:00.000 | 13553314 | 135533140 | 135.5331 | 41048027 | 15612893 | 50143501 | -99954170 | 50035454 | 67582822 | 243913574 | 0.000000 | 0.000000
09-04-2025 17:17:55.000 | 13528500 | 135285000 | 135.285 | 44885054 | 15613818 | 50053701 | -99945007 | 49993397 | 65709248 | 238007263 | 0.000000 | 0.000000
09-04-2025 17:17:50.000 | 13555217 | 135552170 | 135.5522 | 44758354 | 15611633 | 50158760 | -99945534 | 50021339 | 63829136 | 231640015 | 0.000000 | 0.000000
09-04-2025 17:17:45.000 | 13587439 | 135874390 | 135.8744 | 43959082 | 15607324 | 50290742 | -99947708 | 50022144 | 61948237 | 225562149 | 0.000000 | 0.000000
09-04-2025 17:17:40.000 | 13522472 | 135224720 | 135.2247 | 41905625 | 15610633 | 50038022 | -99952019 | 50009457 | 60067217 | 219752380 | 0.000000 | 0.000000
09-04-2025 17:17:35.000 | 13562255 | 135622550 | 135.6225 | 39404346 | 15613539 | 50172759 | -99957817 | 50031719 | 58180938 | 213935928 | 0.000000 | 0.000000
09-04-2025 17:17:30.000 | 13606480 | 136064800 | 136.0648 | 40474084 | 15609404 | 50351655 | -99955788 | 50023556 | 56299150 | 208339783 | 0.000000 | 0.000000
09-04-2025 17:17:25.000 | 13624281 | 136242810 | 136.2428 | 42232617 | 15610758 | 50414316 | -99951988 | 50027473 | 54411348 | 202837845 | 0.000000 | 0.000000
09-04-2025 17:17:20.000 | 13605178 | 136051780 | 136.0518 | 40559482 | 15610271 | 50342769 | -99955589 | 50047020 | 52520483 | 197092758 | 0.000000 | 0.000000
09-04-2025 17:17:15.000 | 13585591 | 135855910 | 135.8559 | 44419033 | 15609732 | 50277314 | -99946594 | 50020382 | 50635938 | 191389984 | 0.000000 | 0.000000
09-04-2025 17:17:10.000 | 13575213 | 135752130 | 135.7521 | 45636216 | 15611395 | 50234556 | -99943542 | 50003765 | 48750337 | 185133133 | 0.000000 | 0.000000
09-04-2025 17:17:05.000 | 13538769 | 135387690 | 135.3877 | 46914116 | 15613888 | 50093071 | -99940018 | 49977310 | 46867656 | 178780624 | 0.000000 | 0.000000
09-04-2025 17:17:00.000 | 13533336 | 135333360 | 135.3334 | 51273286 | 15614635 | 50077192 | -99928307 | 49935612 | 44990190 | 172037811 | 0.000000 | 0.000000
09-04-2025 17:16:55.000 | 13554523 | 135545230 | 135.5452 | 52433428 | 15608438 | 50176948 | -99925262 | 49945339 | 43106899 | 164743927 | 0.000000 | 0.000000
09-04-2025 17:16:50.000 | 13547867 | 135478670 | 135.4787 | 49744824 | 15611943 | 50137417 | -99932655 | 49965111 | 41222329 | 157655807 | 0.000000 | 0.000000
09-04-2025 17:16:45.000 | 13487755 | 134877550 | 134.8776 | 52813662 | 15612332 | 49918691 | -99923424 | 49922123 | 39344634 | 150632965 | 0.000000 | 0.000000
09-04-2025 17:16:40.000 | 13510580 | 135105800 | 135.1058 | 52724800 | 15610935 | 50007334 | -99923943 | 49907631 | 37467495 | 143281494 | 0.000000 | 0.000000
09-04-2025 17:16:35.000 | 13524852 | 135248520 | 135.2485 | 51913604 | 15611082 | 50057944 | -99926414 | 49905445 | 35588459 | 135955124 | 0.000000 | 0.000000
09-04-2025 17:16:30.000 | 13543327 | 135433270 | 135.4333 | 52900967 | 15610066 | 50131533 | -99923798 | 49903351 | 33710627 | 128712357 | 0.000000 | 0.000000
09-04-2025 17:16:25.000 | 13542434 | 135424340 | 135.4243 | 52654482 | 15611519 | 50123008 | -99924500 | 49895752 | 31833162 | 121540520 | 0.000000 | 0.000000
09-04-2025 17:16:20.000 | 13542430 | 135424300 | 135.4243 | 53277666 | 15608871 | 50132280 | -99922707 | 49889610 | 29955496 | 114287315 | 0.000000 | 0.000000
09-04-2025 17:16:15.000 | 13491586 | 134915860 | 134.9159 | 50194932 | 15611977 | 49929839 | -99930862 | 49920692 | 28072522 | 107038361 | 0.000000 | 0.000000
09-04-2025 17:16:10.000 | 13472539 | 134725390 | 134.7254 | 52277710 | 15615014 | 49853003 | -99924797 | 49900692 | 26196326 | 99937782 | 0.000000 | 0.000000
09-04-2025 17:16:05.000 | 13546920 | 135469200 | 135.4692 | 51753755 | 15611480 | 50139326 | -99927109 | 49902809 | 24323188 | 92602837 | 0.000000 | 0.000000
09-04-2025 17:16:00.000 | 13558814 | 135588140 | 135.5881 | 51147856 | 15607553 | 50195269 | -99928925 | 49914726 | 22443274 | 85401192 | 0.000000 | 0.000000
09-04-2025 17:15:55.000 | 13542155 | 135421550 | 135.4215 | 50993096 | 15607849 | 50132051 | -99929176 | 49908936 | 20566379 | 78488503 | 0.000000 | 0.000000
09-04-2025 17:15:50.000 | 13457963 | 134579630 | 134.5796 | 50403711 | 15615568 | 49794585 | -99929939 | 49880436 | 18693335 | 71464653 | 0.000000 | 0.000000
09-04-2025 17:15:45.000 | 13471498 | 134714980 | 134.715 | 53252500 | 15612372 | 49858652 | -99921959 | 49869541 | 16822933 | 64200211 | 0.000000 | 0.000000
09-04-2025 17:15:40.000 | 13513767 | 135137670 | 135.1377 | 49496401 | 15608535 | 50021245 | -99932991 | 49881058 | 14950557 | 56948410 | 0.000000 | 0.000000
09-04-2025 17:15:35.000 | 13413967 | 134139670 | 134.1397 | 51021162 | 15614561 | 49636646 | -99927742 | 49859112 | 13079386 | 49987568 | 0.000000 | 0.000000
09-04-2025 17:15:30.000 | 13416277 | 134162770 | 134.1628 | 54255444 | 15611096 | 49659961 | -99918327 | 49820328 | 11214419 | 42748138 | 0.000000 | 0.000000
09-04-2025 17:15:25.000 | 13450514 | 134505140 | 134.5051 | 53077593 | 15611491 | 49783872 | -99922234 | 49815914 | 934881958 | 35452240 | 0.000000 | 0.000000
09-04-2025 17:15:20.000 | 13473820 | 134738200 | 134.7382 | 50970332 | 15611631 | 49866768 | -99928528 | 49815922 | 747917664 | 28182123 | 0.000000 | 0.000000
09-04-2025 17:15:15.000 | 13482164 | 134821640 | 134.8216 | 51754136 | 15611661 | 49898799 | -99926399 | 49805416 | 560944397 | 21042566 | 0.000000 | 0.000000
09-04-2025 17:15:10.000 | 13429080 | 134290800 | 134.2908 | 51237500 | 15616611 | 49685864 | -99927292 | 49790863 | 374167114 | 13945617 | 0.000000 | 0.000000
09-04-2025 17:15:05.000 | 13445925 | 134459250 | 134.4592 | 50771982 | 15611467 | 49764653 | -99928787 | 49771797 | 187634705 | 6761120 | 0.000000 | 0.000000
09-04-2025 17:15:00.000 | 13560558 | 135605580 | 135.6056 | 45223530 | 15607557 | 50192939 | -99944435 | 49836456 | 33797266 | 10542809 | 0.000000 | 0.000000
09-04-2025 17:14:55.000 | 13493200 | 134932000 | 134.932 | 44497617 | 15614609 | 49919829 | -99945671 | 49829453 | 33609879 | 10481924 | 0.000000 | 0.000000
09-04-2025 17:14:50.000 | 13468602 | 134686020 | 134.686 | 45694272 | 15611604 | 49839917 | -99942497 | 49820709 | 33422582 | 10419473 | 0.000000 | 0.000000
09-04-2025 17:14:45.000 | 13469413 | 134694130 | 134.6941 | 44584595 | 15613889 | 49834541 | -99945259 | 49826721 | 33235070 | 10356353 | 0.000000 | 0.000000
09-04-2025 17:14:40.000 | 13470191 | 134701910 | 134.7019 | 46347686 | 15611435 | 49848013 | -99940857 | 49796116 | 33048441 | 10294136 | 0.000000 | 0.000000
09-04-2025 17:14:35.000 | 13456183 | 134561830 | 134.5618 | 48224209 | 15610754 | 49799849 | -99935844 | 49786777 | 32861645 | 10228420 | 0.000000 | 0.000000
09-04-2025 17:14:30.000 | 13406816 | 134068160 | 134.0682 | 49430444 | 15614385 | 49609092 | -99932098 | 49768669 | 32674742 | 10160925 | 0.000000 | 0.000000
09-04-2025 17:14:25.000 | 13468258 | 134682580 | 134.6826 | 50780820 | 15609380 | 49852871 | -99928993 | 49765099 | 32488193 | 10091066 | 0.000000 | 0.000000
09-04-2025 17:14:20.000 | 13437673 | 134376730 | 134.3767 | 49009478 | 15612633 | 49726577 | -99933556 | 49770908 | 32301109 | 10021266 | 0.000000 | 0.000000
09-04-2025 17:14:15.000 | 13458834 | 134588340 | 134.5883 | 49182715 | 15609936 | 49814624 | -99933296 | 49778397 | 32114273 | 995330872 | 0.000000 | 0.000000
09-04-2025 17:14:10.000 | 13483978 | 134839780 | 134.8398 | 49829189 | 15609517 | 49908643 | -99931786 | 49772301 | 31927326 | 988496277 | 0.000000 | 0.000000
09-04-2025 17:14:05.000 | 13431691 | 134316910 | 134.3169 | 49914585 | 15612635 | 49706074 | -99931023 | 49759796 | 31740355 | 981694336 | 0.000000 | 0.000000
09-04-2025 17:14:00.000 | 13424528 | 134245280 | 134.2453 | 49924644 | 15615672 | 49669502 | -99930923 | 49760422 | 31553396 | 974749451 | 0.000000 | 0.000000
09-04-2025 17:13:55.000 | 13443823 | 134438230 | 134.4382 | 49618726 | 15613811 | 49746851 | -99931961 | 49755627 | 31366629 | 967699341 | 0.000000 | 0.000000
09-04-2025 17:13:50.000 | 13433783 | 134337830 | 134.3378 | 51983999 | 15613111 | 49715039 | -99925217 | 49751045 | 31179709 | 960600647 | 0.000000 | 0.000000
09-04-2025 17:13:45.000 | 13496370 | 134963700 | 134.9637 | 48152056 | 15610332 | 49949976 | -99936417 | 49789715 | 30992313 | 953513367 | 0.000000 | 0.000000
09-04-2025 17:13:40.000 | 13503913 | 135039130 | 135.0391 | 47507119 | 15611620 | 49973394 | -99938171 | 49790966 | 30805029 | 946866028 | 0.000000 | 0.000000
09-04-2025 17:13:35.000 | 13535686 | 135356860 | 135.3569 | 46624590 | 15608501 | 50098770 | -99940727 | 49822662 | 30617221 | 940245728 | 0.000000 | 0.000000
09-04-2025 17:13:30.000 | 13435798 | 134357980 | 134.358 | 45737695 | 15616321 | 49704321 | -99942108 | 49813389 | 30429682 | 933824341 | 0.000000 | 0.000000
09-04-2025 17:13:25.000 | 13480434 | 134804340 | 134.8043 | 49003247 | 15611731 | 49888184 | -99933990 | 49805946 | 30242568 | 927257568 | 0.000000 | 0.000000
09-04-2025 17:13:20.000 | 13481844 | 134818440 | 134.8184 | 45808232 | 15613885 | 49881860 | -99942329 | 49833744 | 30054789 | 920535034 | 0.000000 | 0.000000
09-04-2025 17:13:15.000 | 13476869 | 134768690 | 134.7687 | 46997012 | 15613519 | 49866641 | -99939255 | 49822010 | 29867326 | 914165955 | 0.000000 | 0.000000
09-04-2025 17:13:10.000 | 13518738 | 135187380 | 135.1874 | 48338604 | 15608898 | 50038120 | -99936134 | 49812851 | 29680119 | 907504517 | 0.000000 | 0.000000
09-04-2025 17:13:05.000 | 13545886 | 135458860 | 135.4589 | 45646704 | 15606418 | 50142979 | -99943268 | 49837837 | 29492182 | 900894897 | 0.000000 | 0.000000
09-04-2025 17:13:00.000 | 13458906 | 134589060 | 134.5891 | 46352407 | 15614939 | 49794863 | -99940750 | 49818188 | 29304832 | 894577087 | 0.000000 | 0.000000
09-04-2025 17:12:55.000 | 13474292 | 134742920 | 134.7429 | 47713726 | 15612930 | 49859932 | -99937363 | 49810844 | 29117881 | 887985474 | 0.000000 | 0.000000
09-04-2025 17:12:50.000 | 13495986 | 134959860 | 134.9599 | 47579180 | 15609865 | 49949756 | -99937912 | 49797409 | 28930580 | 881339233 | 0.000000 | 0.000000
09-04-2025 17:12:45.000 | 13518792 | 135187920 | 135.1879 | 48792227 | 15609184 | 50038848 | -99934929 | 49818405 | 28743082 | 874717712 | 0.000000 | 0.000000
09-04-2025 17:12:40.000 | 13460155 | 134601550 | 134.6016 | 49590879 | 15615341 | 49802158 | -99932198 | 49816338 | 28555545 | 868021423 | 0.000000 | 0.000000
09-04-2025 17:12:35.000 | 13540950 | 135409500 | 135.4095 | 51208643 | 15607549 | 50127451 | -99928566 | 49818001 | 28368297 | 861068848 | 0.000000 | 0.000000
09-04-2025 17:12:30.000 | 13500139 | 135001390 | 135.0014 | 47095596 | 15609496 | 49965493 | -99939209 | 49842918 | 28180553 | 854201843 | 0.000000 | 0.000000
09-04-2025 17:12:25.000 | 13484477 | 134844770 | 134.8448 | 45359531 | 15612859 | 49894136 | -99943474 | 49857094 | 27992891 | 847729919 | 0.000000 | 0.000000
09-04-2025 17:12:20.000 | 13475309 | 134753090 | 134.7531 | 44897905 | 15612261 | 49862295 | -99944542 | 49844048 | 27805719 | 841423096 | 0.000000 | 0.000000
09-04-2025 17:12:15.000 | 13485961 | 134859610 | 134.8596 | 46574243 | 15609721 | 49911274 | -99940422 | 49852135 | 27618258 | 834981750 | 0.000000 | 0.000000
09-04-2025 17:12:10.000 | 13433036 | 134330360 | 134.3304 | 46031079 | 15616125 | 49696855 | -99941338 | 49852871 | 27431031 | 828558044 | 0.000000 | 0.000000
09-04-2025 17:12:05.000 | 13528542 | 135285420 | 135.2854 | 47582485 | 15607664 | 50077451 | -99938202 | 49845062 | 27244023 | 822027649 | 0.000000 | 0.000000
09-04-2025 17:12:00.000 | 13546127 | 135461270 | 135.4613 | 45966616 | 15608107 | 50139150 | -99942474 | 49873798 | 27056133 | 815552124 | 0.000000 | 0.000000
09-04-2025 17:11:55.000 | 13519500 | 135195000 | 135.195 | 43942954 | 15612682 | 50022446 | -99947220 | 49881027 | 26868406 | 809319702 | 0.000000 | 0.000000
09-04-2025 17:11:50.000 | 13537198 | 135371980 | 135.372 | 40235742 | 15609126 | 50095342 | -99955856 | 49872425 | 26680734 | 803474854 | 0.000000 | 0.000000
09-04-2025 17:11:45.000 | 13509527 | 135095270 | 135.0953 | 40681589 | 15611468 | 49986001 | -99954689 | 49872257 | 26492883 | 797849487 | 0.000000 | 0.000000
09-04-2025 17:11:40.000 | 13496791 | 134967910 | 134.9679 | 40644568 | 15611492 | 49939150 | -99954689 | 49880695 | 26305486 | 792215515 | 0.000000 | 0.000000
09-04-2025 17:11:35.000 | 13493925 | 134939250 | 134.9392 | 39476694 | 15609197 | 49934180 | -99957237 | 49898441 | 26117965 | 786580688 | 0.000000 | 0.000000
09-04-2025 17:11:30.000 | 13512595 | 135125950 | 135.1259 | 36804966 | 15610801 | 49995039 | -99962929 | 49914066 | 25930225 | 781238464 | 0.000000 | 0.000000
09-04-2025 17:11:25.000 | 13528111 | 135281110 | 135.2811 | 38803059 | 15614836 | 50042168 | -99958885 | 49883617 | 25743021 | 776091980 | 0.000000 | 0.000000
09-04-2025 17:11:20.000 | 13530467 | 135304670 | 135.3047 | 39153779 | 15610701 | 50063740 | -99958160 | 49885220 | 25555287 | 770652222 | 0.000000 | 0.000000
09-04-2025 17:11:15.000 | 13507094 | 135070940 | 135.0709 | 37318208 | 15610096 | 49978325 | -99961853 | 49913147 | 25367195 | 765312073 | 0.000000 | 0.000000
09-04-2025 17:11:10.000 | 13546420 | 135464200 | 135.4642 | 35082507 | 15607338 | 50129858 | -99966484 | 49933826 | 25179236 | 760267639 | 0.000000 | 0.000000
09-04-2025 17:11:05.000 | 13514672 | 135146720 | 135.1467 | 34196665 | 15613099 | 49992935 | -99968002 | 49927082 | 24991172 | 755555237 | 0.000000 | 0.000000
09-04-2025 17:11:00.000 | 13434438 | 134344380 | 134.3444 | 38879722 | 15616587 | 49690522 | -99958153 | 49873291 | 24804166 | 750561279 | 0.000000 | 0.000000
09-04-2025 17:10:55.000 | 13485173 | 134851730 | 134.8517 | 40042664 | 15611895 | 49894351 | -99955940 | 49857071 | 24617027 | 745011169 | 0.000000 | 0.000000
09-04-2025 17:10:50.000 | 13525056 | 135250560 | 135.2506 | 39731196 | 15610076 | 50046577 | -99956879 | 49885452 | 24429184 | 739427124 | 0.000000 | 0.000000
09-04-2025 17:10:45.000 | 13501652 | 135016520 | 135.0165 | 37653960 | 15611845 | 49952285 | -99961136 | 49892262 | 24241537 | 734042480 | 0.000000 | 0.000000
09-04-2025 17:10:40.000 | 13446741 | 134467410 | 134.4674 | 39852319 | 15615443 | 49740718 | -99956108 | 49884163 | 24053992 | 728693848 | 0.000000 | 0.000000
09-04-2025 17:10:35.000 | 13547852 | 135478520 | 135.4785 | 38377224 | 15610320 | 50128623 | -99959900 | 49901459 | 23866691 | 723209167 | 0.000000 | 0.000000
09-04-2025 17:10:30.000 | 13493906 | 134939060 | 134.9391 | 36556279 | 15609069 | 49931362 | -99963326 | 49913406 | 23678877 | 717937744 | 0.000000 | 0.000000
09-04-2025 17:10:25.000 | 13494081 | 134940810 | 134.9408 | 35941206 | 15610434 | 49926763 | -99964546 | 49923862 | 23490986 | 712940491 | 0.000000 | 0.000000
09-04-2025 17:10:20.000 | 13480895 | 134808950 | 134.809 | 36064700 | 15614506 | 49866157 | -99964233 | 49896027 | 23303619 | 708013367 | 0.000000 | 0.000000
09-04-2025 17:10:15.000 | 13505884 | 135058840 | 135.0588 | 37604988 | 15611125 | 49970366 | -99961258 | 49872345 | 23116582 | 702913086 | 0.000000 | 0.000000
09-04-2025 17:10:10.000 | 13471983 | 134719830 | 134.7198 | 37445034 | 15608063 | 49854844 | -99961395 | 49896320 | 22929146 | 697607178 | 0.000000 | 0.000000
09-04-2025 17:10:05.000 | 13465677 | 134656770 | 134.6568 | 36638450 | 15608903 | 49828184 | -99963005 | 49901485 | 22742008 | 692473999 | 0.000000 | 0.000000
09-04-2025 17:10:00.000 | 13429539 | 134295390 | 134.2954 | 37250513 | 15614307 | 49677979 | -99961555 | 49883080 | 22555117 | 687366577 | 0.000000 | 0.000000
09-04-2025 17:09:55.000 | 13461784 | 134617840 | 134.6178 | 41692222 | 15613544 | 49804082 | -99952072 | 49846867 | 22368576 | 681948486 | 0.000000 | 0.000000
09-04-2025 17:09:50.000 | 13498948 | 134989480 | 134.9895 | 39680613 | 15610578 | 49948818 | -99956825 | 49867199 | 22181781 | 676258301 | 0.000000 | 0.000000
09-04-2025 17:09:45.000 | 13467559 | 134675590 | 134.6756 | 37988560 | 15607964 | 49839121 | -99960243 | 49889565 | 21994518 | 670774658 | 0.000000 | 0.000000
09-04-2025 17:09:40.000 | 13444406 | 134444060 | 134.4441 | 37318516 | 15612575 | 49738086 | -99961494 | 49906738 | 21807297 | 665624390 | 0.000000 | 0.000000
09-04-2025 17:09:35.000 | 13466614 | 134666140 | 134.6661 | 36799609 | 15611389 | 49823389 | -99962685 | 49912453 | 21620551 | 660456116 | 0.000000 | 0.000000
09-04-2025 17:09:30.000 | 13470463 | 134704630 | 134.7046 | 35634841 | 15607573 | 49848887 | -99965027 | 49922630 | 21433600 | 655353699 | 0.000000 | 0.000000
09-04-2025 17:09:25.000 | 13491289 | 134912890 | 134.9129 | 36395171 | 15611260 | 49915669 | -99963631 | 49935532 | 21246539 | 650568604 | 0.000000 | 0.000000
09-04-2025 17:09:20.000 | 13462794 | 134627940 | 134.6279 | 36161287 | 15608501 | 49817456 | -99963943 | 49955132 | 21059707 | 645395508 | 0.000000 | 0.000000
09-04-2025 17:09:15.000 | 13401678 | 134016780 | 134.0168 | 35358567 | 15616377 | 49566343 | -99965210 | 49970284 | 20872779 | 640423767 | 0.000000 | 0.000000
09-04-2025 17:09:10.000 | 13458284 | 134582840 | 134.5828 | 37802229 | 15612185 | 49790894 | -99960579 | 49937290 | 20686668 | 635296387 | 0.000000 | 0.000000
09-04-2025 17:09:05.000 | 13429108 | 134291080 | 134.2911 | 38425027 | 15612906 | 49681523 | -99959091 | 49939472 | 20499693 | 630019775 | 0.000000 | 0.000000
09-04-2025 17:09:00.000 | 13471911 | 134719110 | 134.7191 | 39087410 | 15612446 | 49842124 | -99957939 | 49939106 | 20312787 | 624705994 | 0.000000 | 0.000000
09-04-2025 17:08:55.000 | 13479563 | 134795630 | 134.7956 | 41001963 | 15613056 | 49871191 | -99953773 | 49922905 | 20125877 | 619250244 | 0.000000 | 0.000000
09-04-2025 17:08:50.000 | 13464644 | 134646440 | 134.6464 | 40533604 | 15611461 | 49819629 | -99954720 | 49921638 | 19938799 | 613608704 | 0.000000 | 0.000000
09-04-2025 17:08:45.000 | 13484548 | 134845480 | 134.8455 | 37179744 | 15608151 | 49900459 | -99962013 | 49954937 | 19751244 | 608066101 | 0.000000 | 0.000000
09-04-2025 17:08:40.000 | 13459139 | 134591390 | 134.5914 | 37142029 | 15613603 | 49789023 | -99961945 | 49964634 | 19564127 | 602941345 | 0.000000 | 0.000000
09-04-2025 17:08:35.000 | 13492089 | 134920890 | 134.9209 | 37071218 | 15612597 | 49913838 | -99962273 | 49974789 | 19376758 | 597731567 | 0.000000 | 0.000000
09-04-2025 17:08:30.000 | 13496864 | 134968640 | 134.9686 | 37636968 | 15614022 | 49927158 | -99961143 | 49958229 | 19189318 | 592637390 | 0.000000 | 0.000000
09-04-2025 17:08:25.000 | 13503569 | 135035690 | 135.0357 | 38018584 | 15611475 | 49960317 | -99960388 | 49945145 | 19002068 | 587350830 | 0.000000 | 0.000000
09-04-2025 17:08:20.000 | 13540567 | 135405670 | 135.4057 | 37462302 | 15609599 | 50102944 | -99961746 | 49958843 | 18814459 | 582057312 | 0.000000 | 0.000000
09-04-2025 17:08:15.000 | 13525417 | 135254170 | 135.2542 | 36781479 | 15610737 | 50042383 | -99963043 | 49972885 | 18626527 | 576921936 | 0.000000 | 0.000000
09-04-2025 17:08:10.000 | 13498622 | 134986220 | 134.9862 | 35603313 | 15613729 | 49932422 | -99965233 | 49976501 | 18438793 | 571916931 | 0.000000 | 0.000000
09-04-2025 17:08:05.000 | 13507881 | 135078810 | 135.0788 | 36994194 | 15612336 | 49972808 | -99962517 | 49966167 | 18251352 | 566881287 | 0.000000 | 0.000000
09-04-2025 17:08:00.000 | 13544925 | 135449250 | 135.4493 | 37732371 | 15611704 | 50112979 | -99961220 | 49975086 | 18063508 | 561784302 | 0.000000 | 0.000000
09-04-2025 17:07:55.000 | 13501514 | 135015140 | 135.0151 | 36229646 | 15610820 | 49953682 | -99964020 | 49977371 | 17875754 | 556566833 | 0.000000 | 0.000000
09-04-2025 17:07:50.000 | 13493595 | 134935950 | 134.9359 | 38622009 | 15613632 | 49917739 | -99959061 | 49953655 | 17688191 | 551463989 | 0.000000 | 0.000000
09-04-2025 17:07:45.000 | 13561972 | 135619720 | 135.6197 | 38375632 | 15608172 | 50187646 | -99959991 | 49953613 | 17500561 | 546080994 | 0.000000 | 0.000000
09-04-2025 17:07:40.000 | 13502014 | 135020140 | 135.0201 | 36961377 | 15613961 | 49946094 | -99962555 | 49948174 | 17312816 | 540885254 | 0.000000 | 0.000000
09-04-2025 17:07:35.000 | 13487016 | 134870160 | 134.8702 | 39531377 | 15614248 | 49892627 | -99957069 | 49925018 | 17125445 | 535560913 | 0.000000 | 0.000000
09-04-2025 17:07:30.000 | 13524622 | 135246220 | 135.2462 | 38792307 | 15611066 | 50041348 | -99958893 | 49908180 | 16938236 | 530135925 | 0.000000 | 0.000000
09-04-2025 17:07:25.000 | 13451630 | 134516300 | 134.5163 | 40885266 | 15615779 | 49758545 | -99953842 | 49894726 | 16750809 | 524668823 | 0.000000 | 0.000000
09-04-2025 17:07:20.000 | 13500255 | 135002550 | 135.0026 | 41162725 | 15609074 | 49960601 | -99953552 | 49890560 | 16563436 | 518920654 | 0.000000 | 0.000000
09-04-2025 17:07:15.000 | 13507517 | 135075170 | 135.0752 | 40124146 | 15610798 | 49979834 | -99955910 | 49910397 | 16375589 | 513181458 | 0.000000 | 0.000000
09-04-2025 17:07:10.000 | 13526908 | 135269080 | 135.2691 | 38474902 | 15610558 | 50050703 | -99959572 | 49925098 | 16187522 | 507688049 | 0.000000 | 0.000000
09-04-2025 17:07:05.000 | 13556484 | 135564840 | 135.5648 | 36474517 | 15612032 | 50154307 | -99963821 | 49932522 | 15999622 | 502472717 | 0.000000 | 0.000000
09-04-2025 17:07:00.000 | 13537950 | 135379500 | 135.3795 | 37176914 | 15614667 | 50078486 | -99962318 | 49922192 | 15811691 | 497446899 | 0.000000 | 0.000000
09-04-2025 17:06:55.000 | 13552956 | 135529560 | 135.5296 | 37318789 | 15607869 | 50154019 | -99962112 | 49907532 | 15623842 | 492233795 | 0.000000 | 0.000000
09-04-2025 17:06:50.000 | 13578686 | 135786860 | 135.7869 | 37314634 | 15608458 | 50247202 | -99962265 | 49936951 | 15435648 | 487100464 | 0.000000 | 0.000000
09-04-2025 17:06:45.000 | 13509297 | 135092970 | 135.093 | 34302947 | 15612518 | 49974946 | -99967781 | 49947521 | 15247635 | 482096008 | 0.000000 | 0.000000
09-04-2025 17:06:40.000 | 13553944 | 135539440 | 135.5394 | 37147559 | 15612382 | 50143330 | -99962463 | 49921879 | 15059888 | 477258820 | 0.000000 | 0.000000
09-04-2025 17:06:35.000 | 13522438 | 135224380 | 135.2244 | 36929146 | 15612742 | 50025742 | -99962730 | 49922832 | 14872208 | 472165039 | 0.000000 | 0.000000
09-04-2025 17:06:30.000 | 13502278 | 135022780 | 135.0228 | 38395325 | 15615900 | 49942383 | -99959595 | 49908314 | 14684577 | 467008362 | 0.000000 | 0.000000
09-04-2025 17:06:25.000 | 13560523 | 135605230 | 135.6052 | 38812024 | 15608963 | 50180112 | -99959068 | 49906162 | 14496863 | 461636047 | 0.000000 | 0.000000
09-04-2025 17:06:20.000 | 13553056 | 135530560 | 135.5306 | 37037349 | 15611182 | 50144321 | -99962677 | 49924107 | 14308605 | 456342346 | 0.000000 | 0.000000
09-04-2025 17:06:15.000 | 13546836 | 135468360 | 135.4684 | 37941165 | 15613585 | 50114414 | -99960800 | 49934990 | 14120256 | 451160309 | 0.000000 | 0.000000
09-04-2025 17:06:10.000 | 13614142 | 136141420 | 136.1414 | 37041150 | 15607479 | 50381841 | -99963005 | 49964344 | 13931712 | 445851074 | 0.000000 | 0.000000
09-04-2025 17:06:05.000 | 13622100 | 136221000 | 136.221 | 33095317 | 15608452 | 50404297 | -99970497 | 50009644 | 13742784 | 440899261 | 0.000000 | 0.000000
09-04-2025 17:06:00.000 | 13573800 | 135738000 | 135.738 | 32779512 | 15608775 | 50224888 | -99970856 | 50018761 | 13553838 | 436369080 | 0.000000 | 0.000000
09-04-2025 17:05:55.000 | 13576180 | 135761800 | 135.7618 | 31100051 | 15610203 | 50227222 | -99973770 | 50030384 | 13365106 | 431887177 | 0.000000 | 0.000000
09-04-2025 17:05:50.000 | 13520294 | 135202940 | 135.2029 | 33167888 | 15612390 | 50015488 | -99969925 | 50008282 | 13176789 | 427420746 | 0.000000 | 0.000000
09-04-2025 17:05:45.000 | 13462833 | 134628330 | 134.6283 | 37704158 | 15621666 | 49777544 | -99960808 | 49939480 | 12989319 | 422551727 | 0.000000 | 0.000000
09-04-2025 17:05:40.000 | 13608325 | 136083250 | 136.0832 | 40803196 | 15609470 | 50358677 | -99955078 | 49943130 | 12801345 | 416944397 | 0.000000 | 0.000000
09-04-2025 17:05:35.000 | 13597652 | 135976520 | 135.9765 | 38697979 | 15608811 | 50318716 | -99959526 | 49965240 | 12612783 | 411389404 | 0.000000 | 0.000000
09-04-2025 17:05:30.000 | 13579886 | 135798860 | 135.7989 | 36660894 | 15610193 | 50246855 | -99963577 | 49975403 | 12424252 | 406110535 | 0.000000 | 0.000000
09-04-2025 17:05:25.000 | 13563888 | 135638880 | 135.6389 | 38198726 | 15609983 | 50189277 | -99960365 | 49959515 | 12236048 | 400969086 | 0.000000 | 0.000000
09-04-2025 17:05:20.000 | 13505136 | 135051360 | 135.0514 | 40051209 | 15616244 | 49953511 | -99956055 | 49944237 | 12047896 | 395585022 | 0.000000 | 0.000000
09-04-2025 17:05:15.000 | 13551375 | 135513750 | 135.5137 | 42778257 | 15614045 | 50135327 | -99950211 | 49916759 | 11860202 | 389859436 | 0.000000 | 0.000000
09-04-2025 17:05:10.000 | 13553777 | 135537770 | 135.5378 | 42688652 | 15611251 | 50152046 | -99950439 | 49928673 | 11672085 | 383875732 | 0.000000 | 0.000000
09-04-2025 17:05:05.000 | 13525986 | 135259860 | 135.2599 | 43548345 | 15614479 | 50040264 | -99948212 | 49908810 | 11484136 | 377961731 | 0.000000 | 0.000000
09-04-2025 17:05:00.000 | 13604294 | 136042940 | 136.0429 | 41472378 | 15605830 | 50355249 | -99953568 | 49928951 | 11296011 | 372023438 | 0.000000 | 0.000000
09-04-2025 17:04:55.000 | 13546672 | 135466720 | 135.4667 | 39099490 | 15612799 | 50117788 | -99958374 | 49941437 | 11107704 | 366454681 | 0.000000 | 0.000000
09-04-2025 17:04:50.000 | 13450209 | 134502090 | 134.5021 | 44071240 | 15617287 | 49751880 | -99946365 | 49879074 | 10920466 | 360810608 | 0.000000 | 0.000000
09-04-2025 17:04:45.000 | 13542227 | 135422270 | 135.4223 | 44211694 | 15607356 | 50123589 | -99946747 | 49872437 | 10733342 | 354540588 | 0.000000 | 0.000000
09-04-2025 17:04:40.000 | 13449395 | 134493950 | 134.494 | 44086147 | 15616271 | 49752515 | -99946320 | 49877071 | 10545402 | 348476654 | 0.000000 | 0.000000
09-04-2025 17:04:35.000 | 13511039 | 135110390 | 135.1104 | 46755991 | 15613896 | 49990889 | -99940178 | 49855324 | 10358221 | 342172028 | 0.000000 | 0.000000
09-04-2025 17:04:30.000 | 13562452 | 135624520 | 135.6245 | 47334287 | 15609649 | 50195933 | -99939148 | 49856873 | 10170714 | 335619873 | 0.000000 | 0.000000
09-04-2025 17:04:25.000 | 13525202 | 135252020 | 135.252 | 45144199 | 15607267 | 50062871 | -99944344 | 49894230 | 99827158 | 329164490 | 0.000000 | 0.000000
09-04-2025 17:04:20.000 | 13516947 | 135169470 | 135.1695 | 43320566 | 15610170 | 50021299 | -99948685 | 49914707 | 97947793 | 322940948 | 0.000000 | 0.000000
09-04-2025 17:04:15.000 | 13489466 | 134894660 | 134.8947 | 42366025 | 15612101 | 49911270 | -99950714 | 49915340 | 96069463 | 316968628 | 0.000000 | 0.000000
09-04-2025 17:04:10.000 | 13487059 | 134870590 | 134.8706 | 44714746 | 15614754 | 49897295 | -99945084 | 49903065 | 94192529 | 310939789 | 0.000000 | 0.000000
09-04-2025 17:04:05.000 | 13552120 | 135521200 | 135.5212 | 45590703 | 15606990 | 50164258 | -99943459 | 49912609 | 92318418 | 304614716 | 0.000000 | 0.000000
09-04-2025 17:04:00.000 | 13540500 | 135405000 | 135.405 | 43382124 | 15614724 | 50093701 | -99948715 | 49936047 | 90436172 | 298466888 | 0.000000 | 0.000000
09-04-2025 17:03:55.000 | 13529169 | 135291690 | 135.2917 | 43569551 | 15611371 | 50062373 | -99948181 | 49925701 | 88557256 | 292412048 | 0.000000 | 0.000000
09-04-2025 17:03:50.000 | 13583714 | 135837140 | 135.8371 | 42957886 | 15607482 | 50275771 | -99950035 | 49943459 | 86676162 | 286370575 | 0.000000 | 0.000000
09-04-2025 17:03:45.000 | 13507313 | 135073130 | 135.0731 | 42648721 | 15614184 | 49971558 | -99950188 | 49958164 | 84791123 | 280412079 | 0.000000 | 0.000000
09-04-2025 17:03:40.000 | 13552313 | 135523130 | 135.5231 | 44277095 | 15612377 | 50145098 | -99946671 | 49927032 | 82913496 | 274384094 | 0.000000 | 0.000000

## ION SETUP NETO
Date/Time | kW tot | MW | kVAR tot | Vll avg | I avg | PF sign tot | Freq | kWh del int | kVARh del int | kWh rec int | kVARh rec int
09-04-2025 14:06:45000 | -1370798 | 137.0798 | 13113856 | 234357.41 | 339270874 | 99545517 | 50055656 | 0.000000 | 15273320 | 15356837 | 0.000000
09-04-2025 14:06:50000 | -1359731 | 135.9731 | 12884519 | 234511.75 | 336274750 | 99554047 | 50047577 | 0.000000 | 15453802 | 15546571 | 0.000000
09-04-2025 14:06:55000 | -1369850 | 136.985 | 13167493 | 234462.66 | 338891602 | 99541191 | 50047039 | 0.000000 | 15635090 | 15736342 | 0.000000
09-04-2025 14:07:00000 | -1365990 | 136.599 | 13163531 | 234530.92 | 337849213 | 99538887 | 50068703 | 0.000000 | 15817278 | 15926066 | 0.000000
09-04-2025 14:07:05000 | -1362839 | 136.2839 | 13566012 | 234678.05 | 336962860 | 99508217 | 50139778 | 0.000000 | 16003545 | 16115502 | 0.000000
09-04-2025 14:07:10000 | -1373004 | 137.3004 | 13852382 | 234557.91 | 339697235 | 99494904 | 50142002 | 0.000000 | 16195852 | 16306011 | 0.000000
09-04-2025 14:07:15000 | -1370987 | 137.0987 | 13453033 | 234510.58 | 339177338 | 99522003 | 50101154 | 0.000000 | 16384489 | 16496588 | 0.000000
09-04-2025 14:07:20000 | -1364748 | 136.4748 | 13235015 | 234539.66 | 337544525 | 99533058 | 50093979 | 0.000000 | 16569694 | 16686553 | 0.000000
09-04-2025 14:07:25000 | -1370461 | 137.0461 | 13529645 | 234515.81 | 339049652 | 99516220 | 50092129 | 0.000000 | 16755803 | 16876309 | 0.000000
09-04-2025 14:07:30000 | -1363560 | 136.356 | 13294725 | 234569.98 | 337223938 | 99528046 | 50095158 | 0.000000 | 16941552 | 17065896 | 0.000000
09-04-2025 14:07:35000 | -1363435 | 136.3435 | 13407051 | 234588.78 | 337189423 | 99520012 | 50112293 | 0.000000 | 17127791 | 17255564 | 0.000000
09-04-2025 14:07:40000 | -1373156 | 137.3156 | 13649952 | 234523.42 | 339725403 | 99509560 | 50110058 | 0.000000 | 17315739 | 17445713 | 0.000000
09-04-2025 14:07:45000 | -1367212 | 136.7212 | 13339521 | 234508.53 | 338219452 | 99527405 | 50091961 | 0.000000 | 17502498 | 17635719 | 0.000000
09-04-2025 14:07:50000 | -1365274 | 136.5274 | 13434864 | 234581.00 | 337669128 | 99519318 | 50104641 | 0.000000 | 17689146 | 17825543 | 0.000000
09-04-2025 14:07:55000 | -1371701 | 137.1701 | 13773068 | 234591.50 | 339301361 | 99499687 | 50125114 | 0.000000 | 17878207 | 18015734 | 0.000000
09-04-2025 14:08:00000 | -1370223 | 137.0223 | 13643485 | 234593.09 | 338912292 | 99507935 | 50134773 | 0.000000 | 18068180 | 18205963 | 0.000000
09-04-2025 14:08:05000 | -1369024 | 136.9024 | 13454526 | 234554.16 | 338620331 | 99520538 | 50115421 | 0.000000 | 18256229 | 18396547 | 0.000000
09-04-2025 14:08:10000 | -1367179 | 136.7179 | 13328778 | 234592.19 | 338087433 | 99528137 | 50095455 | 0.000000 | 18442701 | 18587029 | 0.000000
09-04-2025 14:08:15000 | -1369143 | 136.9143 | 13551307 | 234575.83 | 338653503 | 99513748 | 50098526 | 0.000000 | 18629961 | 18777084 | 0.000000
09-04-2025 14:08:20000 | -1368029 | 136.8029 | 13605289 | 234595.41 | 338357025 | 99509109 | 50115856 | 0.000000 | 18818459 | 18967141 | 0.000000
09-04-2025 14:08:25000 | -1367363 | 136.7363 | 13832230 | 234656.64 | 338163849 | 99492226 | 50149349 | 0.000000 | 19009764 | 19157221 | 0.000000
09-04-2025 14:08:30000 | -1371151 | 137.1151 | 13654608 | 234560.22 | 339194794 | 99507797 | 50130207 | 0.000000 | 19200476 | 19347572 | 0.000000
09-04-2025 14:08:35000 | -1374604 | 137.4604 | 13505590 | 234486.47 | 340100708 | 99520805 | 50111954 | 0.000000 | 19389176 | 19538293 | 0.000000
09-04-2025 14:08:40000 | -1371368 | 137.1368 | 13444041 | 234541.14 | 339210663 | 99522903 | 50106998 | 0.000000 | 19574697 | 19728715 | 0.000000
09-04-2025 14:08:45000 | -1369853 | 136.9853 | 13431990 | 234583.64 | 338786560 | 99522705 | 50128883 | 0.000000 | 19760780 | 19918893 | 0.000000
09-04-2025 14:08:50000 | -1371640 | 137.164 | 13400577 | 234462.38 | 339390656 | 99526154 | 50126614 | 0.000000 | 19948762 | 20109561 | 0.000000
09-04-2025 14:08:55000 | -1372355 | 137.2355 | 13410984 | 234368.47 | 339697510 | 99525909 | 50112476 | 0.000000 | 20136165 | 20300197 | 0.000000
09-04-2025 14:09:00000 | -1368395 | 136.8395 | 13286073 | 234442.31 | 338593170 | 99531960 | 50099049 | 0.000000 | 20322011 | 20490629 | 0.000000
09-04-2025 14:09:05000 | -1367983 | 136.7983 | 13465708 | 234536.19 | 338401550 | 99519020 | 50141327 | 0.000000 | 20508977 | 20680496 | 0.000000
09-04-2025 14:09:10000 | -1373836 | 137.3836 | 13671315 | 234507.39 | 339919342 | 99508514 | 50140064 | 0.000000 | 20698569 | 20871270 | 0.000000
09-04-2025 14:09:15000 | -1374106 | 137.4106 | 13405949 | 234458.95 | 339991730 | 99527458 | 50092098 | 0.000000 | 20884900 | 21062154 | 0.000000
09-04-2025 14:09:20000 | -1369648 | 136.9648 | 13154846 | 234452.36 | 338850281 | 99541931 | 50085999 | 0.000000 | 21068040 | 21252264 | 0.000000
09-04-2025 14:09:25000 | -1365845 | 136.5845 | 13226674 | 234522.73 | 337838715 | 99534386 | 50094124 | 0.000000 | 21251594 | 21442439 | 0.000000
09-04-2025 14:09:30000 | -1373059 | 137.3059 | 13553873 | 234527.16 | 339671875 | 99516319 | 50127319 | 0.000000 | 21437559 | 21632566 | 0.000000
09-04-2025 14:09:35000 | -1369542 | 136.9542 | 13681373 | 234574.28 | 338773315 | 99504730 | 50145470 | 0.000000 | 21627485 | 21822854 | 0.000000
09-04-2025 14:09:40000 | -1369670 | 136.967 | 13902347 | 234647.42 | 338757538 | 99488823 | 50160709 | 0.000000 | 21818071 | 22013006 | 0.000000
09-04-2025 14:09:45000 | -1374229 | 137.4229 | 14033833 | 234611.89 | 339957977 | 99482605 | 50154007 | 0.000000 | 22012961 | 22203758 | 0.000000
09-04-2025 14:09:50000 | -1372682 | 137.2682 | 14025447 | 234684.89 | 339466370 | 99482063 | 50160583 | 0.000000 | 22207422 | 22394252 | 0.000000
09-04-2025 14:09:55000 | -1367884 | 136.7884 | 13914825 | 234652.27 | 338319672 | 99486580 | 50166996 | 0.000000 | 22402065 | 22584844 | 0.000000
09-04-2025 14:10:00000 | -1371876 | 137.1876 | 13869641 | 234582.33 | 339388550 | 99492828 | 50151855 | 0.000000 | 22595344 | 22775340 | 0.000000
09-04-2025 14:10:05000 | -1365293 | 136.5293 | 13389501 | 234547.05 | 337700531 | 99522552 | 50113426 | 0.000000 | 22785291 | 22965807 | 0.000000
09-04-2025 14:10:10000 | -1369935 | 136.9935 | 13842456 | 234691.94 | 338747864 | 99493378 | 50133427 | 0.000000 | 22973799 | 23155695 | 0.000000
09-04-2025 14:10:15000 | -1371854 | 137.1854 | 14059189 | 234619.17 | 339371796 | 99478958 | 50145718 | 0.000000 | 23167813 | 23345818 | 0.000000
09-04-2025 14:10:20000 | -1365686 | 136.5686 | 13602129 | 234622.53 | 337744751 | 99507660 | 50123703 | 0.000000 | 23359563 | 23536078 | 0.000000
09-04-2025 14:10:25000 | -1366734 | 136.6734 | 13652590 | 234545.78 | 338127350 | 99504784 | 50099270 | 0.000000 | 23551265 | 23726617 | 0.000000
09-04-2025 14:10:30000 | -1361465 | 136.1465 | 13490365 | 234599.78 | 336714111 | 99512672 | 50091145 | 0.000000 | 23738635 | 23916402 | 0.000000
09-04-2025 14:10:35000 | -1366886 | 136.6886 | 13487937 | 234529.25 | 338145691 | 99516678 | 50097431 | 0.000000 | 23926062 | 24106129 | 0.000000
09-04-2025 14:10:40000 | -1366048 | 136.6048 | 13539512 | 234503.16 | 337993896 | 99512405 | 50102409 | 0.000000 | 24114531 | 24295857 | 0.000000
09-04-2025 14:10:45000 | -1361074 | 136.1074 | 13418915 | 234533.95 | 336699982 | 99517509 | 50112961 | 0.000000 | 24300374 | 24485039 | 0.000000
09-04-2025 14:10:50000 | -1365567 | 136.5567 | 13634391 | 234538.67 | 337847168 | 99505257 | 50135269 | 0.000000 | 24488582 | 24674340 | 0.000000
09-04-2025 14:10:55000 | -1360861 | 136.0861 | 13385536 | 234530.59 | 336644501 | 99519737 | 50130169 | 0.000000 | 24676511 | 24863979 | 0.000000
09-04-2025 14:11:00000 | -1362311 | 136.2311 | 13608668 | 234570.97 | 336997925 | 99504761 | 50144882 | 0.000000 | 24863904 | 25053215 | 0.000000
09-04-2025 14:11:05000 | -1363871 | 136.3871 | 13576047 | 234480.91 | 337500244 | 99508232 | 50138523 | 0.000000 | 25054202 | 25242723 | 0.000000
09-04-2025 14:11:10000 | -1360772 | 136.0772 | 13654219 | 234536.20 | 336676605 | 99500343 | 50132626 | 0.000000 | 25243511 | 25432111 | 0.000000
09-04-2025 14:11:15000 | -1366344 | 136.6344 | 13624647 | 234488.91 | 338103485 | 99506516 | 50119263 | 0.000000 | 25432844 | 25621316 | 0.000000
09-04-2025 14:11:20000 | -1364591 | 136.4591 | 13282992 | 234447.00 | 337653137 | 99529579 | 50099274 | 0.000000 | 25617869 | 25810471 | 0.000000
09-04-2025 14:11:25000 | -1361586 | 136.1586 | 13379359 | 234522.64 | 336832428 | 99520683 | 50099380 | 0.000000 | 25801729 | 25999387 | 0.000000
09-04-2025 14:11:30000 | -1361186 | 136.1186 | 13377441 | 234523.09 | 336732758 | 99520546 | 50110851 | 0.000000 | 25986829 | 26188318 | 0.000000
09-04-2025 14:11:35000 | -1362484 | 136.2484 | 13384432 | 234441.48 | 337163971 | 99520950 | 50109264 | 0.000000 | 26173762 | 26377535 | 0.000000
09-04-2025 14:11:40000 | -1354627 | 135.4627 | 13018588 | 234487.56 | 335095947 | 99541367 | 50082954 | 0.000000 | 26357068 | 26566514 | 0.000000
09-04-2025 14:11:45000 | -1358525 | 135.8525 | 13311110 | 234555.38 | 336016937 | 99523407 | 50110344 | 0.000000 | 26539705 | 26754811 | 0.000000
09-04-2025 14:11:50000 | -1357546 | 135.7546 | 13702274 | 234668.47 | 335711975 | 99494476 | 50159698 | 0.000000 | 26726484 | 26942992 | 0.000000
09-04-2025 14:11:55000 | -1365342 | 136.5342 | 13683637 | 234470.56 | 337907410 | 99501534 | 50150307 | 0.000000 | 26918735 | 27132354 | 0.000000
09-04-2025 14:12:00000 | -1365595 | 136.5595 | 13530255 | 234468.19 | 337929688 | 99512749 | 50111572 | 0.000000 | 27106660 | 27321842 | 0.000000
09-04-2025 14:12:05000 | -1355698 | 135.5698 | 13087461 | 234543.08 | 335286133 | 99537262 | 50085701 | 0.000000 | 27292397 | 27510762 | 0.000000
09-04-2025 14:12:10000 | -1356271 | 135.6271 | 13488680 | 234625.52 | 335412140 | 99509079 | 50087158 | 0.000000 | 27478394 | 27699576 | 0.000000
09-04-2025 14:12:15000 | -1362403 | 136.2403 | 13599285 | 234628.47 | 336934784 | 99505508 | 50112511 | 0.000000 | 27666209 | 27888559 | 0.000000
09-04-2025 14:12:20000 | -1364027 | 136.4027 | 13741718 | 234659.58 | 337326965 | 99496368 | 50143501 | 0.000000 | 27855264 | 28077738 | 0.000000
09-04-2025 14:12:25000 | -1367715 | 136.7715 | 13792244 | 234627.08 | 338285645 | 99495392 | 50144501 | 0.000000 | 28047395 | 28267551 | 0.000000
09-04-2025 14:12:30000 | -1368084 | 136.8084 | 13617400 | 234565.70 | 338421478 | 99508278 | 50126522 | 0.000000 | 28236995 | 28457121 | 0.000000
09-04-2025 14:12:35000 | -1366944 | 136.6944 | 13382472 | 234522.59 | 338142059 | 99524193 | 50101028 | 0.000000 | 28423618 | 28646527 | 0.000000
09-04-2025 14:12:40000 | -1359232 | 135.9232 | 13250527 | 234555.88 | 336174072 | 99528191 | 50088940 | 0.000000 | 28609812 | 28835938 | 0.000000
09-04-2025 14:12:45000 | -1363105 | 136.3105 | 13297276 | 234526.47 | 337173187 | 99527557 | 50072647 | 0.000000 | 28793289 | 29025248 | 0.000000
09-04-2025 14:12:50000 | -1360928 | 136.0928 | 13302614 | 234492.98 | 336692017 | 99525673 | 50086357 | 0.000000 | 28978005 | 29214217 | 0.000000
09-04-2025 14:12:55000 | -1363108 | 136.3108 | 13396262 | 234479.47 | 337268982 | 99520546 | 50095966 | 0.000000 | 29162671 | 29403205 | 0.000000
09-04-2025 14:13:00000 | -1359277 | 135.9277 | 13370499 | 234517.47 | 336268372 | 99519699 | 50095787 | 0.000000 | 29347371 | 29592102 | 0.000000
09-04-2025 14:13:05000 | -1359783 | 135.9783 | 13357990 | 234472.73 | 336456787 | 99520950 | 50112682 | 0.000000 | 29533071 | 29780842 | 0.000000
09-04-2025 14:13:10000 | -1355621 | 135.5621 | 13254324 | 234516.75 | 335348389 | 99525421 | 50096638 | 0.000000 | 29718726 | 29969680 | 0.000000
09-04-2025 14:13:15000 | -1364700 | 136.47 | 13518407 | 234501.02 | 337658142 | 99512962 | 50106125 | 0.000000 | 29904585 | 30158453 | 0.000000
09-04-2025 14:13:20000 | -1361874 | 136.1874 | 13743594 | 234579.84 | 336909637 | 99494644 | 50139324 | 0.000000 | 30093499 | 30347240 | 0.000000
09-04-2025 14:13:25000 | -1362745 | 136.2745 | 13553796 | 234501.91 | 337190796 | 99509033 | 50139919 | 0.000000 | 30283347 | 30536615 | 0.000000
09-04-2025 14:13:30000 | -1362170 | 136.217 | 13424222 | 234455.50 | 337079559 | 99517899 | 50122383 | 0.000000 | 30470811 | 30725680 | 0.000000
09-04-2025 14:13:35000 | -1363976 | 136.3976 | 13497311 | 234479.25 | 337512482 | 99513954 | 50115540 | 0.000000 | 30657610 | 30914918 | 0.000000
09-04-2025 14:13:40000 | -1351067 | 135.1067 | 13402533 | 234672.02 | 334039948 | 99511574 | 50143639 | 0.000000 | 30843611 | 31103607 | 0.000000
09-04-2025 14:13:45000 | -1366393 | 136.6393 | 14177612 | 234614.59 | 338077423 | 99466011 | 50186069 | 0.000000 | 31038003 | 31292781 | 0.000000
09-04-2025 14:13:50000 | -1363977 | 136.3977 | 14129429 | 234659.25 | 337405579 | 99467735 | 50187344 | 0.000000 | 31232144 | 31481955 | 0.000000
09-04-2025 14:13:55000 | -1364089 | 136.4089 | 13568449 | 234469.31 | 337565979 | 99508934 | 50129906 | 0.000000 | 31425310 | 31671818 | 0.000000
09-04-2025 14:14:00000 | -1358164 | 135.8164 | 13335280 | 234540.00 | 335953796 | 99521431 | 50135712 | 0.000000 | 31609946 | 31860572 | 0.000000
09-04-2025 14:14:05000 | -1357393 | 135.7393 | 13413255 | 234551.77 | 335766144 | 99515312 | 50134365 | 0.000000 | 31795608 | 32049234 | 0.000000
09-04-2025 14:14:10000 | -1360813 | 136.0813 | 13318488 | 234456.58 | 336725922 | 99524475 | 50126663 | 0.000000 | 31981406 | 32238104 | 0.000000
09-04-2025 14:14:15000 | -1363732 | 136.3732 | 13498460 | 234505.83 | 337421234 | 99513702 | 50142822 | 0.000000 | 32165869 | 32426533 | 0.000000
09-04-2025 14:14:20000 | -1356482 | 135.6482 | 13542307 | 234651.25 | 335430450 | 99505356 | 50171104 | 0.000000 | 32353274 | 32615166 | 0.000000
09-04-2025 14:14:25000 | -1358626 | 135.8626 | 13431297 | 234566.16 | 336052582 | 99514893 | 50155590 | 0.000000 | 32542419 | 32804309 | 0.000000
09-04-2025 14:14:30000 | -1363666 | 136.3666 | 13474610 | 234532.72 | 337344391 | 99515358 | 50150543 | 0.000000 | 32730186 | 32993332 | 0.000000
09-04-2025 14:14:35000 | -1361821 | 136.1821 | 13225257 | 234483.44 | 336908356 | 99531746 | 50123932 | 0.000000 | 32915059 | 33182414 | 0.000000
09-04-2025 14:14:40000 | -1356545 | 135.6545 | 13108935 | 234514.72 | 335540131 | 99536331 | 50126694 | 0.000000 | 33097671 | 33370867 | 0.000000
09-04-2025 14:14:45000 | -1356999 | 135.6999 | 12980574 | 234485.22 | 335666443 | 99545609 | 50118279 | 0.000000 | 33278577 | 33559352 | 0.000000
09-04-2025 14:14:50000 | -1352302 | 135.2302 | 12967715 | 234557.33 | 334408295 | 99543365 | 50139557 | 0.000000 | 33458699 | 33747305 | 0.000000
09-04-2025 14:14:55000 | -1357326 | 135.7326 | 13482476 | 234606.20 | 335692108 | 99510284 | 50173031 | 0.000000 | 33644402 | 33935879 | 0.000000
09-04-2025 14:15:00000 | -1359043 | 135.9043 | 13667170 | 234665.55 | 336071289 | 99498138 | 50209534 | 0.000000 | 33833416 | 34124594 | 0.000000
09-04-2025 14:15:05000 | -1357509 | 135.7509 | 13548069 | 234617.92 | 335732666 | 99505676 | 50200253 | 0.000000 | 19057280 | 189136917 | 0.000000
09-04-2025 14:15:10000 | -1361028 | 136.1028 | 14086046 | 234708.59 | 336611237 | 99468697 | 50217255 | 0.000000 | 38328415 | 378025146 | 0.000000
09-04-2025 14:15:15000 | -1367835 | 136.7835 | 14172267 | 234686.61 | 338313965 | 99467522 | 50212704 | 0.000000 | 57883823 | 567399231 | 0.000000
09-04-2025 14:15:20000 | -1355525 | 135.5525 | 13673804 | 234688.16 | 335181213 | 99495064 | 50190987 | 0.000000 | 77232674 | 756639160 | 0.000000
09-04-2025 14:15:25000 | -1360936 | 136.0936 | 14129448 | 234743.63 | 336539307 | 99465370 | 50217648 | 0.000000 | 96592476 | 945507324 | 0.000000
09-04-2025 14:15:30000 | -1365216 | 136.5216 | 14211601 | 234683.36 | 337692596 | 99462547 | 50216526 | 0.000000 | 116183693 | 11348524 | 0.000000
09-04-2025 14:15:35000 | -1362514 | 136.2514 | 14147787 | 234736.25 | 336938110 | 99465225 | 50222500 | 0.000000 | 135833740 | 13241100 | 0.000000
09-04-2025 14:15:40000 | -1365192 | 136.5192 | 14231479 | 234719.16 | 337639832 | 99461037 | 50232204 | 0.000000 | 155550186 | 15135096 | 0.000000
09-04-2025 14:15:45000 | -1363655 | 136.3655 | 14007656 | 234694.19 | 337252960 | 99476555 | 50209549 | 0.000000 | 175098190 | 17029751 | 0.000000
09-04-2025 14:15:50000 | -1367166 | 136.7166 | 14032295 | 234675.38 | 338135101 | 99477402 | 50194736 | 0.000000 | 194568405 | 18928580 | 0.000000
09-04-2025 14:15:55000 | -1366263 | 136.6263 | 14129731 | 234730.73 | 337855042 | 99469482 | 50216957 | 0.000000 | 214029984 | 20824480 | 0.000000
09-04-2025 14:16:00000 | -1366528 | 136.6528 | 13993008 | 234676.20 | 337965118 | 99479820 | 50218510 | 0.000000 | 233588547 | 22722815 | 0.000000
09-04-2025 14:16:05000 | -1366014 | 136.6014 | 13988148 | 234705.42 | 337795990 | 99479790 | 50209518 | 0.000000 | 253077118 | 24621826 | 0.000000
09-04-2025 14:16:10000 | -1366400 | 136.64 | 13578134 | 234570.45 | 337987183 | 99509888 | 50178925 | 0.000000 | 272283386 | 26524277 | 0.000000
09-04-2025 14:16:15000 | -1366215 | 136.6215 | 13541884 | 234553.38 | 337957428 | 99512352 | 50165604 | 0.000000 | 291173492 | 28423816 | 0.000000
09-04-2025 14:16:20000 | -1365942 | 136.5942 | 13568341 | 234600.03 | 337830811 | 99510269 | 50158859 | 0.000000 | 310111725 | 30324731 | 0.000000
09-04-2025 14:16:25000 | -1369339 | 136.9339 | 13705777 | 234608.77 | 338684601 | 99502831 | 50166077 | 0.000000 | 329047821 | 32224172 | 0.000000
09-04-2025 14:16:30000 | -1371125 | 137.1125 | 13653899 | 234564.08 | 339175446 | 99507835 | 50165760 | 0.000000 | 348036285 | 34125906 | 0.000000
09-04-2025 14:16:35000 | -1366120 | 136.612 | 13663301 | 234638.61 | 337845001 | 99503571 | 50180603 | 0.000000 | 367033295 | 36025938 | 0.000000
09-04-2025 14:16:40000 | -1368326 | 136.8326 | 13572293 | 234570.70 | 338457367 | 99511681 | 50180649 | 0.000000 | 385955780 | 37925266 | 0.000000
09-04-2025 14:16:45000 | -1365388 | 136.5388 | 13419258 | 234578.31 | 337685425 | 99520508 | 50163433 | 0.000000 | 404704071 | 39827112 | 0.000000
09-04-2025 14:16:50000 | -1365088 | 136.5088 | 13518219 | 234624.67 | 337569489 | 99513245 | 50177540 | 0.000000 | 423412933 | 41725078 | 0.000000
09-04-2025 14:16:55000 | -1372194 | 137.2194 | 13632755 | 234510.58 | 339502625 | 99510101 | 50166878 | 0.000000 | 442327606 | 43626460 | 0.000000
09-04-2025 14:17:00000 | -1366201 | 136.6201 | 13241889 | 234527.58 | 337916779 | 99533562 | 50142586 | 0.000000 | 460783356 | 45523623 | 0.000000
09-04-2025 14:17:05000 | -1364398 | 136.4398 | 13259397 | 234536.11 | 337472412 | 99531105 | 50127136 | 0.000000 | 479346649 | 47422559 | 0.000000
09-04-2025 14:17:10000 | -1364162 | 136.4162 | 13418231 | 234593.53 | 337364532 | 99519722 | 50158203 | 0.000000 | 497871704 | 49316509 | 0.000000
09-04-2025 14:17:15000 | -1366345 | 136.6345 | 13510318 | 234508.23 | 338050415 | 99514702 | 50180935 | 0.000000 | 516561218 | 51210195 | 0.000000
09-04-2025 14:17:20000 | -1366975 | 136.6975 | 13366532 | 234485.25 | 338201538 | 99525337 | 50146099 | 0.000000 | 535263428 | 53110264 | 0.000000
09-04-2025 14:17:25000 | -1360452 | 136.0452 | 13060018 | 234513.05 | 336495361 | 99542381 | 50137901 | 0.000000 | 553435608 | 55002017 | 0.000000
09-04-2025 14:17:30000 | -1359552 | 135.9552 | 13099637 | 234537.53 | 336239319 | 99539017 | 50158524 | 0.000000 | 571600647 | 56891123 | 0.000000
09-04-2025 14:17:35000 | -1364118 | 136.4118 | 13633865 | 234611.27 | 337386383 | 99504250 | 50188786 | 0.000000 | 590302429 | 58782476 | 0.000000
09-04-2025 14:17:40000 | -1368233 | 136.8233 | 13630474 | 234572.84 | 338450226 | 99507446 | 50197006 | 0.000000 | 609093384 | 60676011 | 0.000000
09-04-2025 14:17:45000 | -1361207 | 136.1207 | 13266389 | 234551.45 | 336665680 | 99528427 | 50176430 | 0.000000 | 627716003 | 62570713 | 0.000000
09-04-2025 14:17:50000 | -1360873 | 136.0873 | 13482761 | 234618.00 | 336544373 | 99512794 | 50190372 | 0.000000 | 646383240 | 64463213 | 0.000000
09-04-2025 14:17:55000 | -1364375 | 136.4375 | 13635348 | 234591.81 | 337481262 | 99504326 | 50194706 | 0.000000 | 665237610 | 66357593 | 0.000000
09-04-2025 14:18:00000 | -1365965 | 136.5965 | 13248350 | 234411.81 | 338030579 | 99532951 | 50149696 | 0.000000 | 683959106 | 68257490 | 0.000000
09-04-2025 14:18:05000 | -1361966 | 136.1966 | 13039535 | 234523.97 | 336842316 | 99544815 | 50128601 | 0.000000 | 702238464 | 70153403 | 0.000000
09-04-2025 14:18:10000 | -1366972 | 136.6972 | 13167876 | 234465.02 | 338186676 | 99539246 | 50126163 | 0.000000 | 720478027 | 72049165 | 0.000000
09-04-2025 14:18:15000 | -1364694 | 136.4694 | 13127670 | 234476.38 | 337599365 | 99540512 | 50119450 | 0.000000 | 738665100 | 73942397 | 0.000000
09-04-2025 14:18:20000 | -1365804 | 136.5804 | 13307557 | 234524.31 | 337845245 | 99528687 | 50131325 | 0.000000 | 757057434 | 75838232 | 0.000000
09-04-2025 14:18:25000 | -1364078 | 136.4078 | 13272878 | 234551.94 | 337372620 | 99529945 | 50134747 | 0.000000 | 775409485 | 77732300 | 0.000000
09-04-2025 14:18:30000 | -1361898 | 136.1898 | 13356563 | 234544.92 | 336867645 | 99522522 | 50165104 | 0.000000 | 793898438 | 79623081 | 0.000000
09-04-2025 14:18:35000 | -1373637 | 137.3637 | 13419538 | 234384.55 | 339996887 | 99526184 | 50128578 | 0.000000 | 812637207 | 81526704 | 0.000000
09-04-2025 14:18:40000 | -1367269 | 136.7269 | 13048690 | 234424.08 | 338285614 | 99547684 | 50099495 | 0.000000 | 830866211 | 83426221 | 0.000000
09-04-2025 14:18:45000 | -1359519 | 135.9519 | 13011214 | 234596.41 | 336132446 | 99545151 | 50102821 | 0.000000 | 848856445 | 85319180 | 0.000000
09-04-2025 14:18:50000 | -1365772 | 136.5772 | 13464354 | 234555.03 | 337825684 | 99517570 | 50120457 | 0.000000 | 867357300 | 87215283 | 0.000000
09-04-2025 14:18:55000 | -1373562 | 137.3562 | 13485952 | 234447.33 | 339899872 | 99521469 | 50121998 | 0.000000 | 885973450 | 89113721 | 0.000000
09-04-2025 14:19:00000 | -1368482 | 136.8482 | 13291942 | 234518.67 | 338496765 | 99531609 | 50104614 | 0.000000 | 904452393 | 91015137 | 0.000000
09-04-2025 14:19:05000 | -1364375 | 136.4375 | 13289784 | 234559.28 | 337437225 | 99528954 | 50102104 | 0.000000 | 922824463 | 92911768 | 0.000000
09-04-2025 14:19:10000 | -1369434 | 136.9434 | 13538347 | 234585.14 | 338701477 | 99514877 | 50141533 | 0.000000 | 941483154 | 94809375 | 0.000000
09-04-2025 14:19:15000 | -1371995 | 137.1995 | 13901940 | 234627.17 | 339360138 | 99490570 | 50166092 | 0.000000 | 960617554 | 96710967 | 0.000000
09-04-2025 14:19:20000 | -1373028 | 137.3028 | 13719553 | 234540.06 | 339690491 | 99504486 | 50147438 | 0.000000 | 979813660 | 98618584 | 0.000000
09-04-2025 14:19:25000 | -1378039 | 137.8039 | 13674860 | 234466.86 | 341012939 | 99511238 | 50116917 | 0.000000 | 998729736 | 10052576 | 0.000000
09-04-2025 14:19:30000 | -1369525 | 136.9525 | 13408615 | 234530.33 | 338772339 | 99524132 | 50113129 | 0.000000 | 10173352 | 10242780 | 0.000000
09-04-2025 14:19:35000 | -1368370 | 136.837 | 13297781 | 234516.27 | 338491577 | 99531120 | 50072605 | 0.000000 | 10359294 | 10433249 | 0.000000
09-04-2025 14:19:40000 | -1363091 | 136.3091 | 13312163 | 234620.30 | 337040100 | 99526497 | 50092278 | 0.000000 | 10542459 | 10622740 | 0.000000
09-04-2025 14:19:45000 | -1364927 | 136.4927 | 13478438 | 234584.17 | 337592712 | 99515976 | 50126640 | 0.000000 | 10729567 | 10812459 | 0.000000
09-04-2025 14:19:50000 | -1369393 | 136.9393 | 13408375 | 234462.69 | 338841095 | 99524055 | 50086891 | 0.000000 | 10917408 | 11002771 | 0.000000
09-04-2025 14:19:55000 | -1364191 | 136.4191 | 13328195 | 234550.25 | 337418762 | 99526123 | 50075790 | 0.000000 | 11101873 | 11192567 | 0.000000
09-04-2025 14:20:00000 | -1369762 | 136.9762 | 13399122 | 234502.77 | 338868134 | 99524963 | 50080105 | 0.000000 | 11287405 | 11382437 | 0.000000
09-04-2025 14:20:05000 | -1369444 | 136.9444 | 13360871 | 234559.84 | 338701141 | 99527435 | 50078434 | 0.000000 | 11472977 | 11572607 | 0.000000
09-04-2025 14:20:10000 | -1368575 | 136.8575 | 13155015 | 234429.75 | 338618652 | 99541206 | 50070934 | 0.000000 | 11657277 | 11762722 | 0.000000
09-04-2025 14:20:15000 | -1363154 | 136.3154 | 12759287 | 234419.86 | 337217407 | 99564796 | 50061775 | 0.000000 | 11837191 | 11952730 | 0.000000
09-04-2025 14:20:20000 | -1368250 | 136.825 | 13112334 | 234447.00 | 338506256 | 99543945 | 50056450 | 0.000000 | 12017432 | 12142664 | 0.000000
09-04-2025 14:20:25000 | -1363700 | 136.37 | 13083844 | 234557.13 | 337224182 | 99542892 | 50082443 | 0.000000 | 12198135 | 12332090 | 0.000000
09-04-2025 14:20:30000 | -1362709 | 136.2709 | 13294989 | 234527.53 | 337076538 | 99527443 | 50103855 | 0.000000 | 12382218 | 12521745 | 0.000000
09-04-2025 14:20:35000 | -1369208 | 136.9208 | 13253779 | 234445.20 | 338780792 | 99534767 | 50080856 | 0.000000 | 12568173 | 12712061 | 0.000000
09-04-2025 14:20:40000 | -1369545 | 136.9545 | 13163002 | 234493.66 | 338768860 | 99541298 | 50075943 | 0.000000 | 12751023 | 12901921 | 0.000000
09-04-2025 14:20:45000 | -1371896 | 137.1896 | 13294888 | 234473.88 | 339406372 | 99533714 | 50082680 | 0.000000 | 12933792 | 13091754 | 0.000000
09-04-2025 14:20:50000 | -1368714 | 136.8714 | 13207320 | 234491.20 | 338586243 | 99537666 | 50072887 | 0.000000 | 13117465 | 13281779 | 0.000000
09-04-2025 14:20:55000 | -1365695 | 136.5695 | 13205217 | 234533.38 | 337776489 | 99535782 | 50084896 | 0.000000 | 13300277 | 13471379 | 0.000000
09-04-2025 14:21:00000 | -1364488 | 136.4488 | 13415707 | 234610.69 | 337424286 | 99520134 | 50116947 | 0.000000 | 13486520 | 13661219 | 0.000000
09-04-2025 14:21:05000 | -1374022 | 137.4022 | 13675146 | 234564.78 | 339886047 | 99508377 | 50131443 | 0.000000 | 13674989 | 13851570 | 0.000000
09-04-2025 14:21:10000 | -1376578 | 137.6578 | 13757022 | 234526.28 | 340595428 | 99504349 | 50122723 | 0.000000 | 13864504 | 14042118 | 0.000000
09-04-2025 14:21:15000 | -1368870 | 136.887 | 13417965 | 234558.75 | 338578033 | 99523018 | 50103954 | 0.000000 | 14052648 | 14232624 | 0.000000
09-04-2025 14:21:20000 | -1363935 | 136.3935 | 13239032 | 234577.00 | 337291595 | 99532219 | 50086933 | 0.000000 | 14238701 | 14422928 | 0.000000
09-04-2025 14:21:25000 | -1364075 | 136.4075 | 13159279 | 234514.09 | 337406128 | 99537895 | 50110729 | 0.000000 | 14422368 | 14612664 | 0.000000
09-04-2025 14:21:30000 | -1368583 | 136.8583 | 13433552 | 234564.41 | 338497192 | 99521721 | 50119232 | 0.000000 | 14608057 | 14802461 | 0.000000
09-04-2025 14:21:35000 | -1373650 | 137.365 | 13602114 | 234544.53 | 339811584 | 99513313 | 50097248 | 0.000000 | 14795259 | 14993062 | 0.000000
09-04-2025 14:21:40000 | -1372916 | 137.2916 | 13545074 | 234528.36 | 339638275 | 99516846 | 50102509 | 0.000000 | 14983461 | 15183313 | 0.000000
09-04-2025 14:21:45000 | -1368564 | 136.8564 | 13459064 | 234562.52 | 338500732 | 99519897 | 50092705 | 0.000000 | 15169930 | 15373339 | 0.000000
09-04-2025 14:21:50000 | -1364624 | 136.4624 | 13571074 | 234664.08 | 337414185 | 99509132 | 50114151 | 0.000000 | 15357931 | 15563225 | 0.000000
09-04-2025 14:21:55000 | -1366806 | 136.6806 | 13836601 | 234688.08 | 337983887 | 99491501 | 50145302 | 0.000000 | 15548625 | 15753063 | 0.000000
09-04-2025 14:22:00000 | -1373308 | 137.3308 | 14120987 | 234667.58 | 339674316 | 99475510 | 50164742 | 0.000000 | 15742167 | 15942979 | 0.000000
09-04-2025 14:22:05000 | -1373253 | 137.3253 | 13897750 | 234542.03 | 339780853 | 99491798 | 50148415 | 0.000000 | 15938021 | 16133420 | 0.000000
09-04-2025 14:22:10000 | -1368479 | 136.8479 | 13582402 | 234568.03 | 338508942 | 99511063 | 50121536 | 0.000000 | 16128683 | 16323819 | 0.000000
09-04-2025 14:22:15000 | -1367172 | 136.7172 | 13498396 | 234564.52 | 338171021 | 99516129 | 50097744 | 0.000000 | 16316810 | 16513854 | 0.000000
09-04-2025 14:22:20000 | -1364248 | 136.4248 | 13363969 | 234579.23 | 337391174 | 99523636 | 50087940 | 0.000000 | 16504199 | 16704000 | 0.000000
09-04-2025 14:22:25000 | -1367675 | 136.7675 | 13576168 | 234604.34 | 338248169 | 99510941 | 50102463 | 0.000000 | 16691146 | 16893674 | 0.000000
09-04-2025 14:22:30000 | -1364213 | 136.4213 | 13766679 | 234678.64 | 337339569 | 99494682 | 50130676 | 0.000000 | 16880599 | 17083230 | 0.000000
09-04-2025 14:22:35000 | -1370620 | 137.062 | 13750641 | 234572.13 | 339058899 | 99500519 | 50125469 | 0.000000 | 17073398 | 17273693 | 0.000000
09-04-2025 14:22:40000 | -1368589 | 136.8589 | 13615982 | 234593.06 | 338496124 | 99508736 | 50124527 | 0.000000 | 17262617 | 17463777 | 0.000000
09-04-2025 14:22:45000 | -1366186 | 136.6186 | 13557865 | 234610.14 | 337873444 | 99511192 | 50112003 | 0.000000 | 17450693 | 17653791 | 0.000000
09-04-2025 14:22:50000 | -1365617 | 136.5617 | 13780664 | 234712.47 | 337643524 | 99494698 | 50126896 | 0.000000 | 17640419 | 17843607 | 0.000000
09-04-2025 14:22:55000 | -1367202 | 136.7202 | 14090054 | 234765.48 | 338029816 | 99473152 | 50156658 | 0.000000 | 17833508 | 18033406 | 0.000000
09-04-2025 14:23:00000 | -1368300 | 136.83 | 13822449 | 234631.86 | 338420288 | 99493629 | 50123859 | 0.000000 | 18027773 | 18223877 | 0.000000
09-04-2025 14:23:05000 | -1364907 | 136.4907 | 13626063 | 234626.45 | 337550415 | 99505379 | 50113419 | 0.000000 | 18218268 | 18413756 | 0.000000
09-04-2025 14:23:10000 | -1367837 | 136.7837 | 13628643 | 234559.61 | 338368652 | 99507294 | 50089462 | 0.000000 | 18408246 | 18603988 | 0.000000
09-04-2025 14:23:15000 | -1362753 | 136.2753 | 13824890 | 234772.97 | 336865570 | 99489349 | 50133816 | 0.000000 | 18597368 | 18793207 | 0.000000
09-04-2025 14:23:20000 | -1367517 | 136.7517 | 13875701 | 234614.72 | 338275970 | 99489166 | 50138447 | 0.000000 | 18790774 | 18983102 | 0.000000
09-04-2025 14:23:25000 | -1364974 | 136.4974 | 13707771 | 234661.80 | 337542419 | 99499519 | 50094933 | 0.000000 | 18981606 | 19172955 | 0.000000
09-04-2025 14:23:30000 | -1359891 | 135.9891 | 13655969 | 234653.75 | 336298645 | 99499580 | 50099628 | 0.000000 | 19172117 | 19362018 | 0.000000
09-04-2025 14:23:35000 | -1366449 | 136.6449 | 13756494 | 234581.53 | 338025269 | 99497063 | 50084526 | 0.000000 | 19363580 | 19551596 | 0.000000
09-04-2025 14:23:40000 | -1361190 | 136.119 | 13636197 | 234641.95 | 336620209 | 99501961 | 50072113 | 0.000000 | 19551230 | 19740576 | 0.000000
09-04-2025 14:23:45000 | -1363824 | 136.3824 | 13661063 | 234609.05 | 337318756 | 99502068 | 50072536 | 0.000000 | 19740524 | 19929551 | 0.000000
09-04-2025 14:23:50000 | -1359501 | 135.9501 | 13489854 | 234593.98 | 336242035 | 99511314 | 50059528 | 0.000000 | 19930258 | 20118889 | 0.000000
09-04-2025 14:23:55000 | -1363544 | 136.3544 | 13450139 | 234551.58 | 337285248 | 99517021 | 50066833 | 0.000000 | 20117128 | 20308131 | 0.000000
09-04-2025 14:24:00000 | -1361008 | 136.1008 | 13359302 | 234595.27 | 336579620 | 99521706 | 50067245 | 0.000000 | 20302942 | 20497414 | 0.000000
09-04-2025 14:24:05000 | -1360184 | 136.0184 | 13325219 | 234576.28 | 336398102 | 99523560 | 50065449 | 0.000000 | 20489604 | 20686746 | 0.000000
09-04-2025 14:24:10000 | -1363371 | 136.3371 | 13299421 | 234525.19 | 337241852 | 99527588 | 50068130 | 0.000000 | 20673625 | 20875977 | 0.000000
09-04-2025 14:24:15000 | -1364914 | 136.4914 | 13335556 | 234498.20 | 337666138 | 99526100 | 50077110 | 0.000000 | 20858831 | 21065359 | 0.000000
09-04-2025 14:24:20000 | -1363452 | 136.3452 | 13394765 | 234580.39 | 337202484 | 99520897 | 50100765 | 0.000000 | 21044116 | 21254791 | 0.000000
09-04-2025 14:24:25000 | -1369377 | 136.9377 | 14096861 | 234694.94 | 338660034 | 99474304 | 50142246 | 0.000000 | 21235347 | 21444330 | 0.000000
09-04-2025 14:24:30000 | -1368731 | 136.8731 | 13919599 | 234611.66 | 338582062 | 99486862 | 50124710 | 0.000000 | 21430547 | 21634535 | 0.000000
09-04-2025 14:24:35000 | -1364516 | 136.4516 | 13947063 | 234738.86 | 337374359 | 99481689 | 50146008 | 0.000000 | 21622896 | 21824037 | 0.000000
09-04-2025 14:24:40000 | -1370653 | 137.0653 | 14322418 | 234730.00 | 338984741 | 99458488 | 50180817 | 0.000000 | 21819973 | 22013916 | 0.000000
09-04-2025 14:24:45000 | -1368473 | 136.8473 | 14194565 | 234711.50 | 338448090 | 99466354 | 50181007 | 0.000000 | 22018843 | 22204369 | 0.000000
09-04-2025 14:24:50000 | -1368070 | 136.807 | 14141733 | 234664.77 | 338401550 | 99469978 | 50150650 | 0.000000 | 22217251 | 22395088 | 0.000000
09-04-2025 14:24:55000 | -1370280 | 137.028 | 13990821 | 234626.86 | 338961639 | 99482803 | 50114902 | 0.000000 | 22412563 | 22585592 | 0.000000
09-04-2025 14:25:00000 | -1366079 | 136.6079 | 13801086 | 234696.03 | 337786682 | 99493553 | 50127022 | 0.000000 | 22603848 | 22775338 | 0.000000
09-04-2025 14:25:05000 | -1371208 | 137.1208 | 14122927 | 234681.20 | 339138367 | 99473770 | 50133141 | 0.000000 | 22797793 | 22965350 | 0.000000
09-04-2025 14:25:10000 | -1374476 | 137.4476 | 14211188 | 234652.36 | 340002472 | 99469734 | 50129192 | 0.000000 | 22993440 | 23155586 | 0.000000
09-04-2025 14:25:15000 | -1367337 | 136.7337 | 13833832 | 234623.03 | 338200897 | 99492088 | 50084419 | 0.000000 | 23187258 | 23345791 | 0.000000
09-04-2025 14:25:20000 | -1360154 | 136.0154 | 13832688 | 234746.27 | 336267639 | 99486839 | 50113926 | 0.000000 | 23379238 | 23535213 | 0.000000
09-04-2025 14:25:25000 | -1370284 | 137.0284 | 13726697 | 234473.25 | 339117035 | 99501999 | 50080120 | 0.000000 | 23572236 | 23725164 | 0.000000
09-04-2025 14:25:30000 | -1362185 | 136.2185 | 12961095 | 234412.67 | 337035217 | 99550385 | 50030170 | 0.000000 | 23755769 | 23914664 | 0.000000
09-04-2025 14:25:35000 | -1361943 | 136.1943 | 12951887 | 234407.55 | 336982758 | 99550858 | 50005554 | 0.000000 | 23935903 | 24103789 | 0.000000
09-04-2025 14:25:40000 | -1357204 | 135.7204 | 12830574 | 234383.05 | 335832733 | 99556114 | 49981972 | 0.000000 | 24113975 | 24292516 | 0.000000
09-04-2025 14:25:45000 | -1352861 | 135.2861 | 12798361 | 234394.27 | 334735016 | 99555504 | 49980667 | 0.000000 | 24292151 | 24480797 | 0.000000
09-04-2025 14:25:50000 | -1358241 | 135.8241 | 13290088 | 234474.31 | 336055878 | 99524704 | 50004768 | 0.000000 | 24474517 | 24669205 | 0.000000
09-04-2025 14:25:55000 | -1363219 | 136.3219 | 13536885 | 234432.63 | 337397308 | 99510582 | 50032993 | 0.000000 | 24660322 | 24857938 | 0.000000
09-04-2025 14:26:00000 | -1360027 | 136.0027 | 13434346 | 234505.31 | 336489929 | 99515663 | 50052471 | 0.000000 | 24847158 | 25046850 | 0.000000
09-04-2025 14:26:05000 | -1362831 | 136.2831 | 13553082 | 234449.70 | 337279602 | 99509140 | 50065456 | 0.000000 | 25035898 | 25236070 | 0.000000
09-04-2025 14:26:10000 | -1359237 | 135.9237 | 13570889 | 234523.61 | 336302399 | 99505272 | 50066975 | 0.000000 | 25223843 | 25425211 | 0.000000
09-04-2025 14:26:15000 | -1359895 | 135.9895 | 13739161 | 234670.56 | 336289429 | 99493507 | 50094574 | 0.000000 | 25414453 | 25614170 | 0.000000
09-04-2025 14:26:20000 | -1364552 | 136.4552 | 13880395 | 234636.83 | 337514221 | 99486618 | 50102509 | 0.000000 | 25606682 | 25803527 | 0.000000
09-04-2025 14:26:25000 | -1361570 | 136.157 | 13605795 | 234615.31 | 336745850 | 99504433 | 50089642 | 0.000000 | 25796934 | 25992693 | 0.000000
09-04-2025 14:26:30000 | -1357152 | 135.7152 | 13482000 | 234623.16 | 335622375 | 99510193 | 50064590 | 0.000000 | 25986216 | 26181752 | 0.000000
09-04-2025 14:26:35000 | -1354972 | 135.4972 | 13429913 | 234624.28 | 335071930 | 99512390 | 50070683 | 0.000000 | 26173064 | 26370182 | 0.000000
09-04-2025 14:26:40000 | -1354868 | 135.4868 | 13484907 | 234639.22 | 335039459 | 99508347 | 50089924 | 0.000000 | 26360332 | 26558342 | 0.000000
09-04-2025 14:26:45000 | -1353715 | 135.3715 | 13550995 | 234578.47 | 334862122 | 99502708 | 50102615 | 0.000000 | 26548982 | 26746531 | 0.000000
09-04-2025 14:26:50000 | -1352177 | 135.2177 | 13834533 | 234653.45 | 334446045 | 99480675 | 50114304 | 0.000000 | 26739507 | 26934682 | 0.000000
09-04-2025 14:26:55000 | -1359607 | 135.9607 | 14115747 | 234633.77 | 336368652 | 99465363 | 50136559 | 0.000000 | 26932788 | 27122938 | 0.000000
09-04-2025 14:27:00000 | -1356678 | 135.6678 | 14116312 | 234704.53 | 335551239 | 99463028 | 50162560 | 0.000000 | 27127996 | 27311211 | 0.000000
09-04-2025 14:27:05000 | -1363152 | 136.3152 | 14345282 | 234617.89 | 337323334 | 99450829 | 50155762 | 0.000000 | 27325869 | 27500029 | 0.000000
09-04-2025 14:27:10000 | -1357872 | 135.7872 | 13969895 | 234595.17 | 335966492 | 99474945 | 50124569 | 0.000000 | 27521018 | 27688797 | 0.000000
09-04-2025 14:27:15000 | -1353530 | 135.353 | 13771356 | 234580.09 | 334866577 | 99486389 | 50101089 | 0.000000 | 27713972 | 27877248 | 0.000000
09-04-2025 14:27:20000 | -1350765 | 135.0765 | 13710836 | 234725.58 | 333978973 | 99488792 | 50120819 | 0.000000 | 27904058 | 28065188 | 0.000000
09-04-2025 14:27:25000 | -1357727 | 135.7727 | 14059728 | 234612.67 | 335923096 | 99468109 | 50140633 | 0.000000 | 28097188 | 28253199 | 0.000000
09-04-2025 14:27:30000 | -1354006 | 135.4006 | 13811195 | 234680.44 | 334853821 | 99483803 | 50144268 | 0.000000 | 28290010 | 28441318 | 0.000000
09-04-2025 14:27:35000 | -1361886 | 136.1886 | 14259975 | 234684.31 | 336888794 | 99456284 | 50164234 | 0.000000 | 28485496 | 28629713 | 0.000000
09-04-2025 14:27:40000 | -1361474 | 136.1474 | 14035708 | 234650.72 | 336782074 | 99472801 | 50131897 | 0.000000 | 28680366 | 28818568 | 0.000000
09-04-2025 14:27:45000 | -1356693 | 135.6693 | 13854988 | 234746.63 | 335424622 | 99482582 | 50121666 | 0.000000 | 28872708 | 29007158 | 0.000000
09-04-2025 14:27:50000 | -1363294 | 136.3294 | 14041297 | 234652.47 | 337228027 | 99473778 | 50117523 | 0.000000 | 29066643 | 29196084 | 0.000000
09-04-2025 14:27:55000 | -1359523 | 135.9523 | 13883862 | 234691.08 | 336209320 | 99482590 | 50120010 | 0.000000 | 29257720 | 29384369 | 0.000000
09-04-2025 14:28:00000 | -1353653 | 135.3653 | 13674607 | 234716.89 | 334676880 | 99493622 | 50119595 | 0.000000 | 29448716 | 29572986 | 0.000000
09-04-2025 14:28:05000 | -1357811 | 135.7811 | 13750803 | 234624.64 | 335849091 | 99491112 | 50106976 | 0.000000 | 29639878 | 29761826 | 0.000000
09-04-2025 14:28:10000 | -1358068 | 135.8068 | 13628904 | 234611.69 | 335896057 | 99500214 | 50105633 | 0.000000 | 29829229 | 29950295 | 0.000000
09-04-2025 14:28:15000 | -1355316 | 135.5316 | 13745692 | 234598.63 | 335272125 | 99489624 | 50125553 | 0.000000 | 30020210 | 30138697 | 0.000000
09-04-2025 14:28:20000 | -1356029 | 135.6029 | 13757957 | 234637.23 | 335394104 | 99489258 | 50138165 | 0.000000 | 30211174 | 30326992 | 0.000000
09-04-2025 14:28:25000 | -1358021 | 135.8021 | 13665855 | 234593.31 | 335918640 | 99497490 | 50142956 | 0.000000 | 30402766 | 30515553 | 0.000000
09-04-2025 14:28:30000 | -1362207 | 136.2207 | 14213571 | 234727.84 | 336888885 | 99460037 | 50170685 | 0.000000 | 30597656 | 30704342 | 0.000000
09-04-2025 14:28:35000 | -1364205 | 136.4205 | 14249724 | 234737.28 | 337372955 | 99458885 | 50159294 | 0.000000 | 30795264 | 30893730 | 0.000000
09-04-2025 14:28:40000 | -1360682 | 136.0682 | 14126473 | 234783.61 | 336417999 | 99465401 | 50167011 | 0.000000 | 30991467 | 31082863 | 0.000000
09-04-2025 14:28:45000 | -1360451 | 136.0451 | 13999202 | 234688.78 | 336470123 | 99474731 | 50167381 | 0.000000 | 31188735 | 31272416 | 0.000000
09-04-2025 14:28:50000 | -1365740 | 136.574 | 14236021 | 234741.53 | 337742096 | 99461121 | 50160694 | 0.000000 | 31385627 | 31462068 | 0.000000
09-04-2025 14:28:55000 | -1367418 | 136.7418 | 14112996 | 234667.98 | 338231445 | 99471611 | 50162346 | 0.000000 | 31582856 | 31651623 | 0.000000
09-04-2025 14:29:00000 | -1371047 | 137.1047 | 14344072 | 234710.34 | 339121521 | 99457169 | 50162312 | 0.000000 | 31780356 | 31841391 | 0.000000
09-04-2025 14:29:05000 | -1369045 | 136.9045 | 14092014 | 234669.69 | 338618530 | 99474411 | 50143246 | 0.000000 | 31976377 | 32031244 | 0.000000
09-04-2025 14:29:10000 | -1365283 | 136.5283 | 14011406 | 234662.08 | 337689178 | 99477516 | 50127140 | 0.000000 | 32171450 | 32220588 | 0.000000
09-04-2025 14:29:15000 | -1364244 | 136.4244 | 13828130 | 234609.25 | 337461365 | 99490219 | 50104610 | 0.000000 | 32364954 | 32410127 | 0.000000
09-04-2025 14:29:20000 | -1361535 | 136.1535 | 13923323 | 234669.00 | 336743805 | 99481194 | 50094189 | 0.000000 | 32558428 | 32599318 | 0.000000
09-04-2025 14:29:25000 | -1359256 | 135.9256 | 13534128 | 234447.27 | 336409088 | 99507942 | 50052788 | 0.000000 | 32749761 | 32788582 | 0.000000
09-04-2025 14:29:30000 | -1356650 | 135.665 | 13579397 | 234520.72 | 335677429 | 99502785 | 50071270 | 0.000000 | 32938201 | 32977121 | 0.000000
09-04-2025 14:29:35000 | -1361332 | 136.1332 | 13594743 | 234524.53 | 336813995 | 99505066 | 50079662 | 0.000000 | 33127231 | 33165852 | 0.000000
09-04-2025 14:29:40000 | -1356855 | 135.6855 | 13221630 | 234515.34 | 335640930 | 99528595 | 50052036 | 0.000000 | 33313450 | 33354703 | 0.000000
09-04-2025 14:29:45000 | -1353839 | 135.3839 | 13300968 | 234589.56 | 334813751 | 99520851 | 50057297 | 0.000000 | 33497744 | 33543105 | 0.000000
09-04-2025 14:29:50000 | -1361394 | 136.1394 | 13661336 | 234616.03 | 336712524 | 99500282 | 50083412 | 0.000000 | 33685305 | 33731500 | 0.000000
09-04-2025 14:29:55000 | -1359933 | 135.9933 | 13520149 | 234589.64 | 336359009 | 99509438 | 50070385 | 0.000000 | 33873960 | 33920535 | 0.000000
09-04-2025 14:30:00000 | -1355645 | 135.5645 | 13348403 | 234591.80 | 335268738 | 99518723 | 50071957 | 0.000000 | 34061289 | 34109242 | 0.000000
09-04-2025 14:30:05000 | -1354545 | 135.4545 | 13424674 | 234623.27 | 334969116 | 99512466 | 50085480 | 0.000000 | 18670868 | 188314178 | 0.000000
09-04-2025 14:30:10000 | -1357444 | 135.7444 | 13374631 | 234558.63 | 335760651 | 99518120 | 50072243 | 0.000000 | 37429787 | 376976013 | 0.000000
09-04-2025 14:30:15000 | -1358340 | 135.834 | 13712239 | 234657.23 | 335930328 | 99494331 | 50079704 | 0.000000 | 56252159 | 565481262 | 0.000000
09-04-2025 14:30:20000 | -1367138 | 136.7138 | 13832395 | 234564.30 | 338236053 | 99492050 | 50069744 | 0.000000 | 75247452 | 754331787 | 0.000000
09-04-2025 14:30:25000 | -1360105 | 136.0105 | 13484758 | 234598.47 | 336380737 | 99512108 | 50037136 | 0.000000 | 94056076 | 943333862 | 0.000000
09-04-2025 14:30:30000 | -1360384 | 136.0384 | 13194842 | 234490.83 | 336535034 | 99532906 | 50006760 | 0.000000 | 112619118 | 11324319 | 0.000000
09-04-2025 14:30:35000 | -1359948 | 135.9948 | 13160929 | 234485.34 | 336425323 | 99534988 | 50007885 | 0.000000 | 130867554 | 13210662 | 0.000000
09-04-2025 14:30:40000 | -1357127 | 135.7127 | 13086941 | 234528.63 | 335656738 | 99538269 | 50016369 | 0.000000 | 149004959 | 15095336 | 0.000000
09-04-2025 14:30:45000 | -1353023 | 135.3023 | 13143097 | 234569.06 | 334605927 | 99531517 | 50039108 | 0.000000 | 167249893 | 16976793 | 0.000000
09-04-2025 14:30:50000 | -1360315 | 136.0315 | 13334735 | 234497.25 | 336544495 | 99522972 | 50043198 | 0.000000 | 185761520 | 18861211 | 0.000000
09-04-2025 14:30:55000 | -1357129 | 135.7129 | 13037408 | 234478.78 | 335718658 | 99541733 | 50027584 | 0.000000 | 204035202 | 20749675 | 0.000000
09-04-2025 14:31:00000 | -1360778 | 136.0778 | 13049918 | 234471.42 | 336626343 | 99543304 | 50026180 | 0.000000 | 222114243 | 22637175 | 0.000000
09-04-2025 14:31:05000 | -1360131 | 136.0131 | 13032572 | 234467.52 | 336465393 | 99544075 | 49985874 | 0.000000 | 240226898 | 24527336 | 0.000000
09-04-2025 14:31:10000 | -1358464 | 135.8464 | 12777158 | 234435.70 | 336043365 | 99560585 | 49962997 | 0.000000 | 258123962 | 26415200 | 0.000000
09-04-2025 14:31:15000 | -1356637 | 135.6637 | 12825639 | 234467.44 | 335565735 | 99556084 | 49955856 | 0.000000 | 275886169 | 28302119 | 0.000000
09-04-2025 14:31:20000 | -1351919 | 135.1919 | 12666140 | 234513.38 | 334301636 | 99563980 | 49976757 | 0.000000 | 293494934 | 30182678 | 0.000000
09-04-2025 14:31:25000 | -1354538 | 135.4538 | 12952452 | 234482.80 | 335054993 | 99545929 | 50006126 | 0.000000 | 311518372 | 32065286 | 0.000000
09-04-2025 14:31:30000 | -1356000 | 135.6 | 12764232 | 234440.17 | 335431366 | 99559883 | 50016350 | 0.000000 | 329474274 | 33951797 | 0.000000
09-04-2025 14:31:35000 | -1360880 | 136.088 | 12868458 | 234465.77 | 336614990 | 99555901 | 50028511 | 0.000000 | 347315918 | 35839172 | 0.000000
09-04-2025 14:31:40000 | -1357741 | 135.7741 | 12739984 | 234398.44 | 335913086 | 99562660 | 50000721 | 0.000000 | 365194183 | 37729959 | 0.000000
09-04-2025 14:31:45000 | -1359298 | 135.9298 | 12777970 | 234410.16 | 336289001 | 99561066 | 49980061 | 0.000000 | 383125031 | 39621328 | 0.000000
09-04-2025 14:31:50000 | -1359221 | 135.9221 | 12774074 | 234438.75 | 336227020 | 99561287 | 49975502 | 0.000000 | 400816254 | 41509658 | 0.000000
09-04-2025 14:31:55000 | -1356549 | 135.6549 | 12793233 | 234497.09 | 335498169 | 99558250 | 49992245 | 0.000000 | 418655243 | 43398311 | 0.000000
09-04-2025 14:32:00000 | -1364050 | 136.405 | 13233650 | 234491.31 | 337449280 | 99532677 | 50024689 | 0.000000 | 436898438 | 45288496 | 0.000000
09-04-2025 14:32:05000 | -1362326 | 136.2326 | 12998238 | 234471.17 | 336997803 | 99547913 | 50010574 | 0.000000 | 455111969 | 47183848 | 0.000000
09-04-2025 14:32:10000 | -1364477 | 136.4477 | 12951964 | 234420.73 | 337579956 | 99552505 | 49997257 | 0.000000 | 473243530 | 49079614 | 0.000000
09-04-2025 14:32:15000 | -1363391 | 136.3391 | 13067813 | 234523.83 | 337204620 | 99543800 | 49999783 | 0.000000 | 491267975 | 50973096 | 0.000000
09-04-2025 14:32:20000 | -1362613 | 136.2613 | 13062208 | 234479.09 | 337063782 | 99543671 | 50000317 | 0.000000 | 509473877 | 52865996 | 0.000000
09-04-2025 14:32:25000 | -1362531 | 136.2531 | 13102385 | 234442.94 | 337110901 | 99540825 | 49988430 | 0.000000 | 527731567 | 54760356 | 0.000000
09-04-2025 14:32:30000 | -1360688 | 136.0688 | 12957334 | 234470.44 | 336590759 | 99549660 | 49973122 | 0.000000 | 545811768 | 56652446 | 0.000000
09-04-2025 14:32:35000 | -1359448 | 135.9448 | 12871725 | 234500.08 | 336217163 | 99554741 | 49973083 | 0.000000 | 563581116 | 58538589 | 0.000000
09-04-2025 14:32:40000 | -1362911 | 136.2911 | 13063443 | 234471.78 | 337168396 | 99543785 | 49971066 | 0.000000 | 581731140 | 60431689 | 0.000000
09-04-2025 14:32:45000 | -1366224 | 136.6224 | 12937889 | 234388.67 | 338051910 | 99554604 | 49960133 | 0.000000 | 599786804 | 62325991 | 0.000000
09-04-2025 14:32:50000 | -1364147 | 136.4147 | 12765306 | 234384.64 | 337511261 | 99565018 | 49938229 | 0.000000 | 617489868 | 64218521 | 0.000000
09-04-2025 14:32:55000 | -1357870 | 135.787 | 12591661 | 234406.94 | 335899872 | 99572800 | 49926304 | 0.000000 | 635069763 | 66109824 | 0.000000
09-04-2025 14:33:00000 | -1360463 | 136.0463 | 12452118 | 234330.09 | 336615448 | 99583740 | 49909908 | 0.000000 | 652510132 | 68001172 | 0.000000
09-04-2025 14:33:05000 | -1356335 | 135.6335 | 12354762 | 234379.22 | 335513245 | 99587700 | 49920170 | 0.000000 | 669668701 | 69887134 | 0.000000
09-04-2025 14:33:10000 | -1364601 | 136.4601 | 12512417 | 234294.98 | 337700867 | 99582253 | 49909153 | 0.000000 | 687078918 | 71778188 | 0.000000
09-04-2025 14:33:15000 | -1356800 | 135.68 | 12472912 | 234386.20 | 335640320 | 99580116 | 49895409 | 0.000000 | 704416199 | 73666704 | 0.000000
09-04-2025 14:33:20000 | -1357902 | 135.7902 | 12601381 | 234404.81 | 335918091 | 99572166 | 49944592 | 0.000000 | 721752869 | 75550645 | 0.000000
09-04-2025 14:33:25000 | -1355798 | 135.5798 | 12501775 | 234352.08 | 335448792 | 99577560 | 49943150 | 0.000000 | 739287415 | 77438794 | 0.000000
09-04-2025 14:33:30000 | -1356888 | 135.6888 | 12300000 | 234295.30 | 335753174 | 99591660 | 49895603 | 0.000000 | 756746216 | 79331646 | 0.000000
09-04-2025 14:33:35000 | -1353643 | 135.3643 | 12280242 | 234393.52 | 334810425 | 99591019 | 49914772 | 0.000000 | 773762329 | 81213530 | 0.000000
09-04-2025 14:33:40000 | -1359163 | 135.9163 | 12678318 | 234402.30 | 336244568 | 99567757 | 49945198 | 0.000000 | 791312561 | 83100010 | 0.000000
09-04-2025 14:33:45000 | -1361284 | 136.1284 | 12776729 | 234398.19 | 336789124 | 99562424 | 49951710 | 0.000000 | 808953918 | 84987725 | 0.000000
09-04-2025 14:33:50000 | -1359186 | 135.9186 | 12838731 | 234424.83 | 336252075 | 99556839 | 49975197 | 0.000000 | 826689758 | 86874463 | 0.000000
09-04-2025 14:33:55000 | -1363501 | 136.3501 | 12925538 | 234364.72 | 337415924 | 99553688 | 49960266 | 0.000000 | 844660706 | 88766670 | 0.000000
09-04-2025 14:34:00000 | -1363973 | 136.3973 | 12781203 | 234370.58 | 337490906 | 99563835 | 49934589 | 0.000000 | 862399475 | 90659727 | 0.000000
09-04-2025 14:34:05000 | -1361196 | 136.1196 | 12524978 | 234363.72 | 336759979 | 99579338 | 49941032 | 0.000000 | 879804138 | 92546035 | 0.000000
09-04-2025 14:34:10000 | -1359292 | 135.9292 | 12923161 | 234500.05 | 336195435 | 99551102 | 49964561 | 0.000000 | 897469910 | 94432793 | 0.000000
09-04-2025 14:34:15000 | -1363347 | 136.3347 | 12988094 | 234401.94 | 337341461 | 99549286 | 49966022 | 0.000000 | 915441040 | 96321924 | 0.000000
09-04-2025 14:34:20000 | -1362374 | 136.2374 | 12666966 | 234355.09 | 337099548 | 99570541 | 49937870 | 0.000000 | 933240845 | 98213984 | 0.000000
09-04-2025 14:34:25000 | -1358510 | 135.851 | 12590500 | 234380.84 | 336096741 | 99573280 | 49934303 | 0.000000 | 950749084 | 10010227 | 0.000000
09-04-2025 14:34:30000 | -1363102 | 136.3102 | 12775054 | 234371.39 | 337276855 | 99563698 | 49933422 | 0.000000 | 968428955 | 10199255 | 0.000000
09-04-2025 14:34:35000 | -1359131 | 135.9131 | 12425457 | 234349.28 | 336253693 | 99584702 | 49917561 | 0.000000 | 985883240 | 10388188 | 0.000000
09-04-2025 14:34:40000 | -1353747 | 135.3747 | 12535276 | 234446.28 | 334818298 | 99574028 | 49939590 | 0.000000 | 10031951 | 10576587 | 0.000000
09-04-2025 14:34:45000 | -1359952 | 135.9952 | 12984756 | 234440.94 | 336454773 | 99547279 | 49979889 | 0.000000 | 10209576 | 10765193 | 0.000000
09-04-2025 14:34:50000 | -1358198 | 135.8198 | 12824555 | 234452.84 | 335967072 | 99557175 | 49973095 | 0.000000 | 10389255 | 10954162 | 0.000000
09-04-2025 14:34:55000 | -1358221 | 135.8221 | 12811658 | 234472.59 | 335939514 | 99558067 | 49983898 | 0.000000 | 10568400 | 11143180 | 0.000000
09-04-2025 14:35:00000 | -1368719 | 136.8719 | 13240423 | 234446.16 | 338657990 | 99535370 | 49998035 | 0.000000 | 10749495 | 11332439 | 0.000000
09-04-2025 14:35:05000 | -1367379 | 136.7379 | 13147569 | 234442.73 | 338307739 | 99540924 | 49982407 | 0.000000 | 10931121 | 11521933 | 0.000000
09-04-2025 14:35:10000 | -1363213 | 136.3213 | 13071981 | 234448.38 | 337267761 | 99543396 | 49971897 | 0.000000 | 11112267 | 11711272 | 0.000000
09-04-2025 14:35:15000 | -1361919 | 136.1919 | 12877521 | 234210.03 | 337250977 | 99555954 | 49950745 | 0.000000 | 11292590 | 11900469 | 0.000000
09-04-2025 14:35:20000 | -1355210 | 135.521 | 12731593 | 234273.13 | 335469574 | 99561615 | 49956860 | 0.000000 | 11470140 | 12088949 | 0.000000
09-04-2025 14:35:25000 | -1357411 | 135.7411 | 12989339 | 234309.47 | 336018311 | 99545273 | 49970638 | 0.000000 | 11650597 | 12277820 | 0.000000
09-04-2025 14:35:30000 | -1359617 | 135.9617 | 13262890 | 234351.94 | 336564301 | 99527580 | 49996178 | 0.000000 | 11832568 | 12466574 | 0.000000
09-04-2025 14:35:35000 | -1361366 | 136.1366 | 13146935 | 234282.63 | 337063782 | 99536934 | 50002651 | 0.000000 | 12014945 | 12655304 | 0.000000
09-04-2025 14:35:40000 | -1363466 | 136.3466 | 12998127 | 234213.47 | 337652191 | 99548668 | 49966873 | 0.000000 | 12196577 | 12844648 | 0.000000
09-04-2025 14:35:45000 | -1361830 | 136.183 | 12827864 | 234206.64 | 337212799 | 99559288 | 49940483 | 0.000000 | 12374875 | 13033884 | 0.000000
09-04-2025 14:35:50000 | -1357288 | 135.7288 | 12759758 | 234270.59 | 335994812 | 99561020 | 49943382 | 0.000000 | 12552555 | 13222816 | 0.000000
09-04-2025 14:35:55000 | -1361305 | 136.1305 | 12835063 | 234211.27 | 337081604 | 99558456 | 49927391 | 0.000000 | 12731736 | 13412172 | 0.000000
09-04-2025 14:36:00000 | -1361518 | 136.1518 | 12849062 | 234175.16 | 337186646 | 99557640 | 49926880 | 0.000000 | 12909423 | 13601173 | 0.000000
09-04-2025 14:36:05000 | -1358977 | 135.8977 | 12853352 | 234182.72 | 336559601 | 99555702 | 49944061 | 0.000000 | 13089186 | 13790193 | 0.000000
09-04-2025 14:36:10000 | -1361120 | 136.112 | 12846868 | 234226.42 | 337019745 | 99557533 | 49937981 | 0.000000 | 13268064 | 13979414 | 0.000000
09-04-2025 14:36:15000 | -1364024 | 136.4024 | 12988645 | 234228.59 | 337759766 | 99549690 | 49951653 | 0.000000 | 13447511 | 14168541 | 0.000000
09-04-2025 14:36:20000 | -1359604 | 135.9604 | 12838549 | 234228.25 | 336643372 | 99557121 | 49949783 | 0.000000 | 13626589 | 14357736 | 0.000000
09-04-2025 14:36:25000 | -1360604 | 136.0604 | 13001437 | 234268.41 | 336868713 | 99546555 | 49951736 | 0.000000 | 13806942 | 14546854 | 0.000000
09-04-2025 14:36:30000 | -1360080 | 136.008 | 12944260 | 234254.45 | 336739288 | 99550163 | 49942783 | 0.000000 | 13987457 | 14735925 | 0.000000
09-04-2025 14:36:35000 | -1354263 | 135.4263 | 12962615 | 234268.14 | 335300781 | 99545036 | 49965275 | 0.000000 | 14166702 | 14924208 | 0.000000
09-04-2025 14:36:40000 | -1359195 | 135.9195 | 13299913 | 234340.64 | 336485016 | 99524666 | 49988731 | 0.000000 | 14349420 | 15112525 | 0.000000
09-04-2025 14:36:45000 | -1360738 | 136.0738 | 13433769 | 234373.56 | 336850464 | 99516212 | 49996334 | 0.000000 | 14534165 | 15300990 | 0.000000
09-04-2025 14:36:50000 | -1354283 | 135.4283 | 13177443 | 234302.84 | 335309937 | 99529953 | 49992527 | 0.000000 | 14719547 | 15489631 | 0.000000
09-04-2025 14:36:55000 | -1351719 | 135.1719 | 13097939 | 234355.39 | 334583191 | 99533813 | 49981049 | 0.000000 | 14902408 | 15677797 | 0.000000
09-04-2025 14:37:00000 | -1356151 | 135.6151 | 13295087 | 234236.42 | 335887085 | 99522888 | 49997078 | 0.000000 | 15085707 | 15865826 | 0.000000
09-04-2025 14:37:05000 | -1356001 | 135.6001 | 13160001 | 234197.13 | 335874969 | 99532364 | 49973812 | 0.000000 | 15269366 | 16054245 | 0.000000
09-04-2025 14:37:10000 | -1356182 | 135.6182 | 13095727 | 234285.09 | 335782623 | 99537010 | 49975464 | 0.000000 | 15450525 | 16242456 | 0.000000
09-04-2025 14:37:15000 | -1352533 | 135.2533 | 13259604 | 234397.69 | 334762329 | 99522888 | 50010017 | 0.000000 | 15633948 | 16430412 | 0.000000
09-04-2025 14:37:20000 | -1352569 | 135.2569 | 13909817 | 234643.09 | 334579346 | 99475357 | 50074162 | 0.000000 | 15822844 | 16618416 | 0.000000
09-04-2025 14:37:25000 | -1364457 | 136.4457 | 14384816 | 234483.92 | 337838287 | 99448868 | 50096653 | 0.000000 | 16020577 | 16807277 | 0.000000
09-04-2025 14:37:30000 | -1360574 | 136.0574 | 13785679 | 234349.98 | 336928009 | 99490608 | 50055885 | 0.000000 | 16216069 | 16996332 | 0.000000
09-04-2025 14:37:35000 | -1360195 | 136.0195 | 13776283 | 234344.53 | 336839752 | 99491013 | 50043251 | 0.000000 | 16406849 | 17185178 | 0.000000
09-04-2025 14:37:40000 | -1358985 | 135.8985 | 13855547 | 234396.92 | 336490417 | 99484276 | 50033607 | 0.000000 | 16599215 | 17373904 | 0.000000
09-04-2025 14:37:45000 | -1355136 | 135.5136 | 13880303 | 234670.19 | 335161102 | 99479523 | 50063141 | 0.000000 | 16791345 | 17562268 | 0.000000
09-04-2025 14:37:50000 | -1360071 | 136.0071 | 14020105 | 234633.75 | 336453918 | 99472885 | 50080803 | 0.000000 | 16986252 | 17751156 | 0.000000
09-04-2025 14:37:55000 | -1362405 | 136.2405 | 14159286 | 234646.66 | 337052032 | 99464279 | 50107292 | 0.000000 | 17180607 | 17939785 | 0.000000
09-04-2025 14:38:00000 | -1360483 | 136.0483 | 13997135 | 234541.47 | 336683502 | 99474915 | 50079609 | 0.000000 | 17376053 | 18128627 | 0.000000
09-04-2025 14:38:05000 | -1351996 | 135.1996 | 13503120 | 234522.47 | 334507690 | 99504944 | 50043293 | 0.000000 | 17567520 | 18317117 | 0.000000
09-04-2025 14:38:10000 | -1357279 | 135.7279 | 13739646 | 234511.95 | 335877838 | 99491539 | 50042057 | 0.000000 | 17755756 | 18505006 | 0.000000
09-04-2025 14:38:15000 | -1353415 | 135.3415 | 13572842 | 234452.61 | 334974701 | 99500900 | 50003635 | 0.000000 | 17945731 | 18693250 | 0.000000
09-04-2025 14:38:20000 | -1353427 | 135.3427 | 13671399 | 234487.83 | 334950500 | 99493690 | 50018093 | 0.000000 | 18135338 | 18881252 | 0.000000
09-04-2025 14:38:25000 | -1352074 | 135.2074 | 13608952 | 234506.72 | 334585449 | 99497269 | 50027889 | 0.000000 | 18323461 | 19068902 | 0.000000
09-04-2025 14:38:30000 | -1353689 | 135.3689 | 13713369 | 234503.25 | 335009460 | 99490791 | 50040394 | 0.000000 | 18512692 | 19256570 | 0.000000
09-04-2025 14:38:35000 | -1355881 | 135.5881 | 13693586 | 234481.34 | 335571442 | 99493881 | 50036682 | 0.000000 | 18702753 | 19444621 | 0.000000
09-04-2025 14:38:40000 | -1359234 | 135.9234 | 13792606 | 234452.95 | 336459778 | 99489098 | 50033070 | 0.000000 | 18893110 | 19632793 | 0.000000
09-04-2025 14:38:45000 | -1353055 | 135.3055 | 13509212 | 234446.30 | 334877045 | 99505272 | 50005116 | 0.000000 | 19082297 | 19821008 | 0.000000
09-04-2025 14:38:50000 | -1353658 | 135.3658 | 13721453 | 234532.34 | 334955414 | 99490173 | 50033688 | 0.000000 | 19272041 | 20008990 | 0.000000
09-04-2025 14:38:55000 | -1355393 | 135.5393 | 13681452 | 234541.09 | 335364410 | 99494408 | 50054337 | 0.000000 | 19462224 | 20197223 | 0.000000
09-04-2025 14:39:00000 | -1358781 | 135.8781 | 13726844 | 234480.14 | 336286194 | 99493591 | 50025169 | 0.000000 | 19653292 | 20385902 | 0.000000
09-04-2025 14:39:05000 | -1360969 | 136.0969 | 13774882 | 234483.39 | 336835571 | 99491692 | 50013878 | 0.000000 | 19843735 | 20574582 | 0.000000
09-04-2025 14:39:10000 | -1355341 | 135.5341 | 13578095 | 234481.03 | 335405701 | 99501923 | 50009098 | 0.000000 | 20033057 | 20762869 | 0.000000
09-04-2025 14:39:15000 | -1351954 | 135.1954 | 13744744 | 234593.58 | 334459503 | 99487175 | 50047874 | 0.000000 | 20223058 | 20950918 | 0.000000
09-04-2025 14:39:20000 | -1354820 | 135.482 | 13834442 | 234517.81 | 335296936 | 99482689 | 50063099 | 0.000000 | 20416765 | 21139434 | 0.000000
09-04-2025 14:39:25000 | -1360935 | 136.0935 | 13897665 | 234501.91 | 336824890 | 99482635 | 50044857 | 0.000000 | 20610046 | 21328244 | 0.000000
09-04-2025 14:39:30000 | -1356153 | 135.6153 | 13494622 | 234483.91 | 335579346 | 99508568 | 50024025 | 0.000000 | 20800828 | 21517053 | 0.000000
09-04-2025 14:39:35000 | -1361670 | 136.167 | 13811962 | 234473.86 | 337022186 | 99489494 | 50011387 | 0.000000 | 20991592 | 21705924 | 0.000000
09-04-2025 14:39:40000 | -1356057 | 135.6057 | 13528078 | 234497.69 | 335545868 | 99506073 | 50008717 | 0.000000 | 21180208 | 21894516 | 0.000000
09-04-2025 14:39:45000 | -1354569 | 135.4569 | 13475978 | 234513.97 | 335142853 | 99508774 | 50000530 | 0.000000 | 21367922 | 22082928 | 0.000000
09-04-2025 14:39:50000 | -1354794 | 135.4794 | 13611881 | 234536.88 | 335200317 | 99499062 | 50013000 | 0.000000 | 21556499 | 22271258 | 0.000000
09-04-2025 14:39:55000 | -1357746 | 135.7746 | 13744049 | 234542.13 | 335953644 | 99491562 | 50032516 | 0.000000 | 21745469 | 22459375 | 0.000000
09-04-2025 14:40:00000 | -1358149 | 135.8149 | 13826642 | 234524.30 | 336099060 | 99485779 | 50021542 | 0.000000 | 21937388 | 22648137 | 0.000000
09-04-2025 14:40:05000 | -1359607 | 135.9607 | 13689853 | 234507.88 | 336438385 | 99496902 | 50015453 | 0.000000 | 22128010 | 22836834 | 0.000000
09-04-2025 14:40:10000 | -1358173 | 135.8173 | 13711047 | 234540.84 | 336048859 | 99494293 | 50026836 | 0.000000 | 22316912 | 23025316 | 0.000000
09-04-2025 14:40:15000 | -1361365 | 136.1365 | 13882313 | 234565.48 | 336844086 | 99484093 | 50042942 | 0.000000 | 22508804 | 23213984 | 0.000000
09-04-2025 14:40:20000 | -1356363 | 135.6363 | 13717394 | 234529.83 | 335623718 | 99492493 | 50027576 | 0.000000 | 22700283 | 23402682 | 0.000000
09-04-2025 14:40:25000 | -1351631 | 135.1631 | 13770731 | 234626.14 | 334343628 | 99485008 | 50047623 | 0.000000 | 22891387 | 23590736 | 0.000000
09-04-2025 14:40:30000 | -1360645 | 136.0645 | 14184723 | 234581.44 | 336712280 | 99460983 | 50059483 | 0.000000 | 23086917 | 23779260 | 0.000000
09-04-2025 14:40:35000 | -1359757 | 135.9757 | 14143757 | 234596.52 | 336463348 | 99463379 | 50061218 | 0.000000 | 23283259 | 23968004 | 0.000000
09-04-2025 14:40:40000 | -1356741 | 135.6741 | 13973876 | 234550.98 | 335750153 | 99473778 | 50048603 | 0.000000 | 23478215 | 24156701 | 0.000000
09-04-2025 14:40:45000 | -1359408 | 135.9408 | 13940949 | 234480.25 | 336494629 | 99478271 | 50037361 | 0.000000 | 23672922 | 24345563 | 0.000000
09-04-2025 14:40:50000 | -1361015 | 136.1015 | 13864248 | 234495.59 | 336846436 | 99485161 | 50024342 | 0.000000 | 23865007 | 24534357 | 0.000000
09-04-2025 14:40:55000 | -1361208 | 136.1208 | 13732486 | 234445.11 | 336931335 | 99494965 | 50019672 | 0.000000 | 24055645 | 24723137 | 0.000000
09-04-2025 14:41:00000 | -1360761 | 136.0761 | 13738610 | 234491.61 | 336756744 | 99494194 | 50018379 | 0.000000 | 24245378 | 24911854 | 0.000000
09-04-2025 14:41:05000 | -1358767 | 135.8767 | 13399740 | 234422.72 | 336291077 | 99517250 | 49988762 | 0.000000 | 24432749 | 25100775 | 0.000000
09-04-2025 14:41:10000 | -1352390 | 135.239 | 13343007 | 234521.52 | 334575317 | 99516808 | 49985016 | 0.000000 | 24618071 | 25288988 | 0.000000
09-04-2025 14:41:15000 | -1353891 | 135.3891 | 13688040 | 234542.95 | 334987183 | 99492805 | 50008366 | 0.000000 | 24805854 | 25476850 | 0.000000
09-04-2025 14:41:20000 | -1356329 | 135.6329 | 13698499 | 234464.84 | 335698700 | 99493851 | 50024033 | 0.000000 | 24994973 | 25664861 | 0.000000
09-04-2025 14:41:25000 | -1352479 | 135.2479 | 13577893 | 234452.94 | 334746704 | 99499847 | 50023750 | 0.000000 | 25183987 | 25852791 | 0.000000
09-04-2025 14:41:30000 | -1356338 | 135.6338 | 13776969 | 234558.55 | 335586517 | 99488083 | 50030956 | 0.000000 | 25374697 | 26040920 | 0.000000
09-04-2025 14:41:35000 | -1350514 | 135.0514 | 13537583 | 234605.42 | 334035828 | 99501350 | 50026917 | 0.000000 | 25563989 | 26228932 | 0.000000
09-04-2025 14:41:40000 | -1356441 | 135.6441 | 13876299 | 234621.91 | 335547180 | 99480812 | 50054722 | 0.000000 | 25754888 | 26416867 | 0.000000
09-04-2025 14:41:45000 | -1354321 | 135.4321 | 13678868 | 234578.80 | 335042053 | 99493805 | 50034298 | 0.000000 | 25947585 | 26605357 | 0.000000
09-04-2025 14:41:50000 | -1352850 | 135.285 | 13653726 | 234577.02 | 334677704 | 99494560 | 50032677 | 0.000000 | 26137283 | 26793166 | 0.000000
09-04-2025 14:41:55000 | -1358323 | 135.8323 | 13618123 | 234529.39 | 336080109 | 99501183 | 50025688 | 0.000000 | 26326372 | 26981262 | 0.000000
09-04-2025 14:42:00000 | -1356390 | 135.639 | 13518151 | 234472.91 | 335663544 | 99507034 | 49989555 | 0.000000 | 26514712 | 27169586 | 0.000000
09-04-2025 14:42:05000 | -1348573 | 134.8573 | 13281106 | 234534.83 | 333601288 | 99518555 | 49977062 | 0.000000 | 26700398 | 27357340 | 0.000000
09-04-2025 14:42:10000 | -1352090 | 135.209 | 13475790 | 234520.98 | 334527679 | 99507004 | 49995369 | 0.000000 | 26885762 | 27544805 | 0.000000
09-04-2025 14:42:15000 | -1353963 | 135.3963 | 13265529 | 234432.00 | 335062988 | 99523468 | 49957218 | 0.000000 | 27071885 | 27732939 | 0.000000
09-04-2025 14:42:20000 | -1353287 | 135.3287 | 13205806 | 234467.94 | 334831146 | 99527252 | 49947350 | 0.000000 | 27255115 | 27920945 | 0.000000
09-04-2025 14:42:25000 | -1350779 | 135.0779 | 13307965 | 234373.70 | 334378723 | 99518188 | 49965370 | 0.000000 | 27437913 | 28108434 | 0.000000
09-04-2025 14:42:30000 | -1352076 | 135.2076 | 13156737 | 234402.00 | 334618011 | 99529900 | 49967747 | 0.000000 | 27621980 | 28296125 | 0.000000
09-04-2025 14:42:35000 | -1356546 | 135.6546 | 12692110 | 234184.86 | 335917236 | 99565163 | 49912964 | 0.000000 | 27802529 | 28484467 | 0.000000
09-04-2025 14:42:40000 | -1348718 | 134.8718 | 12208732 | 234227.84 | 333825684 | 99592796 | 49885303 | 0.000000 | 27974233 | 28672209 | 0.000000
09-04-2025 14:42:45000 | -1344611 | 134.4611 | 12397100 | 234325.06 | 332724487 | 99577667 | 49935947 | 0.000000 | 28145081 | 28858912 | 0.000000
09-04-2025 14:42:50000 | -1348600 | 134.86 | 12609143 | 234301.05 | 333779602 | 99565750 | 49938019 | 0.000000 | 28319639 | 29046256 | 0.000000
09-04-2025 14:42:55000 | -1355626 | 135.5626 | 12709197 | 234254.92 | 335594635 | 99563408 | 49923267 | 0.000000 | 28495710 | 29234037 | 0.000000
09-04-2025 14:43:00000 | -1351252 | 135.1252 | 12736932 | 234368.11 | 334364075 | 99558685 | 49933559 | 0.000000 | 28671814 | 29421830 | 0.000000
09-04-2025 14:43:05000 | -1351978 | 135.1978 | 12926048 | 234373.77 | 334584076 | 99546059 | 49964993 | 0.000000 | 28850566 | 29609582 | 0.000000
09-04-2025 14:43:10000 | -1355923 | 135.5923 | 13229411 | 234438.05 | 335529114 | 99527397 | 49993027 | 0.000000 | 29032195 | 29797428 | 0.000000
09-04-2025 14:43:15000 | -1356064 | 135.6064 | 13041859 | 234351.47 | 335656494 | 99540710 | 49958927 | 0.000000 | 29215386 | 29986221 | 0.000000
09-04-2025 14:43:20000 | -1353724 | 135.3724 | 12888787 | 234540.33 | 334768402 | 99549812 | 49957485 | 0.000000 | 29393491 | 30174424 | 0.000000
09-04-2025 14:43:25000 | -1353722 | 135.3722 | 13240681 | 234595.30 | 334768463 | 99525070 | 50018509 | 0.000000 | 29574656 | 30362010 | 0.000000
09-04-2025 14:43:30000 | -1355327 | 135.5327 | 13369243 | 234520.47 | 335300110 | 99517006 | 50013462 | 0.000000 | 29760815 | 30550408 | 0.000000
09-04-2025 14:43:35000 | -1355127 | 135.5127 | 13467632 | 234600.75 | 335159271 | 99509781 | 50028076 | 0.000000 | 29946311 | 30738645 | 0.000000
09-04-2025 14:43:40000 | -1363271 | 136.3271 | 13617008 | 234518.86 | 337308411 | 99504852 | 50016178 | 0.000000 | 30134871 | 30927322 | 0.000000
09-04-2025 14:43:45000 | -1355813 | 135.5813 | 12968375 | 234443.92 | 335428650 | 99545670 | 49956028 | 0.000000 | 30318145 | 31116025 | 0.000000
09-04-2025 14:43:50000 | -1351711 | 135.1711 | 12866609 | 234496.70 | 334323761 | 99550018 | 49965927 | 0.000000 | 30497021 | 31303789 | 0.000000
09-04-2025 14:43:55000 | -1350850 | 135.085 | 13197226 | 234583.88 | 334064789 | 99526169 | 50003277 | 0.000000 | 30678650 | 31491266 | 0.000000
09-04-2025 14:44:00000 | -1354878 | 135.4878 | 13365990 | 234434.00 | 335311981 | 99516922 | 50019897 | 0.000000 | 30862947 | 31679266 | 0.000000
09-04-2025 14:44:05000 | -1360762 | 136.0762 | 13131354 | 234376.09 | 336783508 | 99537613 | 50010468 | 0.000000 | 31047891 | 31867863 | 0.000000
09-04-2025 14:44:10000 | -1357048 | 135.7048 | 13110104 | 234362.56 | 335880249 | 99536591 | 49996376 | 0.000000 | 31228335 | 32056141 | 0.000000
09-04-2025 14:44:15000 | -1350294 | 135.0294 | 12864555 | 234374.36 | 334148529 | 99549225 | 49969864 | 0.000000 | 31409956 | 32244602 | 0.000000
09-04-2025 14:44:20000 | -1353577 | 135.3577 | 12870740 | 234399.75 | 334923431 | 99550964 | 49964046 | 0.000000 | 31588655 | 32432701 | 0.000000
09-04-2025 14:44:25000 | -1357543 | 135.7543 | 12912951 | 234362.20 | 335959137 | 99550659 | 49969307 | 0.000000 | 31766389 | 32620615 | 0.000000
09-04-2025 14:44:30000 | -1356698 | 135.6698 | 12703439 | 234323.91 | 335756195 | 99564484 | 49937092 | 0.000000 | 31944597 | 32809070 | 0.000000
09-04-2025 14:44:35000 | -1344824 | 134.4824 | 12571618 | 234352.23 | 332772522 | 99565903 | 49939892 | 0.000000 | 32118691 | 32996590 | 0.000000
09-04-2025 14:44:40000 | -1349568 | 134.9568 | 12867608 | 234417.72 | 333911743 | 99548531 | 49981361 | 0.000000 | 32295740 | 33183715 | 0.000000
09-04-2025 14:44:45000 | -1351770 | 135.177 | 13054959 | 234410.86 | 334507324 | 99536880 | 49995697 | 0.000000 | 32476931 | 33371539 | 0.000000
09-04-2025 14:44:50000 | -1354022 | 135.4022 | 13113566 | 234417.14 | 335062744 | 99534286 | 50010658 | 0.000000 | 32658499 | 33559492 | 0.000000
09-04-2025 14:44:55000 | -1351176 | 135.1176 | 13134979 | 234464.45 | 334301239 | 99530823 | 50022602 | 0.000000 | 32840491 | 33747293 | 0.000000
09-04-2025 14:45:00000 | -1356980 | 135.698 | 13349963 | 234398.38 | 335870300 | 99519554 | 50017555 | 0.000000 | 33025088 | 33935375 | 0.000000
09-04-2025 14:45:05000 | -1354193 | 135.4193 | 13057345 | 234398.53 | 335118195 | 99538361 | 49974377 | 0.000000 | 18228209 | 188263977 | 0.000000
09-04-2025 14:45:10000 | -1347583 | 134.7583 | 12863095 | 234403.98 | 333450378 | 99547523 | 49982594 | 0.000000 | 36274429 | 375880005 | 0.000000
09-04-2025 14:45:15000 | -1351728 | 135.1728 | 13130819 | 234404.63 | 334522858 | 99531494 | 49986809 | 0.000000 | 54412380 | 563614258 | 0.000000
09-04-2025 14:45:20000 | -1350349 | 135.0349 | 13131581 | 234471.28 | 334092773 | 99530487 | 49983528 | 0.000000 | 72584625 | 751296875 | 0.000000
09-04-2025 14:45:25000 | -1350986 | 135.0986 | 13059612 | 234419.66 | 334305481 | 99536018 | 49970654 | 0.000000 | 90745514 | 939159302 | 0.000000
09-04-2025 14:45:30000 | -1354511 | 135.4511 | 13178941 | 234468.98 | 335122223 | 99529999 | 49982292 | 0.000000 | 108914528 | 11269752 | 0.000000
09-04-2025 14:45:35000 | -1354085 | 135.4085 | 13027458 | 234392.94 | 335092743 | 99540382 | 49971527 | 0.000000 | 127038780 | 13149148 | 0.000000
09-04-2025 14:45:40000 | -1352996 | 135.2996 | 12888560 | 234395.88 | 334797882 | 99549347 | 49955006 | 0.000000 | 144949753 | 15027883 | 0.000000
09-04-2025 14:45:45000 | -1356965 | 135.6965 | 12837072 | 234294.55 | 335896851 | 99555511 | 49937675 | 0.000000 | 162769379 | 16907980 | 0.000000
09-04-2025 14:45:50000 | -1350512 | 135.0512 | 12768067 | 234394.03 | 334155212 | 99556061 | 49950981 | 0.000000 | 180452728 | 18785251 | 0.000000
09-04-2025 14:45:55000 | -1350895 | 135.0895 | 12650496 | 234343.56 | 334289001 | 99564392 | 49939110 | 0.000000 | 198128403 | 20663171 | 0.000000
09-04-2025 14:46:00000 | -1349057 | 134.9057 | 12484346 | 234309.55 | 333853699 | 99574539 | 49929508 | 0.000000 | 215578964 | 22538828 | 0.000000
09-04-2025 14:46:05000 | -1353200 | 135.32 | 12688787 | 234316.20 | 334911224 | 99563248 | 49936131 | 0.000000 | 233123779 | 24413533 | 0.000000
09-04-2025 14:46:10000 | -1346816 | 134.6816 | 12643401 | 234350.72 | 333283478 | 99562256 | 49953583 | 0.000000 | 250791016 | 26286768 | 0.000000
09-04-2025 14:46:15000 | -1355213 | 135.5213 | 12909571 | 234289.67 | 335488831 | 99549355 | 49972187 | 0.000000 | 268661957 | 28163723 | 0.000000
09-04-2025 14:46:20000 | -1352466 | 135.2466 | 12642046 | 234326.66 | 334699493 | 99565971 | 49946583 | 0.000000 | 286275665 | 30042341 | 0.000000
09-04-2025 14:46:25000 | -1354583 | 135.4583 | 12898312 | 234348.05 | 335250183 | 99549721 | 49961346 | 0.000000 | 304042114 | 31921111 | 0.000000
09-04-2025 14:46:30000 | -1353696 | 135.3696 | 12759645 | 234352.00 | 334993805 | 99558708 | 49949268 | 0.000000 | 321814789 | 33801575 | 0.000000
09-04-2025 14:46:35000 | -1352784 | 135.2784 | 12990095 | 234525.47 | 334585358 | 99542122 | 49985245 | 0.000000 | 339674194 | 35675366 | 0.000000
09-04-2025 14:46:40000 | -1351252 | 135.1252 | 12674406 | 234355.22 | 334370880 | 99562981 | 49960205 | 0.000000 | 357731873 | 37556655 | 0.000000
09-04-2025 14:46:45000 | -1350964 | 135.0964 | 12690749 | 234420.09 | 334207489 | 99561676 | 49964539 | 0.000000 | 375370819 | 39432322 | 0.000000
09-04-2025 14:46:50000 | -1353111 | 135.3111 | 12783370 | 234407.11 | 334781067 | 99556702 | 49959957 | 0.000000 | 393063690 | 41310156 | 0.000000
09-04-2025 14:46:55000 | -1346589 | 134.6589 | 12439270 | 234410.84 | 333095490 | 99576042 | 49956486 | 0.000000 | 410482330 | 43183701 | 0.000000
09-04-2025 14:47:00000 | -1354718 | 135.4718 | 13011391 | 234444.16 | 335177643 | 99541931 | 49984936 | 0.000000 | 428303192 | 45059390 | 0.000000
09-04-2025 14:47:05000 | -1353156 | 135.3156 | 12922172 | 234453.69 | 334763458 | 99547119 | 49989849 | 0.000000 | 446163177 | 46934268 | 0.000000
09-04-2025 14:47:10000 | -1352763 | 135.2763 | 13003001 | 234487.59 | 334628418 | 99541206 | 49995968 | 0.000000 | 464105316 | 48808706 | 0.000000
09-04-2025 14:47:15000 | -1353772 | 135.3772 | 12885513 | 234444.67 | 334920441 | 99550072 | 50000034 | 0.000000 | 482052734 | 50686514 | 0.000000
09-04-2025 14:47:20000 | -1348407 | 134.8407 | 12725767 | 234497.48 | 333486450 | 99557610 | 49996002 | 0.000000 | 499847900 | 52562310 | 0.000000
09-04-2025 14:47:25000 | -1348149 | 134.8149 | 12741989 | 234474.53 | 333461578 | 99556320 | 49992615 | 0.000000 | 517742126 | 54442334 | 0.000000
09-04-2025 14:47:30000 | -1350988 | 135.0988 | 12852243 | 234472.30 | 334179138 | 99550545 | 49988365 | 0.000000 | 535643188 | 56323594 | 0.000000
09-04-2025 14:47:35000 | -1354183 | 135.4183 | 12839529 | 234435.80 | 335015045 | 99553528 | 49998196 | 0.000000 | 553374207 | 58199556 | 0.000000
09-04-2025 14:47:40000 | -1351339 | 135.1339 | 12534565 | 234443.14 | 334236603 | 99572563 | 49964161 | 0.000000 | 570902283 | 60080322 | 0.000000
09-04-2025 14:47:45000 | -1351863 | 135.1863 | 13214500 | 234598.23 | 334304138 | 99525642 | 49993671 | 0.000000 | 588914185 | 61955674 | 0.000000
09-04-2025 14:47:50000 | -1356592 | 135.6592 | 13140070 | 234510.75 | 335570953 | 99534172 | 49999535 | 0.000000 | 607193542 | 63837007 | 0.000000
09-04-2025 14:47:55000 | -1358501 | 135.8501 | 12896213 | 234398.91 | 336138031 | 99552437 | 49974209 | 0.000000 | 625273865 | 65721187 | 0.000000
09-04-2025 14:48:00000 | -1353422 | 135.3422 | 12505805 | 234362.55 | 334856445 | 99575813 | 49928631 | 0.000000 | 642959229 | 67605488 | 0.000000
09-04-2025 14:48:05000 | -1348503 | 134.8503 | 12487645 | 234443.34 | 333527740 | 99573967 | 49946384 | 0.000000 | 660262695 | 69481563 | 0.000000
09-04-2025 14:48:10000 | -1350103 | 135.0103 | 12497604 | 234404.34 | 333976807 | 99574295 | 49962265 | 0.000000 | 677644165 | 71357109 | 0.000000
09-04-2025 14:48:15000 | -1349325 | 134.9325 | 12548639 | 234407.30 | 333795105 | 99570343 | 49958080 | 0.000000 | 695168396 | 73235439 | 0.000000
09-04-2025 14:48:20000 | -1351749 | 135.1749 | 12353469 | 234323.16 | 334461548 | 99584999 | 49943832 | 0.000000 | 712523438 | 75112852 | 0.000000
09-04-2025 14:48:25000 | -1348260 | 134.826 | 12448552 | 234416.88 | 333498077 | 99576462 | 49959702 | 0.000000 | 729726318 | 76986270 | 0.000000
09-04-2025 14:48:30000 | -1350447 | 135.0447 | 12419563 | 234338.83 | 334142517 | 99579773 | 49936501 | 0.000000 | 747015930 | 78863867 | 0.000000
09-04-2025 14:48:35000 | -1349380 | 134.938 | 12375325 | 234402.41 | 333776154 | 99582085 | 49933804 | 0.000000 | 764107239 | 80736396 | 0.000000
09-04-2025 14:48:40000 | -1342778 | 134.2778 | 12285648 | 234430.42 | 332097504 | 99584053 | 49951561 | 0.000000 | 781278931 | 82607051 | 0.000000
09-04-2025 14:48:45000 | -1350613 | 135.0613 | 12580746 | 234381.27 | 334151428 | 99568970 | 49960892 | 0.000000 | 798684021 | 84480420 | 0.000000
09-04-2025 14:48:50000 | -1348436 | 134.8436 | 12365968 | 234365.59 | 333592621 | 99582130 | 49955048 | 0.000000 | 815940857 | 86354063 | 0.000000
09-04-2025 14:48:55000 | -1348560 | 134.856 | 12442398 | 234412.92 | 333577057 | 99577065 | 49969727 | 0.000000 | 833184509 | 88226572 | 0.000000
09-04-2025 14:49:00000 | -1349851 | 134.9851 | 12733700 | 234481.33 | 333859894 | 99557999 | 49991005 | 0.000000 | 850698242 | 90100518 | 0.000000
09-04-2025 14:49:05000 | -1349854 | 134.9854 | 12627843 | 234403.00 | 333952789 | 99565277 | 49980484 | 0.000000 | 868299438 | 91972754 | 0.000000
09-04-2025 14:49:10000 | -1346544 | 134.6544 | 12605272 | 234396.81 | 333140350 | 99564697 | 49953659 | 0.000000 | 886006531 | 93849990 | 0.000000
09-04-2025 14:49:15000 | -1343888 | 134.3888 | 12473778 | 234446.22 | 332387909 | 99571999 | 49950237 | 0.000000 | 903401733 | 95722080 | 0.000000
09-04-2025 14:49:20000 | -1345724 | 134.5724 | 12581640 | 234484.81 | 332812531 | 99565796 | 49958622 | 0.000000 | 920722595 | 97589697 | 0.000000
09-04-2025 14:49:25000 | -1354256 | 135.4256 | 12698483 | 234337.36 | 335141693 | 99563263 | 49956295 | 0.000000 | 938317871 | 99464141 | 0.000000
09-04-2025 14:49:30000 | -1348230 | 134.823 | 12501305 | 234427.84 | 333493256 | 99572868 | 49951180 | 0.000000 | 955574097 | 10133741 | 0.000000
09-04-2025 14:49:35000 | -1345060 | 134.506 | 12565396 | 234467.31 | 332669067 | 99566483 | 49961964 | 0.000000 | 973023865 | 10320962 | 0.000000
09-04-2025 14:49:40000 | -1349341 | 134.9341 | 12720870 | 234496.17 | 333712646 | 99558556 | 49973812 | 0.000000 | 990628296 | 10508564 | 0.000000
09-04-2025 14:49:45000 | -1352626 | 135.2626 | 12618054 | 234360.97 | 334691620 | 99567711 | 49959515 | 0.000000 | 10083124 | 10696401 | 0.000000
09-04-2025 14:49:50000 | -1348405 | 134.8405 | 11996945 | 234281.63 | 333623383 | 99606537 | 49907661 | 0.000000 | 10252241 | 10883984 | 0.000000
09-04-2025 14:49:55000 | -1343436 | 134.3436 | 12006803 | 234331.17 | 332340912 | 99602989 | 49931774 | 0.000000 | 10418252 | 11070675 | 0.000000
09-04-2025 14:50:00000 | -1349368 | 134.9368 | 12295294 | 234342.22 | 333838226 | 99587433 | 49948265 | 0.000000 | 10587070 | 11257592 | 0.000000
09-04-2025 14:50:05000 | -1350068 | 135.0068 | 12360055 | 234344.05 | 334023376 | 99583534 | 49940819 | 0.000000 | 10759760 | 11445229 | 0.000000
09-04-2025 14:50:10000 | -1352440 | 135.244 | 12362543 | 234317.45 | 334647858 | 99584816 | 49922222 | 0.000000 | 10931633 | 11632782 | 0.000000
09-04-2025 14:50:15000 | -1349467 | 134.9467 | 12326294 | 234353.58 | 333853058 | 99585426 | 49928467 | 0.000000 | 11101461 | 11819795 | 0.000000
09-04-2025 14:50:20000 | -1349164 | 134.9164 | 12396341 | 234331.38 | 333825745 | 99580544 | 49947437 | 0.000000 | 11273363 | 12006844 | 0.000000
09-04-2025 14:50:25000 | -1352779 | 135.2779 | 12616018 | 234351.23 | 334734314 | 99567947 | 49952183 | 0.000000 | 11446976 | 12194094 | 0.000000
09-04-2025 14:50:30000 | -1349204 | 134.9204 | 12292643 | 234327.84 | 333820984 | 99587509 | 49920815 | 0.000000 | 11620594 | 12381899 | 0.000000
09-04-2025 14:50:35000 | -1351956 | 135.1956 | 12315534 | 234311.34 | 334529297 | 99587654 | 49912361 | 0.000000 | 11791985 | 12569575 | 0.000000
09-04-2025 14:50:40000 | -1355282 | 135.5282 | 12228567 | 234305.22 | 335333771 | 99595406 | 49894520 | 0.000000 | 11961427 | 12757362 | 0.000000
09-04-2025 14:50:45000 | -1351027 | 135.1027 | 11919852 | 234257.33 | 334283752 | 99613045 | 49888306 | 0.000000 | 12127345 | 12944919 | 0.000000
09-04-2025 14:50:50000 | -1343155 | 134.3155 | 11788684 | 234304.53 | 332257050 | 99617043 | 49902748 | 0.000000 | 12292181 | 13132169 | 0.000000
09-04-2025 14:50:55000 | -1350015 | 135.0015 | 12393904 | 234384.63 | 333959656 | 99581230 | 49943516 | 0.000000 | 12460641 | 13319414 | 0.000000
09-04-2025 14:51:00000 | -1352231 | 135.2231 | 12685796 | 234427.22 | 334508118 | 99562836 | 49982647 | 0.000000 | 12635380 | 13507088 | 0.000000
09-04-2025 14:51:05000 | -1354084 | 135.4084 | 12400669 | 234275.55 | 335119446 | 99583275 | 49947762 | 0.000000 | 12810761 | 13695563 | 0.000000
09-04-2025 14:51:10000 | -1352507 | 135.2507 | 12286358 | 234348.17 | 334607086 | 99589928 | 49934040 | 0.000000 | 12981262 | 13883373 | 0.000000
09-04-2025 14:51:15000 | -1351374 | 135.1374 | 12416162 | 234396.16 | 334283997 | 99580574 | 49948643 | 0.000000 | 13152051 | 14070817 | 0.000000
09-04-2025 14:51:20000 | -1349242 | 134.9242 | 12250991 | 234338.27 | 333808167 | 99590309 | 49937298 | 0.000000 | 13324334 | 14258523 | 0.000000
09-04-2025 14:51:25000 | -1353095 | 135.3095 | 12479897 | 234356.73 | 334778961 | 99577354 | 49957951 | 0.000000 | 13496409 | 14445919 | 0.000000
09-04-2025 14:51:30000 | -1346998 | 134.6998 | 12305089 | 234400.70 | 333178131 | 99585335 | 49963528 | 0.000000 | 13667782 | 14633029 | 0.000000
09-04-2025 14:51:35000 | -1348713 | 134.8713 | 12388173 | 234329.66 | 333716797 | 99580811 | 49953720 | 0.000000 | 13841631 | 14820665 | 0.000000
09-04-2025 14:51:40000 | -1344258 | 134.4258 | 12285158 | 234384.91 | 332527527 | 99584991 | 49934639 | 0.000000 | 14011484 | 15007799 | 0.000000
09-04-2025 14:51:45000 | -1344482 | 134.4482 | 12343302 | 234427.42 | 332532074 | 99581215 | 49933327 | 0.000000 | 14182855 | 15194805 | 0.000000
09-04-2025 14:51:50000 | -1341401 | 134.1401 | 12361216 | 234506.66 | 331669525 | 99578087 | 49943760 | 0.000000 | 14354386 | 15381834 | 0.000000
09-04-2025 14:51:55000 | -1345705 | 134.5705 | 12914598 | 234557.98 | 332774231 | 99542656 | 49997383 | 0.000000 | 14530674 | 15568284 | 0.000000
09-04-2025 14:52:00000 | -1353062 | 135.3062 | 13045203 | 234478.09 | 334725067 | 99538445 | 50018894 | 0.000000 | 14710940 | 15755475 | 0.000000
09-04-2025 14:52:05000 | -1351493 | 135.1493 | 12896508 | 234462.83 | 334331421 | 99547798 | 50004162 | 0.000000 | 14891331 | 15943361 | 0.000000
09-04-2025 14:52:10000 | -1347829 | 134.7829 | 12852404 | 234490.73 | 333374695 | 99548439 | 49989475 | 0.000000 | 15069363 | 16130613 | 0.000000
09-04-2025 14:52:15000 | -1344921 | 134.4921 | 12752938 | 234499.28 | 332632874 | 99553436 | 49987827 | 0.000000 | 15246782 | 16317604 | 0.000000
09-04-2025 14:52:20000 | -1350850 | 135.085 | 13012482 | 234475.81 | 334176605 | 99539246 | 49970573 | 0.000000 | 15427391 | 16505365 | 0.000000
09-04-2025 14:52:25000 | -1354539 | 135.4539 | 12972635 | 234485.41 | 335055511 | 99544518 | 49974545 | 0.000000 | 15606802 | 16692961 | 0.000000
09-04-2025 14:52:30000 | -1354143 | 135.4143 | 12869912 | 234423.92 | 335026672 | 99551399 | 49951088 | 0.000000 | 15785754 | 16880746 | 0.000000
09-04-2025 14:52:35000 | -1350225 | 135.0225 | 12437161 | 234359.30 | 334060486 | 99578453 | 49907887 | 0.000000 | 15960813 | 17068412 | 0.000000
09-04-2025 14:52:40000 | -1346342 | 134.6342 | 12561565 | 234471.33 | 332975128 | 99567566 | 49933514 | 0.000000 | 16133175 | 17255287 | 0.000000
09-04-2025 14:52:45000 | -1347177 | 134.7177 | 12599548 | 234436.94 | 333232483 | 99565498 | 49953812 | 0.000000 | 16308538 | 17442631 | 0.000000
09-04-2025 14:52:50000 | -1352929 | 135.2929 | 13071366 | 234509.23 | 334649506 | 99536514 | 49987514 | 0.000000 | 16487865 | 17630152 | 0.000000
09-04-2025 14:52:55000 | -1356297 | 135.6297 | 12506847 | 234276.73 | 335683380 | 99577530 | 49911705 | 0.000000 | 16666101 | 17818977 | 0.000000
09-04-2025 14:53:00000 | -1351664 | 135.1664 | 12269842 | 234355.28 | 334380920 | 99590515 | 49888355 | 0.000000 | 16835908 | 18006645 | 0.000000
09-04-2025 14:53:05000 | -1346769 | 134.6769 | 12293379 | 234376.45 | 333157196 | 99585976 | 49882568 | 0.000000 | 17007793 | 18194336 | 0.000000
09-04-2025 14:53:10000 | -1350257 | 135.0257 | 12027116 | 234261.20 | 334116150 | 99605644 | 49861042 | 0.000000 | 17177224 | 18382150 | 0.000000
09-04-2025 14:53:15000 | -1347181 | 134.7181 | 12040170 | 234373.34 | 333202606 | 99602997 | 49881306 | 0.000000 | 17343245 | 18569271 | 0.000000
09-04-2025 14:53:20000 | -1351288 | 135.1288 | 12348202 | 234337.88 | 334326508 | 99585075 | 49887463 | 0.000000 | 17514232 | 18757055 | 0.000000
09-04-2025 14:53:25000 | -1357372 | 135.7372 | 12341599 | 234280.75 | 335900818 | 99589195 | 49883007 | 0.000000 | 17684268 | 18944852 | 0.000000
09-04-2025 14:53:30000 | -1352460 | 135.246 | 11965832 | 234236.20 | 334678833 | 99610893 | 49866688 | 0.000000 | 17852368 | 19132631 | 0.000000
09-04-2025 14:53:35000 | -1346370 | 134.637 | 11791238 | 234287.67 | 333071960 | 99618698 | 49848804 | 0.000000 | 18017478 | 19320303 | 0.000000
09-04-2025 14:53:40000 | -1352043 | 135.2043 | 12119698 | 234276.27 | 334550415 | 99600639 | 49878559 | 0.000000 | 18184325 | 19507756 | 0.000000
09-04-2025 14:53:45000 | -1353651 | 135.3651 | 12153118 | 234267.64 | 334962311 | 99599396 | 49869251 | 0.000000 | 18353623 | 19695787 | 0.000000
09-04-2025 14:53:50000 | -1353235 | 135.3235 | 12042459 | 234255.03 | 334860443 | 99606377 | 49867119 | 0.000000 | 18521307 | 19883709 | 0.000000
09-04-2025 14:53:55000 | -1353642 | 135.3642 | 11936919 | 234243.28 | 334953827 | 99613434 | 49857208 | 0.000000 | 18687180 | 20071615 | 0.000000
09-04-2025 14:54:00000 | -1348617 | 134.8617 | 11912999 | 234337.25 | 333586609 | 99612114 | 49862949 | 0.000000 | 18852776 | 20259189 | 0.000000
09-04-2025 14:54:05000 | -1348164 | 134.8164 | 12302875 | 234417.25 | 333446014 | 99586197 | 49914711 | 0.000000 | 19021315 | 20446406 | 0.000000
09-04-2025 14:54:10000 | -1354805 | 135.4805 | 12505683 | 234324.55 | 335250824 | 99576683 | 49925014 | 0.000000 | 19194016 | 20634146 | 0.000000
09-04-2025 14:54:15000 | -1354638 | 135.4638 | 12203314 | 234229.91 | 335275055 | 99596687 | 49903736 | 0.000000 | 19365404 | 20822244 | 0.000000
09-04-2025 14:54:20000 | -1351164 | 135.1164 | 12169021 | 234302.67 | 334311676 | 99596878 | 49897163 | 0.000000 | 19535178 | 21010191 | 0.000000
09-04-2025 14:54:25000 | -1353336 | 135.3336 | 12135238 | 234284.47 | 334861206 | 99600380 | 49894417 | 0.000000 | 19703633 | 21198039 | 0.000000
09-04-2025 14:54:30000 | -1354664 | 135.4664 | 12379015 | 234366.88 | 335123779 | 99585075 | 49924763 | 0.000000 | 19873838 | 21385852 | 0.000000
09-04-2025 14:54:35000 | -1359641 | 135.9641 | 12784717 | 234360.25 | 336450043 | 99560829 | 49951981 | 0.000000 | 20049038 | 21574055 | 0.000000
09-04-2025 14:54:40000 | -1361124 | 136.1124 | 12629386 | 234325.70 | 336822754 | 99572296 | 49930805 | 0.000000 | 20224459 | 21762668 | 0.000000
09-04-2025 14:54:45000 | -1352333 | 135.2333 | 12273975 | 234352.81 | 334555481 | 99590645 | 49935120 | 0.000000 | 20396512 | 21950609 | 0.000000
09-04-2025 14:54:50000 | -1356534 | 135.6534 | 12544813 | 234337.52 | 335662079 | 99575127 | 49937489 | 0.000000 | 20569539 | 22138682 | 0.000000
09-04-2025 14:54:55000 | -1349951 | 134.9951 | 12544243 | 234438.14 | 333908508 | 99571037 | 49949299 | 0.000000 | 20741863 | 22326199 | 0.000000
09-04-2025 14:55:00000 | -1355181 | 135.5181 | 12665373 | 234391.69 | 335284241 | 99566109 | 49943317 | 0.000000 | 20917532 | 22514189 | 0.000000
09-04-2025 14:55:05000 | -1350942 | 135.0942 | 12344137 | 234354.50 | 334218658 | 99585136 | 49931660 | 0.000000 | 21091660 | 22702213 | 0.000000
09-04-2025 14:55:10000 | -1356392 | 135.6392 | 12692355 | 234406.42 | 335570618 | 99565048 | 49949886 | 0.000000 | 21265154 | 22890078 | 0.000000
09-04-2025 14:55:15000 | -1354112 | 135.4112 | 12260413 | 234300.53 | 335054321 | 99592613 | 49920444 | 0.000000 | 21437764 | 23078209 | 0.000000
09-04-2025 14:55:20000 | -1348830 | 134.883 | 12132965 | 234350.98 | 333655487 | 99597870 | 49912651 | 0.000000 | 21607649 | 23266014 | 0.000000
09-04-2025 14:55:25000 | -1344909 | 134.4909 | 12449267 | 234520.84 | 332522278 | 99574310 | 49951763 | 0.000000 | 21779395 | 23453484 | 0.000000
09-04-2025 14:55:30000 | -1355849 | 135.5849 | 12886590 | 234440.36 | 335425720 | 99551369 | 49977051 | 0.000000 | 21956797 | 23641537 | 0.000000
09-04-2025 14:55:35000 | -1353656 | 135.3656 | 12774691 | 234486.22 | 334793762 | 99557648 | 49968559 | 0.000000 | 22134797 | 23829971 | 0.000000
09-04-2025 14:55:40000 | -1357552 | 135.7552 | 13117042 | 234520.23 | 335783966 | 99536446 | 50005409 | 0.000000 | 22314683 | 24018137 | 0.000000
09-04-2025 14:55:45000 | -1350525 | 135.0525 | 12804647 | 234497.11 | 334017944 | 99553535 | 49994282 | 0.000000 | 22494709 | 24206379 | 0.000000
09-04-2025 14:55:50000 | -1354637 | 135.4637 | 12841703 | 234444.58 | 335107056 | 99553673 | 49973934 | 0.000000 | 22674309 | 24394805 | 0.000000
09-04-2025 14:55:55000 | -1352936 | 135.2936 | 12781578 | 234501.95 | 334598969 | 99556709 | 49967468 | 0.000000 | 22852002 | 24582850 | 0.000000
09-04-2025 14:56:00000 | -1362826 | 136.2826 | 12944648 | 234381.94 | 337229279 | 99551933 | 49948723 | 0.000000 | 23030154 | 24771094 | 0.000000
09-04-2025 14:56:05000 | -1357253 | 135.7253 | 12598399 | 234321.03 | 335872192 | 99571960 | 49914650 | 0.000000 | 23206951 | 24959355 | 0.000000
09-04-2025 14:56:10000 | -1350236 | 135.0236 | 12367362 | 234388.56 | 334003998 | 99583145 | 49904682 | 0.000000 | 23377944 | 25146734 | 0.000000
09-04-2025 14:56:15000 | -1350344 | 135.0344 | 12630836 | 234453.92 | 333995178 | 99565384 | 49930576 | 0.000000 | 23551865 | 25334250 | 0.000000
09-04-2025 14:56:20000 | -1359289 | 135.9289 | 12686959 | 234281.55 | 336453766 | 99567253 | 49902699 | 0.000000 | 23728999 | 25522754 | 0.000000
09-04-2025 14:56:25000 | -1355002 | 135.5002 | 12381929 | 234341.44 | 335241028 | 99585091 | 49899097 | 0.000000 | 23901199 | 25710820 | 0.000000
09-04-2025 14:56:30000 | -1356527 | 135.6527 | 12512413 | 234411.53 | 335547791 | 99577301 | 49926628 | 0.000000 | 24073354 | 25898867 | 0.000000
09-04-2025 14:56:35000 | -1360033 | 136.0033 | 12482210 | 234277.05 | 336594696 | 99581474 | 49902233 | 0.000000 | 24247437 | 26087514 | 0.000000
09-04-2025 14:56:40000 | -1359521 | 135.9521 | 12399861 | 234274.64 | 336454132 | 99586639 | 49885181 | 0.000000 | 24419539 | 26275883 | 0.000000
09-04-2025 14:56:45000 | -1349186 | 134.9186 | 12293304 | 234425.50 | 333681580 | 99587456 | 49889393 | 0.000000 | 24591599 | 26463889 | 0.000000
09-04-2025 14:56:50000 | -1353779 | 135.3779 | 12706833 | 234484.50 | 334809967 | 99562386 | 49931648 | 0.000000 | 24766238 | 26651707 | 0.000000
09-04-2025 14:56:55000 | -1356471 | 135.6471 | 12840873 | 234439.91 | 335563202 | 99554924 | 49946072 | 0.000000 | 24945295 | 26840084 | 0.000000
09-04-2025 14:57:00000 | -1353437 | 135.3437 | 12865643 | 234476.94 | 334778778 | 99551231 | 49960514 | 0.000000 | 25123662 | 27028211 | 0.000000
09-04-2025 14:57:05000 | -1355323 | 135.5323 | 13016828 | 234539.13 | 335183472 | 99541962 | 49981594 | 0.000000 | 25303096 | 27216473 | 0.000000
09-04-2025 14:57:10000 | -1355972 | 135.5972 | 12921923 | 234473.95 | 335416809 | 99548996 | 49984886 | 0.000000 | 25482688 | 27404588 | 0.000000
09-04-2025 14:57:15000 | -1354089 | 135.4089 | 12920977 | 234441.78 | 335011353 | 99547821 | 49983486 | 0.000000 | 25663157 | 27592748 | 0.000000
09-04-2025 14:57:20000 | -1358762 | 135.8762 | 13055733 | 234472.05 | 336137482 | 99541550 | 49976398 | 0.000000 | 25843203 | 27781008 | 0.000000
09-04-2025 14:57:25000 | -1352139 | 135.2139 | 12494052 | 234362.77 | 334537628 | 99575806 | 49930943 | 0.000000 | 26018906 | 27968955 | 0.000000
09-04-2025 14:57:30000 | -1350668 | 135.0668 | 12355332 | 234356.98 | 334153076 | 99584221 | 49905941 | 0.000000 | 26190852 | 28156555 | 0.000000
09-04-2025 14:57:35000 | -1349741 | 134.9741 | 12250549 | 234357.55 | 333900787 | 99590637 | 49884392 | 0.000000 | 26361052 | 28343938 | 0.000000
09-04-2025 14:57:40000 | -1348017 | 134.8017 | 12361550 | 234366.33 | 333490631 | 99582176 | 49887428 | 0.000000 | 26532153 | 28531109 | 0.000000
09-04-2025 14:57:45000 | -1346114 | 134.6114 | 12407565 | 234435.75 | 332932800 | 99577896 | 49909496 | 0.000000 | 26703965 | 28718422 | 0.000000
09-04-2025 14:57:50000 | -1355800 | 135.58 | 12684331 | 234349.83 | 335501526 | 99565216 | 49946785 | 0.000000 | 26878667 | 28905777 | 0.000000
09-04-2025 14:57:55000 | -1353303 | 135.3303 | 12535607 | 234359.94 | 334836365 | 99573730 | 49919777 | 0.000000 | 27053394 | 29093689 | 0.000000
09-04-2025 14:58:00000 | -1342104 | 134.2104 | 12227406 | 234417.72 | 331937439 | 99587547 | 49899269 | 0.000000 | 27225149 | 29280943 | 0.000000
09-04-2025 14:58:05000 | -1345875 | 134.5875 | 12481965 | 234431.63 | 332898682 | 99572701 | 49922882 | 0.000000 | 27396384 | 29467736 | 0.000000
09-04-2025 14:58:10000 | -1354663 | 135.4663 | 12634832 | 234340.55 | 335216888 | 99567863 | 49895828 | 0.000000 | 27571785 | 29655488 | 0.000000
09-04-2025 14:58:15000 | -1350374 | 135.0374 | 12304281 | 234350.30 | 334079376 | 99587448 | 49866707 | 0.000000 | 27745645 | 29843453 | 0.000000
09-04-2025 14:58:20000 | -1346837 | 134.6837 | 12275770 | 234416.16 | 333111969 | 99587196 | 49884216 | 0.000000 | 27916091 | 30030795 | 0.000000
09-04-2025 14:58:25000 | -1344960 | 134.496 | 12382253 | 234472.94 | 332593597 | 99578888 | 49904785 | 0.000000 | 28088154 | 30218121 | 0.000000
09-04-2025 14:58:30000 | -1350701 | 135.0701 | 12560563 | 234426.59 | 334104706 | 99570396 | 49910717 | 0.000000 | 28261799 | 30405813 | 0.000000
09-04-2025 14:58:35000 | -1348754 | 134.8754 | 12800153 | 234505.13 | 333569305 | 99552689 | 49957138 | 0.000000 | 28437129 | 30593012 | 0.000000
09-04-2025 14:58:40000 | -1353204 | 135.3204 | 12693907 | 234418.39 | 334761597 | 99562904 | 49955074 | 0.000000 | 28614399 | 30780994 | 0.000000
09-04-2025 14:58:45000 | -1356648 | 135.6648 | 12957859 | 234448.06 | 335624969 | 99546951 | 49958996 | 0.000000 | 28793706 | 30969246 | 0.000000
09-04-2025 14:58:50000 | -1359383 | 135.9383 | 12900423 | 234418.63 | 336327850 | 99552727 | 49935940 | 0.000000 | 28972981 | 31157691 | 0.000000
09-04-2025 14:58:55000 | -1354316 | 135.4316 | 12597451 | 234425.52 | 335001556 | 99570175 | 49930225 | 0.000000 | 29148828 | 31345834 | 0.000000
09-04-2025 14:59:00000 | -1350743 | 135.0743 | 12515987 | 234435.31 | 334094604 | 99573448 | 49943802 | 0.000000 | 29323108 | 31533635 | 0.000000
09-04-2025 14:59:05000 | -1350238 | 135.0238 | 12686197 | 234469.77 | 333955170 | 99561523 | 49960258 | 0.000000 | 29499043 | 31721393 | 0.000000
09-04-2025 14:59:10000 | -1357466 | 135.7466 | 13101085 | 234465.23 | 335831909 | 99537506 | 50006680 | 0.000000 | 29678533 | 31909273 | 0.000000
09-04-2025 14:59:15000 | -1360432 | 136.0432 | 13002752 | 234426.86 | 336594086 | 99546349 | 49987175 | 0.000000 | 29859597 | 32097910 | 0.000000
09-04-2025 14:59:20000 | -1360308 | 136.0308 | 12798620 | 234410.66 | 336541016 | 99560303 | 49968418 | 0.000000 | 30037249 | 32286412 | 0.000000
09-04-2025 14:59:25000 | -1355447 | 135.5447 | 12560631 | 234401.80 | 335304199 | 99573380 | 49950775 | 0.000000 | 30212659 | 32474572 | 0.000000
09-04-2025 14:59:30000 | -1349927 | 134.9927 | 12696219 | 234482.27 | 333871887 | 99560631 | 49957558 | 0.000000 | 30388518 | 32662402 | 0.000000
09-04-2025 14:59:35000 | -1352761 | 135.2761 | 12919444 | 234470.59 | 334632141 | 99547043 | 49976627 | 0.000000 | 30567053 | 32850109 | 0.000000
09-04-2025 14:59:40000 | -1351106 | 135.1106 | 13001691 | 234549.86 | 334138550 | 99540184 | 49992298 | 0.000000 | 30746255 | 33037684 | 0.000000
09-04-2025 14:59:45000 | -1352597 | 135.2597 | 13253442 | 234599.38 | 334492950 | 99523376 | 50023045 | 0.000000 | 30928579 | 33225496 | 0.000000
09-04-2025 14:59:50000 | -1357663 | 135.7663 | 13491427 | 234579.78 | 335813812 | 99509880 | 50038116 | 0.000000 | 31114075 | 33413344 | 0.000000
09-04-2025 14:59:55000 | -1349075 | 134.9075 | 13186842 | 234593.47 | 333616547 | 99525673 | 50038273 | 0.000000 | 31299314 | 33601246 | 0.000000
09-04-2025 15:00:00000 | -1352965 | 135.2965 | 13618290 | 234665.42 | 334577393 | 99497246 | 50058899 | 0.000000 | 31485706 | 33789188 | 0.000000
09-04-2025 15:00:05000 | -1359536 | 135.9536 | 13292291 | 234439.94 | 336424286 | 99525444 | 50008381 | 0.000000 | 18791126 | 188747192 | 0.000000
09-04-2025 15:00:10000 | -1350567 | 135.0567 | 12782888 | 234507.27 | 334013519 | 99555069 | 49983364 | 0.000000 | 36740292 | 376754730 | 0.000000
09-04-2025 15:00:15000 | -1353612 | 135.3612 | 12988872 | 234508.13 | 334809875 | 99542770 | 49989681 | 0.000000 | 54617630 | 564610718 | 0.000000
09-04-2025 15:00:20000 | -1358285 | 135.8285 | 12896869 | 234402.17 | 336085083 | 99552254 | 49966946 | 0.000000 | 72524078 | 752670776 | 0.000000
09-04-2025 15:00:25000 | -1349083 | 134.9083 | 12386799 | 234379.19 | 333736328 | 99581131 | 49937489 | 0.000000 | 89980034 | 940263184 | 0.000000
09-04-2025 15:00:30000 | -1345418 | 134.5418 | 12377978 | 234414.05 | 332785889 | 99579460 | 49953762 | 0.000000 | 107197014 | 11273241 | 0.000000
09-04-2025 15:00:35000 | -1349663 | 134.9663 | 12828570 | 234464.89 | 333864502 | 99551308 | 49979553 | 0.000000 | 124806252 | 13145647 | 0.000000
09-04-2025 15:00:40000 | -1353275 | 135.3275 | 13053823 | 234520.53 | 334719452 | 99537987 | 49998867 | 0.000000 | 142744461 | 15021749 | 0.000000
09-04-2025 15:00:45000 | -1353146 | 135.3146 | 13003866 | 234487.19 | 334725861 | 99541405 | 50026562 | 0.000000 | 160892334 | 16902667 | 0.000000
09-04-2025 15:00:50000 | -1357349 | 135.7349 | 13600374 | 234651.38 | 335658051 | 99501762 | 50087490 | 0.000000 | 179291306 | 18782688 | 0.000000
09-04-2025 15:00:55000 | -1358914 | 135.8914 | 13604844 | 234630.50 | 336085754 | 99502579 | 50095150 | 0.000000 | 198204025 | 20669133 | 0.000000
09-04-2025 15:01:00000 | -1360582 | 136.0582 | 13604480 | 234622.63 | 336495605 | 99503815 | 50076969 | 0.000000 | 217076645 | 22559050 | 0.000000
09-04-2025 15:01:05000 | -1358567 | 135.8567 | 13394138 | 234581.95 | 336006470 | 99517517 | 50060326 | 0.000000 | 235779236 | 24447297 | 0.000000
09-04-2025 15:01:10000 | -1357633 | 135.7633 | 13556071 | 234649.28 | 335725952 | 99505188 | 50080437 | 0.000000 | 254479034 | 26331868 | 0.000000
09-04-2025 15:01:15000 | -1359871 | 135.9871 | 13673180 | 234673.03 | 336268982 | 99498306 | 50081570 | 0.000000 | 273356415 | 28218416 | 0.000000
09-04-2025 15:01:20000 | -1361610 | 136.161 | 13741641 | 234677.80 | 336698059 | 99494598 | 50099751 | 0.000000 | 292225189 | 30102380 | 0.000000
09-04-2025 15:01:25000 | -1358813 | 135.8813 | 14014980 | 234714.63 | 336033295 | 99472298 | 50121910 | 0.000000 | 311682526 | 31990559 | 0.000000
09-04-2025 15:01:30000 | -1361604 | 136.1604 | 13892357 | 234671.47 | 336743561 | 99483528 | 50111279 | 0.000000 | 331162689 | 33883591 | 0.000000
09-04-2025 15:01:35000 | -1360735 | 136.0735 | 13843383 | 234704.31 | 336470856 | 99486488 | 50098690 | 0.000000 | 350380280 | 35774072 | 0.000000
09-04-2025 15:01:40000 | -1361656 | 136.1656 | 13800170 | 234607.20 | 336828857 | 99490349 | 50071583 | 0.000000 | 369542816 | 37662754 | 0.000000
09-04-2025 15:01:45000 | -1359522 | 135.9522 | 13418882 | 234522.13 | 336329163 | 99516418 | 50014812 | 0.000000 | 388422882 | 39554119 | 0.000000
09-04-2025 15:01:50000 | -1356835 | 135.6835 | 13270080 | 234593.27 | 335537872 | 99525146 | 49999752 | 0.000000 | 406759216 | 41435518 | 0.000000
09-04-2025 15:01:55000 | -1348697 | 134.8697 | 13238094 | 234648.70 | 333455933 | 99521736 | 50012337 | 0.000000 | 425133362 | 43312339 | 0.000000
09-04-2025 15:02:00000 | -1354463 | 135.4463 | 13607714 | 234670.39 | 334924347 | 99499123 | 50047050 | 0.000000 | 443785278 | 45189761 | 0.000000
09-04-2025 15:02:05000 | -1359277 | 135.9277 | 13865299 | 234680.86 | 336155243 | 99483772 | 50066814 | 0.000000 | 462860840 | 47073174 | 0.000000
09-04-2025 15:02:10000 | -1356660 | 135.666 | 13803378 | 234689.80 | 335483124 | 99486382 | 50075977 | 0.000000 | 482088623 | 48958481 | 0.000000
09-04-2025 15:02:15000 | -1356123 | 135.6123 | 13742477 | 234641.89 | 335408691 | 99490463 | 50041924 | 0.000000 | 501272461 | 50844580 | 0.000000
09-04-2025 15:02:20000 | -1359180 | 135.918 | 13834105 | 234661.84 | 336150696 | 99486008 | 50044762 | 0.000000 | 520293701 | 52726045 | 0.000000
09-04-2025 15:02:25000 | -1358658 | 135.8658 | 13446039 | 234557.98 | 336083862 | 99513855 | 50002003 | 0.000000 | 539231018 | 54614858 | 0.000000
09-04-2025 15:02:30000 | -1356190 | 135.619 | 13324138 | 234594.25 | 335393127 | 99520844 | 50007988 | 0.000000 | 557628662 | 56495801 | 0.000000
09-04-2025 15:02:35000 | -1353175 | 135.3175 | 13407398 | 234664.72 | 334569550 | 99512733 | 50034649 | 0.000000 | 576176636 | 58376582 | 0.000000
09-04-2025 15:02:40000 | -1348092 | 134.8092 | 13244494 | 234598.06 | 333388458 | 99520851 | 50031116 | 0.000000 | 594831238 | 60257241 | 0.000000
09-04-2025 15:02:45000 | -1356160 | 135.616 | 13524886 | 234623.70 | 335394135 | 99506386 | 50040577 | 0.000000 | 613520691 | 62140127 | 0.000000
09-04-2025 15:02:50000 | -1356182 | 135.6182 | 13271665 | 234527.22 | 335471832 | 99524574 | 49997566 | 0.000000 | 632136353 | 64024805 | 0.000000
09-04-2025 15:02:55000 | -1355295 | 135.5295 | 13078981 | 234508.44 | 335237518 | 99537590 | 49982433 | 0.000000 | 650304138 | 65905586 | 0.000000
09-04-2025 15:03:00000 | -1355360 | 135.536 | 12992862 | 234466.27 | 335289673 | 99543655 | 49959141 | 0.000000 | 668357971 | 67786753 | 0.000000
09-04-2025 15:03:05000 | -1352086 | 135.2086 | 12614950 | 234440.27 | 334436890 | 99567574 | 49948601 | 0.000000 | 686016602 | 69665063 | 0.000000
09-04-2025 15:03:10000 | -1351707 | 135.1707 | 13015164 | 234551.30 | 334282166 | 99539642 | 49979752 | 0.000000 | 703873657 | 71541118 | 0.000000
09-04-2025 15:03:15000 | -1357669 | 135.7669 | 13446850 | 234604.03 | 335773712 | 99513100 | 50007233 | 0.000000 | 722272339 | 73421133 | 0.000000
09-04-2025 15:03:20000 | -1359252 | 135.9252 | 13215368 | 234470.66 | 336293793 | 99530685 | 49981636 | 0.000000 | 740701904 | 75304951 | 0.000000
09-04-2025 15:03:25000 | -1353038 | 135.3038 | 12766157 | 234462.66 | 334675873 | 99557838 | 49958008 | 0.000000 | 758660889 | 77186709 | 0.000000
09-04-2025 15:03:30000 | -1348667 | 134.8667 | 12921173 | 234577.41 | 333476532 | 99544189 | 49981701 | 0.000000 | 776439453 | 79060278 | 0.000000
09-04-2025 15:03:35000 | -1347507 | 134.7507 | 13194676 | 234639.31 | 333170441 | 99524010 | 50027328 | 0.000000 | 794576477 | 80930444 | 0.000000
09-04-2025 15:03:40000 | -1355055 | 135.5055 | 13396559 | 234519.80 | 335242188 | 99514854 | 50040154 | 0.000000 | 813297302 | 82811631 | 0.000000
09-04-2025 15:03:45000 | -1356938 | 135.6938 | 13231427 | 234502.59 | 335683594 | 99527962 | 50003277 | 0.000000 | 831739746 | 84695078 | 0.000000
09-04-2025 15:03:50000 | -1352290 | 135.229 | 13162433 | 234587.81 | 334409882 | 99529640 | 50006031 | 0.000000 | 849966064 | 86572559 | 0.000000
09-04-2025 15:03:55000 | -1352826 | 135.2826 | 13215092 | 234571.81 | 334575287 | 99526268 | 50017982 | 0.000000 | 868353699 | 88451729 | 0.000000
09-04-2025 15:04:00000 | -1357946 | 135.7946 | 13294191 | 234497.94 | 335960144 | 99524200 | 50007011 | 0.000000 | 886763672 | 90333564 | 0.000000
09-04-2025 15:04:05000 | -1351147 | 135.1147 | 13190402 | 234622.75 | 334082306 | 99526863 | 50003716 | 0.000000 | 904988708 | 92211113 | 0.000000
09-04-2025 15:04:10000 | -1353071 | 135.3071 | 13134630 | 234512.17 | 334702820 | 99532150 | 49989868 | 0.000000 | 923419189 | 94092549 | 0.000000
09-04-2025 15:04:15000 | -1354614 | 135.4614 | 13294514 | 234569.45 | 335031738 | 99521851 | 49996719 | 0.000000 | 941697266 | 95970283 | 0.000000
09-04-2025 15:04:20000 | -1351578 | 135.1578 | 13182240 | 234580.86 | 334251831 | 99527740 | 49972340 | 0.000000 | 959959351 | 97846396 | 0.000000
09-04-2025 15:04:25000 | -1346526 | 134.6526 | 12923423 | 234583.98 | 332947571 | 99542587 | 49945435 | 0.000000 | 978137207 | 99723975 | 0.000000
09-04-2025 15:04:30000 | -1350452 | 135.0452 | 13430028 | 234662.63 | 333910248 | 99509140 | 49992649 | 0.000000 | 996346802 | 10159625 | 0.000000
09-04-2025 15:04:35000 | -1349618 | 134.9618 | 13295133 | 234585.89 | 333788696 | 99518288 | 49994946 | 0.000000 | 10149833 | 10347313 | 0.000000
09-04-2025 15:04:40000 | -1354398 | 135.4398 | 13274012 | 234489.20 | 335089325 | 99523163 | 49976776 | 0.000000 | 10336017 | 10535449 | 0.000000
09-04-2025 15:04:45000 | -1352090 | 135.209 | 13015422 | 234510.42 | 334437195 | 99539879 | 49953789 | 0.000000 | 10517483 | 10723295 | 0.000000
09-04-2025 15:04:50000 | -1355699 | 135.5699 | 13283573 | 234581.91 | 335276428 | 99523392 | 49978069 | 0.000000 | 10699867 | 10911319 | 0.000000
09-04-2025 15:04:55000 | -1350306 | 135.0306 | 13001919 | 234537.16 | 333960876 | 99539627 | 49982903 | 0.000000 | 10882009 | 11099181 | 0.000000
09-04-2025 15:05:00000 | -1355633 | 135.5633 | 13320985 | 234547.67 | 335326813 | 99520676 | 49999676 | 0.000000 | 11064203 | 11286726 | 0.000000
09-04-2025 15:05:05000 | -1349402 | 134.9402 | 13134969 | 234575.06 | 333726532 | 99529594 | 49980961 | 0.000000 | 11248755 | 11474938 | 0.000000
09-04-2025 15:05:10000 | -1349483 | 134.9483 | 13222230 | 234636.19 | 333670349 | 99523422 | 50004528 | 0.000000 | 11431664 | 11662562 | 0.000000
09-04-2025 15:05:15000 | -1352375 | 135.2375 | 13337834 | 234581.45 | 334478058 | 99517174 | 50026798 | 0.000000 | 11617415 | 11850429 | 0.000000
09-04-2025 15:05:20000 | -1350330 | 135.033 | 13410699 | 234620.38 | 333955292 | 99510452 | 50032413 | 0.000000 | 11804423 | 12038508 | 0.000000
09-04-2025 15:05:25000 | -1349500 | 134.95 | 13292672 | 234632.67 | 333689240 | 99518379 | 50022537 | 0.000000 | 11990249 | 12226530 | 0.000000
09-04-2025 15:05:30000 | -1351051 | 135.1051 | 13243836 | 234601.25 | 334105530 | 99522980 | 50007423 | 0.000000 | 12173661 | 12414341 | 0.000000
09-04-2025 15:05:35000 | -1348328 | 134.8328 | 12979212 | 234543.16 | 333453735 | 99539879 | 49989559 | 0.000000 | 12355669 | 12601938 | 0.000000
09-04-2025 15:05:40000 | -1351309 | 135.1309 | 13053656 | 234516.97 | 334242065 | 99536659 | 49974155 | 0.000000 | 12537307 | 12789645 | 0.000000
09-04-2025 15:05:45000 | -1344838 | 134.4838 | 13103310 | 234639.63 | 332494568 | 99528679 | 50007149 | 0.000000 | 12719078 | 12976931 | 0.000000
09-04-2025 15:05:50000 | -1354245 | 135.4245 | 13455285 | 234547.42 | 335016052 | 99510040 | 50042534 | 0.000000 | 12906456 | 13164799 | 0.000000
09-04-2025 15:05:55000 | -1353264 | 135.3264 | 13397459 | 234567.34 | 334736481 | 99513512 | 50033192 | 0.000000 | 13092955 | 13352812 | 0.000000
09-04-2025 15:06:00000 | -1350299 | 135.0299 | 13274764 | 234628.56 | 333888397 | 99520233 | 50037636 | 0.000000 | 13277856 | 13540307 | 0.000000
09-04-2025 15:06:05000 | -1350508 | 135.0508 | 13445774 | 234649.91 | 333952332 | 99508034 | 50050949 | 0.000000 | 13463889 | 13727771 | 0.000000
09-04-2025 15:06:10000 | -1354800 | 135.48 | 13539911 | 234627.03 | 335059723 | 99504303 | 50052036 | 0.000000 | 13651194 | 13915568 | 0.000000
09-04-2025 15:06:15000 | -1351948 | 135.1948 | 13363055 | 234591.08 | 334366638 | 99515053 | 50044437 | 0.000000 | 13837037 | 14103323 | 0.000000
09-04-2025 15:06:20000 | -1351142 | 135.1142 | 13419405 | 234630.30 | 334133850 | 99510406 | 50045082 | 0.000000 | 14023829 | 14291128 | 0.000000
09-04-2025 15:06:25000 | -1351446 | 135.1446 | 13440328 | 234621.97 | 334222412 | 99509109 | 50039898 | 0.000000 | 14210453 | 14478700 | 0.000000
09-04-2025 15:06:30000 | -1352243 | 135.2243 | 13448774 | 234623.70 | 334419647 | 99509071 | 50039551 | 0.000000 | 14395946 | 14666090 | 0.000000
09-04-2025 15:06:35000 | -1347136 | 134.7136 | 13316754 | 234670.95 | 333064453 | 99514961 | 50040833 | 0.000000 | 14580398 | 14853431 | 0.000000
09-04-2025 15:06:40000 | -1353803 | 135.3803 | 13632549 | 234581.38 | 334909302 | 99496819 | 50046848 | 0.000000 | 14768468 | 15040812 | 0.000000
09-04-2025 15:06:45000 | -1344503 | 134.4503 | 13081093 | 234581.06 | 332488831 | 99530037 | 50008194 | 0.000000 | 14953444 | 15228334 | 0.000000
09-04-2025 15:06:50000 | -1347165 | 134.7165 | 13166713 | 234567.84 | 333186615 | 99525772 | 50015629 | 0.000000 | 15135591 | 15415320 | 0.000000
09-04-2025 15:06:55000 | -1350450 | 135.045 | 13223635 | 234579.14 | 333985504 | 99524002 | 50010887 | 0.000000 | 15318748 | 15602750 | 0.000000
09-04-2025 15:07:00000 | -1349664 | 134.9664 | 13107872 | 234510.36 | 333859741 | 99531700 | 50024284 | 0.000000 | 15501355 | 15789813 | 0.000000
09-04-2025 15:07:05000 | -1352294 | 135.2294 | 12928150 | 234421.94 | 334592499 | 99546127 | 50000404 | 0.000000 | 15682998 | 15977544 | 0.000000
09-04-2025 15:07:10000 | -1343993 | 134.3993 | 12581782 | 234446.81 | 332441284 | 99564674 | 49957314 | 0.000000 | 15860579 | 16164883 | 0.000000
09-04-2025 15:07:15000 | -1339339 | 133.9339 | 12942660 | 234616.69 | 331145081 | 99536331 | 50006783 | 0.000000 | 16037218 | 16350904 | 0.000000
09-04-2025 15:07:20000 | -1348638 | 134.8638 | 13292742 | 234538.80 | 333615631 | 99517769 | 50031883 | 0.000000 | 16221461 | 16537914 | 0.000000
09-04-2025 15:07:25000 | -1355276 | 135.5276 | 13617026 | 234587.70 | 335250793 | 99499039 | 50048405 | 0.000000 | 16407321 | 16725152 | 0.000000
09-04-2025 15:07:30000 | -1349640 | 134.964 | 13329285 | 234599.09 | 333780243 | 99515846 | 50037621 | 0.000000 | 16593949 | 16912807 | 0.000000
09-04-2025 15:07:35000 | -1350096 | 135.0096 | 13333625 | 234608.61 | 333878662 | 99515854 | 50028454 | 0.000000 | 16778901 | 17100334 | 0.000000
09-04-2025 15:07:40000 | -1352168 | 135.2168 | 13509024 | 234608.89 | 334428436 | 99504639 | 50034908 | 0.000000 | 16966810 | 17287930 | 0.000000
09-04-2025 15:07:45000 | -1351768 | 135.1768 | 13248158 | 234520.23 | 334396820 | 99523170 | 49989792 | 0.000000 | 17152854 | 17475971 | 0.000000
09-04-2025 15:07:50000 | -1350985 | 135.0985 | 13187756 | 234583.95 | 334099884 | 99526932 | 49974369 | 0.000000 | 17334921 | 17663563 | 0.000000
09-04-2025 15:07:55000 | -1349006 | 134.9006 | 13174616 | 234589.14 | 333605286 | 99526497 | 49979218 | 0.000000 | 17517058 | 17850859 | 0.000000
09-04-2025 15:08:00000 | -1347588 | 134.7588 | 13049111 | 234533.53 | 333310699 | 99534439 | 49972847 | 0.000000 | 17699880 | 18038232 | 0.000000
09-04-2025 15:08:05000 | -1345213 | 134.5213 | 12996196 | 234571.28 | 332658783 | 99536560 | 49979832 | 0.000000 | 17880939 | 18225328 | 0.000000
09-04-2025 15:08:10000 | -1346671 | 134.6671 | 13168647 | 234588.48 | 333035156 | 99525291 | 49992184 | 0.000000 | 18062656 | 18412375 | 0.000000
09-04-2025 15:08:15000 | -1350229 | 135.0229 | 13305822 | 234595.72 | 333928253 | 99517952 | 50004803 | 0.000000 | 18246820 | 18599727 | 0.000000
09-04-2025 15:08:20000 | -1352497 | 135.2497 | 13506354 | 234628.00 | 334485138 | 99505074 | 50028641 | 0.000000 | 18431797 | 18787078 | 0.000000
09-04-2025 15:08:25000 | -1359267 | 135.9267 | 13575412 | 234560.67 | 336259552 | 99504967 | 50036530 | 0.000000 | 18619352 | 18974979 | 0.000000
09-04-2025 15:08:30000 | -1345662 | 134.5662 | 13358178 | 234702.55 | 332675415 | 99510902 | 50035919 | 0.000000 | 18805967 | 19162732 | 0.000000
09-04-2025 15:08:35000 | -1351529 | 135.1529 | 13677529 | 234711.47 | 334173645 | 99491821 | 50065350 | 0.000000 | 18994149 | 19350373 | 0.000000
09-04-2025 15:08:40000 | -1349823 | 134.9823 | 13767041 | 234731.41 | 333745026 | 99483910 | 50066570 | 0.000000 | 19185557 | 19538410 | 0.000000
09-04-2025 15:08:45000 | -1353292 | 135.3292 | 13836437 | 234689.77 | 334670715 | 99481384 | 50066956 | 0.000000 | 19377701 | 19726271 | 0.000000
09-04-2025 15:08:50000 | -1353233 | 135.3233 | 13888424 | 234744.17 | 334590973 | 99477463 | 50058537 | 0.000000 | 19570532 | 19914422 | 0.000000
09-04-2025 15:08:55000 | -1353341 | 135.3341 | 13752545 | 234694.13 | 334656311 | 99487640 | 50050682 | 0.000000 | 19761737 | 20102303 | 0.000000
09-04-2025 15:09:00000 | -1355312 | 135.5312 | 13702625 | 234620.50 | 335237427 | 99492790 | 50037487 | 0.000000 | 19952092 | 20290367 | 0.000000
09-04-2025 15:09:05000 | -1353354 | 135.3354 | 13454656 | 234608.33 | 334709625 | 99509445 | 50017246 | 0.000000 | 20139525 | 20478387 | 0.000000
09-04-2025 15:09:10000 | -1356213 | 135.6213 | 13384545 | 234600.22 | 335404907 | 99516541 | 50010952 | 0.000000 | 20326000 | 20666621 | 0.000000
09-04-2025 15:09:15000 | -1355070 | 135.507 | 13687366 | 234667.73 | 335099762 | 99493736 | 50046619 | 0.000000 | 20513694 | 20854553 | 0.000000
09-04-2025 15:09:20000 | -1360068 | 136.0068 | 13831478 | 234656.77 | 336376373 | 99486862 | 50060429 | 0.000000 | 20704197 | 21042959 | 0.000000
09-04-2025 15:09:25000 | -1356228 | 135.6228 | 13641095 | 234661.45 | 335377563 | 99497978 | 50039856 | 0.000000 | 20894124 | 21231475 | 0.000000
09-04-2025 15:09:30000 | -1352389 | 135.2389 | 13502719 | 234687.66 | 334373932 | 99505257 | 50039646 | 0.000000 | 21083767 | 21420012 | 0.000000
09-04-2025 15:09:35000 | -1353860 | 135.386 | 13566899 | 234647.34 | 334806763 | 99501656 | 50034325 | 0.000000 | 21270984 | 21608074 | 0.000000
09-04-2025 15:09:40000 | -1355370 | 135.537 | 13610521 | 234647.23 | 335185333 | 99499580 | 50052261 | 0.000000 | 21459731 | 21796137 | 0.000000
09-04-2025 15:09:45000 | -1355042 | 135.5042 | 13673630 | 234672.20 | 335090118 | 99494720 | 50048092 | 0.000000 | 21649600 | 21984504 | 0.000000
09-04-2025 15:09:50000 | -1359425 | 135.9425 | 13705614 | 234628.02 | 336232605 | 99495613 | 50047539 | 0.000000 | 21838511 | 22172822 | 0.000000
09-04-2025 15:09:55000 | -1355621 | 135.5621 | 13507774 | 234628.58 | 335248108 | 99507233 | 50044781 | 0.000000 | 22026985 | 22361256 | 0.000000
09-04-2025 15:10:00000 | -1355253 | 135.5253 | 13520005 | 234648.08 | 335134186 | 99506081 | 50052528 | 0.000000 | 22214146 | 22549352 | 0.000000
09-04-2025 15:10:05000 | -1350800 | 135.08 | 13658126 | 234698.13 | 334002655 | 99492714 | 50061726 | 0.000000 | 22403604 | 22737322 | 0.000000
09-04-2025 15:10:10000 | -1353160 | 135.316 | 13604180 | 234677.14 | 334604370 | 99498421 | 50058434 | 0.000000 | 22593218 | 22925629 | 0.000000
09-04-2025 15:10:15000 | -1362608 | 136.2608 | 13843496 | 234607.69 | 337068695 | 99487877 | 50059078 | 0.000000 | 22783879 | 23114055 | 0.000000
09-04-2025 15:10:20000 | -1355568 | 135.5568 | 13558468 | 234654.75 | 335207733 | 99503517 | 50055233 | 0.000000 | 22972683 | 23302512 | 0.000000
09-04-2025 15:10:25000 | -1355186 | 135.5186 | 13752561 | 234717.16 | 335076202 | 99489021 | 50077568 | 0.000000 | 23163716 | 23490977 | 0.000000
09-04-2025 15:10:30000 | -1359853 | 135.9853 | 13975591 | 234717.75 | 336270050 | 99476036 | 50101871 | 0.000000 | 23357632 | 23679598 | 0.000000
09-04-2025 15:10:35000 | -1361716 | 136.1716 | 14038137 | 234678.38 | 336796326 | 99472809 | 50105545 | 0.000000 | 23551992 | 23868588 | 0.000000
09-04-2025 15:10:40000 | -1361743 | 136.1743 | 13918953 | 234685.77 | 336771393 | 99481674 | 50086327 | 0.000000 | 23745164 | 24057490 | 0.000000
09-04-2025 15:10:45000 | -1358983 | 135.8983 | 13748971 | 234663.41 | 336076630 | 99492119 | 50043503 | 0.000000 | 23938232 | 24246697 | 0.000000
09-04-2025 15:10:50000 | -1360149 | 136.0149 | 13880384 | 234730.20 | 336307739 | 99483315 | 50049549 | 0.000000 | 24128926 | 24435320 | 0.000000
09-04-2025 15:10:55000 | -1362200 | 136.22 | 13904151 | 234657.09 | 336915375 | 99483109 | 50047279 | 0.000000 | 24321858 | 24624281 | 0.000000
09-04-2025 15:11:00000 | -1362127 | 136.2127 | 13939129 | 234720.41 | 336813934 | 99480469 | 50060493 | 0.000000 | 24513787 | 24813041 | 0.000000
09-04-2025 15:11:05000 | -1362196 | 136.2196 | 13801707 | 234627.86 | 336928467 | 99490639 | 50056774 | 0.000000 | 24706409 | 25002084 | 0.000000
09-04-2025 15:11:10000 | -1360521 | 136.0521 | 13725467 | 234629.86 | 336497040 | 99494972 | 50047283 | 0.000000 | 24897578 | 25191164 | 0.000000
09-04-2025 15:11:15000 | -1360151 | 136.0151 | 13627367 | 234657.67 | 336348175 | 99501846 | 50042969 | 0.000000 | 25085134 | 25379764 | 0.000000
09-04-2025 15:11:20000 | -1361332 | 136.1332 | 13918830 | 234724.50 | 336611053 | 99481369 | 50058449 | 0.000000 | 25275837 | 25568350 | 0.000000
09-04-2025 15:11:25000 | -1360214 | 136.0214 | 13598995 | 234599.08 | 336435974 | 99503944 | 50032238 | 0.000000 | 25467112 | 25757348 | 0.000000
09-04-2025 15:11:30000 | -1357022 | 135.7022 | 13504868 | 234651.72 | 335557404 | 99508453 | 50030228 | 0.000000 | 25654387 | 25945893 | 0.000000
09-04-2025 15:11:35000 | -1359779 | 135.9779 | 13645503 | 234645.69 | 336274353 | 99500259 | 50051521 | 0.000000 | 25843103 | 26134650 | 0.000000
09-04-2025 15:11:40000 | -1359484 | 135.9484 | 13875661 | 234733.11 | 336132935 | 99483162 | 50087326 | 0.000000 | 26035227 | 26323486 | 0.000000
09-04-2025 15:11:45000 | -1366181 | 136.6181 | 14041785 | 234683.02 | 337888550 | 99475952 | 50087170 | 0.000000 | 26229233 | 26512707 | 0.000000
09-04-2025 15:11:50000 | -1359568 | 135.9568 | 13838443 | 234715.09 | 336167633 | 99485977 | 50069221 | 0.000000 | 26421936 | 26701705 | 0.000000
09-04-2025 15:11:55000 | -1359089 | 135.9089 | 13883357 | 234727.03 | 336051361 | 99482300 | 50060627 | 0.000000 | 26615496 | 26890893 | 0.000000
09-04-2025 15:12:00000 | -1361175 | 136.1175 | 14165442 | 234781.36 | 336550262 | 99462852 | 50083389 | 0.000000 | 26810889 | 27079814 | 0.000000
09-04-2025 15:12:05000 | -1363331 | 136.3331 | 14267754 | 234762.56 | 337129303 | 99456841 | 50107353 | 0.000000 | 27008757 | 27268865 | 0.000000
09-04-2025 15:12:10000 | -1362373 | 136.2373 | 14313505 | 234751.69 | 336925049 | 99452614 | 50114719 | 0.000000 | 27209292 | 27458230 | 0.000000
09-04-2025 15:12:15000 | -1360599 | 136.0599 | 14002489 | 234710.97 | 336471161 | 99474602 | 50075333 | 0.000000 | 27405754 | 27647637 | 0.000000
09-04-2025 15:12:20000 | -1362671 | 136.2671 | 13803616 | 234623.02 | 337052002 | 99490852 | 50042629 | 0.000000 | 27598596 | 27836822 | 0.000000
09-04-2025 15:12:25000 | -1361772 | 136.1772 | 13837751 | 234702.56 | 336735687 | 99487679 | 50035782 | 0.000000 | 27790105 | 28025939 | 0.000000
09-04-2025 15:12:30000 | -1362578 | 136.2578 | 13805096 | 234648.27 | 336993958 | 99490669 | 50033920 | 0.000000 | 27981497 | 28214998 | 0.000000
09-04-2025 15:12:35000 | -1360359 | 136.0359 | 13696129 | 234611.67 | 336480408 | 99496994 | 50023342 | 0.000000 | 28172603 | 28404262 | 0.000000
09-04-2025 15:12:40000 | -1360899 | 136.0899 | 13716441 | 234677.30 | 336519287 | 99495911 | 50047054 | 0.000000 | 28362703 | 28593145 | 0.000000
09-04-2025 15:12:45000 | -1362187 | 136.2187 | 13486249 | 234563.84 | 336942291 | 99513481 | 50033432 | 0.000000 | 28551904 | 28782197 | 0.000000
09-04-2025 15:12:50000 | -1356873 | 135.6873 | 13502287 | 234659.44 | 335509949 | 99508530 | 50040939 | 0.000000 | 28740273 | 28971115 | 0.000000
09-04-2025 15:12:55000 | -1362142 | 136.2142 | 13750556 | 234641.31 | 336888672 | 99494339 | 50058407 | 0.000000 | 28930461 | 29160174 | 0.000000
09-04-2025 15:13:00000 | -1359321 | 135.9321 | 13680548 | 234666.59 | 336142517 | 99497368 | 50041603 | 0.000000 | 29121038 | 29349299 | 0.000000
09-04-2025 15:13:05000 | -1357944 | 135.7944 | 13560370 | 234635.52 | 335819153 | 99505104 | 50026211 | 0.000000 | 29310349 | 29538332 | 0.000000
09-04-2025 15:13:10000 | -1359172 | 135.9172 | 13553549 | 234619.22 | 336138458 | 99506485 | 50021618 | 0.000000 | 29498562 | 29727193 | 0.000000
09-04-2025 15:13:15000 | -1353877 | 135.3877 | 13620883 | 234714.89 | 334725830 | 99497726 | 50051777 | 0.000000 | 29686792 | 29915324 | 0.000000
09-04-2025 15:13:20000 | -1355850 | 135.585 | 13885342 | 234730.94 | 335246948 | 99479691 | 50077316 | 0.000000 | 29878335 | 30103494 | 0.000000
09-04-2025 15:13:25000 | -1357543 | 135.7543 | 14063429 | 234767.63 | 335656677 | 99467690 | 50078945 | 0.000000 | 30072136 | 30291922 | 0.000000
09-04-2025 15:13:30000 | -1354917 | 135.4917 | 14068127 | 234804.05 | 334964508 | 99465286 | 50081882 | 0.000000 | 30267498 | 30480336 | 0.000000
09-04-2025 15:13:35000 | -1359170 | 135.917 | 14118265 | 234750.97 | 336099670 | 99464836 | 50075680 | 0.000000 | 30463445 | 30668932 | 0.000000
09-04-2025 15:13:40000 | -1361409 | 136.1409 | 13995125 | 234666.55 | 336732727 | 99475769 | 50042637 | 0.000000 | 30658245 | 30857885 | 0.000000
09-04-2025 15:13:45000 | -1355855 | 135.5855 | 13698036 | 234702.14 | 335252258 | 99493530 | 50040138 | 0.000000 | 30849895 | 31046596 | 0.000000
09-04-2025 15:13:50000 | -1355603 | 135.5603 | 13645038 | 234665.02 | 335224792 | 99497231 | 50034439 | 0.000000 | 31041340 | 31235293 | 0.000000
09-04-2025 15:13:55000 | -1356313 | 135.6313 | 13718861 | 234696.94 | 335373993 | 99492348 | 50023312 | 0.000000 | 31230481 | 31423705 | 0.000000
09-04-2025 15:14:00000 | -1351799 | 135.1799 | 13705375 | 234713.42 | 334243317 | 99489967 | 50021202 | 0.000000 | 31422021 | 31612074 | 0.000000
09-04-2025 15:14:05000 | -1357008 | 135.7008 | 13572062 | 234605.75 | 335634308 | 99503578 | 50016361 | 0.000000 | 31612202 | 31800461 | 0.000000
09-04-2025 15:14:10000 | -1359619 | 135.9619 | 13628798 | 234618.69 | 336266205 | 99501350 | 50010834 | 0.000000 | 31800444 | 31989066 | 0.000000
09-04-2025 15:14:15000 | -1356883 | 135.6883 | 13837666 | 234725.39 | 335499329 | 99484009 | 50037697 | 0.000000 | 31990654 | 32177238 | 0.000000
09-04-2025 15:14:20000 | -1351071 | 135.1071 | 13645192 | 234728.03 | 334023041 | 99493866 | 50043831 | 0.000000 | 32181113 | 32365451 | 0.000000
09-04-2025 15:14:25000 | -1358675 | 135.8675 | 13908656 | 234696.61 | 335997040 | 99480110 | 50052635 | 0.000000 | 32373394 | 32553951 | 0.000000
09-04-2025 15:14:30000 | -1358048 | 135.8048 | 13876165 | 234687.34 | 335851563 | 99482040 | 50053967 | 0.000000 | 32566240 | 32742498 | 0.000000
09-04-2025 15:14:35000 | -1353715 | 135.3715 | 13855235 | 234760.06 | 334676514 | 99480309 | 50054543 | 0.000000 | 32758984 | 32931000 | 0.000000
09-04-2025 15:14:40000 | -1356715 | 135.6715 | 14156658 | 234770.28 | 335475006 | 99460014 | 50079731 | 0.000000 | 32954731 | 33119258 | 0.000000
09-04-2025 15:14:45000 | -1355058 | 135.5058 | 14084909 | 234772.75 | 335053253 | 99464127 | 50074089 | 0.000000 | 33149795 | 33307316 | 0.000000
09-04-2025 15:14:50000 | -1349569 | 134.9569 | 13968903 | 234817.83 | 333611115 | 99468590 | 50076809 | 0.000000 | 33344832 | 33495172 | 0.000000
09-04-2025 15:14:55000 | -1357905 | 135.7905 | 14377967 | 234784.13 | 335798950 | 99444107 | 50102806 | 0.000000 | 33542075 | 33682984 | 0.000000
09-04-2025 15:15:00000 | -1354479 | 135.4479 | 14058403 | 234732.48 | 334956055 | 99465675 | 50082153 | 0.000000 | 33739587 | 33871277 | 0.000000
09-04-2025 15:15:05000 | -1353165 | 135.3165 | 14123155 | 234800.69 | 334552673 | 99459740 | 50084736 | 0.000000 | 19534203 | 188079712 | 0.000000
09-04-2025 15:15:10000 | -1358370 | 135.837 | 14198419 | 234738.81 | 335938690 | 99458160 | 50076435 | 0.000000 | 39208862 | 376318481 | 0.000000
09-04-2025 15:15:15000 | -1356539 | 135.6539 | 13960629 | 234694.16 | 335497192 | 99474609 | 50054733 | 0.000000 | 58689247 | 564579224 | 0.000000
09-04-2025 15:15:20000 | -1355221 | 135.5221 | 13926414 | 234723.13 | 335122498 | 99476151 | 50043182 | 0.000000 | 77968620 | 752738586 | 0.000000
09-04-2025 15:15:25000 | -1351166 | 135.1166 | 14282605 | 234860.75 | 334020691 | 99445953 | 50109089 | 0.000000 | 97555969 | 939809082 | 0.000000
09-04-2025 15:15:30000 | -1353764 | 135.3764 | 14232771 | 234769.55 | 334770569 | 99451874 | 50097672 | 0.000000 | 117460205 | 11278566 | 0.000000
09-04-2025 15:15:35000 | -1356727 | 135.6727 | 14151059 | 234732.34 | 335529541 | 99460442 | 50057953 | 0.000000 | 137216888 | 13161913 | 0.000000
09-04-2025 15:15:40000 | -1347911 | 134.7911 | 13872861 | 234794.17 | 333217712 | 99474533 | 50036621 | 0.000000 | 156561539 | 15039543 | 0.000000
09-04-2025 15:15:45000 | -1352225 | 135.2225 | 14021521 | 234783.77 | 334324341 | 99466690 | 50055817 | 0.000000 | 175869553 | 16912866 | 0.000000
09-04-2025 15:15:50000 | -1352811 | 135.2811 | 14240553 | 234816.28 | 334478729 | 99450508 | 50050739 | 0.000000 | 195428787 | 18789403 | 0.000000
09-04-2025 15:15:55000 | -1347125 | 134.7125 | 13971443 | 234785.34 | 333064606 | 99466484 | 50041431 | 0.000000 | 214996155 | 20663611 | 0.000000
09-04-2025 15:16:00000 | -1349163 | 134.9163 | 14094498 | 234808.44 | 333560455 | 99458740 | 50056072 | 0.000000 | 234520126 | 22536995 | 0.000000
09-04-2025 15:16:05000 | -1346357 | 134.6357 | 14122069 | 234823.72 | 332855286 | 99454391 | 50053642 | 0.000000 | 254170395 | 24409448 | 0.000000
09-04-2025 15:16:10000 | -1345385 | 134.5385 | 14311268 | 234876.83 | 332597504 | 99438995 | 50084831 | 0.000000 | 273902557 | 26277681 | 0.000000
09-04-2025 15:16:15000 | -1351062 | 135.1062 | 14263211 | 234767.28 | 334125092 | 99447357 | 50071995 | 0.000000 | 293895325 | 28153977 | 0.000000
09-04-2025 15:16:20000 | -1351266 | 135.1266 | 14125710 | 234757.98 | 334152557 | 99458038 | 50045235 | 0.000000 | 313513153 | 30028262 | 0.000000
09-04-2025 15:16:25000 | -1344863 | 134.4863 | 14193386 | 234885.02 | 332424835 | 99447701 | 50057682 | 0.000000 | 333183624 | 31899546 | 0.000000
09-04-2025 15:16:30000 | -1346588 | 134.6588 | 14176689 | 234814.06 | 332939941 | 99450386 | 50056423 | 0.000000 | 352900238 | 33768994 | 0.000000
09-04-2025 15:16:35000 | -1349902 | 134.9902 | 14180545 | 234761.39 | 333826111 | 99452766 | 50029408 | 0.000000 | 372550751 | 35643027 | 0.000000
09-04-2025 15:16:40000 | -1346263 | 134.6263 | 14047057 | 234825.42 | 332811859 | 99460052 | 50028778 | 0.000000 | 392119110 | 37515542 | 0.000000
09-04-2025 15:16:45000 | -1347594 | 134.7594 | 13940704 | 234751.41 | 333213989 | 99469170 | 50021370 | 0.000000 | 411704315 | 39391157 | 0.000000
09-04-2025 15:16:50000 | -1349246 | 134.9246 | 14053764 | 234764.58 | 333634094 | 99461906 | 50020245 | 0.000000 | 431093201 | 41264478 | 0.000000
09-04-2025 15:16:55000 | -1348012 | 134.8012 | 13880537 | 234726.73 | 333340881 | 99474030 | 50010719 | 0.000000 | 450484131 | 43137314 | 0.000000
09-04-2025 15:17:00000 | -1339739 | 133.9739 | 13619850 | 234761.27 | 331205505 | 99487228 | 49991611 | 0.000000 | 469612732 | 45007007 | 0.000000
09-04-2025 15:17:05000 | -1348815 | 134.8815 | 13957771 | 234755.47 | 333511932 | 99468842 | 50012054 | 0.000000 | 488743622 | 46873862 | 0.000000
09-04-2025 15:17:10000 | -1349841 | 134.9841 | 13882253 | 234701.00 | 333819946 | 99475319 | 49997604 | 0.000000 | 508161621 | 48748662 | 0.000000
09-04-2025 15:17:15000 | -1348029 | 134.8029 | 13666854 | 234721.17 | 333296265 | 99489990 | 49972687 | 0.000000 | 527250427 | 50623794 | 0.000000
09-04-2025 15:17:20000 | -1348871 | 134.8871 | 13945461 | 234800.02 | 333459259 | 99469810 | 50004517 | 0.000000 | 546415466 | 52494790 | 0.000000
09-04-2025 15:17:25000 | -1351387 | 135.1387 | 14200084 | 234811.47 | 334123962 | 99452461 | 50046204 | 0.000000 | 565957214 | 54367930 | 0.000000
09-04-2025 15:17:30000 | -1357115 | 135.7115 | 14325621 | 234757.05 | 335634644 | 99447472 | 50052631 | 0.000000 | 585722778 | 56247554 | 0.000000
09-04-2025 15:17:35000 | -1349938 | 134.9938 | 13949670 | 234762.77 | 333774536 | 99470322 | 50024559 | 0.000000 | 605457336 | 58129268 | 0.000000
09-04-2025 15:17:40000 | -1352752 | 135.2752 | 14246689 | 234809.06 | 334484497 | 99449997 | 50047958 | 0.000000 | 625103821 | 60007300 | 0.000000
09-04-2025 15:17:45000 | -1352815 | 135.2815 | 14398074 | 234866.83 | 334446442 | 99438393 | 50058228 | 0.000000 | 644995056 | 61886484 | 0.000000
09-04-2025 15:17:50000 | -1349285 | 134.9285 | 14296069 | 234844.88 | 333590698 | 99443382 | 50065254 | 0.000000 | 664855713 | 63761313 | 0.000000
09-04-2025 15:17:55000 | -1354386 | 135.4386 | 14564517 | 234875.11 | 334860138 | 99426765 | 50076946 | 0.000000 | 684940369 | 65640210 | 0.000000
09-04-2025 15:18:00000 | -1354066 | 135.4066 | 14389156 | 234794.77 | 334852112 | 99440109 | 50049778 | 0.000000 | 705114258 | 67522544 | 0.000000
09-04-2025 15:18:05000 | -1351767 | 135.1767 | 14024079 | 234765.28 | 334237183 | 99466141 | 50013378 | 0.000000 | 724821106 | 69403071 | 0.000000
09-04-2025 15:18:10000 | -1351591 | 135.1591 | 14103102 | 234773.95 | 334206390 | 99460014 | 50012596 | 0.000000 | 744227295 | 71278105 | 0.000000
09-04-2025 15:18:15000 | -1352227 | 135.2227 | 14037073 | 234784.20 | 334326447 | 99465523 | 50020134 | 0.000000 | 763709412 | 73153496 | 0.000000
09-04-2025 15:18:20000 | -1346939 | 134.6939 | 13823988 | 234751.30 | 333026215 | 99477455 | 50011314 | 0.000000 | 783193542 | 75030337 | 0.000000
09-04-2025 15:18:25000 | -1349725 | 134.9725 | 13944768 | 234771.67 | 333706787 | 99470528 | 50015961 | 0.000000 | 802400757 | 76903486 | 0.000000
09-04-2025 15:18:30000 | -1352454 | 135.2454 | 14257882 | 234846.95 | 334348114 | 99448898 | 50025570 | 0.000000 | 821950378 | 78777578 | 0.000000
09-04-2025 15:18:35000 | -1349970 | 134.997 | 14269476 | 234829.50 | 333766296 | 99445992 | 50037243 | 0.000000 | 841802185 | 80654609 | 0.000000
09-04-2025 15:18:40000 | -1352999 | 135.2999 | 14340368 | 234828.23 | 334530029 | 99443001 | 50043835 | 0.000000 | 861786560 | 82534580 | 0.000000
09-04-2025 15:18:45000 | -1355003 | 135.5003 | 14480719 | 234890.20 | 334968414 | 99433800 | 50051292 | 0.000000 | 881787842 | 84414297 | 0.000000
09-04-2025 15:18:50000 | -1351573 | 135.1573 | 14383468 | 234874.59 | 334123993 | 99438499 | 50056252 | 0.000000 | 901910889 | 86295566 | 0.000000
09-04-2025 15:18:55000 | -1356252 | 135.6252 | 14581779 | 234849.27 | 335354858 | 99426987 | 50062931 | 0.000000 | 922027954 | 88176162 | 0.000000
09-04-2025 15:19:00000 | -1358952 | 135.8952 | 14546532 | 234839.69 | 336023254 | 99431976 | 50063286 | 0.000000 | 942247253 | 90060801 | 0.000000
09-04-2025 15:19:05000 | -1356699 | 135.6699 | 14327647 | 234799.73 | 335469513 | 99446983 | 50051907 | 0.000000 | 962252869 | 91944434 | 0.000000
09-04-2025 15:19:10000 | -1354664 | 135.4664 | 14262915 | 234835.45 | 334907349 | 99450294 | 50030193 | 0.000000 | 982171265 | 93830225 | 0.000000
09-04-2025 15:19:15000 | -1356048 | 135.6048 | 14270164 | 234788.72 | 335315125 | 99450851 | 50027500 | 0.000000 | 10020098 | 95712295 | 0.000000
09-04-2025 15:19:20000 | -1354321 | 135.4321 | 14240336 | 234816.27 | 334845612 | 99451744 | 50010147 | 0.000000 | 10217493 | 97593818 | 0.000000
09-04-2025 15:19:25000 | -1355145 | 135.5145 | 14251563 | 234773.31 | 335108521 | 99451546 | 50003143 | 0.000000 | 10414604 | 99473809 | 0.000000
09-04-2025 15:19:30000 | -1352195 | 135.2195 | 14073847 | 234787.08 | 334322968 | 99462715 | 49985451 | 0.000000 | 10610044 | 10135144 | 0.000000
09-04-2025 15:19:35000 | -1347169 | 134.7169 | 14086803 | 234837.28 | 333024475 | 99457741 | 49990429 | 0.000000 | 10805441 | 10322542 | 0.000000
09-04-2025 15:19:40000 | -1347152 | 134.7152 | 14195479 | 234827.06 | 333062073 | 99449394 | 50015053 | 0.000000 | 11002434 | 10509785 | 0.000000
09-04-2025 15:19:45000 | -1356915 | 135.6915 | 13934273 | 234605.61 | 335699707 | 99476860 | 49974335 | 0.000000 | 11197549 | 10697593 | 0.000000
09-04-2025 15:19:50000 | -1345747 | 134.5747 | 13290310 | 234637.34 | 332760834 | 99515884 | 49929699 | 0.000000 | 11385359 | 10885113 | 0.000000
09-04-2025 15:19:55000 | -1346208 | 134.6208 | 13644511 | 234721.39 | 332852753 | 99490280 | 49954628 | 0.000000 | 11572500 | 11071895 | 0.000000
09-04-2025 15:20:00000 | -1344028 | 134.4028 | 13545383 | 234670.27 | 332360840 | 99495987 | 49954220 | 0.000000 | 11762668 | 11258815 | 0.000000
09-04-2025 15:20:05000 | -1344302 | 134.4302 | 13484805 | 234674.67 | 332403503 | 99500648 | 49950203 | 0.000000 | 11950470 | 11445640 | 0.000000
09-04-2025 15:20:10000 | -1342705 | 134.2705 | 13527851 | 234713.67 | 331971710 | 99496300 | 49948700 | 0.000000 | 12139009 | 11632482 | 0.000000
09-04-2025 15:20:15000 | -1343249 | 134.3249 | 13583635 | 234705.20 | 332130188 | 99492569 | 49951153 | 0.000000 | 12326810 | 11818819 | 0.000000
09-04-2025 15:20:20000 | -1348828 | 134.8828 | 13794063 | 234649.75 | 333627350 | 99481140 | 49942566 | 0.000000 | 12517255 | 12005700 | 0.000000
09-04-2025 15:20:25000 | -1344165 | 134.4165 | 13500381 | 234700.92 | 332341187 | 99499405 | 49937218 | 0.000000 | 12705667 | 12192444 | 0.000000
09-04-2025 15:20:30000 | -1342204 | 134.2204 | 13691021 | 234735.23 | 331859222 | 99483788 | 49968895 | 0.000000 | 12895638 | 12378916 | 0.000000
09-04-2025 15:20:35000 | -1344183 | 134.4183 | 13459140 | 234638.36 | 332421021 | 99502449 | 49950214 | 0.000000 | 13085172 | 12565912 | 0.000000
09-04-2025 15:20:40000 | -1345893 | 134.5893 | 13306344 | 234593.44 | 332864197 | 99514824 | 49934364 | 0.000000 | 13270457 | 12752623 | 0.000000
09-04-2025 15:20:45000 | -1341683 | 134.1683 | 13078936 | 234605.33 | 331762665 | 99528229 | 49897629 | 0.000000 | 13453529 | 12939494 | 0.000000
09-04-2025 15:20:50000 | -1339040 | 133.904 | 13186260 | 234655.81 | 331073578 | 99518631 | 49922615 | 0.000000 | 13635167 | 13125666 | 0.000000
09-04-2025 15:20:55000 | -1342931 | 134.2931 | 13360578 | 234630.05 | 332109009 | 99508751 | 49935215 | 0.000000 | 13820409 | 13312138 | 0.000000
09-04-2025 15:21:00000 | -1342620 | 134.262 | 13254027 | 234617.00 | 332020264 | 99516273 | 49925465 | 0.000000 | 14005643 | 13498928 | 0.000000
09-04-2025 15:21:05000 | -1341920 | 134.192 | 13323880 | 234700.30 | 331747040 | 99510696 | 49937271 | 0.000000 | 14189240 | 13685332 | 0.000000
09-04-2025 15:21:10000 | -1345331 | 134.5331 | 13413165 | 234659.45 | 332667969 | 99506653 | 49945843 | 0.000000 | 14375028 | 13871970 | 0.000000
09-04-2025 15:21:15000 | -1345224 | 134.5224 | 13670326 | 234718.66 | 332612671 | 99487625 | 49987125 | 0.000000 | 14562748 | 14058444 | 0.000000
09-04-2025 15:21:20000 | -1348018 | 134.8018 | 13715047 | 234668.06 | 333379089 | 99486412 | 49973785 | 0.000000 | 14753876 | 14245649 | 0.000000
09-04-2025 15:21:25000 | -1345340 | 134.534 | 13588985 | 234654.58 | 332712372 | 99493744 | 49957253 | 0.000000 | 14943077 | 14432454 | 0.000000
09-04-2025 15:21:30000 | -1341777 | 134.1777 | 13700260 | 234781.27 | 331687561 | 99482765 | 49954044 | 0.000000 | 15132972 | 14619402 | 0.000000
09-04-2025 15:21:35000 | -1345330 | 134.533 | 13782998 | 234750.88 | 332624451 | 99479286 | 49960835 | 0.000000 | 15323647 | 14806282 | 0.000000
09-04-2025 15:21:40000 | -1352289 | 135.2289 | 14039592 | 234771.83 | 334363342 | 99465378 | 49987194 | 0.000000 | 15515613 | 14993172 | 0.000000
09-04-2025 15:21:45000 | -1351783 | 135.1783 | 14001240 | 234722.91 | 334295624 | 99467880 | 49978012 | 0.000000 | 15710663 | 15180892 | 0.000000
09-04-2025 15:21:50000 | -1354813 | 135.4813 | 13961241 | 234721.56 | 335037476 | 99473236 | 49981697 | 0.000000 | 15902875 | 15368507 | 0.000000
09-04-2025 15:21:55000 | -1350802 | 135.0802 | 13721926 | 234703.83 | 334010010 | 99487999 | 49972691 | 0.000000 | 16094336 | 15556275 | 0.000000
09-04-2025 15:22:00000 | -1354354 | 135.4354 | 13657463 | 234631.59 | 334970917 | 99495399 | 49937534 | 0.000000 | 16285365 | 15744320 | 0.000000
09-04-2025 15:22:05000 | -1351821 | 135.1821 | 13849020 | 234740.98 | 334241333 | 99479324 | 49938190 | 0.000000 | 16474844 | 15931858 | 0.000000
09-04-2025 15:22:10000 | -1349344 | 134.9344 | 13560662 | 234659.73 | 333680115 | 99498802 | 49929241 | 0.000000 | 16664432 | 16119358 | 0.000000
09-04-2025 15:22:15000 | -1346433 | 134.6433 | 13185609 | 234603.56 | 332955933 | 99523911 | 49900345 | 0.000000 | 16850942 | 16307180 | 0.000000
09-04-2025 15:22:20000 | -1345394 | 134.5394 | 13152543 | 234614.89 | 332677124 | 99525551 | 49905190 | 0.000000 | 17033997 | 16494125 | 0.000000
09-04-2025 15:22:25000 | -1350469 | 135.0469 | 13523898 | 234638.94 | 333974670 | 99502319 | 49931858 | 0.000000 | 17220516 | 16681461 | 0.000000
09-04-2025 15:22:30000 | -1352418 | 135.2418 | 13867566 | 234760.53 | 334365479 | 99478394 | 49969311 | 0.000000 | 17409886 | 16868820 | 0.000000
09-04-2025 15:22:35000 | -1355769 | 135.5769 | 13845401 | 234593.59 | 335414368 | 99482597 | 49963974 | 0.000000 | 17602886 | 17056896 | 0.000000
09-04-2025 15:22:40000 | -1350268 | 135.0268 | 13287418 | 234632.67 | 333877045 | 99519302 | 49925133 | 0.000000 | 17789674 | 17244779 | 0.000000
09-04-2025 15:22:45000 | -1356523 | 135.6523 | 13809924 | 234686.41 | 335464783 | 99485794 | 49949368 | 0.000000 | 17978099 | 17432379 | 0.000000
09-04-2025 15:22:50000 | -1353498 | 135.3498 | 13763414 | 234710.02 | 334676941 | 99486954 | 49967815 | 0.000000 | 18168362 | 17619865 | 0.000000
09-04-2025 15:22:55000 | -1347326 | 134.7326 | 13760294 | 234745.77 | 333112976 | 99482513 | 49975780 | 0.000000 | 18360132 | 17807514 | 0.000000
09-04-2025 15:23:00000 | -1348396 | 134.8396 | 13876223 | 234763.33 | 333378021 | 99474655 | 50000027 | 0.000000 | 18551925 | 17994861 | 0.000000
09-04-2025 15:23:05000 | -1354819 | 135.4819 | 14195314 | 234761.94 | 335031860 | 99455574 | 50020901 | 0.000000 | 18747570 | 18182520 | 0.000000
09-04-2025 15:23:10000 | -1356233 | 135.6233 | 13841055 | 234658.05 | 335440979 | 99483269 | 49972210 | 0.000000 | 18941982 | 18370986 | 0.000000
09-04-2025 15:23:15000 | -1351549 | 135.1549 | 13263916 | 234563.95 | 334285461 | 99521889 | 49910145 | 0.000000 | 19129116 | 18558883 | 0.000000
09-04-2025 15:23:20000 | -1345329 | 134.5329 | 13469174 | 234742.83 | 332559143 | 99502556 | 49951321 | 0.000000 | 19313004 | 18745584 | 0.000000
09-04-2025 15:23:25000 | -1348000 | 134.8 | 13614508 | 234628.48 | 333409912 | 99493843 | 49946648 | 0.000000 | 19502800 | 18932701 | 0.000000
09-04-2025 15:23:30000 | -1345166 | 134.5166 | 13355700 | 234631.13 | 332650177 | 99510719 | 49924049 | 0.000000 | 19689187 | 19119592 | 0.000000
09-04-2025 15:23:35000 | -1341956 | 134.1956 | 13416201 | 234696.55 | 331783569 | 99503967 | 49944874 | 0.000000 | 19875376 | 19306396 | 0.000000
09-04-2025 15:23:40000 | -1346640 | 134.664 | 13632221 | 234647.84 | 333058807 | 99491516 | 49958820 | 0.000000 | 20064282 | 19493410 | 0.000000
09-04-2025 15:23:45000 | -1347213 | 134.7213 | 13613588 | 234661.36 | 333169373 | 99493324 | 49952400 | 0.000000 | 20254048 | 19680592 | 0.000000
09-04-2025 15:23:50000 | -1341556 | 134.1556 | 13324045 | 234699.16 | 331666382 | 99510414 | 49956116 | 0.000000 | 20440836 | 19867590 | 0.000000
09-04-2025 15:23:55000 | -1347146 | 134.7146 | 13725148 | 234698.47 | 333128448 | 99485001 | 49962955 | 0.000000 | 20629983 | 20054615 | 0.000000
09-04-2025 15:24:00000 | -1346401 | 134.6401 | 13508598 | 234654.16 | 332955353 | 99500450 | 49966904 | 0.000000 | 20818171 | 20241484 | 0.000000
09-04-2025 15:24:05000 | -1346300 | 134.63 | 13533918 | 234662.95 | 332920929 | 99498520 | 49971191 | 0.000000 | 21006396 | 20428355 | 0.000000
09-04-2025 15:24:10000 | -1341977 | 134.1977 | 13539091 | 234722.64 | 331792969 | 99494919 | 49984421 | 0.000000 | 21194780 | 20615045 | 0.000000
09-04-2025 15:24:15000 | -1341911 | 134.1911 | 13566048 | 234707.16 | 331796906 | 99492874 | 49993164 | 0.000000 | 21383938 | 20801637 | 0.000000
09-04-2025 15:24:20000 | -1346433 | 134.6433 | 13846188 | 234701.78 | 332977417 | 99475395 | 50016159 | 0.000000 | 21575166 | 20988271 | 0.000000
09-04-2025 15:24:25000 | -1344303 | 134.4303 | 13795406 | 234746.27 | 332381042 | 99477570 | 50014214 | 0.000000 | 21767449 | 21175064 | 0.000000
09-04-2025 15:24:30000 | -1344945 | 134.4945 | 13647646 | 234689.28 | 332580078 | 99489098 | 49988926 | 0.000000 | 21958027 | 21361771 | 0.000000
09-04-2025 15:24:35000 | -1341198 | 134.1198 | 13621721 | 234770.34 | 331547150 | 99488197 | 50010006 | 0.000000 | 22146345 | 21547977 | 0.000000
09-04-2025 15:24:40000 | -1351613 | 135.1613 | 13729547 | 234626.52 | 334327881 | 99488045 | 49997116 | 0.000000 | 22336553 | 21734992 | 0.000000
09-04-2025 15:24:45000 | -1342757 | 134.2757 | 13408239 | 234654.19 | 332041992 | 99505135 | 49974300 | 0.000000 | 22524949 | 21921754 | 0.000000
09-04-2025 15:24:50000 | -1337952 | 133.7952 | 13395473 | 234732.70 | 330743958 | 99502541 | 49983280 | 0.000000 | 22710242 | 22107975 | 0.000000
09-04-2025 15:24:55000 | -1343330 | 134.333 | 13641351 | 234717.36 | 332150726 | 99488350 | 49989906 | 0.000000 | 22898547 | 22294529 | 0.000000
09-04-2025 15:25:00000 | -1339744 | 133.9744 | 13666188 | 234794.34 | 331173767 | 99483765 | 50015182 | 0.000000 | 23087388 | 22480688 | 0.000000
09-04-2025 15:25:05000 | -1347090 | 134.709 | 14075570 | 234757.48 | 333115967 | 99458534 | 50048607 | 0.000000 | 23281643 | 22667490 | 0.000000
09-04-2025 15:25:10000 | -1346395 | 134.6395 | 13834821 | 234698.53 | 332967621 | 99476219 | 50023151 | 0.000000 | 23474563 | 22854623 | 0.000000
09-04-2025 15:25:15000 | -1340449 | 134.0449 | 13832579 | 234800.56 | 331371429 | 99471771 | 50054810 | 0.000000 | 23665261 | 23040859 | 0.000000
09-04-2025 15:25:20000 | -1348725 | 134.8725 | 14247561 | 234725.81 | 333605743 | 99446663 | 50068111 | 0.000000 | 23862461 | 23227883 | 0.000000
09-04-2025 15:25:25000 | -1347713 | 134.7713 | 14300114 | 234817.09 | 333243042 | 99441780 | 50065746 | 0.000000 | 24060383 | 23415029 | 0.000000
09-04-2025 15:25:30000 | -1347803 | 134.7803 | 14145476 | 234742.73 | 333331909 | 99453758 | 50063831 | 0.000000 | 24258413 | 23602338 | 0.000000
09-04-2025 15:25:35000 | -1346687 | 134.6687 | 14093104 | 234757.39 | 333022980 | 99456871 | 50057178 | 0.000000 | 24454692 | 23789605 | 0.000000
09-04-2025 15:25:40000 | -1349355 | 134.9355 | 14171133 | 234726.98 | 333740112 | 99453041 | 50051010 | 0.000000 | 24651086 | 23976986 | 0.000000
09-04-2025 15:25:45000 | -1349115 | 134.9115 | 14178364 | 234726.97 | 333687408 | 99452301 | 50046906 | 0.000000 | 24847424 | 24164430 | 0.000000
09-04-2025 15:25:50000 | -1349338 | 134.9338 | 14053167 | 234674.83 | 333778656 | 99462029 | 50013443 | 0.000000 | 25043333 | 24352170 | 0.000000
09-04-2025 15:25:55000 | -1349791 | 134.9791 | 14172583 | 234808.05 | 333730133 | 99453285 | 50026882 | 0.000000 | 25238557 | 24539375 | 0.000000
09-04-2025 15:26:00000 | -1352461 | 135.2461 | 14225178 | 234772.05 | 334450653 | 99451408 | 50020813 | 0.000000 | 25437280 | 24727195 | 0.000000
09-04-2025 15:26:05000 | -1349264 | 134.9264 | 14003150 | 234766.22 | 333622070 | 99465759 | 50015144 | 0.000000 | 25632673 | 24914701 | 0.000000
09-04-2025 15:26:10000 | -1348053 | 134.8053 | 14186568 | 234811.83 | 333304504 | 99450813 | 50033283 | 0.000000 | 25828806 | 25101945 | 0.000000
09-04-2025 15:26:15000 | -1347789 | 134.7789 | 14124800 | 234797.42 | 333244995 | 99455330 | 50033104 | 0.000000 | 26025813 | 25289447 | 0.000000
09-04-2025 15:26:20000 | -1351557 | 135.1557 | 14295656 | 234810.39 | 334192108 | 99445267 | 50025867 | 0.000000 | 26223159 | 25477207 | 0.000000
09-04-2025 15:26:25000 | -1351555 | 135.1555 | 14277385 | 234799.48 | 334210083 | 99446671 | 50035915 | 0.000000 | 26420608 | 25664740 | 0.000000
09-04-2025 15:26:30000 | -1348631 | 134.8631 | 14196353 | 234704.39 | 333599854 | 99450523 | 50034649 | 0.000000 | 26618538 | 25852379 | 0.000000
09-04-2025 15:26:35000 | -1346737 | 134.6737 | 14240863 | 234738.98 | 333103149 | 99445564 | 50041607 | 0.000000 | 26816460 | 26039762 | 0.000000
09-04-2025 15:26:40000 | -1344147 | 134.4147 | 14367330 | 234752.06 | 332487732 | 99433594 | 50071499 | 0.000000 | 27015510 | 26226637 | 0.000000
09-04-2025 15:26:45000 | -1348217 | 134.8217 | 14513182 | 234742.13 | 333531921 | 99425591 | 50073261 | 0.000000 | 27217229 | 26414070 | 0.000000
09-04-2025 15:26:50000 | -1349617 | 134.9617 | 14772068 | 234784.34 | 333881958 | 99406319 | 50087021 | 0.000000 | 27420847 | 26601490 | 0.000000
09-04-2025 15:26:55000 | -1347702 | 134.7702 | 14569949 | 234805.69 | 333332275 | 99420692 | 50083199 | 0.000000 | 27622791 | 26788578 | 0.000000
09-04-2025 15:27:00000 | -1346572 | 134.6572 | 14509401 | 234792.47 | 333057129 | 99424500 | 50075558 | 0.000000 | 27825469 | 26976240 | 0.000000
09-04-2025 15:27:05000 | -1352301 | 135.2301 | 14767485 | 234755.95 | 334577332 | 99409019 | 50084648 | 0.000000 | 28029468 | 27163613 | 0.000000
09-04-2025 15:27:10000 | -1354139 | 135.4139 | 14694278 | 234796.00 | 334953705 | 99416389 | 50078346 | 0.000000 | 28233711 | 27351371 | 0.000000
09-04-2025 15:27:15000 | -1350328 | 135.0328 | 14471026 | 234683.81 | 334113525 | 99430664 | 50046719 | 0.000000 | 28435830 | 27539230 | 0.000000
09-04-2025 15:27:20000 | -1351245 | 135.1245 | 14470166 | 234830.58 | 334129272 | 99431496 | 50055859 | 0.000000 | 28635752 | 27726566 | 0.000000
09-04-2025 15:27:25000 | -1352606 | 135.2606 | 14687534 | 234859.41 | 334478333 | 99415604 | 50067467 | 0.000000 | 28837727 | 27914090 | 0.000000
09-04-2025 15:27:30000 | -1355278 | 135.5278 | 14501844 | 234652.50 | 335381653 | 99432388 | 50042789 | 0.000000 | 29039875 | 28102010 | 0.000000
09-04-2025 15:27:35000 | -1351863 | 135.1863 | 14074286 | 234706.00 | 334361176 | 99462418 | 50029568 | 0.000000 | 29236665 | 28289717 | 0.000000
09-04-2025 15:27:40000 | -1342108 | 134.2108 | 13917942 | 234781.13 | 331830231 | 99466591 | 50039204 | 0.000000 | 29431707 | 28476957 | 0.000000
09-04-2025 15:27:45000 | -1347735 | 134.7735 | 14238215 | 234688.13 | 333421204 | 99446579 | 50060997 | 0.000000 | 29629856 | 28664184 | 0.000000
09-04-2025 15:27:50000 | -1348341 | 134.8341 | 14208512 | 234718.80 | 333514252 | 99449356 | 50054943 | 0.000000 | 29827356 | 28851508 | 0.000000
09-04-2025 15:27:55000 | -1347865 | 134.7865 | 14135665 | 234686.80 | 333428314 | 99454559 | 50064507 | 0.000000 | 30025151 | 29039096 | 0.000000
09-04-2025 15:28:00000 | -1354358 | 135.4358 | 14539973 | 234753.08 | 335021820 | 99428658 | 50082565 | 0.000000 | 30224844 | 29226965 | 0.000000
09-04-2025 15:28:05000 | -1358684 | 135.8684 | 14594389 | 234776.42 | 336064209 | 99428040 | 50113766 | 0.000000 | 30426482 | 29414949 | 0.000000
09-04-2025 15:28:10000 | -1352565 | 135.2565 | 14463626 | 234779.28 | 334524170 | 99433105 | 50090538 | 0.000000 | 30628989 | 29603193 | 0.000000
09-04-2025 15:28:15000 | -1351400 | 135.14 | 14349408 | 234811.61 | 334166870 | 99440994 | 50065338 | 0.000000 | 30829048 | 29791227 | 0.000000
09-04-2025 15:28:20000 | -1347454 | 134.7454 | 14515168 | 234885.08 | 333145233 | 99424789 | 50111317 | 0.000000 | 31030864 | 29978754 | 0.000000
09-04-2025 15:28:25000 | -1346180 | 134.618 | 14564650 | 234891.36 | 332837616 | 99419807 | 50133656 | 0.000000 | 31235171 | 30166539 | 0.000000
09-04-2025 15:28:30000 | -1354549 | 135.4549 | 14820824 | 234831.11 | 335033569 | 99406738 | 50138458 | 0.000000 | 31439900 | 30354402 | 0.000000
09-04-2025 15:28:35000 | -1356852 | 135.6852 | 14983583 | 234905.38 | 335535156 | 99395790 | 50144928 | 0.000000 | 31645735 | 30542348 | 0.000000
09-04-2025 15:28:40000 | -1357074 | 135.7074 | 14835494 | 234772.22 | 335737762 | 99407761 | 50114109 | 0.000000 | 31853750 | 30731008 | 0.000000
09-04-2025 15:28:45000 | -1351790 | 135.179 | 15183696 | 235067.05 | 334123047 | 99375084 | 50147449 | 0.000000 | 32059973 | 30918465 | 0.000000
09-04-2025 15:28:50000 | -1355754 | 135.5754 | 15413243 | 235000.97 | 335247345 | 99359955 | 50162674 | 0.000000 | 32272837 | 31106426 | 0.000000
09-04-2025 15:28:55000 | -1357421 | 135.7421 | 15430241 | 234987.23 | 335677124 | 99360115 | 50167072 | 0.000000 | 32488511 | 31295098 | 0.000000
09-04-2025 15:29:00000 | -1355489 | 135.5489 | 15518355 | 235089.53 | 335082001 | 99351028 | 50190731 | 0.000000 | 32703311 | 31483465 | 0.000000
09-04-2025 15:29:05000 | -1360849 | 136.0849 | 15606584 | 235017.47 | 336515747 | 99348808 | 50176632 | 0.000000 | 32921863 | 31672664 | 0.000000
09-04-2025 15:29:10000 | -1362481 | 136.2481 | 15650081 | 235034.72 | 336907349 | 99346764 | 50187386 | 0.000000 | 33137354 | 31861537 | 0.000000
09-04-2025 15:29:15000 | -1357358 | 135.7358 | 15530004 | 234964.81 | 335719788 | 99351837 | 50176102 | 0.000000 | 33353809 | 32050320 | 0.000000
09-04-2025 15:29:20000 | -1353587 | 135.3587 | 15424435 | 234924.61 | 334829163 | 99357002 | 50162998 | 0.000000 | 33569583 | 32238777 | 0.000000
09-04-2025 15:29:25000 | -1357014 | 135.7014 | 15494559 | 234925.89 | 335687347 | 99354439 | 50153580 | 0.000000 | 33784158 | 32427041 | 0.000000
09-04-2025 15:29:30000 | -1353547 | 135.3547 | 15344810 | 234959.14 | 334748596 | 99363518 | 50153748 | 0.000000 | 33997209 | 32615123 | 0.000000
09-04-2025 15:29:35000 | -1353840 | 135.384 | 15428097 | 234966.69 | 334832642 | 99356934 | 50159523 | 0.000000 | 34211860 | 32803133 | 0.000000
09-04-2025 15:29:40000 | -1354051 | 135.4051 | 15271831 | 234900.63 | 334932800 | 99369965 | 50139450 | 0.000000 | 34424297 | 32991012 | 0.000000
09-04-2025 15:29:45000 | -1352103 | 135.2103 | 15275438 | 234951.00 | 334389191 | 99367874 | 50132984 | 0.000000 | 34636846 | 33178996 | 0.000000
09-04-2025 15:29:50000 | -1354771 | 135.4771 | 15071686 | 234816.55 | 335178131 | 99386871 | 50119400 | 0.000000 | 34848169 | 33367117 | 0.000000
09-04-2025 15:29:55000 | -1353814 | 135.3814 | 14949347 | 234797.89 | 334933167 | 99395844 | 50091694 | 0.000000 | 35055588 | 33555094 | 0.000000
09-04-2025 15:30:00000 | -1353212 | 135.3212 | 14710098 | 234715.19 | 334843048 | 99414345 | 50055016 | 0.000000 | 35261824 | 33743148 | 0.000000
09-04-2025 15:30:05000 | -1346823 | 134.6823 | 14465751 | 234787.28 | 333115234 | 99428139 | 50044121 | 0.000000 | 20144825 | 187221695 | 0.000000
09-04-2025 15:30:10000 | -1350247 | 135.0247 | 14728971 | 234780.59 | 334026672 | 99410294 | 50057777 | 0.000000 | 40353245 | 374203400 | 0.000000
09-04-2025 15:30:15000 | -1345014 | 134.5014 | 14447883 | 234744.66 | 332725800 | 99428009 | 50037880 | 0.000000 | 60453808 | 561114197 | 0.000000
09-04-2025 15:30:20000 | -1340344 | 134.0344 | 14291736 | 234721.03 | 331575409 | 99436333 | 50032639 | 0.000000 | 80529602 | 747846436 | 0.000000
09-04-2025 15:30:25000 | -1342961 | 134.2961 | 14525307 | 234763.84 | 332219147 | 99420166 | 50037918 | 0.000000 | 100625275 | 934418823 | 0.000000
09-04-2025 15:30:30000 | -1351556 | 135.1556 | 14678664 | 234711.22 | 334433655 | 99415405 | 50031094 | 0.000000 | 120962173 | 11217090 | 0.000000
09-04-2025 15:30:35000 | -1350998 | 135.0998 | 14952286 | 234813.91 | 334229095 | 99393112 | 50055267 | 0.000000 | 141504333 | 13090140 | 0.000000
09-04-2025 15:30:40000 | -1353728 | 135.3728 | 14795949 | 234669.77 | 335058380 | 99407997 | 50044315 | 0.000000 | 162132248 | 14966007 | 0.000000
09-04-2025 15:30:45000 | -1347418 | 134.7418 | 14475703 | 234746.77 | 333319580 | 99427856 | 50019073 | 0.000000 | 182554077 | 16843920 | 0.000000
09-04-2025 15:30:50000 | -1347806 | 134.7806 | 14517888 | 234758.50 | 333413391 | 99424873 | 50011505 | 0.000000 | 202628418 | 18717588 | 0.000000
09-04-2025 15:30:55000 | -1350566 | 135.0566 | 14491850 | 234676.66 | 334200195 | 99429237 | 49987869 | 0.000000 | 222784927 | 20592471 | 0.000000
09-04-2025 15:31:00000 | -1347185 | 134.7185 | 14218621 | 234629.69 | 333362854 | 99447639 | 49955559 | 0.000000 | 242807175 | 22469502 | 0.000000
09-04-2025 15:31:05000 | -1348747 | 134.8747 | 14254539 | 234688.30 | 333668701 | 99446144 | 49967381 | 0.000000 | 262536011 | 24340813 | 0.000000
09-04-2025 15:31:10000 | -1347748 | 134.7748 | 14624773 | 234779.42 | 333398407 | 99416397 | 50027561 | 0.000000 | 282405182 | 26205981 | 0.000000
09-04-2025 15:31:15000 | -1350067 | 135.0067 | 14948019 | 234769.52 | 334059845 | 99392624 | 50059319 | 0.000000 | 303100677 | 28078999 | 0.000000
09-04-2025 15:31:20000 | -1351646 | 135.1646 | 14803104 | 234784.33 | 334389832 | 99405617 | 50062798 | 0.000000 | 323780457 | 29954622 | 0.000000
09-04-2025 15:31:25000 | -1352572 | 135.2572 | 14760451 | 234834.33 | 334531769 | 99409813 | 50044991 | 0.000000 | 344299835 | 31833208 | 0.000000
09-04-2025 15:31:30000 | -1343745 | 134.3745 | 14279073 | 234794.31 | 332297729 | 99440140 | 50029739 | 0.000000 | 364403839 | 33707896 | 0.000000
09-04-2025 15:31:35000 | -1347030 | 134.703 | 14350236 | 234783.27 | 333146393 | 99437325 | 50035244 | 0.000000 | 384326904 | 35578008 | 0.000000
09-04-2025 15:31:40000 | -1349785 | 134.9785 | 14253934 | 234721.72 | 333873352 | 99447037 | 50012817 | 0.000000 | 404195435 | 37450259 | 0.000000
09-04-2025 15:31:45000 | -1351077 | 135.1077 | 14511416 | 234791.30 | 334159882 | 99428139 | 50045864 | 0.000000 | 424039093 | 39318066 | 0.000000
09-04-2025 15:31:50000 | -1352183 | 135.2183 | 14479091 | 234773.97 | 334446869 | 99431587 | 50048660 | 0.000000 | 444138794 | 41193271 | 0.000000
09-04-2025 15:31:55000 | -1347461 | 134.7461 | 14352311 | 234746.44 | 333296387 | 99437523 | 50042862 | 0.000000 | 464088440 | 43064707 | 0.000000
09-04-2025 15:32:00000 | -1347990 | 134.799 | 14344635 | 234669.91 | 333538391 | 99438553 | 50039936 | 0.000000 | 484204742 | 44939512 | 0.000000
09-04-2025 15:32:05000 | -1347056 | 134.7056 | 14274157 | 234664.77 | 333299438 | 99443253 | 50038754 | 0.000000 | 504094177 | 46810996 | 0.000000
09-04-2025 15:32:10000 | -1347696 | 134.7696 | 14284287 | 234754.75 | 333323425 | 99442993 | 50045021 | 0.000000 | 523967712 | 48684634 | 0.000000
09-04-2025 15:32:15000 | -1352197 | 135.2197 | 14568034 | 234779.75 | 334463257 | 99424652 | 50073368 | 0.000000 | 543983154 | 50558535 | 0.000000
09-04-2025 15:32:20000 | -1354824 | 135.4824 | 14657582 | 234706.48 | 335230469 | 99419853 | 50055737 | 0.000000 | 564256165 | 52440000 | 0.000000
09-04-2025 15:32:25000 | -1351075 | 135.1075 | 14372587 | 234675.58 | 334291107 | 99438934 | 50054546 | 0.000000 | 584348999 | 54320542 | 0.000000
09-04-2025 15:32:30000 | -1352027 | 135.2027 | 14344822 | 234642.48 | 334558716 | 99441864 | 50044037 | 0.000000 | 604491760 | 56203687 | 0.000000
09-04-2025 15:32:35000 | -1354375 | 135.4375 | 14265658 | 234797.20 | 334890991 | 99449852 | 50043568 | 0.000000 | 624314209 | 58085112 | 0.000000
09-04-2025 15:32:40000 | -1354927 | 135.4927 | 14377765 | 234759.64 | 335109253 | 99441696 | 50056870 | 0.000000 | 644255615 | 59965347 | 0.000000
09-04-2025 15:32:45000 | -1355396 | 135.5396 | 14203908 | 234751.30 | 335193695 | 99455376 | 50028011 | 0.000000 | 663988098 | 61847456 | 0.000000
09-04-2025 15:32:50000 | -1348078 | 134.8078 | 14341199 | 234942.03 | 333172455 | 99438896 | 50061211 | 0.000000 | 683696655 | 63722056 | 0.000000
09-04-2025 15:32:55000 | -1358997 | 135.8997 | 14781613 | 234824.44 | 336120392 | 99413666 | 50097614 | 0.000000 | 704099854 | 65602969 | 0.000000
09-04-2025 15:33:00000 | -1355944 | 135.5944 | 14692662 | 234866.98 | 335293823 | 99418053 | 50081646 | 0.000000 | 724543030 | 67486953 | 0.000000
09-04-2025 15:33:05000 | -1358180 | 135.818 | 14433087 | 234738.98 | 335946991 | 99440094 | 50059471 | 0.000000 | 744790466 | 69370703 | 0.000000
09-04-2025 15:33:10000 | -1355011 | 135.5011 | 14325333 | 234773.75 | 335098236 | 99445793 | 50035469 | 0.000000 | 764811096 | 71256348 | 0.000000
09-04-2025 15:33:15000 | -1351259 | 135.1259 | 14504408 | 234947.23 | 333981384 | 99428841 | 50064972 | 0.000000 | 784729797 | 73134453 | 0.000000
09-04-2025 15:33:20000 | -1360845 | 136.0845 | 15030688 | 234901.25 | 336529327 | 99395554 | 50098309 | 0.000000 | 805230408 | 75016353 | 0.000000
09-04-2025 15:33:25000 | -1360579 | 136.0579 | 15020101 | 234885.70 | 336485504 | 99396164 | 50090508 | 0.000000 | 826032166 | 76904375 | 0.000000
09-04-2025 15:33:30000 | -1359408 | 135.9408 | 14712545 | 234804.17 | 336229492 | 99419434 | 50050789 | 0.000000 | 846670959 | 78794570 | 0.000000
09-04-2025 15:33:35000 | -1354000 | 135.4 | 14206137 | 234719.47 | 334899750 | 99454094 | 50027046 | 0.000000 | 866733643 | 80680313 | 0.000000
09-04-2025 15:33:40000 | -1350017 | 135.0017 | 14256047 | 234780.92 | 333852814 | 99447060 | 50030014 | 0.000000 | 886618103 | 82562021 | 0.000000
09-04-2025 15:33:45000 | -1360081 | 136.0081 | 14343367 | 234634.81 | 336543610 | 99448509 | 50022285 | 0.000000 | 906598328 | 84446836 | 0.000000
09-04-2025 15:33:50000 | -1347937 | 134.7937 | 14059684 | 234817.19 | 333238800 | 99460419 | 50023708 | 0.000000 | 926174072 | 86322725 | 0.000000
09-04-2025 15:33:55000 | -1359651 | 135.9651 | 14542395 | 234744.08 | 336338776 | 99432877 | 50063499 | 0.000000 | 946074219 | 88202266 | 0.000000
09-04-2025 15:34:00000 | -1360393 | 136.0393 | 14221121 | 234659.66 | 336554016 | 99458038 | 50027374 | 0.000000 | 965921509 | 90086895 | 0.000000
09-04-2025 15:34:05000 | -1354493 | 135.4493 | 14015477 | 234701.38 | 335006104 | 99468918 | 50012726 | 0.000000 | 985505493 | 91969883 | 0.000000
09-04-2025 15:34:10000 | -1355201 | 135.5201 | 13956363 | 234612.61 | 335281219 | 99473900 | 49996063 | 0.000000 | 10049815 | 93853213 | 0.000000
09-04-2025 15:34:15000 | -1345942 | 134.5942 | 13365092 | 234592.50 | 332901093 | 99510597 | 49955265 | 0.000000 | 10239336 | 95733457 | 0.000000
09-04-2025 15:34:20000 | -1345797 | 134.5797 | 13801105 | 234798.94 | 332672668 | 99478287 | 50015301 | 0.000000 | 10429006 | 97603721 | 0.000000
09-04-2025 15:34:25000 | -1357321 | 135.7321 | 14415477 | 234762.31 | 335702911 | 99440750 | 50046314 | 0.000000 | 10627089 | 99484121 | 0.000000
09-04-2025 15:34:30000 | -1357309 | 135.7309 | 14281447 | 234777.25 | 335639465 | 99451004 | 50048908 | 0.000000 | 10824418 | 10136673 | 0.000000
09-04-2025 15:34:35000 | -1353408 | 135.3408 | 14439016 | 234822.06 | 334678131 | 99435715 | 50060452 | 0.000000 | 11025914 | 10324928 | 0.000000
09-04-2025 15:34:40000 | -1354011 | 135.4011 | 14512550 | 234870.03 | 334759857 | 99430504 | 50046940 | 0.000000 | 11228744 | 10513520 | 0.000000
09-04-2025 15:34:45000 | -1353952 | 135.3952 | 14538670 | 234881.47 | 334740845 | 99428421 | 50067940 | 0.000000 | 11430818 | 10701426 | 0.000000
09-04-2025 15:34:50000 | -1350705 | 135.0705 | 14758216 | 234941.78 | 333919098 | 99408371 | 50099106 | 0.000000 | 11635619 | 10889330 | 0.000000
09-04-2025 15:34:55000 | -1355017 | 135.5017 | 14826222 | 234908.89 | 335038147 | 99406715 | 50092796 | 0.000000 | 11841008 | 11077510 | 0.000000
09-04-2025 15:35:00000 | -1350925 | 135.0925 | 14720566 | 234944.97 | 333953644 | 99411552 | 50099308 | 0.000000 | 12046128 | 11265254 | 0.000000
09-04-2025 15:35:05000 | -1359960 | 135.996 | 14866231 | 234827.61 | 336379059 | 99407829 | 50099953 | 0.000000 | 12251600 | 11453380 | 0.000000
09-04-2025 15:35:10000 | -1356584 | 135.6584 | 14655331 | 234835.67 | 335482880 | 99421524 | 50059963 | 0.000000 | 12455679 | 11642032 | 0.000000
09-04-2025 15:35:15000 | -1352437 | 135.2437 | 14536905 | 234839.23 | 334431793 | 99427284 | 50069592 | 0.000000 | 12656779 | 11829877 | 0.000000
09-04-2025 15:35:20000 | -1356003 | 135.6003 | 14827771 | 234828.77 | 335394287 | 99407448 | 50086224 | 0.000000 | 12862479 | 12018077 | 0.000000
09-04-2025 15:35:25000 | -1355048 | 135.5048 | 14446063 | 234789.30 | 335115082 | 99436523 | 50058529 | 0.000000 | 13065079 | 12206551 | 0.000000
09-04-2025 15:35:30000 | -1352390 | 135.239 | 14425300 | 234864.73 | 334354492 | 99435936 | 50067841 | 0.000000 | 13264310 | 12394425 | 0.000000
09-04-2025 15:35:35000 | -1358230 | 135.823 | 14694384 | 234812.03 | 335931305 | 99419861 | 50087997 | 0.000000 | 13467246 | 12582319 | 0.000000
09-04-2025 15:35:40000 | -1355493 | 135.5493 | 14560141 | 234810.91 | 335221954 | 99428040 | 50056316 | 0.000000 | 13669885 | 12770797 | 0.000000
09-04-2025 15:35:45000 | -1351821 | 135.1821 | 14549901 | 234861.63 | 334247284 | 99425751 | 50085423 | 0.000000 | 13872573 | 12958777 | 0.000000
09-04-2025 15:35:50000 | -1355206 | 135.5206 | 14880481 | 234897.17 | 335112152 | 99402573 | 50124008 | 0.000000 | 14077716 | 13146907 | 0.000000
09-04-2025 15:35:55000 | -1357210 | 135.721 | 14765081 | 234832.13 | 335666687 | 99413437 | 50098888 | 0.000000 | 14283239 | 13335625 | 0.000000
09-04-2025 15:36:00000 | -1358839 | 135.8839 | 14802274 | 234778.17 | 336157074 | 99411903 | 50092537 | 0.000000 | 14487601 | 13524116 | 0.000000
09-04-2025 15:36:05000 | -1356962 | 135.6962 | 14591037 | 234746.02 | 335681152 | 99426857 | 50077385 | 0.000000 | 14691700 | 13712580 | 0.000000
09-04-2025 15:36:10000 | -1349619 | 134.9619 | 14500503 | 234850.59 | 333721924 | 99427765 | 50085926 | 0.000000 | 14893456 | 13900522 | 0.000000
09-04-2025 15:36:15000 | -1355541 | 135.5541 | 14834119 | 234834.11 | 335270935 | 99406540 | 50118988 | 0.000000 | 15099554 | 14088694 | 0.000000
09-04-2025 15:36:20000 | -1354292 | 135.4292 | 14642289 | 234773.08 | 335006500 | 99420601 | 50102867 | 0.000000 | 15304166 | 14277121 | 0.000000
09-04-2025 15:36:25000 | -1355030 | 135.503 | 14590963 | 234780.38 | 335161987 | 99425247 | 50094769 | 0.000000 | 15505955 | 14465144 | 0.000000
09-04-2025 15:36:30000 | -1352423 | 135.2423 | 14499991 | 234845.45 | 334406525 | 99430153 | 50102406 | 0.000000 | 15708829 | 14653222 | 0.000000
09-04-2025 15:36:35000 | -1357590 | 135.759 | 14887155 | 234915.00 | 335675018 | 99404114 | 50111637 | 0.000000 | 15913405 | 14841494 | 0.000000
09-04-2025 15:36:40000 | -1352865 | 135.2865 | 14803305 | 234974.33 | 334411255 | 99406662 | 50129990 | 0.000000 | 16119771 | 15029816 | 0.000000
09-04-2025 15:36:45000 | -1358285 | 135.8285 | 14879439 | 234865.14 | 335912201 | 99405334 | 50113960 | 0.000000 | 16327515 | 15218575 | 0.000000
09-04-2025 15:36:50000 | -1357289 | 135.7289 | 14790249 | 234891.44 | 335612061 | 99411522 | 50080639 | 0.000000 | 16532615 | 15407346 | 0.000000
09-04-2025 15:36:55000 | -1355830 | 135.583 | 14563372 | 234874.20 | 335214905 | 99428070 | 50098568 | 0.000000 | 16735881 | 15595664 | 0.000000
09-04-2025 15:37:00000 | -1362123 | 136.2123 | 14676994 | 234849.09 | 336824036 | 99424492 | 50104645 | 0.000000 | 16937920 | 15784201 | 0.000000
09-04-2025 15:37:05000 | -1359944 | 135.9944 | 14654044 | 234835.16 | 336299194 | 99424454 | 50101128 | 0.000000 | 17141698 | 15972803 | 0.000000
09-04-2025 15:37:10000 | -1357245 | 135.7245 | 14687276 | 234857.39 | 335618103 | 99419579 | 50116028 | 0.000000 | 17345273 | 16161228 | 0.000000
09-04-2025 15:37:15000 | -1353187 | 135.3187 | 14607104 | 234878.13 | 334572906 | 99422424 | 50105099 | 0.000000 | 17548706 | 16349373 | 0.000000
09-04-2025 15:37:20000 | -1354929 | 135.4929 | 14733321 | 234934.25 | 334950562 | 99413986 | 50111095 | 0.000000 | 17751919 | 16537414 | 0.000000
09-04-2025 15:37:25000 | -1354009 | 135.4009 | 14688311 | 234890.11 | 334776855 | 99416748 | 50103821 | 0.000000 | 17955602 | 16725414 | 0.000000
09-04-2025 15:37:30000 | -1350546 | 135.0546 | 14482567 | 234860.17 | 333919189 | 99429947 | 50070499 | 0.000000 | 18159471 | 16913834 | 0.000000
09-04-2025 15:37:35000 | -1349580 | 134.958 | 14507082 | 234920.28 | 333609863 | 99427216 | 50096737 | 0.000000 | 18360168 | 17101240 | 0.000000
09-04-2025 15:37:40000 | -1355873 | 135.5873 | 14844439 | 234936.19 | 335212067 | 99406013 | 50133976 | 0.000000 | 18563688 | 17288871 | 0.000000
09-04-2025 15:37:45000 | -1354753 | 135.4753 | 14452577 | 234820.00 | 334999664 | 99435776 | 50109253 | 0.000000 | 18765999 | 17477031 | 0.000000
09-04-2025 15:37:50000 | -1351400 | 135.14 | 14436281 | 234886.14 | 334077881 | 99434265 | 50110512 | 0.000000 | 18966359 | 17664758 | 0.000000
09-04-2025 15:37:55000 | -1347284 | 134.7284 | 14793835 | 235086.91 | 332881744 | 99402542 | 50149403 | 0.000000 | 19169939 | 17852385 | 0.000000
09-04-2025 15:38:00000 | -1363615 | 136.3615 | 15536430 | 234989.64 | 337210938 | 99357185 | 50194851 | 0.000000 | 19383114 | 18040818 | 0.000000
09-04-2025 15:38:05000 | -1357449 | 135.7449 | 15261930 | 235040.80 | 335561096 | 99373894 | 50175354 | 0.000000 | 19595470 | 18229578 | 0.000000
09-04-2025 15:38:10000 | -1359877 | 135.9877 | 15373133 | 235046.58 | 336180206 | 99367065 | 50166176 | 0.000000 | 19809022 | 18418330 | 0.000000
09-04-2025 15:38:15000 | -1357263 | 135.7263 | 15294271 | 235056.27 | 335498138 | 99371094 | 50173874 | 0.000000 | 20020774 | 18606666 | 0.000000
09-04-2025 15:38:20000 | -1355197 | 135.5197 | 15096864 | 234979.94 | 335054840 | 99385223 | 50172630 | 0.000000 | 20232325 | 18795092 | 0.000000
09-04-2025 15:38:25000 | -1354550 | 135.455 | 15116438 | 235009.69 | 334857178 | 99383057 | 50158566 | 0.000000 | 20442108 | 18983416 | 0.000000
09-04-2025 15:38:30000 | -1352983 | 135.2983 | 15283826 | 235052.38 | 334457672 | 99367996 | 50189049 | 0.000000 | 20653052 | 19171145 | 0.000000
09-04-2025 15:38:35000 | -1357703 | 135.7703 | 15393898 | 235021.05 | 335686279 | 99363358 | 50182388 | 0.000000 | 20867039 | 19359650 | 0.000000
09-04-2025 15:38:40000 | -1359763 | 135.9763 | 15462409 | 235005.30 | 336234467 | 99359657 | 50168228 | 0.000000 | 21081436 | 19548268 | 0.000000
09-04-2025 15:38:45000 | -1354884 | 135.4884 | 15172797 | 234966.66 | 335019775 | 99378792 | 50149364 | 0.000000 | 21293159 | 19736576 | 0.000000
09-04-2025 15:38:50000 | -1352933 | 135.2933 | 15196534 | 234996.42 | 334507721 | 99375084 | 50143005 | 0.000000 | 21504973 | 19924895 | 0.000000
09-04-2025 15:38:55000 | -1357239 | 135.7239 | 15193635 | 234965.39 | 335600952 | 99379242 | 50138058 | 0.000000 | 21715615 | 20113188 | 0.000000
09-04-2025 15:39:00000 | -1360895 | 136.0895 | 14921313 | 234856.34 | 336576874 | 99404282 | 50120537 | 0.000000 | 21924009 | 20301727 | 0.000000
09-04-2025 15:39:05000 | -1356547 | 135.6547 | 14668088 | 234830.58 | 335478821 | 99420494 | 50078411 | 0.000000 | 22129336 | 20490396 | 0.000000
09-04-2025 15:39:10000 | -1355170 | 135.517 | 14626187 | 234904.55 | 335031281 | 99422607 | 50079372 | 0.000000 | 22331375 | 20678418 | 0.000000
09-04-2025 15:39:15000 | -1352597 | 135.2597 | 14929793 | 234983.34 | 334370392 | 99396339 | 50132137 | 0.000000 | 22536335 | 20866115 | 0.000000
09-04-2025 15:39:20000 | -1356101 | 135.6101 | 14877873 | 234845.83 | 335407837 | 99403557 | 50124607 | 0.000000 | 22744990 | 21054764 | 0.000000
09-04-2025 15:39:25000 | -1356903 | 135.6903 | 14709025 | 234848.22 | 335554840 | 99417587 | 50092278 | 0.000000 | 22950134 | 21243420 | 0.000000
09-04-2025 15:39:30000 | -1354189 | 135.4189 | 14429002 | 234764.33 | 334936401 | 99437134 | 50055443 | 0.000000 | 23152808 | 21431832 | 0.000000
09-04-2025 15:39:35000 | -1348554 | 134.8554 | 14059133 | 234759.75 | 333468384 | 99460953 | 50059750 | 0.000000 | 23349773 | 21619436 | 0.000000
09-04-2025 15:39:40000 | -1353642 | 135.3642 | 14407725 | 234767.09 | 334795135 | 99438332 | 50068890 | 0.000000 | 23547759 | 21807059 | 0.000000
09-04-2025 15:39:45000 | -1349467 | 134.9467 | 14292618 | 234778.63 | 333724976 | 99443794 | 50073338 | 0.000000 | 23746667 | 21994729 | 0.000000
09-04-2025 15:39:50000 | -1351024 | 135.1024 | 14287947 | 234771.52 | 334118713 | 99445427 | 50077534 | 0.000000 | 23945615 | 22182508 | 0.000000
09-04-2025 15:39:55000 | -1350811 | 135.0811 | 14275316 | 234735.03 | 334113464 | 99446228 | 50074909 | 0.000000 | 24143921 | 22370023 | 0.000000
09-04-2025 15:40:00000 | -1349286 | 134.9286 | 14350979 | 234781.80 | 333691437 | 99439133 | 50083633 | 0.000000 | 24342676 | 22557457 | 0.000000
09-04-2025 15:40:05000 | -1351856 | 135.1856 | 14956050 | 234872.13 | 334356445 | 99393570 | 50134529 | 0.000000 | 24546636 | 22745121 | 0.000000
09-04-2025 15:40:10000 | -1356256 | 135.6256 | 14856571 | 234904.17 | 335362946 | 99405380 | 50136765 | 0.000000 | 24753582 | 22933336 | 0.000000
09-04-2025 15:40:15000 | -1354511 | 135.4511 | 14832311 | 234959.50 | 334839722 | 99405792 | 50139820 | 0.000000 | 24959294 | 23121623 | 0.000000
09-04-2025 15:40:20000 | -1355837 | 135.5837 | 14859916 | 234943.84 | 335198181 | 99404755 | 50131622 | 0.000000 | 25165713 | 23310025 | 0.000000
09-04-2025 15:40:25000 | -1354256 | 135.4256 | 14731457 | 234885.30 | 334858917 | 99413559 | 50113033 | 0.000000 | 25370818 | 23498262 | 0.000000
09-04-2025 15:40:30000 | -1349318 | 134.9318 | 14310138 | 234849.28 | 333595215 | 99442322 | 50059891 | 0.000000 | 25572397 | 23686365 | 0.000000
09-04-2025 15:40:35000 | -1355316 | 135.5316 | 14570304 | 234875.89 | 335086761 | 99427094 | 50065525 | 0.000000 | 25773430 | 23874277 | 0.000000
09-04-2025 15:40:40000 | -1353257 | 135.3257 | 14465585 | 234813.78 | 334649292 | 99433525 | 50056335 | 0.000000 | 25975195 | 24062262 | 0.000000
09-04-2025 15:40:45000 | -1349698 | 134.9698 | 14414315 | 234898.06 | 333640869 | 99434555 | 50063351 | 0.000000 | 26175388 | 24250174 | 0.000000
09-04-2025 15:40:50000 | -1353062 | 135.3062 | 14679513 | 234933.41 | 334481415 | 99416626 | 50076931 | 0.000000 | 26377969 | 24438002 | 0.000000
09-04-2025 15:40:55000 | -1349818 | 134.9818 | 14635993 | 234965.22 | 333633087 | 99417290 | 50098461 | 0.000000 | 26581821 | 24625721 | 0.000000
09-04-2025 15:41:00000 | -1353825 | 135.3825 | 14835275 | 234948.69 | 334689636 | 99404961 | 50128654 | 0.000000 | 26786929 | 24813592 | 0.000000
09-04-2025 15:41:05000 | -1359979 | 135.9979 | 14870640 | 234896.50 | 336276001 | 99407494 | 50118568 | 0.000000 | 26991973 | 25002076 | 0.000000
09-04-2025 15:41:10000 | -1356094 | 135.6094 | 14588841 | 234832.94 | 335349091 | 99426308 | 50096939 | 0.000000 | 27195740 | 25190500 | 0.000000
09-04-2025 15:41:15000 | -1344904 | 134.4904 | 14048166 | 234833.80 | 332470764 | 99458885 | 50065071 | 0.000000 | 27394529 | 25378463 | 0.000000
09-04-2025 15:41:20000 | -1353313 | 135.3313 | 14715828 | 234904.55 | 334596191 | 99413979 | 50100388 | 0.000000 | 27596409 | 25566191 | 0.000000
09-04-2025 15:41:25000 | -1360128 | 136.0128 | 14636021 | 234815.61 | 336372131 | 99426010 | 50094532 | 0.000000 | 27798386 | 25754328 | 0.000000
09-04-2025 15:41:30000 | -1352793 | 135.2793 | 14392180 | 234867.83 | 334435974 | 99438835 | 50095562 | 0.000000 | 27998052 | 25942279 | 0.000000
09-04-2025 15:41:35000 | -1355020 | 135.502 | 14501125 | 234846.58 | 335037903 | 99432228 | 50107845 | 0.000000 | 28198169 | 26130010 | 0.000000
09-04-2025 15:41:40000 | -1349678 | 134.9678 | 14309548 | 234884.59 | 333631653 | 99442657 | 50103962 | 0.000000 | 28397720 | 26317813 | 0.000000
09-04-2025 15:41:45000 | -1351290 | 135.129 | 14192174 | 234792.44 | 334128021 | 99452988 | 50086819 | 0.000000 | 28595874 | 26505713 | 0.000000
09-04-2025 15:41:50000 | -1354502 | 135.4502 | 14369884 | 234810.17 | 334932892 | 99441956 | 50100952 | 0.000000 | 28794658 | 26693385 | 0.000000
09-04-2025 15:41:55000 | -1346664 | 134.6664 | 14339773 | 234899.19 | 332885010 | 99437836 | 50106304 | 0.000000 | 28995110 | 26881250 | 0.000000
09-04-2025 15:42:00000 | -1357390 | 135.739 | 14779070 | 234853.52 | 335683350 | 99412491 | 50128830 | 0.000000 | 29198926 | 27069270 | 0.000000
09-04-2025 15:42:05000 | -1354870 | 135.487 | 14479052 | 234852.20 | 335005371 | 99433823 | 50091747 | 0.000000 | 29399688 | 27257311 | 0.000000
09-04-2025 15:42:10000 | -1348525 | 134.8525 | 14344543 | 234883.05 | 333359894 | 99439003 | 50079472 | 0.000000 | 29600835 | 27445229 | 0.000000
09-04-2025 15:42:15000 | -1359113 | 135.9113 | 14816586 | 234887.05 | 336064148 | 99411011 | 50103848 | 0.000000 | 29803943 | 27633309 | 0.000000
09-04-2025 15:42:20000 | -1355247 | 135.5247 | 14582886 | 234862.31 | 335097229 | 99426056 | 50115803 | 0.000000 | 30006633 | 27821404 | 0.000000
09-04-2025 15:42:25000 | -1355229 | 135.5229 | 14517103 | 234856.75 | 335081543 | 99431168 | 50104530 | 0.000000 | 30209861 | 28010006 | 0.000000
09-04-2025 15:42:30000 | -1358034 | 135.8034 | 14599130 | 234865.31 | 335774292 | 99427124 | 50091671 | 0.000000 | 30412141 | 28198531 | 0.000000
09-04-2025 15:42:35000 | -1352722 | 135.2722 | 14310559 | 234808.78 | 334486359 | 99445068 | 50065224 | 0.000000 | 30613110 | 28386844 | 0.000000
09-04-2025 15:42:40000 | -1344136 | 134.4136 | 14337526 | 235003.48 | 332113281 | 99435913 | 50076679 | 0.000000 | 30811462 | 28574695 | 0.000000
09-04-2025 15:42:45000 | -1359603 | 135.9603 | 14694532 | 234802.56 | 336281525 | 99421005 | 50087803 | 0.000000 | 31014839 | 28762867 | 0.000000
09-04-2025 15:42:50000 | -1350255 | 135.0255 | 14196805 | 234889.19 | 333736816 | 99451805 | 50078114 | 0.000000 | 31213992 | 28950988 | 0.000000
09-04-2025 15:42:55000 | -1354131 | 135.4131 | 14482787 | 234858.14 | 334797058 | 99432915 | 50088734 | 0.000000 | 31414480 | 29139061 | 0.000000
09-04-2025 15:43:00000 | -1353932 | 135.3932 | 14306415 | 234791.72 | 334804199 | 99446373 | 50066662 | 0.000000 | 31614717 | 29327260 | 0.000000
09-04-2025 15:43:05000 | -1349093 | 134.9093 | 14175308 | 234853.06 | 333498718 | 99452515 | 50056904 | 0.000000 | 31812664 | 29515189 | 0.000000
09-04-2025 15:43:10000 | -1352768 | 135.2768 | 14391813 | 234826.91 | 334486328 | 99438843 | 50051521 | 0.000000 | 32012598 | 29703227 | 0.000000
09-04-2025 15:43:15000 | -1358732 | 135.8732 | 14684646 | 234873.69 | 335960327 | 99421043 | 50067017 | 0.000000 | 32213706 | 29891189 | 0.000000
09-04-2025 15:43:20000 | -1358190 | 135.819 | 14403164 | 234787.80 | 335876312 | 99442406 | 50049088 | 0.000000 | 32415166 | 30079590 | 0.000000
09-04-2025 15:43:25000 | -1354596 | 135.4596 | 14301446 | 234850.95 | 334878845 | 99447289 | 50042362 | 0.000000 | 32613904 | 30267826 | 0.000000
09-04-2025 15:43:30000 | -1351028 | 135.1028 | 14265602 | 234862.67 | 333980804 | 99447151 | 50048275 | 0.000000 | 32812632 | 30455613 | 0.000000
09-04-2025 15:43:35000 | -1351360 | 135.136 | 14406952 | 234844.67 | 334126434 | 99436508 | 50053326 | 0.000000 | 33013481 | 30643672 | 0.000000
09-04-2025 15:43:40000 | -1357835 | 135.7835 | 14369262 | 234780.38 | 335792358 | 99444717 | 50036907 | 0.000000 | 33213003 | 30831834 | 0.000000
09-04-2025 15:43:45000 | -1351550 | 135.155 | 14254250 | 234889.61 | 334068695 | 99448441 | 50019516 | 0.000000 | 33411316 | 31019734 | 0.000000
09-04-2025 15:43:50000 | -1350678 | 135.0678 | 14576160 | 234913.16 | 333909271 | 99422729 | 50067223 | 0.000000 | 33612537 | 31207125 | 0.000000
09-04-2025 15:43:55000 | -1349639 | 134.9639 | 14439370 | 234879.78 | 333662598 | 99432556 | 50052082 | 0.000000 | 33814397 | 31394986 | 0.000000
09-04-2025 15:44:00000 | -1346916 | 134.6916 | 14189143 | 234830.25 | 332998840 | 99449692 | 50036579 | 0.000000 | 34014143 | 31582605 | 0.000000
09-04-2025 15:44:05000 | -1346482 | 134.6482 | 14296350 | 234876.27 | 332858673 | 99441055 | 50044758 | 0.000000 | 34212476 | 31769896 | 0.000000
09-04-2025 15:44:10000 | -1353469 | 135.3469 | 14525040 | 234834.23 | 334683105 | 99429077 | 50056473 | 0.000000 | 34412712 | 31957398 | 0.000000
09-04-2025 15:44:15000 | -1349426 | 134.9426 | 13940198 | 234727.97 | 333696686 | 99470642 | 50009258 | 0.000000 | 34610544 | 32145434 | 0.000000
09-04-2025 15:44:20000 | -1343630 | 134.363 | 14043095 | 234858.31 | 332117065 | 99458252 | 50034832 | 0.000000 | 34804824 | 32332238 | 0.000000
09-04-2025 15:44:25000 | -1348532 | 134.8532 | 14293131 | 234857.53 | 333389526 | 99442993 | 50059486 | 0.000000 | 35001565 | 32519074 | 0.000000
09-04-2025 15:44:30000 | -1351261 | 135.1261 | 14445370 | 234846.91 | 334109558 | 99433441 | 50052681 | 0.000000 | 35202019 | 32706773 | 0.000000
09-04-2025 15:44:35000 | -1349456 | 134.9456 | 14194104 | 234779.86 | 333694153 | 99451363 | 50042812 | 0.000000 | 35400195 | 32894090 | 0.000000
09-04-2025 15:44:40000 | -1346809 | 134.6809 | 14434724 | 234930.63 | 332899628 | 99430550 | 50075207 | 0.000000 | 35597407 | 33080809 | 0.000000
09-04-2025 15:44:45000 | -1352648 | 135.2648 | 14570564 | 234849.23 | 334472809 | 99424835 | 50068104 | 0.000000 | 35800728 | 33268668 | 0.000000
09-04-2025 15:44:50000 | -1348222 | 134.8222 | 14416107 | 234905.63 | 333274323 | 99433189 | 50062496 | 0.000000 | 36000576 | 33456156 | 0.000000
09-04-2025 15:44:55000 | -1354190 | 135.419 | 14609468 | 234869.61 | 334833038 | 99423088 | 50084953 | 0.000000 | 36202388 | 33643707 | 0.000000
09-04-2025 15:45:00000 | -1349672 | 134.9672 | 14263970 | 234807.22 | 333726685 | 99446175 | 50066856 | 0.000000 | 36402271 | 33831270 | 0.000000
09-04-2025 15:45:05000 | -1349026 | 134.9026 | 14361539 | 234903.34 | 333456787 | 99438103 | 50051693 | 0.000000 | 19789843 | 187405121 | 0.000000
09-04-2025 15:45:10000 | -1348670 | 134.867 | 14663010 | 234930.67 | 333412323 | 99414162 | 50091312 | 0.000000 | 40086861 | 374535461 | 0.000000
09-04-2025 15:45:15000 | -1349551 | 134.9551 | 14666748 | 234909.06 | 333661987 | 99414627 | 50096718 | 0.000000 | 60463219 | 561940491 | 0.000000
09-04-2025 15:45:20000 | -1347951 | 134.7951 | 14635994 | 234937.58 | 333225281 | 99415688 | 50085941 | 0.000000 | 80933525 | 749834106 | 0.000000
09-04-2025 15:45:25000 | -1350144 | 135.0144 | 14611284 | 234886.88 | 333819885 | 99419510 | 50070946 | 0.000000 | 101328888 | 937604553 | 0.000000
09-04-2025 15:45:30000 | -1352545 | 135.2545 | 14842233 | 234929.02 | 334414703 | 99403290 | 50086361 | 0.000000 | 121717789 | 11250802 | 0.000000
09-04-2025 15:45:35000 | -1352365 | 135.2365 | 14480988 | 234861.17 | 334363556 | 99431587 | 50071880 | 0.000000 | 141971359 | 13127684 | 0.000000
09-04-2025 15:45:40000 | -1346305 | 134.6305 | 14464221 | 234912.33 | 332810547 | 99427818 | 50055725 | 0.000000 | 162158600 | 15002960 | 0.000000
09-04-2025 15:45:45000 | -1350112 | 135.0112 | 14500295 | 234889.88 | 333775574 | 99428200 | 50049950 | 0.000000 | 182229172 | 16876056 | 0.000000
09-04-2025 15:45:50000 | -1346341 | 134.6341 | 14582304 | 234931.20 | 332820038 | 99418549 | 50058079 | 0.000000 | 202500763 | 18748292 | 0.000000
09-04-2025 15:45:55000 | -1351898 | 135.1898 | 14860367 | 234946.36 | 334231354 | 99401276 | 50085873 | 0.000000 | 222901108 | 20619177 | 0.000000
09-04-2025 15:46:00000 | -1350696 | 135.0696 | 14751343 | 234936.69 | 333918274 | 99408913 | 50080948 | 0.000000 | 243544281 | 22495652 | 0.000000
09-04-2025 15:46:05000 | -1354782 | 135.4782 | 14652847 | 234899.92 | 334952576 | 99420189 | 50064598 | 0.000000 | 263899811 | 24374060 | 0.000000
09-04-2025 15:46:10000 | -1346612 | 134.6612 | 14665395 | 235010.20 | 332792908 | 99412201 | 50088551 | 0.000000 | 284304047 | 26246423 | 0.000000
09-04-2025 15:46:15000 | -1349673 | 134.9673 | 14894027 | 234997.47 | 333618347 | 99396614 | 50108124 | 0.000000 | 304883392 | 28120508 | 0.000000
09-04-2025 15:46:20000 | -1354502 | 135.4502 | 15281537 | 235037.48 | 334846771 | 99369591 | 50124718 | 0.000000 | 325898865 | 29998838 | 0.000000
09-04-2025 15:46:25000 | -1352123 | 135.2123 | 14860078 | 234963.36 | 334260376 | 99401497 | 50095654 | 0.000000 | 346734955 | 31879746 | 0.000000
09-04-2025 15:46:30000 | -1350695 | 135.0695 | 14772012 | 234956.80 | 333898590 | 99407265 | 50083988 | 0.000000 | 367273865 | 33754612 | 0.000000
09-04-2025 15:46:35000 | -1349636 | 134.9636 | 14690222 | 234971.05 | 333601013 | 99412842 | 50070179 | 0.000000 | 387680023 | 35628198 | 0.000000
09-04-2025 15:46:40000 | -1345228 | 134.5228 | 14587759 | 234953.69 | 332517883 | 99417168 | 50069664 | 0.000000 | 408074371 | 37498777 | 0.000000
09-04-2025 15:46:45000 | -1346562 | 134.6562 | 14898322 | 234980.70 | 332893555 | 99393501 | 50073109 | 0.000000 | 428583801 | 39369565 | 0.000000
09-04-2025 15:46:50000 | -1344532 | 134.4532 | 14852865 | 235011.16 | 332341553 | 99395363 | 50085819 | 0.000000 | 449283234 | 41240229 | 0.000000
09-04-2025 15:46:55000 | -1348882 | 134.8882 | 15099836 | 235026.56 | 333444885 | 99379265 | 50096485 | 0.000000 | 470186707 | 43113213 | 0.000000
09-04-2025 15:47:00000 | -1354096 | 135.4096 | 15118850 | 234993.70 | 334773376 | 99382454 | 50095592 | 0.000000 | 491088257 | 44987432 | 0.000000
09-04-2025 15:47:05000 | -1347938 | 134.7938 | 14891446 | 234981.72 | 333217865 | 99395287 | 50084469 | 0.000000 | 511843750 | 46861294 | 0.000000
09-04-2025 15:47:10000 | -1350750 | 135.075 | 14817518 | 234909.88 | 333996674 | 99403687 | 50064751 | 0.000000 | 532519287 | 48737173 | 0.000000
09-04-2025 15:47:15000 | -1348348 | 134.8348 | 14466780 | 234909.72 | 333320831 | 99429337 | 50034603 | 0.000000 | 552787964 | 50613159 | 0.000000
09-04-2025 15:47:20000 | -1350988 | 135.0988 | 14832157 | 234977.08 | 333959290 | 99402733 | 50066925 | 0.000000 | 573174744 | 52486255 | 0.000000
09-04-2025 15:47:25000 | -1351288 | 135.1288 | 14850207 | 234998.73 | 334002838 | 99401550 | 50080933 | 0.000000 | 593779602 | 54362813 | 0.000000
09-04-2025 15:47:30000 | -1349579 | 134.9579 | 14831856 | 234963.91 | 333632843 | 99401520 | 50075165 | 0.000000 | 614283447 | 56238447 | 0.000000
09-04-2025 15:47:35000 | -1354983 | 135.4983 | 14796433 | 234899.48 | 335032684 | 99409050 | 50062401 | 0.000000 | 634863220 | 58117202 | 0.000000
09-04-2025 15:47:40000 | -1347317 | 134.7317 | 14455656 | 234935.52 | 333015625 | 99429344 | 50047234 | 0.000000 | 655034119 | 59992275 | 0.000000
09-04-2025 15:47:45000 | -1347035 | 134.7035 | 14775072 | 235008.83 | 332939667 | 99403824 | 50086090 | 0.000000 | 675281677 | 61861567 | 0.000000
09-04-2025 15:47:50000 | -1350157 | 135.0157 | 14571247 | 234830.28 | 333892303 | 99422676 | 50041382 | 0.000000 | 695766479 | 63740254 | 0.000000
09-04-2025 15:47:55000 | -1344950 | 134.495 | 14531693 | 234971.66 | 332409607 | 99421364 | 50052963 | 0.000000 | 715864136 | 65609780 | 0.000000
09-04-2025 15:48:00000 | -1348984 | 134.8984 | 14670793 | 234914.63 | 333512817 | 99413818 | 50072353 | 0.000000 | 736156311 | 67480801 | 0.000000
09-04-2025 15:48:05000 | -1354727 | 135.4727 | 14838363 | 234860.88 | 335043243 | 99405502 | 50057758 | 0.000000 | 756612366 | 69354902 | 0.000000
09-04-2025 15:48:10000 | -1348224 | 134.8224 | 14451073 | 234905.92 | 333281799 | 99430458 | 50049408 | 0.000000 | 776641846 | 71224849 | 0.000000
09-04-2025 15:48:15000 | -1342392 | 134.2392 | 14178225 | 234875.31 | 331832062 | 99446854 | 50044975 | 0.000000 | 796500854 | 73092773 | 0.000000
09-04-2025 15:48:20000 | -1346625 | 134.6625 | 14492247 | 234884.14 | 332930420 | 99425888 | 50035671 | 0.000000 | 816572693 | 74966523 | 0.000000
09-04-2025 15:48:25000 | -1349433 | 134.9433 | 14520575 | 234885.75 | 333623779 | 99426041 | 50034161 | 0.000000 | 836696472 | 76840015 | 0.000000
09-04-2025 15:48:30000 | -1343086 | 134.3086 | 14287508 | 234919.94 | 331962646 | 99438942 | 50043854 | 0.000000 | 856725220 | 78709990 | 0.000000
09-04-2025 15:48:35000 | -1350676 | 135.0676 | 14623063 | 234849.48 | 334018127 | 99419037 | 50054455 | 0.000000 | 876966248 | 80583574 | 0.000000
09-04-2025 15:48:40000 | -1347718 | 134.7718 | 14532076 | 234906.48 | 333176605 | 99423683 | 50041237 | 0.000000 | 897232971 | 82456836 | 0.000000
09-04-2025 15:48:45000 | -1350519 | 135.0519 | 14492124 | 234815.89 | 333983734 | 99429176 | 50038204 | 0.000000 | 917426514 | 84330752 | 0.000000
09-04-2025 15:48:50000 | -1350817 | 135.0817 | 14847238 | 235042.17 | 333826294 | 99401375 | 50056908 | 0.000000 | 937810181 | 86206055 | 0.000000
09-04-2025 15:48:55000 | -1354651 | 135.4651 | 14921895 | 234929.48 | 334943481 | 99398781 | 50068172 | 0.000000 | 958570129 | 88083262 | 0.000000
09-04-2025 15:49:00000 | -1348846 | 134.8846 | 14350291 | 234802.20 | 333554871 | 99438828 | 50017544 | 0.000000 | 978937683 | 89962871 | 0.000000
09-04-2025 15:49:05000 | -1345831 | 134.5831 | 14196631 | 234840.06 | 332723785 | 99448235 | 50008560 | 0.000000 | 998662659 | 91834258 | 0.000000
09-04-2025 15:49:10000 | -1347851 | 134.7851 | 14330061 | 234874.31 | 333203979 | 99439575 | 50012402 | 0.000000 | 10184346 | 93704053 | 0.000000
09-04-2025 15:49:15000 | -1347820 | 134.782 | 14483661 | 234925.56 | 333159180 | 99427574 | 50043022 | 0.000000 | 10384540 | 95575254 | 0.000000
09-04-2025 15:49:20000 | -1351393 | 135.1393 | 14439227 | 234798.17 | 334204346 | 99434029 | 50036049 | 0.000000 | 10585278 | 97447988 | 0.000000
09-04-2025 15:49:25000 | -1345660 | 134.566 | 14219385 | 234804.95 | 332740417 | 99446342 | 50025547 | 0.000000 | 10783967 | 99317070 | 0.000000
09-04-2025 15:49:30000 | -1343851 | 134.3851 | 14037901 | 234808.44 | 332247864 | 99458824 | 50008949 | 0.000000 | 10981067 | 10118928 | 0.000000
09-04-2025 15:49:35000 | -1343526 | 134.3526 | 13936896 | 234796.61 | 332162018 | 99466270 | 50010406 | 0.000000 | 11175614 | 10305863 | 0.000000
09-04-2025 15:49:40000 | -1349485 | 134.9485 | 14246556 | 234774.80 | 333728424 | 99447357 | 50030228 | 0.000000 | 11371750 | 10492656 | 0.000000
09-04-2025 15:49:45000 | -1343673 | 134.3673 | 14193246 | 234904.36 | 332102783 | 99446739 | 50033173 | 0.000000 | 11568903 | 10679733 | 0.000000
09-04-2025 15:49:50000 | -1353140 | 135.314 | 14577521 | 234857.42 | 334588257 | 99424706 | 50052483 | 0.000000 | 11769126 | 10866905 | 0.000000
09-04-2025 15:49:55000 | -1346204 | 134.6204 | 14357419 | 234888.02 | 332792450 | 99436081 | 50044075 | 0.000000 | 11969417 | 11054292 | 0.000000
09-04-2025 15:50:00000 | -1346060 | 134.606 | 14399818 | 234889.56 | 332764282 | 99432655 | 50053940 | 0.000000 | 12170680 | 11241677 | 0.000000
09-04-2025 15:50:05000 | -1350573 | 135.0573 | 14479319 | 234885.81 | 333890717 | 99430222 | 50057007 | 0.000000 | 12370980 | 11428978 | 0.000000
09-04-2025 15:50:10000 | -1348718 | 134.8718 | 14650655 | 234946.53 | 333394897 | 99415184 | 50077259 | 0.000000 | 12573655 | 11616253 | 0.000000
09-04-2025 15:50:15000 | -1355224 | 135.5224 | 14634662 | 234834.19 | 335144836 | 99421989 | 50059341 | 0.000000 | 12777770 | 11804161 | 0.000000
09-04-2025 15:50:20000 | -1351865 | 135.1865 | 14222325 | 234800.50 | 334263184 | 99451141 | 50007740 | 0.000000 | 12977076 | 11991949 | 0.000000
09-04-2025 15:50:25000 | -1344711 | 134.4711 | 14147742 | 234868.63 | 332397949 | 99451096 | 50012901 | 0.000000 | 13173486 | 12178969 | 0.000000
09-04-2025 15:50:30000 | -1345556 | 134.5556 | 14452429 | 234901.58 | 332637756 | 99428116 | 50030319 | 0.000000 | 13372709 | 12366016 | 0.000000
09-04-2025 15:50:35000 | -1348574 | 134.8574 | 14433044 | 234846.09 | 333442841 | 99432159 | 50032951 | 0.000000 | 13572987 | 12553180 | 0.000000
09-04-2025 15:50:40000 | -1347101 | 134.7101 | 14351813 | 234884.13 | 333015076 | 99437263 | 50029106 | 0.000000 | 13771736 | 12740145 | 0.000000
09-04-2025 15:50:45000 | -1352378 | 135.2378 | 14314973 | 234762.48 | 334470795 | 99444450 | 50003407 | 0.000000 | 13970393 | 12927483 | 0.000000
09-04-2025 15:50:50000 | -1350033 | 135.0033 | 13948973 | 234663.52 | 333937225 | 99470451 | 49952396 | 0.000000 | 14166202 | 13114853 | 0.000000
09-04-2025 15:50:55000 | -1339444 | 133.9444 | 13467477 | 234745.47 | 331108704 | 99498329 | 49947124 | 0.000000 | 14355472 | 13301520 | 0.000000
09-04-2025 15:51:00000 | -1343451 | 134.3451 | 13939988 | 234801.61 | 332131592 | 99465973 | 49977512 | 0.000000 | 14546715 | 13487867 | 0.000000
09-04-2025 15:51:05000 | -1343485 | 134.3485 | 13854347 | 234782.77 | 332149384 | 99472488 | 49980171 | 0.000000 | 14739235 | 13674279 | 0.000000
09-04-2025 15:51:10000 | -1343848 | 134.3848 | 14018183 | 234803.81 | 332246155 | 99460335 | 49995369 | 0.000000 | 14933667 | 13860972 | 0.000000
09-04-2025 15:51:15000 | -1342621 | 134.2621 | 14040753 | 234823.42 | 331925568 | 99457626 | 50000549 | 0.000000 | 15128986 | 14047644 | 0.000000
09-04-2025 15:51:20000 | -1341785 | 134.1785 | 14202457 | 234861.81 | 331710205 | 99444481 | 50029278 | 0.000000 | 15325958 | 14234208 | 0.000000
09-04-2025 15:51:25000 | -1344478 | 134.4478 | 14300279 | 234841.70 | 332415649 | 99439102 | 50037033 | 0.000000 | 15524725 | 14421162 | 0.000000
09-04-2025 15:51:30000 | -1351649 | 135.1649 | 14395409 | 234790.50 | 334264587 | 99437637 | 50036213 | 0.000000 | 15723901 | 14608272 | 0.000000
09-04-2025 15:51:35000 | -1341436 | 134.1436 | 14070975 | 234840.17 | 331618622 | 99454353 | 50021828 | 0.000000 | 15920409 | 14795155 | 0.000000
09-04-2025 15:51:40000 | -1335027 | 133.5027 | 13968961 | 234874.53 | 329973175 | 99457039 | 50032387 | 0.000000 | 16116261 | 14981356 | 0.000000
09-04-2025 15:51:45000 | -1341884 | 134.1884 | 14227862 | 234852.39 | 331750000 | 99442589 | 50044559 | 0.000000 | 16312517 | 15167740 | 0.000000
09-04-2025 15:51:50000 | -1343536 | 134.3536 | 14200363 | 234839.23 | 332162659 | 99446075 | 50038544 | 0.000000 | 16510737 | 15354541 | 0.000000
09-04-2025 15:51:55000 | -1342517 | 134.2517 | 14044686 | 234775.47 | 331966461 | 99457237 | 50023502 | 0.000000 | 16706633 | 15541047 | 0.000000
09-04-2025 15:52:00000 | -1345044 | 134.5044 | 14113167 | 234798.38 | 332568115 | 99454018 | 50026405 | 0.000000 | 16900854 | 15727466 | 0.000000
09-04-2025 15:52:05000 | -1345888 | 134.5888 | 13933568 | 234708.88 | 332856201 | 99468376 | 50001465 | 0.000000 | 17094546 | 15914148 | 0.000000
09-04-2025 15:52:10000 | -1335135 | 133.5135 | 13870329 | 234939.47 | 329884521 | 99464706 | 49997860 | 0.000000 | 17286378 | 16100438 | 0.000000
09-04-2025 15:52:15000 | -1342844 | 134.2844 | 14544905 | 234932.67 | 331953674 | 99418510 | 50060101 | 0.000000 | 17483845 | 16286290 | 0.000000
09-04-2025 15:52:20000 | -1341390 | 134.139 | 14798416 | 235012.66 | 331552032 | 99396957 | 50109657 | 0.000000 | 17687831 | 16472533 | 0.000000
09-04-2025 15:52:25000 | -1345997 | 134.5997 | 14970607 | 234994.44 | 332749084 | 99387154 | 50119030 | 0.000000 | 17894767 | 16659322 | 0.000000
09-04-2025 15:52:30000 | -1345202 | 134.5202 | 14892367 | 235008.16 | 332515625 | 99392769 | 50127537 | 0.000000 | 18100809 | 16845885 | 0.000000
09-04-2025 15:52:35000 | -1347170 | 134.717 | 14986027 | 234971.27 | 333075226 | 99386955 | 50100281 | 0.000000 | 18308977 | 17033100 | 0.000000
09-04-2025 15:52:40000 | -1348418 | 134.8418 | 14813174 | 234945.16 | 333368896 | 99401993 | 50083931 | 0.000000 | 18514393 | 17219969 | 0.000000
09-04-2025 15:52:45000 | -1342397 | 134.2397 | 14676887 | 234967.45 | 331842133 | 99407616 | 50095985 | 0.000000 | 18718624 | 17406484 | 0.000000
09-04-2025 15:52:50000 | -1343462 | 134.3462 | 14713897 | 234946.66 | 332134369 | 99405586 | 50081600 | 0.000000 | 18923541 | 17593338 | 0.000000
09-04-2025 15:52:55000 | -1339847 | 133.9847 | 14569755 | 234954.16 | 331199738 | 99413956 | 50078945 | 0.000000 | 19126772 | 17779635 | 0.000000
09-04-2025 15:53:00000 | -1345138 | 134.5138 | 14855662 | 234977.97 | 332532318 | 99395676 | 50086445 | 0.000000 | 19331222 | 17965891 | 0.000000
09-04-2025 15:53:05000 | -1346797 | 134.6797 | 14882221 | 234972.88 | 332953888 | 99395012 | 50099323 | 0.000000 | 19537103 | 18152598 | 0.000000
09-04-2025 15:53:10000 | -1346283 | 134.6283 | 14777350 | 234941.55 | 332845856 | 99402985 | 50074680 | 0.000000 | 19743790 | 18339617 | 0.000000
09-04-2025 15:53:15000 | -1341962 | 134.1962 | 14520302 | 234938.84 | 331721863 | 99419708 | 50069424 | 0.000000 | 19947314 | 18526246 | 0.000000
09-04-2025 15:53:20000 | -1344099 | 134.4099 | 14376742 | 234872.98 | 332300049 | 99432816 | 50058708 | 0.000000 | 20148694 | 18712709 | 0.000000
09-04-2025 15:53:25000 | -1342664 | 134.2664 | 14211346 | 234774.92 | 332044373 | 99444511 | 50010475 | 0.000000 | 20347676 | 18899443 | 0.000000
09-04-2025 15:53:30000 | -1338889 | 133.8889 | 14032079 | 234799.31 | 331045502 | 99455292 | 49999508 | 0.000000 | 20542791 | 19085525 | 0.000000
09-04-2025 15:53:35000 | -1335504 | 133.5504 | 14143267 | 234889.84 | 330112976 | 99443909 | 50003918 | 0.000000 | 20738953 | 19271646 | 0.000000
09-04-2025 15:53:40000 | -1338957 | 133.8957 | 14322169 | 234891.23 | 331003357 | 99432785 | 50048706 | 0.000000 | 20935872 | 19457293 | 0.000000
09-04-2025 15:53:45000 | -1345625 | 134.5625 | 14738372 | 234910.16 | 332715790 | 99405525 | 50077679 | 0.000000 | 21137996 | 19643707 | 0.000000
09-04-2025 15:53:50000 | -1342872 | 134.2872 | 14588810 | 234905.63 | 332008728 | 99415054 | 50076046 | 0.000000 | 21341462 | 19830354 | 0.000000
09-04-2025 15:53:55000 | -1345183 | 134.5183 | 14581439 | 234904.06 | 332573853 | 99417625 | 50072388 | 0.000000 | 21543721 | 20016914 | 0.000000
09-04-2025 15:54:00000 | -1344493 | 134.4493 | 14717791 | 234921.00 | 332420898 | 99406174 | 50077507 | 0.000000 | 21748940 | 20203826 | 0.000000
09-04-2025 15:54:05000 | -1345194 | 134.5194 | 14613639 | 234840.39 | 332684052 | 99415085 | 50052589 | 0.000000 | 21954128 | 20391143 | 0.000000
09-04-2025 15:54:10000 | -1343430 | 134.343 | 14437364 | 234867.19 | 332163971 | 99427505 | 50036259 | 0.000000 | 22155493 | 20578000 | 0.000000
09-04-2025 15:54:15000 | -1345923 | 134.5923 | 14690229 | 234893.48 | 332798126 | 99409622 | 50039295 | 0.000000 | 22358709 | 20764887 | 0.000000
09-04-2025 15:54:20000 | -1344012 | 134.4012 | 14717536 | 234890.11 | 332344421 | 99405777 | 50039276 | 0.000000 | 22561982 | 20951539 | 0.000000
09-04-2025 15:54:25000 | -1343983 | 134.3983 | 14758916 | 234901.31 | 332333435 | 99402435 | 50060371 | 0.000000 | 22766494 | 21138111 | 0.000000
09-04-2025 15:54:30000 | -1344020 | 134.402 | 14571755 | 234830.31 | 332389191 | 99417397 | 50047421 | 0.000000 | 22971653 | 21325064 | 0.000000
09-04-2025 15:54:35000 | -1345627 | 134.5627 | 14493933 | 234822.09 | 332777527 | 99424911 | 50004536 | 0.000000 | 23173164 | 21512209 | 0.000000
09-04-2025 15:54:40000 | -1340646 | 134.0646 | 14249775 | 234853.16 | 331456665 | 99439857 | 50012302 | 0.000000 | 23372329 | 21698730 | 0.000000
09-04-2025 15:54:45000 | -1343486 | 134.3486 | 14481600 | 234881.69 | 332168274 | 99424065 | 50028744 | 0.000000 | 23572136 | 21885455 | 0.000000
09-04-2025 15:54:50000 | -1354066 | 135.4066 | 14782910 | 234819.69 | 334918182 | 99409325 | 50024544 | 0.000000 | 23775535 | 22072529 | 0.000000
09-04-2025 15:54:55000 | -1345771 | 134.5771 | 14006037 | 234693.88 | 332867401 | 99462784 | 49962585 | 0.000000 | 23975464 | 22260000 | 0.000000
09-04-2025 15:55:00000 | -1339645 | 133.9645 | 13894959 | 234841.11 | 331129608 | 99466400 | 49960983 | 0.000000 | 24168215 | 22446623 | 0.000000
09-04-2025 15:55:05000 | -1343181 | 134.3181 | 14264621 | 234871.75 | 332045837 | 99440804 | 50001827 | 0.000000 | 24363716 | 22632770 | 0.000000
09-04-2025 15:55:10000 | -1344993 | 134.4993 | 14498973 | 234899.55 | 332510712 | 99423981 | 50027878 | 0.000000 | 24563728 | 22819283 | 0.000000
09-04-2025 15:55:15000 | -1347184 | 134.7184 | 14521263 | 234863.84 | 333103241 | 99424080 | 50040703 | 0.000000 | 24765671 | 23006305 | 0.000000
09-04-2025 15:55:20000 | -1347157 | 134.7157 | 14437333 | 234861.69 | 333077240 | 99430641 | 50021420 | 0.000000 | 24966785 | 23193398 | 0.000000
09-04-2025 15:55:25000 | -1342509 | 134.2509 | 14537248 | 234942.31 | 331858826 | 99418831 | 50030621 | 0.000000 | 25168582 | 23380283 | 0.000000
09-04-2025 15:55:30000 | -1341578 | 134.1578 | 14572646 | 234957.92 | 331632141 | 99415222 | 50031826 | 0.000000 | 25371704 | 23567145 | 0.000000
09-04-2025 15:55:35000 | -1346495 | 134.6495 | 14787423 | 234996.09 | 332817993 | 99402359 | 50044285 | 0.000000 | 25576821 | 23754102 | 0.000000
09-04-2025 15:55:40000 | -1349579 | 134.9579 | 15071012 | 235008.42 | 333634369 | 99382240 | 50051449 | 0.000000 | 25784492 | 23941346 | 0.000000
09-04-2025 15:55:45000 | -1349584 | 134.9584 | 14965891 | 234979.36 | 333647705 | 99390755 | 50028763 | 0.000000 | 25991851 | 24128746 | 0.000000
09-04-2025 15:55:50000 | -1349369 | 134.9369 | 14821960 | 234953.84 | 333587677 | 99402122 | 50016430 | 0.000000 | 26198152 | 24316080 | 0.000000
09-04-2025 15:55:55000 | -1346535 | 134.6535 | 14669487 | 234916.20 | 332912537 | 99411804 | 50008064 | 0.000000 | 26403545 | 24503369 | 0.000000
09-04-2025 15:56:00000 | -1344137 | 134.4137 | 14593975 | 234919.47 | 332305420 | 99415733 | 49996761 | 0.000000 | 26606306 | 24690262 | 0.000000
09-04-2025 15:56:05000 | -1346235 | 134.6235 | 14594315 | 234887.11 | 332862000 | 99417511 | 49979675 | 0.000000 | 26808730 | 24877219 | 0.000000
09-04-2025 15:56:10000 | -1342612 | 134.2612 | 14353543 | 234890.66 | 331905212 | 99433388 | 49967365 | 0.000000 | 27009641 | 25064123 | 0.000000
09-04-2025 15:56:15000 | -1341293 | 134.1293 | 14118759 | 234873.14 | 331546631 | 99450554 | 49968010 | 0.000000 | 27206489 | 25250311 | 0.000000
09-04-2025 15:56:20000 | -1339186 | 133.9186 | 14498254 | 234973.69 | 330992767 | 99419075 | 50016090 | 0.000000 | 27405588 | 25436328 | 0.000000
09-04-2025 15:56:25000 | -1340197 | 134.0197 | 14810857 | 234998.20 | 331289398 | 99394882 | 50038483 | 0.000000 | 27610313 | 25622768 | 0.000000
09-04-2025 15:56:30000 | -1345829 | 134.5829 | 15112395 | 235042.73 | 332683197 | 99375443 | 50070618 | 0.000000 | 27816326 | 25808910 | 0.000000
09-04-2025 15:56:35000 | -1348513 | 134.8513 | 14965111 | 234930.33 | 333456177 | 99389862 | 50057598 | 0.000000 | 28024849 | 25995494 | 0.000000
09-04-2025 15:56:40000 | -1347198 | 134.7198 | 14706027 | 234909.36 | 333093475 | 99409477 | 50021748 | 0.000000 | 28230432 | 26182438 | 0.000000
09-04-2025 15:56:45000 | -1341781 | 134.1781 | 14654446 | 234975.14 | 331661194 | 99408875 | 50014084 | 0.000000 | 28432915 | 26368727 | 0.000000
09-04-2025 15:56:50000 | -1347047 | 134.7047 | 14862826 | 234932.11 | 333064850 | 99396797 | 50023846 | 0.000000 | 28637959 | 26555172 | 0.000000
09-04-2025 15:56:55000 | -1342695 | 134.2695 | 14632763 | 234933.23 | 331938965 | 99411400 | 50013409 | 0.000000 | 28842776 | 26741955 | 0.000000
09-04-2025 15:57:00000 | -1341388 | 134.1388 | 14792498 | 235030.63 | 331524994 | 99397430 | 50048004 | 0.000000 | 29045820 | 26927955 | 0.000000
09-04-2025 15:57:05000 | -1341667 | 134.1667 | 14940623 | 235003.95 | 331673370 | 99385674 | 50053143 | 0.000000 | 29253311 | 27114393 | 0.000000
09-04-2025 15:57:10000 | -1338736 | 133.8736 | 14809156 | 235016.39 | 330911469 | 99393715 | 50051849 | 0.000000 | 29460608 | 27301000 | 0.000000
09-04-2025 15:57:15000 | -1344551 | 134.4551 | 14569732 | 234848.09 | 332496643 | 99418015 | 50016956 | 0.000000 | 29665093 | 27487697 | 0.000000
09-04-2025 15:57:20000 | -1340905 | 134.0905 | 14296544 | 234866.00 | 331508331 | 99436424 | 49978710 | 0.000000 | 29864634 | 27674057 | 0.000000
09-04-2025 15:57:25000 | -1338659 | 133.8659 | 13767631 | 234709.36 | 331049774 | 99475288 | 49929855 | 0.000000 | 30059348 | 27860209 | 0.000000
09-04-2025 15:57:30000 | -1337918 | 133.7918 | 13784077 | 234749.59 | 330816162 | 99473465 | 49921108 | 0.000000 | 30248650 | 28045600 | 0.000000
09-04-2025 15:57:35000 | -1334286 | 133.4286 | 13669465 | 234738.94 | 329908905 | 99479317 | 49920727 | 0.000000 | 30439568 | 28231291 | 0.000000
09-04-2025 15:57:40000 | -1340078 | 134.0078 | 14214207 | 234772.64 | 331416138 | 99442162 | 49955151 | 0.000000 | 30633442 | 28417016 | 0.000000
09-04-2025 15:57:45000 | -1336072 | 133.6072 | 14217158 | 234773.13 | 330441986 | 99438606 | 49987705 | 0.000000 | 30829775 | 28602570 | 0.000000
09-04-2025 15:57:50000 | -1337674 | 133.7674 | 14405486 | 234752.72 | 330907288 | 99425133 | 50008205 | 0.000000 | 31030757 | 28788643 | 0.000000
09-04-2025 15:57:55000 | -1342303 | 134.2303 | 14524454 | 234854.83 | 331928589 | 99419670 | 50024754 | 0.000000 | 31231367 | 28974707 | 0.000000
09-04-2025 15:58:00000 | -1338577 | 133.8577 | 14404744 | 234885.20 | 330942963 | 99425957 | 50012417 | 0.000000 | 31432097 | 29161035 | 0.000000
09-04-2025 15:58:05000 | -1343720 | 134.372 | 14732505 | 234863.33 | 332315887 | 99404320 | 50031891 | 0.000000 | 31634341 | 29347119 | 0.000000
09-04-2025 15:58:10000 | -1346531 | 134.6531 | 14710664 | 234810.41 | 333077698 | 99408524 | 50011116 | 0.000000 | 31838887 | 29534082 | 0.000000
09-04-2025 15:58:15000 | -1346627 | 134.6627 | 14578937 | 234839.25 | 333018768 | 99419060 | 49975399 | 0.000000 | 32042993 | 29721115 | 0.000000
09-04-2025 15:58:20000 | -1345037 | 134.5037 | 14473477 | 234849.34 | 332588043 | 99426025 | 49959183 | 0.000000 | 32244561 | 29907951 | 0.000000
09-04-2025 15:58:25000 | -1342932 | 134.2932 | 14642123 | 234946.48 | 331992859 | 99410858 | 49989212 | 0.000000 | 32445239 | 30094109 | 0.000000
09-04-2025 15:58:30000 | -1344409 | 134.4409 | 14607479 | 234839.84 | 332481812 | 99414894 | 50001194 | 0.000000 | 32648066 | 30280387 | 0.000000
09-04-2025 15:58:35000 | -1338884 | 133.8884 | 14194494 | 234804.05 | 331074921 | 99442711 | 49964794 | 0.000000 | 32848503 | 30466920 | 0.000000
09-04-2025 15:58:40000 | -1345320 | 134.532 | 14539402 | 234796.05 | 332753723 | 99421066 | 49980297 | 0.000000 | 33048779 | 30653230 | 0.000000
09-04-2025 15:58:45000 | -1344731 | 134.4731 | 14126135 | 234691.05 | 332647247 | 99452774 | 49948200 | 0.000000 | 33247622 | 30840223 | 0.000000
09-04-2025 15:58:50000 | -1342374 | 134.2374 | 14050082 | 234781.77 | 331928528 | 99456711 | 49948750 | 0.000000 | 33443911 | 31026912 | 0.000000
09-04-2025 15:58:55000 | -1344247 | 134.4247 | 14462379 | 234880.94 | 332353485 | 99426224 | 49987144 | 0.000000 | 33641665 | 31213180 | 0.000000
09-04-2025 15:59:00000 | -1345928 | 134.5928 | 14301357 | 234751.06 | 332902771 | 99440216 | 49956085 | 0.000000 | 33842947 | 31400615 | 0.000000
09-04-2025 15:59:05000 | -1343040 | 134.304 | 14344761 | 234894.34 | 332001190 | 99434433 | 49982124 | 0.000000 | 34040439 | 31587191 | 0.000000
09-04-2025 15:59:10000 | -1343214 | 134.3214 | 14374035 | 234691.55 | 332342957 | 99432289 | 50002865 | 0.000000 | 34241299 | 31774051 | 0.000000
09-04-2025 15:59:15000 | -1347254 | 134.7254 | 14446283 | 234686.95 | 333350922 | 99430023 | 49978653 | 0.000000 | 34442017 | 31961074 | 0.000000
09-04-2025 15:59:20000 | -1344514 | 134.4514 | 14429805 | 234724.78 | 332622833 | 99429008 | 49975258 | 0.000000 | 34642485 | 32147951 | 0.000000
09-04-2025 15:59:25000 | -1343656 | 134.3656 | 14438953 | 234744.59 | 332394012 | 99427567 | 49974621 | 0.000000 | 34843909 | 32334863 | 0.000000
09-04-2025 15:59:30000 | -1338446 | 133.8446 | 14287002 | 234790.36 | 331014404 | 99435120 | 49975624 | 0.000000 | 35044734 | 32521684 | 0.000000
09-04-2025 15:59:35000 | -1348854 | 134.8854 | 14649031 | 234763.58 | 333692413 | 99415428 | 49977417 | 0.000000 | 35245464 | 32708377 | 0.000000
09-04-2025 15:59:40000 | -1344118 | 134.4118 | 14434013 | 234790.28 | 332440552 | 99428345 | 49961678 | 0.000000 | 35447375 | 32895387 | 0.000000
09-04-2025 15:59:45000 | -1343935 | 134.3935 | 14629139 | 234948.08 | 332223541 | 99412766 | 49977631 | 0.000000 | 35648179 | 33082199 | 0.000000
09-04-2025 15:59:50000 | -1351156 | 135.1156 | 14620107 | 234791.16 | 334212250 | 99419678 | 49985565 | 0.000000 | 35850745 | 33269266 | 0.000000
09-04-2025 15:59:55000 | -1338987 | 133.8987 | 14375431 | 234892.94 | 331025269 | 99428619 | 49973236 | 0.000000 | 36051855 | 33456188 | 0.000000
09-04-2025 16:00:00000 | -1345912 | 134.5912 | 14520487 | 234842.52 | 332828949 | 99423065 | 49979862 | 0.000000 | 36254280 | 33643113 | 0.000000
09-04-2025 16:00:05000 | -1347422 | 134.7422 | 14677270 | 234825.23 | 333273682 | 99411957 | 49976971 | 0.000000 | 20333031 | 187158020 | 0.000000
09-04-2025 16:00:10000 | -1347568 | 134.7568 | 14573547 | 234670.83 | 333488708 | 99420288 | 49951118 | 0.000000 | 40797573 | 374632355 | 0.000000
09-04-2025 16:00:15000 | -1349488 | 134.9488 | 14484743 | 234652.44 | 333964844 | 99428886 | 49936478 | 0.000000 | 60968628 | 561855042 | 0.000000
09-04-2025 16:00:20000 | -1347349 | 134.7349 | 14174652 | 234672.09 | 333334564 | 99451157 | 49957386 | 0.000000 | 80595192 | 748520691 | 0.000000
09-04-2025 16:00:25000 | -1349257 | 134.9257 | 14592032 | 234719.72 | 333839508 | 99420273 | 49981121 | 0.000000 | 100611954 | 935568176 | 0.000000
09-04-2025 16:00:30000 | -1348946 | 134.8946 | 14814346 | 234798.22 | 333705627 | 99402359 | 49991383 | 0.000000 | 121015038 | 11226656 | 0.000000
09-04-2025 16:00:35000 | -1343102 | 134.3102 | 14411629 | 234798.30 | 332169830 | 99429245 | 49981640 | 0.000000 | 141233521 | 13095396 | 0.000000
09-04-2025 16:00:40000 | -1349703 | 134.9703 | 14398618 | 234636.59 | 334010712 | 99435783 | 49940628 | 0.000000 | 161365768 | 14970081 | 0.000000
09-04-2025 16:00:45000 | -1342462 | 134.2462 | 14133602 | 234725.61 | 332048462 | 99450356 | 49930878 | 0.000000 | 181105438 | 16840009 | 0.000000
09-04-2025 16:00:50000 | -1344133 | 134.4133 | 14242297 | 234741.53 | 332457642 | 99443321 | 49955494 | 0.000000 | 200864380 | 18706298 | 0.000000
09-04-2025 16:00:55000 | -1352224 | 135.2224 | 14454728 | 234631.78 | 334649017 | 99433510 | 49951302 | 0.000000 | 220801834 | 20576919 | 0.000000
09-04-2025 16:01:00000 | -1340385 | 134.0385 | 14087203 | 234699.25 | 331561584 | 99452255 | 49945053 | 0.000000 | 240549988 | 22445200 | 0.000000
09-04-2025 16:01:05000 | -1347697 | 134.7697 | 14454628 | 234747.03 | 333378052 | 99429741 | 49984566 | 0.000000 | 260450684 | 24311648 | 0.000000
09-04-2025 16:01:10000 | -1347787 | 134.7787 | 14743177 | 234805.45 | 333396912 | 99407028 | 49992458 | 0.000000 | 280706604 | 26180356 | 0.000000
09-04-2025 16:01:15000 | -1343063 | 134.3063 | 14432836 | 234789.33 | 332192474 | 99427551 | 49994141 | 0.000000 | 300824768 | 28046162 | 0.000000
09-04-2025 16:01:20000 | -1348955 | 134.8955 | 14552362 | 234785.86 | 333662537 | 99423141 | 49982964 | 0.000000 | 320935242 | 29916802 | 0.000000
09-04-2025 16:01:25000 | -1342343 | 134.2343 | 14127848 | 234688.80 | 332073517 | 99450706 | 49954185 | 0.000000 | 340834747 | 31785247 | 0.000000
09-04-2025 16:01:30000 | -1336590 | 133.659 | 14052487 | 234726.52 | 330585419 | 99451851 | 49951767 | 0.000000 | 360503540 | 33648167 | 0.000000
09-04-2025 16:01:35000 | -1342890 | 134.289 | 14254854 | 234674.72 | 332259949 | 99441322 | 49956486 | 0.000000 | 380440338 | 35511243 | 0.000000
09-04-2025 16:01:40000 | -1344175 | 134.4175 | 14133953 | 234652.08 | 332571899 | 99451721 | 49949623 | 0.000000 | 400207428 | 37375332 | 0.000000
09-04-2025 16:01:45000 | -1342218 | 134.2218 | 13958643 | 234651.31 | 332053223 | 99463577 | 49950695 | 0.000000 | 419824219 | 39242612 | 0.000000
09-04-2025 16:01:50000 | -1342716 | 134.2716 | 14233104 | 234714.92 | 332155701 | 99442863 | 49961308 | 0.000000 | 439496155 | 41108936 | 0.000000
09-04-2025 16:01:55000 | -1346377 | 134.6377 | 14281199 | 234735.81 | 333033356 | 99442146 | 49965363 | 0.000000 | 459313812 | 42977749 | 0.000000
09-04-2025 16:02:00000 | -1349003 | 134.9003 | 14145402 | 234630.53 | 333782257 | 99454727 | 49929928 | 0.000000 | 479022217 | 44849751 | 0.000000
09-04-2025 16:02:05000 | -1342246 | 134.2246 | 13881534 | 234672.89 | 332002655 | 99469467 | 49923187 | 0.000000 | 498305786 | 46714976 | 0.000000
09-04-2025 16:02:10000 | -1344458 | 134.4458 | 13929249 | 234612.70 | 332651154 | 99467583 | 49912796 | 0.000000 | 517647522 | 48580659 | 0.000000
09-04-2025 16:02:15000 | -1336714 | 133.6714 | 13762994 | 234646.58 | 330657196 | 99474129 | 49933372 | 0.000000 | 536938171 | 50442412 | 0.000000
09-04-2025 16:02:20000 | -1343627 | 134.3627 | 14167462 | 234697.39 | 332376007 | 99448692 | 49953068 | 0.000000 | 556290527 | 52306094 | 0.000000
09-04-2025 16:02:25000 | -1342866 | 134.2866 | 14004921 | 234652.89 | 332216431 | 99460564 | 49959042 | 0.000000 | 575843140 | 54173032 | 0.000000
09-04-2025 16:02:30000 | -1343110 | 134.311 | 14328051 | 234801.22 | 332148499 | 99435799 | 49984589 | 0.000000 | 595501343 | 56037959 | 0.000000
09-04-2025 16:02:35000 | -1346517 | 134.6517 | 14165201 | 234649.22 | 333159943 | 99451210 | 49967785 | 0.000000 | 615346558 | 57908008 | 0.000000
09-04-2025 16:02:40000 | -1349512 | 134.9512 | 14023407 | 234568.19 | 333971954 | 99464424 | 49929962 | 0.000000 | 635008606 | 59780483 | 0.000000
09-04-2025 16:02:45000 | -1344772 | 134.4772 | 13610515 | 234506.56 | 332794861 | 99491722 | 49879456 | 0.000000 | 654132202 | 61649790 | 0.000000
09-04-2025 16:02:50000 | -1343298 | 134.3298 | 13595700 | 234632.88 | 332250031 | 99491714 | 49872654 | 0.000000 | 672869629 | 63513770 | 0.000000
09-04-2025 16:02:55000 | -1343932 | 134.3932 | 13616896 | 234559.41 | 332518188 | 99490616 | 49874260 | 0.000000 | 691670654 | 65375713 | 0.000000
09-04-2025 16:03:00000 | -1340580 | 134.058 | 13515319 | 234559.70 | 331665771 | 99495636 | 49900242 | 0.000000 | 710509033 | 67236514 | 0.000000
09-04-2025 16:03:05000 | -1345113 | 134.5113 | 13858116 | 234541.55 | 332892395 | 99473473 | 49925690 | 0.000000 | 729706177 | 69101577 | 0.000000
09-04-2025 16:03:10000 | -1348200 | 134.82 | 13886521 | 234557.64 | 333629425 | 99473732 | 49930561 | 0.000000 | 748924133 | 70967847 | 0.000000
09-04-2025 16:03:15000 | -1346258 | 134.6258 | 13404147 | 234460.67 | 333167328 | 99507988 | 49876194 | 0.000000 | 767801147 | 72838379 | 0.000000
09-04-2025 16:03:20000 | -1338894 | 133.8894 | 13373826 | 234557.55 | 331220245 | 99504829 | 49890652 | 0.000000 | 786323914 | 74698130 | 0.000000
09-04-2025 16:03:25000 | -1340762 | 134.0762 | 13580518 | 234606.19 | 331658600 | 99490936 | 49903759 | 0.000000 | 805137146 | 76561128 | 0.000000
09-04-2025 16:03:30000 | -1337506 | 133.7506 | 13419957 | 234574.47 | 330865601 | 99500404 | 49898750 | 0.000000 | 823854248 | 78422246 | 0.000000
09-04-2025 16:03:35000 | -1340441 | 134.0441 | 13644951 | 234610.05 | 331594391 | 99485886 | 49915375 | 0.000000 | 842678101 | 80285132 | 0.000000
09-04-2025 16:03:40000 | -1349889 | 134.9889 | 13768214 | 234472.08 | 334133820 | 99483871 | 49912163 | 0.000000 | 861858215 | 82153154 | 0.000000
09-04-2025 16:03:45000 | -1342157 | 134.2157 | 13650695 | 234617.34 | 332004028 | 99486763 | 49918720 | 0.000000 | 880792603 | 84018584 | 0.000000
09-04-2025 16:03:50000 | -1347117 | 134.7117 | 13908947 | 234603.78 | 333304626 | 99471199 | 49922321 | 0.000000 | 899879456 | 85884199 | 0.000000
09-04-2025 16:03:55000 | -1344983 | 134.4983 | 13433318 | 234498.66 | 332811462 | 99504929 | 49892902 | 0.000000 | 918757690 | 87749648 | 0.000000
09-04-2025 16:04:00000 | -1335799 | 133.5799 | 13351552 | 234586.88 | 330418121 | 99504196 | 49890495 | 0.000000 | 937490967 | 89611680 | 0.000000
09-04-2025 16:04:05000 | -1344813 | 134.4813 | 13755314 | 234558.22 | 332764221 | 99480965 | 49912617 | 0.000000 | 956292053 | 91471270 | 0.000000
09-04-2025 16:04:10000 | -1345918 | 134.5918 | 13753426 | 234523.16 | 333082611 | 99481956 | 49901337 | 0.000000 | 975404846 | 93336025 | 0.000000
09-04-2025 16:04:15000 | -1347278 | 134.7278 | 13656709 | 234494.47 | 333440552 | 99490181 | 49876385 | 0.000000 | 994473206 | 95203564 | 0.000000
09-04-2025 16:04:20000 | -1343294 | 134.3294 | 13722759 | 234591.48 | 332341949 | 99482239 | 49879204 | 0.000000 | 10132484 | 97066348 | 0.000000
09-04-2025 16:04:25000 | -1338095 | 133.8095 | 13427162 | 234563.42 | 331031494 | 99500313 | 49891876 | 0.000000 | 10320074 | 98927139 | 0.000000
09-04-2025 16:04:30000 | -1342712 | 134.2712 | 13583934 | 234502.44 | 332288574 | 99492149 | 49904808 | 0.000000 | 10508851 | 10078913 | 0.000000
09-04-2025 16:04:35000 | -1336773 | 133.6773 | 13231643 | 234505.22 | 330735565 | 99513702 | 49870476 | 0.000000 | 10695416 | 10265066 | 0.000000
09-04-2025 16:04:40000 | -1335286 | 133.5286 | 13185315 | 234506.58 | 330358582 | 99516006 | 49852337 | 0.000000 | 10879625 | 10450940 | 0.000000
09-04-2025 16:04:45000 | -1341569 | 134.1569 | 13280675 | 234451.08 | 332004150 | 99513588 | 49852051 | 0.000000 | 11063033 | 10636643 | 0.000000
09-04-2025 16:04:50000 | -1339774 | 133.9774 | 13047999 | 234435.50 | 331531128 | 99529114 | 49834991 | 0.000000 | 11244329 | 10822087 | 0.000000
09-04-2025 16:04:55000 | -1334395 | 133.4395 | 13150059 | 234484.00 | 330168091 | 99517929 | 49839031 | 0.000000 | 11426882 | 11007526 | 0.000000
09-04-2025 16:05:00000 | -1333112 | 133.3112 | 13108205 | 234463.42 | 329873779 | 99520058 | 49847958 | 0.000000 | 11608469 | 11192643 | 0.000000
09-04-2025 16:05:05000 | -1331537 | 133.1537 | 12916029 | 234414.94 | 329512207 | 99532837 | 49843601 | 0.000000 | 11788928 | 11377592 | 0.000000
09-04-2025 16:05:10000 | -1330974 | 133.0974 | 13087960 | 234572.63 | 329189789 | 99520004 | 49852413 | 0.000000 | 11967799 | 11562349 | 0.000000
09-04-2025 16:05:15000 | -1340424 | 134.0424 | 13371150 | 234417.08 | 331796814 | 99506149 | 49869488 | 0.000000 | 12152334 | 11747559 | 0.000000
09-04-2025 16:05:20000 | -1328991 | 132.8991 | 12477693 | 234304.33 | 328932739 | 99562141 | 49785336 | 0.000000 | 12331316 | 11933201 | 0.000000
09-04-2025 16:05:25000 | -1328312 | 132.8312 | 12539190 | 234502.61 | 328507690 | 99557396 | 49811665 | 0.000000 | 12504762 | 12117729 | 0.000000
09-04-2025 16:05:30000 | -1332523 | 133.2523 | 12846699 | 234462.39 | 329666992 | 99538483 | 49822506 | 0.000000 | 12682587 | 12302634 | 0.000000
09-04-2025 16:05:35000 | -1332178 | 133.2178 | 12912219 | 234534.69 | 329495789 | 99533554 | 49828934 | 0.000000 | 12860740 | 12487814 | 0.000000
09-04-2025 16:05:40000 | -1337320 | 133.732 | 12909269 | 234469.55 | 330845764 | 99537323 | 49830204 | 0.000000 | 13038978 | 12673040 | 0.000000
09-04-2025 16:05:45000 | -1330053 | 133.0053 | 12725378 | 234510.11 | 328965088 | 99545425 | 49826443 | 0.000000 | 13216321 | 12858061 | 0.000000
09-04-2025 16:05:50000 | -1334051 | 133.4051 | 12797677 | 234416.81 | 330092041 | 99543015 | 49813995 | 0.000000 | 13394454 | 13043313 | 0.000000
09-04-2025 16:05:55000 | -1331933 | 133.1933 | 12768417 | 234396.55 | 329600586 | 99543648 | 49802429 | 0.000000 | 13571614 | 13228312 | 0.000000
09-04-2025 16:06:00000 | -1331163 | 133.1163 | 12612056 | 234358.75 | 329421326 | 99554169 | 49785427 | 0.000000 | 13748790 | 13413417 | 0.000000
09-04-2025 16:06:05000 | -1332731 | 133.2731 | 12646070 | 234332.53 | 329855835 | 99552826 | 49777233 | 0.000000 | 13923376 | 13598272 | 0.000000
09-04-2025 16:06:10000 | -1328343 | 132.8343 | 12073639 | 234249.30 | 328762634 | 99589470 | 49737423 | 0.000000 | 14094314 | 13783191 | 0.000000
09-04-2025 16:06:15000 | -1324016 | 132.4016 | 12047685 | 234350.00 | 327554047 | 99588562 | 49742149 | 0.000000 | 14261888 | 13967291 | 0.000000
09-04-2025 16:06:20000 | -1325997 | 132.5997 | 12430082 | 234377.94 | 328088562 | 99563499 | 49766296 | 0.000000 | 14432765 | 14151324 | 0.000000
09-04-2025 16:06:25000 | -1321816 | 132.1816 | 12322017 | 234371.67 | 327045074 | 99568306 | 49778603 | 0.000000 | 14606484 | 14335621 | 0.000000
09-04-2025 16:06:30000 | -1330824 | 133.0824 | 12605522 | 234333.58 | 329372406 | 99554405 | 49785023 | 0.000000 | 14780776 | 14520174 | 0.000000
09-04-2025 16:06:35000 | -1332371 | 133.2371 | 12526592 | 234279.17 | 329810272 | 99560944 | 49758022 | 0.000000 | 14955153 | 14705082 | 0.000000
09-04-2025 16:06:40000 | -1321041 | 132.1041 | 12160137 | 234441.34 | 326718536 | 99579018 | 49746235 | 0.000000 | 15125771 | 14889395 | 0.000000
09-04-2025 16:06:45000 | -1330740 | 133.074 | 12840624 | 234453.20 | 329239624 | 99537689 | 49792835 | 0.000000 | 15300405 | 15073456 | 0.000000
09-04-2025 16:06:50000 | -1327956 | 132.7956 | 12735701 | 234461.08 | 328525177 | 99543266 | 49785522 | 0.000000 | 15478138 | 15258215 | 0.000000
09-04-2025 16:06:55000 | -1323572 | 132.3572 | 12723495 | 234522.34 | 327359863 | 99541130 | 49799198 | 0.000000 | 15655175 | 15442374 | 0.000000
09-04-2025 16:07:00000 | -1329023 | 132.9023 | 12863844 | 234469.48 | 328801453 | 99534836 | 49808266 | 0.000000 | 15834136 | 15627056 | 0.000000
09-04-2025 16:07:05000 | -1332630 | 133.263 | 12909488 | 234448.64 | 329731750 | 99534065 | 49801243 | 0.000000 | 16011309 | 15811500 | 0.000000
09-04-2025 16:07:10000 | -1326873 | 132.6873 | 12556804 | 234424.28 | 328272186 | 99555199 | 49765076 | 0.000000 | 16187537 | 15996173 | 0.000000
09-04-2025 16:07:15000 | -1327214 | 132.7214 | 12644269 | 234425.55 | 328369141 | 99549255 | 49772659 | 0.000000 | 16361874 | 16180311 | 0.000000
09-04-2025 16:07:20000 | -1326728 | 132.6728 | 12783847 | 234482.16 | 328202637 | 99538979 | 49785400 | 0.000000 | 16538168 | 16364579 | 0.000000
09-04-2025 16:07:25000 | -1328764 | 132.8764 | 13072952 | 234505.38 | 328737885 | 99519508 | 49791710 | 0.000000 | 16719103 | 16549227 | 0.000000
09-04-2025 16:07:30000 | -1335014 | 133.5014 | 13256347 | 234489.02 | 330337280 | 99510620 | 49796993 | 0.000000 | 16901658 | 16733945 | 0.000000
09-04-2025 16:07:35000 | -1328982 | 132.8982 | 13007036 | 234491.75 | 328795746 | 99524467 | 49787197 | 0.000000 | 17083298 | 16918633 | 0.000000
09-04-2025 16:07:40000 | -1330803 | 133.0803 | 13091049 | 234529.27 | 329209961 | 99519653 | 49798496 | 0.000000 | 17264058 | 17103311 | 0.000000
09-04-2025 16:07:45000 | -1336620 | 133.662 | 13230957 | 234444.73 | 330793457 | 99513641 | 49794880 | 0.000000 | 17447325 | 17288254 | 0.000000
09-04-2025 16:07:50000 | -1327455 | 132.7455 | 12633080 | 234487.77 | 328335022 | 99550209 | 49773560 | 0.000000 | 17625829 | 17473160 | 0.000000
09-04-2025 16:07:55000 | -1332179 | 133.2179 | 12891123 | 234487.13 | 329557800 | 99535065 | 49778999 | 0.000000 | 17804619 | 17657969 | 0.000000
09-04-2025 16:08:00000 | -1330485 | 133.0485 | 12656143 | 234438.02 | 329156921 | 99550613 | 49767357 | 0.000000 | 17980743 | 17842586 | 0.000000
09-04-2025 16:08:05000 | -1327479 | 132.7479 | 12449654 | 234452.66 | 328352844 | 99563103 | 49757122 | 0.000000 | 18154161 | 18027125 | 0.000000
09-04-2025 16:08:10000 | -1328511 | 132.8511 | 12746549 | 234522.22 | 328572601 | 99542870 | 49788113 | 0.000000 | 18329445 | 18211643 | 0.000000
09-04-2025 16:08:15000 | -1331883 | 133.1883 | 12694462 | 234430.94 | 329516205 | 99548851 | 49788975 | 0.000000 | 18506627 | 18396371 | 0.000000
09-04-2025 16:08:20000 | -1329981 | 132.9981 | 12615130 | 234446.72 | 329012177 | 99553169 | 49783997 | 0.000000 | 18682150 | 18581168 | 0.000000
09-04-2025 16:08:25000 | -1330673 | 133.0673 | 12842604 | 234520.02 | 329128235 | 99537498 | 49802292 | 0.000000 | 18858390 | 18765895 | 0.000000
09-04-2025 16:08:30000 | -1330593 | 133.0593 | 12786044 | 234501.34 | 329126068 | 99541481 | 49814178 | 0.000000 | 19036691 | 18950834 | 0.000000
09-04-2025 16:08:35000 | -1333005 | 133.3005 | 12887080 | 234462.63 | 329793762 | 99535927 | 49808849 | 0.000000 | 19216724 | 19136293 | 0.000000
09-04-2025 16:08:40000 | -1332816 | 133.2816 | 13028095 | 234523.14 | 329698090 | 99525658 | 49839111 | 0.000000 | 19395603 | 19321041 | 0.000000
09-04-2025 16:08:45000 | -1331582 | 133.1582 | 12990786 | 234501.75 | 329416626 | 99527481 | 49830906 | 0.000000 | 19578069 | 19506428 | 0.000000
09-04-2025 16:08:50000 | -1332057 | 133.2057 | 12926944 | 234555.13 | 329439697 | 99532417 | 49828548 | 0.000000 | 19757546 | 19691824 | 0.000000
09-04-2025 16:08:55000 | -1329217 | 132.9217 | 12909388 | 234610.31 | 328666626 | 99531693 | 49838020 | 0.000000 | 19936808 | 19876891 | 0.000000
09-04-2025 16:09:00000 | -1329015 | 132.9015 | 12964314 | 234585.08 | 328663086 | 99527588 | 49851196 | 0.000000 | 20117271 | 20062104 | 0.000000
09-04-2025 16:09:05000 | -1328901 | 132.8901 | 12921720 | 234620.83 | 328579285 | 99530586 | 49874409 | 0.000000 | 20296556 | 20246711 | 0.000000
09-04-2025 16:09:10000 | -1332734 | 133.2734 | 12982870 | 234521.69 | 329675446 | 99528862 | 49850861 | 0.000000 | 20476753 | 20431900 | 0.000000
09-04-2025 16:09:15000 | -1335245 | 133.5245 | 13050959 | 234575.36 | 330223267 | 99525719 | 49840607 | 0.000000 | 20656563 | 20617154 | 0.000000
09-04-2025 16:09:20000 | -1332337 | 133.2337 | 12777964 | 234541.23 | 329494049 | 99543243 | 49839699 | 0.000000 | 20834463 | 20802125 | 0.000000
09-04-2025 16:09:25000 | -1331556 | 133.1556 | 12796057 | 234525.94 | 329327789 | 99541428 | 49841053 | 0.000000 | 21012913 | 20987078 | 0.000000
09-04-2025 16:09:30000 | -1328695 | 132.8695 | 12704820 | 234485.75 | 328665497 | 99545967 | 49830685 | 0.000000 | 21191157 | 21172205 | 0.000000
09-04-2025 16:09:35000 | -1328848 | 132.8848 | 12836545 | 234569.48 | 328621124 | 99536674 | 49855263 | 0.000000 | 21368833 | 21356973 | 0.000000
09-04-2025 16:09:40000 | -1332437 | 133.2437 | 12845015 | 234501.64 | 329586700 | 99538544 | 49842720 | 0.000000 | 21547798 | 21542146 | 0.000000
09-04-2025 16:09:45000 | -1328232 | 132.8232 | 12533771 | 234477.36 | 328521912 | 99557724 | 49809788 | 0.000000 | 21723850 | 21726998 | 0.000000
09-04-2025 16:09:50000 | -1324424 | 132.4424 | 12839148 | 234664.23 | 327401062 | 99533401 | 49838081 | 0.000000 | 21898621 | 21910941 | 0.000000
09-04-2025 16:09:55000 | -1331097 | 133.1097 | 12840780 | 234500.64 | 329260254 | 99537926 | 49837620 | 0.000000 | 22078235 | 22095811 | 0.000000
09-04-2025 16:10:00000 | -1336119 | 133.6119 | 13106892 | 234527.05 | 330516876 | 99522293 | 49852104 | 0.000000 | 22257937 | 22280596 | 0.000000
09-04-2025 16:10:05000 | -1332123 | 133.2123 | 12982113 | 234561.13 | 329459778 | 99528488 | 49860916 | 0.000000 | 22438655 | 22465471 | 0.000000
09-04-2025 16:10:10000 | -1334068 | 133.4068 | 13193739 | 234600.23 | 329935822 | 99514511 | 49885311 | 0.000000 | 22622051 | 22650418 | 0.000000
09-04-2025 16:10:15000 | -1334163 | 133.4163 | 12825066 | 234456.25 | 330072571 | 99541145 | 49846603 | 0.000000 | 22803323 | 22835791 | 0.000000
09-04-2025 16:10:20000 | -1327356 | 132.7356 | 12805761 | 234570.94 | 328243469 | 99537849 | 49836864 | 0.000000 | 22981692 | 23020631 | 0.000000
09-04-2025 16:10:25000 | -1330929 | 133.0929 | 13096386 | 234602.13 | 329134796 | 99519356 | 49867325 | 0.000000 | 23161018 | 23205092 | 0.000000
09-04-2025 16:10:30000 | -1334172 | 133.4172 | 13425553 | 234681.08 | 329919678 | 99497513 | 49905006 | 0.000000 | 23343765 | 23389791 | 0.000000
09-04-2025 16:10:35000 | -1335727 | 133.5727 | 13217371 | 234517.66 | 330461639 | 99513985 | 49884319 | 0.000000 | 23529761 | 23575564 | 0.000000
09-04-2025 16:10:40000 | -1330836 | 133.0836 | 13011451 | 234605.53 | 329093292 | 99525459 | 49882362 | 0.000000 | 23710938 | 23760727 | 0.000000
09-04-2025 16:10:45000 | -1333478 | 133.3478 | 13144126 | 234602.72 | 329770935 | 99517708 | 49911243 | 0.000000 | 23892603 | 23945877 | 0.000000
09-04-2025 16:10:50000 | -1333400 | 133.34 | 13061997 | 234536.17 | 329835876 | 99523613 | 49881023 | 0.000000 | 24076790 | 24131771 | 0.000000
09-04-2025 16:10:55000 | -1331371 | 133.1371 | 12963807 | 234582.70 | 329241547 | 99529282 | 49888874 | 0.000000 | 24257761 | 24316896 | 0.000000
09-04-2025 16:11:00000 | -1335922 | 133.5922 | 13109523 | 234555.88 | 330427155 | 99521965 | 49906330 | 0.000000 | 24438948 | 24502131 | 0.000000
09-04-2025 16:11:05000 | -1342122 | 134.2122 | 13186781 | 234500.61 | 332044769 | 99520782 | 49907738 | 0.000000 | 24621023 | 24687807 | 0.000000
09-04-2025 16:11:10000 | -1333951 | 133.3951 | 13108719 | 234635.36 | 329835938 | 99520622 | 49927200 | 0.000000 | 24802651 | 24873270 | 0.000000
09-04-2025 16:11:15000 | -1342170 | 134.217 | 13323963 | 234559.00 | 332004639 | 99510864 | 49936897 | 0.000000 | 24986855 | 25059313 | 0.000000
09-04-2025 16:11:20000 | -1340986 | 134.0986 | 13395076 | 234615.56 | 331658722 | 99504807 | 49949413 | 0.000000 | 25172664 | 25245539 | 0.000000
09-04-2025 16:11:25000 | -1342441 | 134.2441 | 13629350 | 234690.38 | 331966217 | 99488571 | 49983566 | 0.000000 | 25359980 | 25431652 | 0.000000
09-04-2025 16:11:30000 | -1346012 | 134.6012 | 13864686 | 234668.70 | 332934875 | 99473679 | 50001324 | 0.000000 | 25551887 | 25618295 | 0.000000
09-04-2025 16:11:35000 | -1341897 | 134.1897 | 13573626 | 234654.72 | 331861938 | 99492302 | 49978607 | 0.000000 | 25741462 | 25804732 | 0.000000
09-04-2025 16:11:40000 | -1336868 | 133.6868 | 13372552 | 234658.83 | 330585022 | 99503433 | 49974022 | 0.000000 | 25929429 | 25991004 | 0.000000
09-04-2025 16:11:45000 | -1341529 | 134.1529 | 13749331 | 234696.41 | 331767487 | 99478889 | 49999081 | 0.000000 | 26120017 | 26177508 | 0.000000
09-04-2025 16:11:50000 | -1346249 | 134.6249 | 14027621 | 234736.72 | 332927887 | 99461525 | 50013447 | 0.000000 | 26314341 | 26364342 | 0.000000
09-04-2025 16:11:55000 | -1346942 | 134.6942 | 13785857 | 234674.91 | 333126129 | 99480309 | 49990932 | 0.000000 | 26507725 | 26551561 | 0.000000
09-04-2025 16:12:00000 | -1347332 | 134.7332 | 13804830 | 234710.95 | 333179077 | 99479187 | 49981678 | 0.000000 | 26697800 | 26738223 | 0.000000
09-04-2025 16:12:05000 | -1341425 | 134.1425 | 13745495 | 234718.72 | 331703217 | 99479103 | 49996914 | 0.000000 | 26888530 | 26924434 | 0.000000
09-04-2025 16:12:10000 | -1343160 | 134.316 | 13904537 | 234740.17 | 332134979 | 99468437 | 49996593 | 0.000000 | 27081189 | 27111063 | 0.000000
09-04-2025 16:12:15000 | -1346011 | 134.6011 | 13699861 | 234624.89 | 332952148 | 99486015 | 49961823 | 0.000000 | 27272666 | 27297898 | 0.000000
09-04-2025 16:12:20000 | -1341149 | 134.1149 | 13685640 | 234740.48 | 331591461 | 99483383 | 49981113 | 0.000000 | 27461790 | 27483979 | 0.000000
09-04-2025 16:12:25000 | -1339858 | 133.9858 | 13388491 | 234604.20 | 331396118 | 99504463 | 49945442 | 0.000000 | 27651873 | 27670623 | 0.000000
09-04-2025 16:12:30000 | -1333944 | 133.3944 | 13325354 | 234711.73 | 329781067 | 99504761 | 49937046 | 0.000000 | 27837446 | 27856408 | 0.000000
09-04-2025 16:12:35000 | -1340339 | 134.0339 | 13735693 | 234718.94 | 331437561 | 99479004 | 49951664 | 0.000000 | 28026855 | 28042629 | 0.000000
09-04-2025 16:12:40000 | -1343950 | 134.395 | 13638156 | 234657.75 | 332382019 | 99489052 | 49957310 | 0.000000 | 28217537 | 28229260 | 0.000000
09-04-2025 16:12:45000 | -1347284 | 134.7284 | 13674896 | 234655.58 | 333213013 | 99488838 | 49939327 | 0.000000 | 28406038 | 28416064 | 0.000000
09-04-2025 16:12:50000 | -1341859 | 134.1859 | 13560563 | 234719.80 | 331768921 | 99493240 | 49942772 | 0.000000 | 28593496 | 28602547 | 0.000000
09-04-2025 16:12:55000 | -1346692 | 134.6692 | 13703488 | 234648.30 | 333081482 | 99486267 | 49961136 | 0.000000 | 28782810 | 28789240 | 0.000000
09-04-2025 16:13:00000 | -1342801 | 134.2801 | 13519398 | 234655.39 | 332072662 | 99496994 | 49948929 | 0.000000 | 28970671 | 28975832 | 0.000000
09-04-2025 16:13:05000 | -1337454 | 133.7454 | 13368102 | 234648.11 | 330740143 | 99504196 | 49943996 | 0.000000 | 29158220 | 29162377 | 0.000000
09-04-2025 16:13:10000 | -1343293 | 134.3293 | 13404474 | 234622.28 | 332215149 | 99505806 | 49939255 | 0.000000 | 29344480 | 29348885 | 0.000000
09-04-2025 16:13:15000 | -1338771 | 133.8771 | 13244016 | 234635.63 | 331047638 | 99514236 | 49936260 | 0.000000 | 29529753 | 29535209 | 0.000000
09-04-2025 16:13:20000 | -1347109 | 134.7109 | 13318352 | 234523.55 | 333267517 | 99514832 | 49939682 | 0.000000 | 29715129 | 29721824 | 0.000000
09-04-2025 16:13:25000 | -1344156 | 134.4156 | 13450170 | 234706.70 | 332318909 | 99503090 | 49938568 | 0.000000 | 29901069 | 29908387 | 0.000000
09-04-2025 16:13:30000 | -1342182 | 134.2182 | 13316903 | 234640.36 | 331893250 | 99511391 | 49931534 | 0.000000 | 30087104 | 30095010 | 0.000000
09-04-2025 16:13:35000 | -1338347 | 133.8347 | 13187759 | 234646.83 | 330910217 | 99518021 | 49938152 | 0.000000 | 30271997 | 30281408 | 0.000000
09-04-2025 16:13:40000 | -1337254 | 133.7254 | 13347980 | 234694.38 | 330614929 | 99505524 | 49950722 | 0.000000 | 30456509 | 30467492 | 0.000000
09-04-2025 16:13:45000 | -1350404 | 135.0404 | 13765386 | 234591.22 | 334088593 | 99484474 | 49959488 | 0.000000 | 30646282 | 30654291 | 0.000000
09-04-2025 16:13:50000 | -1340441 | 134.0441 | 13465589 | 234681.03 | 331445099 | 99499214 | 49955914 | 0.000000 | 30833926 | 30840598 | 0.000000
09-04-2025 16:13:55000 | -1338003 | 133.8003 | 13522039 | 234716.64 | 330810944 | 99493210 | 49957687 | 0.000000 | 31021267 | 31026574 | 0.000000
09-04-2025 16:14:00000 | -1344666 | 134.4666 | 13783347 | 234664.58 | 332587189 | 99478752 | 49968391 | 0.000000 | 31212273 | 31212883 | 0.000000
09-04-2025 16:14:05000 | -1341969 | 134.1969 | 13451695 | 234633.52 | 331890503 | 99501366 | 49934162 | 0.000000 | 31401504 | 31399625 | 0.000000
09-04-2025 16:14:10000 | -1344172 | 134.4172 | 13526334 | 234649.06 | 332423035 | 99497498 | 49934975 | 0.000000 | 31587280 | 31585902 | 0.000000
09-04-2025 16:14:15000 | -1341271 | 134.1271 | 13392484 | 234599.36 | 331749054 | 99505203 | 49939510 | 0.000000 | 31774656 | 31772191 | 0.000000
09-04-2025 16:14:20000 | -1341522 | 134.1522 | 13580714 | 234687.25 | 331731445 | 99491493 | 49943172 | 0.000000 | 31962087 | 31958619 | 0.000000
09-04-2025 16:14:25000 | -1339498 | 133.9498 | 13707191 | 234744.91 | 331183838 | 99480499 | 49978275 | 0.000000 | 32151834 | 32144465 | 0.000000
09-04-2025 16:14:30000 | -1339515 | 133.9515 | 13707102 | 234691.08 | 331266205 | 99480515 | 49966949 | 0.000000 | 32342659 | 32330680 | 0.000000
09-04-2025 16:14:35000 | -1345131 | 134.5131 | 13854501 | 234719.14 | 332635925 | 99473763 | 49957909 | 0.000000 | 32532927 | 32517004 | 0.000000
09-04-2025 16:14:40000 | -1341695 | 134.1695 | 13594154 | 234713.06 | 331739380 | 99490623 | 49947071 | 0.000000 | 32722351 | 32703266 | 0.000000
09-04-2025 16:14:45000 | -1341003 | 134.1003 | 13711901 | 234690.13 | 331630524 | 99481300 | 49955448 | 0.000000 | 32913171 | 32889688 | 0.000000
09-04-2025 16:14:50000 | -1342038 | 134.2038 | 13839262 | 234737.13 | 331854095 | 99472504 | 49964008 | 0.000000 | 33104172 | 33075891 | 0.000000
09-04-2025 16:14:55000 | -1344580 | 134.458 | 13843050 | 234703.44 | 332522278 | 99474197 | 49956524 | 0.000000 | 33297334 | 33262543 | 0.000000
09-04-2025 16:15:00000 | -1343394 | 134.3394 | 13688693 | 234710.73 | 332177521 | 99484863 | 49928303 | 0.000000 | 33487593 | 33449250 | 0.000000
09-04-2025 16:15:05000 | -1344087 | 134.4087 | 13671104 | 234674.19 | 332396240 | 99486702 | 49919594 | 0.000000 | 19062399 | 186473862 | 0.000000
09-04-2025 16:15:10000 | -1340768 | 134.0768 | 13616972 | 234681.75 | 331562927 | 99488228 | 49923664 | 0.000000 | 38086632 | 372827484 | 0.000000
09-04-2025 16:15:15000 | -1338619 | 133.8619 | 13472760 | 234662.36 | 331027557 | 99497330 | 49908031 | 0.000000 | 56841255 | 558971008 | 0.000000
09-04-2025 16:15:20000 | -1335410 | 133.541 | 13546606 | 234721.83 | 330179443 | 99489418 | 49929523 | 0.000000 | 75597359 | 744568176 | 0.000000
09-04-2025 16:15:25000 | -1342179 | 134.2179 | 13887237 | 234714.36 | 331931915 | 99468979 | 49945141 | 0.000000 | 94773842 | 930989868 | 0.000000
09-04-2025 16:15:30000 | -1345895 | 134.5895 | 13608512 | 234624.38 | 332902863 | 99492714 | 49904453 | 0.000000 | 113855202 | 11177666 | 0.000000
09-04-2025 16:15:35000 | -1339532 | 133.9532 | 13865652 | 234829.86 | 331112701 | 99468536 | 49945614 | 0.000000 | 132828262 | 13033993 | 0.000000
09-04-2025 16:15:40000 | -1342274 | 134.2274 | 14206549 | 234811.30 | 331896637 | 99444565 | 49955616 | 0.000000 | 152478287 | 14897502 | 0.000000
09-04-2025 16:15:45000 | -1337866 | 133.7866 | 14289445 | 234900.11 | 330717163 | 99434441 | 49980324 | 0.000000 | 172221741 | 16757408 | 0.000000
09-04-2025 16:15:50000 | -1340420 | 134.042 | 14547307 | 234931.52 | 331361572 | 99416237 | 50006195 | 0.000000 | 192290634 | 18616853 | 0.000000
09-04-2025 16:15:55000 | -1342171 | 134.2171 | 14648092 | 234952.97 | 331785278 | 99409721 | 50019104 | 0.000000 | 212559341 | 20478595 | 0.000000
09-04-2025 16:16:00000 | -1340555 | 134.0555 | 14614704 | 234957.19 | 331380707 | 99410980 | 50020378 | 0.000000 | 232939148 | 22340520 | 0.000000
09-04-2025 16:16:05000 | -1339810 | 133.981 | 14644012 | 234957.27 | 331202057 | 99407982 | 50015358 | 0.000000 | 253373184 | 24203562 | 0.000000
09-04-2025 16:16:10000 | -1345439 | 134.5439 | 14616684 | 234879.34 | 332683472 | 99415054 | 50010410 | 0.000000 | 273677246 | 26068855 | 0.000000
09-04-2025 16:16:15000 | -1338926 | 133.8926 | 14455338 | 234945.69 | 330956360 | 99422256 | 49997898 | 0.000000 | 293753693 | 27930584 | 0.000000
09-04-2025 16:16:20000 | -1337529 | 133.7529 | 14589412 | 234977.34 | 330603088 | 99410362 | 50015980 | 0.000000 | 314019104 | 29791470 | 0.000000
09-04-2025 16:16:25000 | -1339876 | 133.9876 | 14381752 | 234890.63 | 331246368 | 99428871 | 50007607 | 0.000000 | 334198090 | 31653506 | 0.000000
09-04-2025 16:16:30000 | -1336827 | 133.6827 | 14521657 | 234998.77 | 330383606 | 99415169 | 50029388 | 0.000000 | 354294525 | 33512773 | 0.000000
09-04-2025 16:16:35000 | -1343833 | 134.3833 | 14344700 | 234771.58 | 332368500 | 99435104 | 50021389 | 0.000000 | 374630585 | 35378706 | 0.000000
09-04-2025 16:16:40000 | -1343164 | 134.3164 | 14059574 | 234794.78 | 332103790 | 99456619 | 49982124 | 0.000000 | 394220306 | 37243184 | 0.000000
09-04-2025 16:16:45000 | -1339438 | 133.9438 | 14019613 | 234795.39 | 331181641 | 99456696 | 49977573 | 0.000000 | 413675568 | 39102109 | 0.000000
09-04-2025 16:16:50000 | -1337267 | 133.7267 | 14091566 | 234791.20 | 330670624 | 99449379 | 49990559 | 0.000000 | 433206757 | 40959490 | 0.000000
09-04-2025 16:16:55000 | -1339466 | 133.9466 | 14083376 | 234781.11 | 331223633 | 99451805 | 49999378 | 0.000000 | 452641235 | 42816323 | 0.000000
09-04-2025 16:17:00000 | -1339978 | 133.9978 | 14072130 | 234802.45 | 331314117 | 99453087 | 50005283 | 0.000000 | 472079285 | 44674932 | 0.000000
09-04-2025 16:17:05000 | -1335267 | 133.5267 | 13764474 | 234766.23 | 330135010 | 99472878 | 49979855 | 0.000000 | 491464478 | 46534517 | 0.000000
09-04-2025 16:17:10000 | -1337247 | 133.7247 | 13994636 | 234787.39 | 330650085 | 99456848 | 49992893 | 0.000000 | 510773529 | 48390537 | 0.000000
09-04-2025 16:17:15000 | -1332278 | 133.2278 | 13941220 | 234826.75 | 329364563 | 99456955 | 49997910 | 0.000000 | 530127014 | 50244263 | 0.000000
09-04-2025 16:17:20000 | -1334923 | 133.4923 | 14203238 | 234870.34 | 330014954 | 99438744 | 50034382 | 0.000000 | 549784119 | 52099321 | 0.000000
09-04-2025 16:17:25000 | -1340377 | 134.0377 | 14449426 | 234871.39 | 331415009 | 99423958 | 50056950 | 0.000000 | 569789734 | 53957891 | 0.000000
09-04-2025 16:17:30000 | -1346226 | 134.6226 | 14368571 | 234742.06 | 333004181 | 99435234 | 50020241 | 0.000000 | 589828430 | 55823696 | 0.000000
09-04-2025 16:17:35000 | -1336927 | 133.6927 | 14172431 | 234945.69 | 330396912 | 99442810 | 50055531 | 0.000000 | 609364319 | 57679204 | 0.000000
09-04-2025 16:17:40000 | -1342675 | 134.2675 | 14449576 | 234820.70 | 332045380 | 99425903 | 50073677 | 0.000000 | 629375122 | 59537495 | 0.000000
09-04-2025 16:17:45000 | -1340936 | 134.0936 | 14294006 | 234840.08 | 331559692 | 99436646 | 50042969 | 0.000000 | 649384949 | 61402778 | 0.000000
09-04-2025 16:17:50000 | -1341581 | 134.1581 | 14299813 | 234872.94 | 331669250 | 99436729 | 50044609 | 0.000000 | 669149841 | 63262476 | 0.000000
09-04-2025 16:17:55000 | -1340949 | 134.0949 | 14331401 | 234856.02 | 331547607 | 99433731 | 50035816 | 0.000000 | 689081665 | 65124019 | 0.000000
09-04-2025 16:18:00000 | -1334888 | 133.4888 | 14101299 | 234894.03 | 329948395 | 99446671 | 50027782 | 0.000000 | 708714233 | 66981807 | 0.000000
09-04-2025 16:18:05000 | -1334494 | 133.4494 | 13980538 | 234809.41 | 329939880 | 99455711 | 50022285 | 0.000000 | 728272766 | 68839043 | 0.000000
09-04-2025 16:18:10000 | -1334989 | 133.4989 | 14209305 | 234907.89 | 329977997 | 99438316 | 50044682 | 0.000000 | 747867188 | 70694175 | 0.000000
09-04-2025 16:18:15000 | -1336581 | 133.6581 | 14102210 | 234825.05 | 330462463 | 99447990 | 50048897 | 0.000000 | 767517578 | 72552158 | 0.000000
09-04-2025 16:18:20000 | -1342378 | 134.2378 | 14355573 | 234816.94 | 331957458 | 99433037 | 50049839 | 0.000000 | 787336182 | 74410225 | 0.000000
09-04-2025 16:18:25000 | -1338963 | 133.8963 | 13800647 | 234732.64 | 331092102 | 99473030 | 50001102 | 0.000000 | 806810364 | 76271411 | 0.000000
09-04-2025 16:18:30000 | -1332788 | 133.2788 | 13941824 | 234880.17 | 329416138 | 99457321 | 50024643 | 0.000000 | 826052185 | 78122397 | 0.000000
09-04-2025 16:18:35000 | -1330859 | 133.0859 | 13964568 | 234860.11 | 328976349 | 99454002 | 50037270 | 0.000000 | 845526855 | 79972998 | 0.000000
09-04-2025 16:18:40000 | -1330373 | 133.0373 | 13997218 | 234817.05 | 328924835 | 99451065 | 50014809 | 0.000000 | 865052979 | 81824976 | 0.000000
09-04-2025 16:18:45000 | -1328901 | 132.8901 | 13704938 | 234799.52 | 328516022 | 99472420 | 50018227 | 0.000000 | 884177673 | 83671699 | 0.000000
09-04-2025 16:18:50000 | -1336413 | 133.6413 | 14076209 | 234811.89 | 330431000 | 99449867 | 50032841 | 0.000000 | 903514954 | 85522598 | 0.000000
09-04-2025 16:18:55000 | -1336456 | 133.6456 | 14086565 | 234810.88 | 330442993 | 99449104 | 50030388 | 0.000000 | 922957764 | 87374727 | 0.000000
09-04-2025 16:19:00000 | -1334228 | 133.4228 | 14052928 | 234814.34 | 329887756 | 99449890 | 50023594 | 0.000000 | 942505615 | 89227412 | 0.000000
09-04-2025 16:19:05000 | -1329063 | 132.9063 | 13828507 | 234821.84 | 328553864 | 99463066 | 50000542 | 0.000000 | 961863037 | 91077842 | 0.000000
09-04-2025 16:19:10000 | -1333013 | 133.3013 | 13881340 | 234764.33 | 329618591 | 99462166 | 49993534 | 0.000000 | 981072388 | 92925059 | 0.000000
09-04-2025 16:19:15000 | -1330549 | 133.0549 | 13973205 | 234843.69 | 328922729 | 99453079 | 50005890 | 0.000000 | 10004823 | 94774150 | 0.000000
09-04-2025 16:19:20000 | -1336461 | 133.6461 | 13938761 | 234738.80 | 330515503 | 99460510 | 49992287 | 0.000000 | 10198883 | 96628096 | 0.000000
09-04-2025 16:19:25000 | -1334807 | 133.4807 | 13771894 | 234754.91 | 330038208 | 99471954 | 49979065 | 0.000000 | 10390906 | 98481318 | 0.000000
09-04-2025 16:19:30000 | -1328095 | 132.8095 | 13508510 | 234849.20 | 328201782 | 99486702 | 49967403 | 0.000000 | 10578645 | 10033027 | 0.000000
09-04-2025 16:19:35000 | -1338147 | 133.8147 | 13740019 | 234610.98 | 331052673 | 99476982 | 49952869 | 0.000000 | 10770525 | 10218324 | 0.000000
09-04-2025 16:19:40000 | -1329791 | 132.9791 | 13211080 | 234668.86 | 328798157 | 99510132 | 49919815 | 0.000000 | 10955013 | 10403056 | 0.000000
09-04-2025 16:19:45000 | -1328758 | 132.8758 | 13600440 | 234812.44 | 328439667 | 99480255 | 49981426 | 0.000000 | 11140358 | 10587313 | 0.000000
09-04-2025 16:19:50000 | -1333784 | 133.3784 | 14004390 | 234790.14 | 329799591 | 99453293 | 50014084 | 0.000000 | 11332343 | 10772239 | 0.000000
09-04-2025 16:19:55000 | -1336675 | 133.6675 | 13979407 | 234775.06 | 330525055 | 99457558 | 50006218 | 0.000000 | 11526301 | 10957755 | 0.000000
09-04-2025 16:20:00000 | -1334551 | 133.4551 | 14024659 | 234837.56 | 329921082 | 99452347 | 50011070 | 0.000000 | 11720671 | 11143262 | 0.000000
09-04-2025 16:20:05000 | -1337694 | 133.7694 | 13809316 | 234731.19 | 330786163 | 99471375 | 49993073 | 0.000000 | 11914099 | 11328855 | 0.000000
09-04-2025 16:20:10000 | -1336208 | 133.6208 | 13532840 | 234658.30 | 330458832 | 99491051 | 49955189 | 0.000000 | 12104233 | 11514497 | 0.000000
09-04-2025 16:20:15000 | -1327514 | 132.7514 | 13240113 | 234713.25 | 328185516 | 99506317 | 49939026 | 0.000000 | 12289242 | 11699361 | 0.000000
09-04-2025 16:20:20000 | -1328880 | 132.888 | 13696003 | 234813.70 | 328489807 | 99473083 | 49979935 | 0.000000 | 12475664 | 11883585 | 0.000000
09-04-2025 16:20:25000 | -1338180 | 133.818 | 14013472 | 234714.94 | 330986328 | 99456154 | 50004646 | 0.000000 | 12667985 | 12068399 | 0.000000
09-04-2025 16:20:30000 | -1336649 | 133.6649 | 13764461 | 234696.83 | 330573730 | 99473961 | 49969139 | 0.000000 | 12860947 | 12254129 | 0.000000
09-04-2025 16:20:35000 | -1337026 | 133.7026 | 13604949 | 234723.44 | 330584381 | 99486282 | 49976082 | 0.000000 | 13048939 | 12439301 | 0.000000
09-04-2025 16:20:40000 | -1331750 | 133.175 | 13693865 | 234798.28 | 329211975 | 99475494 | 49994919 | 0.000000 | 13238228 | 12624309 | 0.000000
09-04-2025 16:20:45000 | -1329599 | 132.9599 | 13640224 | 234729.64 | 328771118 | 99477890 | 49986320 | 0.000000 | 13429243 | 12809273 | 0.000000
09-04-2025 16:20:50000 | -1332686 | 133.2686 | 13497698 | 234658.09 | 329591431 | 99491013 | 49965816 | 0.000000 | 13617964 | 12994138 | 0.000000
09-04-2025 16:20:55000 | -1329903 | 132.9903 | 13553767 | 234730.88 | 328820099 | 99484673 | 49968159 | 0.000000 | 13805547 | 13178792 | 0.000000
09-04-2025 16:21:00000 | -1334188 | 133.4188 | 13960863 | 234843.86 | 329819397 | 99456985 | 49996101 | 0.000000 | 13997007 | 13363811 | 0.000000
09-04-2025 16:21:05000 | -1333049 | 133.3049 | 14099050 | 234856.42 | 329555176 | 99445335 | 50016808 | 0.000000 | 14191851 | 13548954 | 0.000000
09-04-2025 16:21:10000 | -1334076 | 133.4076 | 13565566 | 234629.38 | 329989380 | 99486984 | 49959312 | 0.000000 | 14385604 | 13734922 | 0.000000
09-04-2025 16:21:15000 | -1333277 | 133.3277 | 13378200 | 234681.61 | 329669525 | 99500359 | 49931908 | 0.000000 | 14572388 | 13920165 | 0.000000
09-04-2025 16:21:20000 | -1328420 | 132.842 | 13334562 | 234743.92 | 328379211 | 99499977 | 49951744 | 0.000000 | 14756031 | 14104528 | 0.000000
09-04-2025 16:21:25000 | -1335943 | 133.5943 | 13426324 | 234626.23 | 330416718 | 99498772 | 49939487 | 0.000000 | 14942715 | 14289518 | 0.000000
09-04-2025 16:21:30000 | -1333315 | 133.3315 | 13453951 | 234696.50 | 329682953 | 99494751 | 49941853 | 0.000000 | 15127761 | 14474318 | 0.000000
09-04-2025 16:21:35000 | -1325523 | 132.5523 | 13480539 | 234789.94 | 327648254 | 99486832 | 49962414 | 0.000000 | 15314543 | 14658825 | 0.000000
09-04-2025 16:21:40000 | -1329941 | 132.9941 | 13623823 | 234713.98 | 328869080 | 99479401 | 49977760 | 0.000000 | 15504176 | 14843715 | 0.000000
09-04-2025 16:21:45000 | -1335733 | 133.5733 | 13607704 | 234661.17 | 330356476 | 99485085 | 49955429 | 0.000000 | 15693431 | 15029061 | 0.000000
09-04-2025 16:21:50000 | -1329865 | 132.9865 | 13305622 | 234706.00 | 328781982 | 99503204 | 49934509 | 0.000000 | 15880083 | 15214187 | 0.000000
09-04-2025 16:21:55000 | -1329823 | 132.9823 | 13266390 | 234681.47 | 328799530 | 99506073 | 49940643 | 0.000000 | 16064635 | 15398972 | 0.000000
09-04-2025 16:22:00000 | -1330925 | 133.0925 | 13318994 | 234673.50 | 329098328 | 99502998 | 49947746 | 0.000000 | 16249387 | 15583977 | 0.000000
09-04-2025 16:22:05000 | -1329367 | 132.9367 | 13528564 | 234702.77 | 328721619 | 99486160 | 49973816 | 0.000000 | 16436477 | 15768705 | 0.000000
09-04-2025 16:22:10000 | -1339068 | 133.9068 | 13641238 | 234644.09 | 331206055 | 99485115 | 49966911 | 0.000000 | 16625060 | 15954172 | 0.000000
09-04-2025 16:22:15000 | -1332983 | 133.2983 | 13543740 | 234765.44 | 329521637 | 99487785 | 49981972 | 0.000000 | 16811401 | 16139150 | 0.000000
09-04-2025 16:22:20000 | -1339529 | 133.9529 | 13866017 | 234725.94 | 331267517 | 99468506 | 49999950 | 0.000000 | 17002043 | 16324584 | 0.000000
09-04-2025 16:22:25000 | -1336280 | 133.628 | 13618579 | 234695.81 | 330440125 | 99484688 | 49983738 | 0.000000 | 17192216 | 16510137 | 0.000000
09-04-2025 16:22:30000 | -1333890 | 133.389 | 13465565 | 234667.63 | 329862640 | 99494324 | 49974392 | 0.000000 | 17380945 | 16695500 | 0.000000
09-04-2025 16:22:35000 | -1327029 | 132.7029 | 13279463 | 234724.28 | 328054779 | 99503036 | 49973297 | 0.000000 | 17567327 | 16880473 | 0.000000
09-04-2025 16:22:40000 | -1335069 | 133.5069 | 13556096 | 234716.97 | 330103210 | 99488449 | 49985992 | 0.000000 | 17754303 | 17065664 | 0.000000
09-04-2025 16:22:45000 | -1336849 | 133.6849 | 13523371 | 234681.94 | 330582336 | 99492241 | 49996811 | 0.000000 | 17942537 | 17251262 | 0.000000
09-04-2025 16:22:50000 | -1335131 | 133.5131 | 13641670 | 234741.61 | 330101257 | 99482071 | 50009758 | 0.000000 | 18131700 | 17436715 | 0.000000
09-04-2025 16:22:55000 | -1340505 | 134.0505 | 13456016 | 234584.47 | 331599060 | 99499969 | 49989727 | 0.000000 | 18319364 | 17622352 | 0.000000
09-04-2025 16:23:00000 | -1335345 | 133.5345 | 13481242 | 234738.11 | 330122925 | 99494247 | 49981106 | 0.000000 | 18506027 | 17808002 | 0.000000
09-04-2025 16:23:05000 | -1337075 | 133.7075 | 13707540 | 234764.89 | 330562836 | 99478600 | 50012119 | 0.000000 | 18695286 | 17993619 | 0.000000
09-04-2025 16:23:10000 | -1337940 | 133.794 | 14072944 | 234805.67 | 330811798 | 99451370 | 50047928 | 0.000000 | 18889338 | 18179359 | 0.000000
09-04-2025 16:23:15000 | -1337967 | 133.7967 | 13927299 | 234785.11 | 330810150 | 99462593 | 50040199 | 0.000000 | 19084584 | 18365701 | 0.000000
09-04-2025 16:23:20000 | -1342951 | 134.2951 | 13854953 | 234741.70 | 332071899 | 99472031 | 50026684 | 0.000000 | 19277014 | 18551988 | 0.000000
09-04-2025 16:23:25000 | -1340610 | 134.061 | 13751808 | 234746.97 | 331462585 | 99477997 | 50007065 | 0.000000 | 19467771 | 18737973 | 0.000000
09-04-2025 16:23:30000 | -1335946 | 133.5946 | 13642791 | 234722.13 | 330332977 | 99482613 | 49985477 | 0.000000 | 19659644 | 18924064 | 0.000000
09-04-2025 16:23:35000 | -1331549 | 133.1549 | 13548847 | 234773.11 | 329161285 | 99486305 | 50000553 | 0.000000 | 19848795 | 19109656 | 0.000000
09-04-2025 16:23:40000 | -1330366 | 133.0366 | 13748824 | 234863.33 | 328797668 | 99470215 | 50048153 | 0.000000 | 20038959 | 19294668 | 0.000000
09-04-2025 16:23:45000 | -1341903 | 134.1903 | 14171865 | 234812.30 | 331795746 | 99446945 | 50051624 | 0.000000 | 20234832 | 19480691 | 0.000000
09-04-2025 16:23:50000 | -1341620 | 134.162 | 13996557 | 234770.52 | 331742157 | 99460213 | 50040981 | 0.000000 | 20429431 | 19666895 | 0.000000
09-04-2025 16:23:55000 | -1337514 | 133.7514 | 13731429 | 234681.38 | 330801453 | 99477135 | 50004032 | 0.000000 | 20623398 | 19853232 | 0.000000
09-04-2025 16:24:00000 | -1333794 | 133.3794 | 13628904 | 234798.53 | 329691711 | 99482002 | 49995876 | 0.000000 | 20812112 | 20038832 | 0.000000
09-04-2025 16:24:05000 | -1337339 | 133.7339 | 13954035 | 234832.48 | 330593475 | 99460045 | 50033398 | 0.000000 | 21004226 | 20224293 | 0.000000
09-04-2025 16:24:10000 | -1331365 | 133.1365 | 13752100 | 234797.08 | 329141479 | 99470757 | 50034061 | 0.000000 | 21196934 | 20409842 | 0.000000
09-04-2025 16:24:15000 | -1341441 | 134.1441 | 13642727 | 234643.14 | 331792297 | 99486809 | 49991009 | 0.000000 | 21387373 | 20595906 | 0.000000
09-04-2025 16:24:20000 | -1335316 | 133.5316 | 13118701 | 234584.31 | 330241577 | 99520866 | 49934803 | 0.000000 | 21571091 | 20781615 | 0.000000
09-04-2025 16:24:25000 | -1331230 | 133.123 | 13251111 | 234719.83 | 329081024 | 99508240 | 49961460 | 0.000000 | 21752764 | 20966707 | 0.000000
09-04-2025 16:24:30000 | -1336886 | 133.6886 | 13626861 | 234688.34 | 330604248 | 99484528 | 49997200 | 0.000000 | 21940684 | 21151998 | 0.000000
09-04-2025 16:24:35000 | -1334364 | 133.4364 | 13355526 | 234662.48 | 329954102 | 99502838 | 49979946 | 0.000000 | 22128118 | 21337713 | 0.000000
09-04-2025 16:24:40000 | -1334575 | 133.4575 | 13393060 | 234655.06 | 330025391 | 99500221 | 49981880 | 0.000000 | 22314163 | 21522990 | 0.000000
09-04-2025 16:24:45000 | -1337511 | 133.7511 | 13545446 | 234720.27 | 330690399 | 99491096 | 49983543 | 0.000000 | 22499609 | 21708246 | 0.000000
09-04-2025 16:24:50000 | -1331934 | 133.1934 | 13492193 | 234717.78 | 329315552 | 99490852 | 49994560 | 0.000000 | 22688193 | 21893682 | 0.000000
09-04-2025 16:24:55000 | -1333896 | 133.3896 | 13509999 | 234711.73 | 329813141 | 99491005 | 50013687 | 0.000000 | 22876238 | 22079242 | 0.000000
09-04-2025 16:25:00000 | -1337503 | 133.7503 | 13804878 | 234749.67 | 330716705 | 99471565 | 50037197 | 0.000000 | 23065752 | 22264775 | 0.000000
09-04-2025 16:25:05000 | -1341402 | 134.1402 | 13929415 | 234707.41 | 331757965 | 99465164 | 50038445 | 0.000000 | 23259583 | 22450680 | 0.000000
09-04-2025 16:25:10000 | -1336586 | 133.6586 | 13591687 | 234684.64 | 330528656 | 99486938 | 50008732 | 0.000000 | 23450842 | 22636498 | 0.000000
09-04-2025 16:25:15000 | -1338637 | 133.8637 | 13688521 | 234708.05 | 331020874 | 99481239 | 49990543 | 0.000000 | 23639292 | 22821951 | 0.000000
09-04-2025 16:25:20000 | -1335808 | 133.5808 | 13684884 | 234762.14 | 330247955 | 99479332 | 50001942 | 0.000000 | 23829636 | 23007512 | 0.000000
09-04-2025 16:25:25000 | -1336967 | 133.6967 | 13800146 | 234760.20 | 330564087 | 99471504 | 50011448 | 0.000000 | 24020696 | 23193170 | 0.000000
09-04-2025 16:25:30000 | -1338196 | 133.8196 | 13662426 | 234714.83 | 330894501 | 99482864 | 50020309 | 0.000000 | 24211130 | 23378727 | 0.000000
09-04-2025 16:25:35000 | -1334701 | 133.4701 | 13661876 | 234746.33 | 329994690 | 99480209 | 50025848 | 0.000000 | 24401323 | 23564396 | 0.000000
09-04-2025 16:25:40000 | -1336792 | 133.6792 | 13523152 | 234661.20 | 330591858 | 99492210 | 49976559 | 0.000000 | 24591086 | 23750520 | 0.000000
09-04-2025 16:25:45000 | -1336131 | 133.6131 | 13629247 | 234786.50 | 330280670 | 99483772 | 49984303 | 0.000000 | 24778481 | 23935846 | 0.000000
09-04-2025 16:25:50000 | -1336220 | 133.622 | 13958445 | 234843.50 | 330306061 | 99458809 | 50028149 | 0.000000 | 24971096 | 24121459 | 0.000000
09-04-2025 16:25:55000 | -1341470 | 134.147 | 14089051 | 234760.69 | 331739929 | 99452988 | 50036507 | 0.000000 | 25165999 | 24307545 | 0.000000
09-04-2025 16:26:00000 | -1341981 | 134.1981 | 13752486 | 234691.98 | 331878418 | 99479004 | 49994247 | 0.000000 | 25359597 | 24494053 | 0.000000
09-04-2025 16:26:05000 | -1339883 | 133.9883 | 13538754 | 234665.34 | 331346985 | 99493378 | 49977116 | 0.000000 | 25549099 | 24680354 | 0.000000
09-04-2025 16:26:10000 | -1336104 | 133.6104 | 13701117 | 234826.80 | 330237091 | 99478333 | 49991001 | 0.000000 | 25738025 | 24866029 | 0.000000
09-04-2025 16:26:15000 | -1332479 | 133.2479 | 13797266 | 234826.00 | 329377899 | 99468185 | 50021740 | 0.000000 | 25929001 | 25051311 | 0.000000
09-04-2025 16:26:20000 | -1336830 | 133.683 | 14369153 | 234922.41 | 330461761 | 99427284 | 50069500 | 0.000000 | 26125403 | 25236922 | 0.000000
09-04-2025 16:26:25000 | -1339744 | 133.9744 | 14212388 | 234787.20 | 331313385 | 99442024 | 50045570 | 0.000000 | 26324788 | 25423111 | 0.000000
09-04-2025 16:26:30000 | -1336273 | 133.6273 | 14001605 | 234839.73 | 330337921 | 99455528 | 50025856 | 0.000000 | 26520183 | 25609234 | 0.000000
09-04-2025 16:26:35000 | -1341646 | 134.1646 | 14016262 | 234738.95 | 331801331 | 99458717 | 49996326 | 0.000000 | 26716541 | 25795707 | 0.000000
09-04-2025 16:26:40000 | -1334966 | 133.4966 | 13780997 | 234853.47 | 329942871 | 99471390 | 50006535 | 0.000000 | 26908706 | 25981430 | 0.000000
09-04-2025 16:26:45000 | -1340589 | 134.0589 | 14041659 | 234784.47 | 331479004 | 99455925 | 50025879 | 0.000000 | 27102002 | 26166934 | 0.000000
09-04-2025 16:26:50000 | -1343024 | 134.3024 | 14017148 | 234751.83 | 332115906 | 99459755 | 50019444 | 0.000000 | 27297144 | 26353127 | 0.000000
09-04-2025 16:26:55000 | -1339243 | 133.9243 | 13997413 | 234848.08 | 331050781 | 99458244 | 50031773 | 0.000000 | 27489482 | 26538729 | 0.000000
09-04-2025 16:27:00000 | -1331698 | 133.1698 | 14187275 | 234965.59 | 329089752 | 99437302 | 50036324 | 0.000000 | 27685881 | 26724707 | 0.000000
09-04-2025 16:27:05000 | -1339933 | 133.9933 | 14765696 | 234973.45 | 331249298 | 99398300 | 50104824 | 0.000000 | 27888701 | 26910477 | 0.000000
09-04-2025 16:27:10000 | -1344363 | 134.4363 | 14699134 | 234927.39 | 332372498 | 99407555 | 50097740 | 0.000000 | 28094666 | 27097236 | 0.000000
09-04-2025 16:27:15000 | -1346102 | 134.6102 | 14801274 | 234947.03 | 332798492 | 99400902 | 50107361 | 0.000000 | 28299614 | 27283988 | 0.000000
09-04-2025 16:27:20000 | -1348767 | 134.8767 | 14844162 | 234948.50 | 333461182 | 99399818 | 50091061 | 0.000000 | 28504773 | 27471021 | 0.000000
09-04-2025 16:27:25000 | -1342579 | 134.2579 | 14597130 | 234959.41 | 331864380 | 99414139 | 50088017 | 0.000000 | 28709343 | 27657854 | 0.000000
09-04-2025 16:27:30000 | -1341702 | 134.1702 | 14687583 | 234995.59 | 331627869 | 99406151 | 50114025 | 0.000000 | 28913779 | 27844781 | 0.000000
09-04-2025 16:27:35000 | -1345066 | 134.5066 | 14840564 | 235007.52 | 332466248 | 99396828 | 50150696 | 0.000000 | 29118528 | 28031258 | 0.000000
09-04-2025 16:27:40000 | -1349170 | 134.917 | 15050198 | 235013.92 | 333524414 | 99383560 | 50179226 | 0.000000 | 29327114 | 28218254 | 0.000000
09-04-2025 16:27:45000 | -1353465 | 135.3465 | 15086830 | 234970.45 | 334639252 | 99384476 | 50169235 | 0.000000 | 29536570 | 28405998 | 0.000000
09-04-2025 16:27:50000 | -1346972 | 134.6972 | 15020085 | 235036.25 | 332942352 | 99384018 | 50157757 | 0.000000 | 29744334 | 28593334 | 0.000000
09-04-2025 16:27:55000 | -1345612 | 134.5612 | 15167745 | 235093.70 | 332569183 | 99370697 | 50170910 | 0.000000 | 29954158 | 28780400 | 0.000000
09-04-2025 16:28:00000 | -1350301 | 135.0301 | 15322379 | 235073.25 | 333787354 | 99362335 | 50163773 | 0.000000 | 30165420 | 28967488 | 0.000000
09-04-2025 16:28:05000 | -1351980 | 135.198 | 15211404 | 235006.55 | 334264465 | 99373001 | 50132633 | 0.000000 | 30377534 | 29155135 | 0.000000
09-04-2025 16:28:10000 | -1345640 | 134.564 | 14779709 | 234970.00 | 332648102 | 99402229 | 50109924 | 0.000000 | 30584895 | 29342365 | 0.000000
09-04-2025 16:28:15000 | -1345751 | 134.5751 | 14831095 | 235016.97 | 332625305 | 99398201 | 50110584 | 0.000000 | 30789617 | 29528977 | 0.000000
09-04-2025 16:28:20000 | -1346578 | 134.6578 | 14727411 | 234934.33 | 332914673 | 99407234 | 50107967 | 0.000000 | 30994468 | 29715637 | 0.000000
09-04-2025 16:28:25000 | -1340697 | 134.0697 | 14610764 | 234963.56 | 331403290 | 99411415 | 50105373 | 0.000000 | 31197737 | 29902260 | 0.000000
09-04-2025 16:28:30000 | -1343662 | 134.3662 | 14916054 | 235038.39 | 332105927 | 99389473 | 50128986 | 0.000000 | 31402830 | 30088641 | 0.000000
09-04-2025 16:28:35000 | -1345171 | 134.5171 | 15018539 | 235046.44 | 332491821 | 99382507 | 50135323 | 0.000000 | 31610193 | 30275266 | 0.000000
09-04-2025 16:28:40000 | -1348108 | 134.8108 | 14881942 | 234926.72 | 333337830 | 99396202 | 50106434 | 0.000000 | 31817788 | 30462219 | 0.000000
09-04-2025 16:28:45000 | -1344519 | 134.4519 | 14638945 | 234939.78 | 332374237 | 99412491 | 50075336 | 0.000000 | 32020752 | 30648840 | 0.000000
09-04-2025 16:28:50000 | -1333059 | 133.3059 | 14312482 | 234984.09 | 329428375 | 99428566 | 50075073 | 0.000000 | 32221851 | 30834824 | 0.000000
09-04-2025 16:28:55000 | -1337509 | 133.7509 | 14740801 | 235028.16 | 330571228 | 99398155 | 50114754 | 0.000000 | 32424707 | 31020396 | 0.000000
09-04-2025 16:29:00000 | -1339454 | 133.9454 | 14992801 | 235013.47 | 331135986 | 99379387 | 50130970 | 0.000000 | 32633152 | 31206678 | 0.000000
09-04-2025 16:29:05000 | -1342937 | 134.2937 | 14967933 | 235020.06 | 331967499 | 99384598 | 50134415 | 0.000000 | 32842393 | 31393422 | 0.000000
09-04-2025 16:29:10000 | -1340419 | 134.0419 | 15090680 | 235121.06 | 331248749 | 99372231 | 50150867 | 0.000000 | 33050164 | 31579734 | 0.000000
09-04-2025 16:29:15000 | -1348369 | 134.8369 | 15187218 | 235008.66 | 333368195 | 99371651 | 50153042 | 0.000000 | 33261448 | 31766422 | 0.000000
09-04-2025 16:29:20000 | -1343709 | 134.3709 | 14886731 | 234994.28 | 332171539 | 99391891 | 50107681 | 0.000000 | 33469829 | 31953340 | 0.000000
09-04-2025 16:29:25000 | -1341189 | 134.1189 | 14869792 | 235064.97 | 331454895 | 99390999 | 50120255 | 0.000000 | 33675762 | 32139631 | 0.000000
09-04-2025 16:29:30000 | -1342920 | 134.292 | 15132472 | 235067.97 | 331942352 | 99371109 | 50145199 | 0.000000 | 33884800 | 32326057 | 0.000000
09-04-2025 16:29:35000 | -1344016 | 134.4016 | 15023816 | 234985.58 | 332298767 | 99381020 | 50127468 | 0.000000 | 34095037 | 32512969 | 0.000000
09-04-2025 16:29:40000 | -1347341 | 134.7341 | 14829875 | 234947.38 | 333111633 | 99399704 | 50114494 | 0.000000 | 34302500 | 32699820 | 0.000000
09-04-2025 16:29:45000 | -1340547 | 134.0547 | 14645726 | 235017.98 | 331301880 | 99408493 | 50100880 | 0.000000 | 34506187 | 32886301 | 0.000000
09-04-2025 16:29:50000 | -1344397 | 134.4397 | 15043665 | 235062.31 | 332289307 | 99379753 | 50129780 | 0.000000 | 34713792 | 33072980 | 0.000000
09-04-2025 16:29:55000 | -1345356 | 134.5356 | 14944550 | 235007.09 | 332576874 | 99388687 | 50131592 | 0.000000 | 34922390 | 33259813 | 0.000000
09-04-2025 16:30:00000 | -1342614 | 134.2614 | 15042752 | 235047.55 | 331880554 | 99378189 | 50136116 | 0.000000 | 35131499 | 33446551 | 0.000000
09-04-2025 16:30:05000 | -1350148 | 135.0148 | 15095475 | 235012.25 | 333774994 | 99380768 | 50124100 | 0.000000 | 20911415 | 186972107 | 0.000000
09-04-2025 16:30:10000 | -1348009 | 134.8009 | 14972421 | 234983.11 | 333256897 | 99388817 | 50107037 | 0.000000 | 41705032 | 374067139 | 0.000000
09-04-2025 16:30:15000 | -1346983 | 134.6983 | 14797613 | 234978.31 | 332965912 | 99401978 | 50081303 | 0.000000 | 62405647 | 561409668 | 0.000000
09-04-2025 16:30:20000 | -1345858 | 134.5858 | 14869852 | 235011.00 | 332664795 | 99395172 | 50089157 | 0.000000 | 83000160 | 748278198 | 0.000000
09-04-2025 16:30:25000 | -1344238 | 134.4238 | 14646121 | 234941.92 | 332313293 | 99411674 | 50071869 | 0.000000 | 103573677 | 935477722 | 0.000000
09-04-2025 16:30:30000 | -1344393 | 134.4393 | 14639358 | 234917.58 | 332379700 | 99412346 | 50065506 | 0.000000 | 124093262 | 11226146 | 0.000000
09-04-2025 16:30:35000 | -1350463 | 135.0463 | 14518426 | 234830.61 | 333958130 | 99427071 | 50031166 | 0.000000 | 144346909 | 13099388 | 0.000000
09-04-2025 16:30:40000 | -1344188 | 134.4188 | 14311714 | 234894.09 | 332276093 | 99437973 | 50027130 | 0.000000 | 164245682 | 14967209 | 0.000000
09-04-2025 16:30:45000 | -1341612 | 134.1612 | 14355355 | 234957.84 | 331576965 | 99432411 | 50050217 | 0.000000 | 184158112 | 16831846 | 0.000000
09-04-2025 16:30:50000 | -1347176 | 134.7176 | 14764139 | 234982.84 | 333012482 | 99404823 | 50089211 | 0.000000 | 204408493 | 18695170 | 0.000000
09-04-2025 16:30:55000 | -1352798 | 135.2798 | 14783390 | 234813.05 | 334624847 | 99408188 | 50062668 | 0.000000 | 225061813 | 20569695 | 0.000000
09-04-2025 16:31:00000 | -1345732 | 134.5732 | 14190172 | 234860.75 | 332670441 | 99448654 | 50015701 | 0.000000 | 244967804 | 22441292 | 0.000000
09-04-2025 16:31:05000 | -1344262 | 134.4262 | 14302251 | 234871.53 | 332322510 | 99438766 | 50034435 | 0.000000 | 264779541 | 24308401 | 0.000000
09-04-2025 16:31:10000 | -1346815 | 134.6815 | 14207235 | 234814.44 | 333005066 | 99448219 | 50021931 | 0.000000 | 284661987 | 26180820 | 0.000000
09-04-2025 16:31:15000 | -1345844 | 134.5844 | 14312971 | 234866.39 | 332721558 | 99439240 | 50025459 | 0.000000 | 304379120 | 28047886 | 0.000000
09-04-2025 16:31:20000 | -1344719 | 134.4719 | 14459339 | 234955.98 | 332355530 | 99426865 | 50063236 | 0.000000 | 324316223 | 29914104 | 0.000000
09-04-2025 16:31:25000 | -1346651 | 134.6651 | 14647677 | 234931.59 | 332915588 | 99413643 | 50069733 | 0.000000 | 344616272 | 31785144 | 0.000000
09-04-2025 16:31:30000 | -1346904 | 134.6904 | 14848323 | 234966.31 | 332976654 | 99397835 | 50089386 | 0.000000 | 365062988 | 33653621 | 0.000000
09-04-2025 16:31:35000 | -1345365 | 134.5365 | 14603797 | 234904.89 | 332626709 | 99416008 | 50074448 | 0.000000 | 385503113 | 35523489 | 0.000000
09-04-2025 16:31:40000 | -1349699 | 134.9699 | 14681710 | 234891.19 | 333728363 | 99413574 | 50053974 | 0.000000 | 405904663 | 37395593 | 0.000000
09-04-2025 16:31:45000 | -1348325 | 134.8325 | 14634633 | 234940.56 | 333309814 | 99416115 | 50040489 | 0.000000 | 426248962 | 39268389 | 0.000000
09-04-2025 16:31:50000 | -1347413 | 134.7413 | 14997585 | 235044.23 | 333035217 | 99386238 | 50085388 | 0.000000 | 446858948 | 41137188 | 0.000000
09-04-2025 16:31:55000 | -1351728 | 135.1728 | 14925899 | 234939.13 | 334225403 | 99395882 | 50070755 | 0.000000 | 467751617 | 43014375 | 0.000000
09-04-2025 16:32:00000 | -1347466 | 134.7466 | 14581772 | 234900.59 | 333151825 | 99419556 | 50057823 | 0.000000 | 488144226 | 44885679 | 0.000000
09-04-2025 16:32:05000 | -1346043 | 134.6043 | 14732695 | 234976.59 | 332722595 | 99406342 | 50069386 | 0.000000 | 508521851 | 46755947 | 0.000000
09-04-2025 16:32:10000 | -1350813 | 135.0813 | 14830122 | 234938.33 | 333967255 | 99402740 | 50068695 | 0.000000 | 529129639 | 48629399 | 0.000000
09-04-2025 16:32:15000 | -1349101 | 134.9101 | 14643326 | 234890.89 | 333567535 | 99416092 | 50045689 | 0.000000 | 549580566 | 50504600 | 0.000000
09-04-2025 16:32:20000 | -1346974 | 134.6974 | 14395383 | 234890.14 | 332984222 | 99433762 | 50029011 | 0.000000 | 569624084 | 52375396 | 0.000000
09-04-2025 16:32:25000 | -1349131 | 134.9131 | 14478114 | 234878.20 | 333551849 | 99429108 | 50039230 | 0.000000 | 589739929 | 54247095 | 0.000000
09-04-2025 16:32:30000 | -1350411 | 135.0411 | 14237457 | 234749.69 | 333984894 | 99448814 | 50015270 | 0.000000 | 609825928 | 56123291 | 0.000000
09-04-2025 16:32:35000 | -1346914 | 134.6914 | 14107325 | 234814.92 | 333000183 | 99455971 | 49995483 | 0.000000 | 629462463 | 57996553 | 0.000000
09-04-2025 16:32:40000 | -1347474 | 134.7474 | 14404552 | 234896.03 | 333105042 | 99433464 | 50010612 | 0.000000 | 649281799 | 59866606 | 0.000000
09-04-2025 16:32:45000 | -1351671 | 135.1671 | 14647621 | 234913.39 | 334164398 | 99417953 | 50042831 | 0.000000 | 669426758 | 61738042 | 0.000000
09-04-2025 16:32:50000 | -1349211 | 134.9211 | 14850555 | 234983.27 | 333518066 | 99399696 | 50059864 | 0.000000 | 689882080 | 63611768 | 0.000000
09-04-2025 16:32:55000 | -1349123 | 134.9123 | 14981476 | 234985.34 | 333532928 | 99389084 | 50083618 | 0.000000 | 710600281 | 65485200 | 0.000000
09-04-2025 16:33:00000 | -1350418 | 135.0418 | 14904936 | 234968.50 | 333849976 | 99396400 | 50082451 | 0.000000 | 731369080 | 67361426 | 0.000000
09-04-2025 16:33:05000 | -1351798 | 135.1798 | 14687877 | 234897.83 | 334230194 | 99414886 | 50054737 | 0.000000 | 751823120 | 69237446 | 0.000000
09-04-2025 16:33:10000 | -1351619 | 135.1619 | 14921006 | 235013.59 | 334085236 | 99396179 | 50068203 | 0.000000 | 772251221 | 71110254 | 0.000000
09-04-2025 16:33:15000 | -1351579 | 135.1579 | 15073986 | 234986.61 | 334153809 | 99383812 | 50073818 | 0.000000 | 793231140 | 72987334 | 0.000000
09-04-2025 16:33:20000 | -1347722 | 134.7722 | 14883020 | 234990.09 | 333157654 | 99395775 | 50069893 | 0.000000 | 813998413 | 74860513 | 0.000000
09-04-2025 16:33:25000 | -1347105 | 134.7105 | 15013014 | 235046.83 | 332958618 | 99384712 | 50075943 | 0.000000 | 834690247 | 76731997 | 0.000000
09-04-2025 16:33:30000 | -1351141 | 135.1141 | 15195700 | 235049.61 | 333990204 | 99373512 | 50098385 | 0.000000 | 855767944 | 78607256 | 0.000000
09-04-2025 16:33:35000 | -1351998 | 135.1998 | 15211452 | 235019.13 | 334251831 | 99373009 | 50095703 | 0.000000 | 876805847 | 80481738 | 0.000000
09-04-2025 16:33:40000 | -1353720 | 135.372 | 15006198 | 234958.16 | 334702972 | 99391205 | 50066566 | 0.000000 | 897752319 | 82359199 | 0.000000
09-04-2025 16:33:45000 | -1347428 | 134.7428 | 14633477 | 234930.86 | 333099335 | 99415436 | 50039673 | 0.000000 | 918284973 | 84236455 | 0.000000
09-04-2025 16:33:50000 | -1352396 | 135.2396 | 14692370 | 234925.31 | 334337311 | 99415047 | 50031548 | 0.000000 | 938643616 | 86112090 | 0.000000
09-04-2025 16:33:55000 | -1349052 | 134.9052 | 14732528 | 234964.38 | 333473358 | 99408981 | 50034039 | 0.000000 | 959041931 | 87987266 | 0.000000
09-04-2025 16:34:00000 | -1351633 | 135.1633 | 14869947 | 234939.13 | 334181427 | 99400276 | 50039711 | 0.000000 | 979610352 | 89862031 | 0.000000
09-04-2025 16:34:05000 | -1346559 | 134.6559 | 14376690 | 234866.08 | 332913116 | 99434875 | 50001434 | 0.000000 | 999987610 | 91739336 | 0.000000
09-04-2025 16:34:10000 | -1349501 | 134.9501 | 14544540 | 234904.64 | 333625031 | 99424217 | 49999023 | 0.000000 | 10200861 | 93613164 | 0.000000
09-04-2025 16:34:15000 | -1347653 | 134.7653 | 14532884 | 234911.08 | 333161713 | 99423569 | 50019634 | 0.000000 | 10401880 | 95481221 | 0.000000
09-04-2025 16:34:20000 | -1348356 | 134.8356 | 14391603 | 234830.16 | 333402863 | 99435211 | 50012222 | 0.000000 | 10601654 | 97351650 | 0.000000
09-04-2025 16:34:25000 | -1346205 | 134.6205 | 14262286 | 234820.58 | 332860809 | 99443474 | 50000080 | 0.000000 | 10800958 | 99225186 | 0.000000
09-04-2025 16:34:30000 | -1347514 | 134.7514 | 14227184 | 234807.83 | 333192291 | 99447250 | 49998390 | 0.000000 | 10998322 | 10109645 | 0.000000
09-04-2025 16:34:35000 | -1344236 | 134.4236 | 13864575 | 234770.63 | 332347778 | 99472305 | 49966637 | 0.000000 | 11194025 | 10296944 | 0.000000
09-04-2025 16:34:40000 | -1339692 | 133.9692 | 14047110 | 234923.41 | 331065918 | 99454781 | 49993160 | 0.000000 | 11387994 | 10483238 | 0.000000
09-04-2025 16:34:45000 | -1352374 | 135.2374 | 14401167 | 234769.03 | 334482452 | 99437790 | 49992115 | 0.000000 | 11586857 | 10670209 | 0.000000
09-04-2025 16:34:50000 | -1345604 | 134.5604 | 14159487 | 234791.34 | 332734528 | 99450912 | 49972015 | 0.000000 | 11783888 | 10857322 | 0.000000
09-04-2025 16:34:55000 | -1342658 | 134.2658 | 14046726 | 234824.20 | 331935181 | 99457199 | 49982143 | 0.000000 | 11979054 | 11043886 | 0.000000
09-04-2025 16:35:00000 | -1342315 | 134.2315 | 14063919 | 234840.98 | 331836548 | 99455605 | 49992809 | 0.000000 | 12172992 | 11230118 | 0.000000
09-04-2025 16:35:05000 | -1345930 | 134.593 | 14328604 | 234836.78 | 332783722 | 99438095 | 50010353 | 0.000000 | 12371367 | 11416992 | 0.000000
09-04-2025 16:35:10000 | -1345173 | 134.5173 | 14081074 | 234804.36 | 332582947 | 99456581 | 50013771 | 0.000000 | 12567852 | 11603643 | 0.000000
09-04-2025 16:35:15000 | -1343405 | 134.3405 | 14059084 | 234801.63 | 332150879 | 99456848 | 49997063 | 0.000000 | 12764509 | 11790472 | 0.000000
09-04-2025 16:35:20000 | -1342530 | 134.253 | 14244474 | 234843.69 | 331943787 | 99441826 | 50017704 | 0.000000 | 12960941 | 11977015 | 0.000000
09-04-2025 16:35:25000 | -1347347 | 134.7347 | 14232002 | 234793.97 | 333175934 | 99446739 | 50015919 | 0.000000 | 13158925 | 12163953 | 0.000000
09-04-2025 16:35:30000 | -1343812 | 134.3812 | 14442491 | 234869.08 | 332260956 | 99427422 | 50053738 | 0.000000 | 13358590 | 12350459 | 0.000000
09-04-2025 16:35:35000 | -1349298 | 134.9298 | 14552798 | 234845.20 | 333659729 | 99423393 | 50045860 | 0.000000 | 13561066 | 12537775 | 0.000000
09-04-2025 16:35:40000 | -1348616 | 134.8616 | 14536540 | 234907.89 | 333408417 | 99424095 | 50042755 | 0.000000 | 13761713 | 12724827 | 0.000000
09-04-2025 16:35:45000 | -1346854 | 134.6854 | 14393992 | 234848.47 | 333012848 | 99433769 | 50022137 | 0.000000 | 13962755 | 12912179 | 0.000000
09-04-2025 16:35:50000 | -1349852 | 134.9852 | 14606458 | 234888.16 | 333750031 | 99419647 | 50033031 | 0.000000 | 14163806 | 13099228 | 0.000000
09-04-2025 16:35:55000 | -1352783 | 135.2783 | 14359561 | 234740.73 | 334605652 | 99441345 | 50010780 | 0.000000 | 14365415 | 13286555 | 0.000000
09-04-2025 16:36:00000 | -1348945 | 134.8945 | 13957182 | 234710.84 | 333604675 | 99468987 | 49969929 | 0.000000 | 14561676 | 13473853 | 0.000000
09-04-2025 16:36:05000 | -1342505 | 134.2505 | 13692252 | 234738.97 | 331931183 | 99483925 | 49965340 | 0.000000 | 14752877 | 13660513 | 0.000000
09-04-2025 16:36:10000 | -1344349 | 134.4349 | 14052187 | 234815.69 | 332365417 | 99458130 | 49975269 | 0.000000 | 14945559 | 13847019 | 0.000000
09-04-2025 16:36:15000 | -1347785 | 134.7785 | 13992278 | 234723.64 | 333320038 | 99465424 | 49955585 | 0.000000 | 15141372 | 14034243 | 0.000000
09-04-2025 16:36:20000 | -1348879 | 134.8879 | 14071646 | 234776.41 | 333528198 | 99460258 | 49958244 | 0.000000 | 15335134 | 14221105 | 0.000000
09-04-2025 16:36:25000 | -1346026 | 134.6026 | 14177272 | 234810.44 | 332805176 | 99449883 | 49970100 | 0.000000 | 15530677 | 14407792 | 0.000000
09-04-2025 16:36:30000 | -1347022 | 134.7022 | 14052840 | 234746.81 | 333117340 | 99460213 | 49964542 | 0.000000 | 15726420 | 14594791 | 0.000000
09-04-2025 16:36:35000 | -1348254 | 134.8254 | 13941883 | 234731.63 | 333405121 | 99469597 | 49949169 | 0.000000 | 15920474 | 14781850 | 0.000000
09-04-2025 16:36:40000 | -1336145 | 133.6145 | 13862279 | 234908.16 | 330170715 | 99466118 | 49971493 | 0.000000 | 16112384 | 14968117 | 0.000000
09-04-2025 16:36:45000 | -1350674 | 135.0674 | 14339645 | 234748.91 | 334075775 | 99441154 | 49993286 | 0.000000 | 16309702 | 15154863 | 0.000000
09-04-2025 16:36:50000 | -1348615 | 134.8615 | 14057490 | 234726.47 | 333532379 | 99461128 | 49966187 | 0.000000 | 16505673 | 15342058 | 0.000000
09-04-2025 16:36:55000 | -1337923 | 133.7923 | 13708022 | 234792.08 | 330731201 | 99479218 | 49966625 | 0.000000 | 16697649 | 15528438 | 0.000000
09-04-2025 16:37:00000 | -1348131 | 134.8131 | 14359211 | 234838.89 | 333329529 | 99437538 | 49991352 | 0.000000 | 16894406 | 15715345 | 0.000000
09-04-2025 16:37:05000 | -1345610 | 134.561 | 14100550 | 234801.23 | 332703003 | 99455444 | 49969536 | 0.000000 | 17091787 | 15902608 | 0.000000
09-04-2025 16:37:10000 | -1345901 | 134.5901 | 14430583 | 234908.77 | 332702759 | 99430115 | 49987568 | 0.000000 | 17289926 | 16089645 | 0.000000
09-04-2025 16:37:15000 | -1349834 | 134.9834 | 14653661 | 234919.94 | 333712402 | 99415901 | 50009544 | 0.000000 | 17491088 | 16276691 | 0.000000
09-04-2025 16:37:20000 | -1350133 | 135.0133 | 14520355 | 234901.56 | 333775665 | 99426643 | 50015602 | 0.000000 | 17692606 | 16463963 | 0.000000
09-04-2025 16:37:25000 | -1350289 | 135.0289 | 14317165 | 234820.86 | 333871246 | 99442574 | 49993736 | 0.000000 | 17893043 | 16651520 | 0.000000
09-04-2025 16:37:30000 | -1347797 | 134.7797 | 14087262 | 234777.53 | 333266266 | 99458206 | 49962704 | 0.000000 | 18090300 | 16839068 | 0.000000
09-04-2025 16:37:35000 | -1344394 | 134.4394 | 13927936 | 234791.36 | 332372070 | 99467636 | 49951283 | 0.000000 | 18284844 | 17026055 | 0.000000
09-04-2025 16:37:40000 | -1344243 | 134.4243 | 14080100 | 234850.80 | 332291290 | 99455910 | 49953533 | 0.000000 | 18479752 | 17212941 | 0.000000
09-04-2025 16:37:45000 | -1352772 | 135.2772 | 14167025 | 234696.33 | 334624542 | 99456093 | 49953732 | 0.000000 | 18676676 | 17400094 | 0.000000
09-04-2025 16:37:50000 | -1345225 | 134.5225 | 13851374 | 234764.61 | 332600769 | 99474068 | 49944809 | 0.000000 | 18868981 | 17586930 | 0.000000
09-04-2025 16:37:55000 | -1344790 | 134.479 | 13917229 | 234718.22 | 332575226 | 99468758 | 49933422 | 0.000000 | 19061938 | 17773688 | 0.000000
09-04-2025 16:38:00000 | -1348706 | 134.8706 | 13676285 | 234639.88 | 333579987 | 99489799 | 49910515 | 0.000000 | 19252683 | 17960754 | 0.000000
09-04-2025 16:38:05000 | -1343569 | 134.3569 | 13462290 | 234643.55 | 332266663 | 99501770 | 49887573 | 0.000000 | 19441255 | 18147484 | 0.000000
09-04-2025 16:38:10000 | -1343322 | 134.3322 | 13545910 | 234737.13 | 332091736 | 99495422 | 49893879 | 0.000000 | 19627574 | 18334078 | 0.000000
09-04-2025 16:38:15000 | -1339646 | 133.9646 | 13483290 | 234737.95 | 331173340 | 99497314 | 49913094 | 0.000000 | 19813704 | 18520100 | 0.000000
09-04-2025 16:38:20000 | -1345897 | 134.5897 | 13935328 | 234718.48 | 332848907 | 99468254 | 49938591 | 0.000000 | 20005928 | 18706738 | 0.000000
09-04-2025 16:38:25000 | -1346079 | 134.6079 | 14032082 | 234766.66 | 332851257 | 99461044 | 49953335 | 0.000000 | 20199335 | 18893379 | 0.000000
09-04-2025 16:38:30000 | -1346610 | 134.661 | 13935477 | 234739.23 | 332993988 | 99468796 | 49957039 | 0.000000 | 20393943 | 19080256 | 0.000000
09-04-2025 16:38:35000 | -1344815 | 134.4815 | 13912663 | 234766.75 | 332512970 | 99469124 | 49948597 | 0.000000 | 20588147 | 19267225 | 0.000000
09-04-2025 16:38:40000 | -1345608 | 134.5608 | 14291756 | 234848.67 | 332681702 | 99440697 | 49976856 | 0.000000 | 20783875 | 19453541 | 0.000000
09-04-2025 16:38:45000 | -1347406 | 134.7406 | 14285558 | 234787.59 | 333204437 | 99442657 | 49984013 | 0.000000 | 20982417 | 19640473 | 0.000000
09-04-2025 16:38:50000 | -1347842 | 134.7842 | 14114915 | 234774.38 | 333286499 | 99456131 | 49965382 | 0.000000 | 21178833 | 19827807 | 0.000000
09-04-2025 16:38:55000 | -1344278 | 134.4278 | 14188816 | 234892.58 | 332274200 | 99447571 | 49973911 | 0.000000 | 21374875 | 20014660 | 0.000000
09-04-2025 16:39:00000 | -1346670 | 134.667 | 14268949 | 234832.56 | 332968109 | 99443336 | 49982777 | 0.000000 | 21572600 | 20201494 | 0.000000
09-04-2025 16:39:05000 | -1350628 | 135.0628 | 14374615 | 234826.02 | 333960724 | 99438408 | 49975700 | 0.000000 | 21771638 | 20388791 | 0.000000
09-04-2025 16:39:10000 | -1347414 | 134.7414 | 13935481 | 234713.44 | 333229004 | 99469429 | 49964748 | 0.000000 | 21967314 | 20576004 | 0.000000
09-04-2025 16:39:15000 | -1348756 | 134.8756 | 14127654 | 234767.19 | 333530151 | 99455887 | 49970112 | 0.000000 | 22163542 | 20763182 | 0.000000
09-04-2025 16:39:20000 | -1348521 | 134.8521 | 14016897 | 234759.42 | 333448792 | 99464134 | 49952271 | 0.000000 | 22358655 | 20950232 | 0.000000
09-04-2025 16:39:25000 | -1348525 | 134.8525 | 13780104 | 234663.69 | 333527283 | 99481949 | 49923046 | 0.000000 | 22552280 | 21137502 | 0.000000
09-04-2025 16:39:30000 | -1339654 | 133.9654 | 13279021 | 234664.00 | 331230988 | 99512321 | 49880390 | 0.000000 | 22740737 | 21324457 | 0.000000
09-04-2025 16:39:35000 | -1336765 | 133.6765 | 13680628 | 234851.84 | 330359192 | 99480392 | 49926189 | 0.000000 | 22927354 | 21510285 | 0.000000
09-04-2025 16:39:40000 | -1347871 | 134.7871 | 14123445 | 234756.86 | 333323212 | 99455505 | 49951687 | 0.000000 | 23121821 | 21696816 | 0.000000
09-04-2025 16:39:45000 | -1344138 | 134.4138 | 13868095 | 234742.14 | 332372498 | 99471962 | 49931824 | 0.000000 | 23316909 | 21884000 | 0.000000
09-04-2025 16:39:50000 | -1343406 | 134.3406 | 14187636 | 234886.16 | 332069366 | 99446953 | 49971767 | 0.000000 | 23511135 | 22070539 | 0.000000
09-04-2025 16:39:55000 | -1344864 | 134.4864 | 14463133 | 234918.33 | 332448700 | 99426689 | 50010883 | 0.000000 | 23710737 | 22257264 | 0.000000
09-04-2025 16:40:00000 | -1350903 | 135.0903 | 14918960 | 234974.67 | 333965576 | 99395706 | 50042999 | 0.000000 | 23915452 | 22444563 | 0.000000
09-04-2025 16:40:05000 | -1355064 | 135.5064 | 14948294 | 234948.86 | 335027527 | 99397034 | 50051857 | 0.000000 | 24122029 | 22632309 | 0.000000
09-04-2025 16:40:10000 | -1347449 | 134.7449 | 14339773 | 234846.81 | 333147827 | 99438484 | 50021877 | 0.000000 | 24326345 | 22820203 | 0.000000
09-04-2025 16:40:15000 | -1348265 | 134.8265 | 14536764 | 234921.47 | 333298889 | 99423782 | 50034451 | 0.000000 | 24528582 | 23007785 | 0.000000
09-04-2025 16:40:20000 | -1350762 | 135.0762 | 14513904 | 234931.88 | 333881897 | 99427681 | 50027336 | 0.000000 | 24730383 | 23195441 | 0.000000
09-04-2025 16:40:25000 | -1354676 | 135.4676 | 14527785 | 234796.59 | 335040466 | 99429871 | 50019855 | 0.000000 | 24934041 | 23383422 | 0.000000
09-04-2025 16:40:30000 | -1354032 | 135.4032 | 14595415 | 234839.61 | 334831940 | 99424057 | 50028549 | 0.000000 | 25136404 | 23571035 | 0.000000
09-04-2025 16:40:35000 | -1350934 | 135.0934 | 14241451 | 234823.88 | 334005005 | 99448929 | 50010868 | 0.000000 | 25335315 | 23758740 | 0.000000
09-04-2025 16:40:40000 | -1348688 | 134.8688 | 14322166 | 234849.78 | 333440216 | 99440872 | 49994110 | 0.000000 | 25534763 | 23946508 | 0.000000
09-04-2025 16:40:45000 | -1350838 | 135.0838 | 14250585 | 234823.42 | 333984436 | 99448151 | 49983685 | 0.000000 | 25732754 | 24134059 | 0.000000
09-04-2025 16:40:50000 | -1348298 | 134.8298 | 14104737 | 234811.72 | 333345520 | 99457275 | 49998043 | 0.000000 | 25929382 | 24321297 | 0.000000
09-04-2025 16:40:55000 | -1346382 | 134.6382 | 14204715 | 234815.83 | 332896606 | 99448059 | 50004646 | 0.000000 | 26127021 | 24508637 | 0.000000
09-04-2025 16:41:00000 | -1353166 | 135.3166 | 14224666 | 234744.94 | 334665955 | 99452011 | 49990013 | 0.000000 | 26324421 | 24696277 | 0.000000
09-04-2025 16:41:05000 | -1347656 | 134.7656 | 13933873 | 234750.33 | 333230743 | 99469742 | 49957066 | 0.000000 | 26519524 | 24883570 | 0.000000
09-04-2025 16:41:10000 | -1343522 | 134.3522 | 13943195 | 234826.06 | 332114502 | 99465790 | 49953491 | 0.000000 | 26713396 | 25070516 | 0.000000
09-04-2025 16:41:15000 | -1347360 | 134.736 | 14432620 | 234883.64 | 333096741 | 99431183 | 49983440 | 0.000000 | 26910110 | 25257139 | 0.000000
09-04-2025 16:41:20000 | -1349790 | 134.979 | 14486665 | 234809.88 | 333806519 | 99428993 | 49995125 | 0.000000 | 27112151 | 25444367 | 0.000000
09-04-2025 16:41:25000 | -1352393 | 135.2393 | 14348580 | 234809.17 | 334410980 | 99441872 | 49967346 | 0.000000 | 27311304 | 25632199 | 0.000000
09-04-2025 16:41:30000 | -1345400 | 134.54 | 14136817 | 234842.20 | 332599457 | 99452492 | 49960052 | 0.000000 | 27508152 | 25819387 | 0.000000
09-04-2025 16:41:35000 | -1343951 | 134.3951 | 13913862 | 234801.58 | 332247467 | 99468353 | 49950710 | 0.000000 | 27702400 | 26006258 | 0.000000
09-04-2025 16:41:40000 | -1348218 | 134.8218 | 14460002 | 234887.86 | 333311371 | 99429756 | 49983002 | 0.000000 | 27901885 | 26193328 | 0.000000
09-04-2025 16:41:45000 | -1350945 | 135.0945 | 14192742 | 234750.64 | 334102722 | 99452667 | 49948498 | 0.000000 | 28100952 | 26381008 | 0.000000
09-04-2025 16:41:50000 | -1337721 | 133.7721 | 14186553 | 235028.92 | 330473389 | 99442368 | 49965389 | 0.000000 | 28297053 | 26567889 | 0.000000
09-04-2025 16:41:55000 | -1350255 | 135.0255 | 14576045 | 234852.22 | 333885345 | 99422379 | 49997360 | 0.000000 | 28500039 | 26755209 | 0.000000
09-04-2025 16:42:00000 | -1353689 | 135.3689 | 14472555 | 234814.13 | 334751587 | 99433342 | 49979282 | 0.000000 | 28701265 | 26942863 | 0.000000
09-04-2025 16:42:05000 | -1348560 | 134.856 | 14181286 | 234813.47 | 333425598 | 99451630 | 49962215 | 0.000000 | 28898896 | 27130283 | 0.000000
09-04-2025 16:42:10000 | -1345957 | 134.5957 | 13939702 | 234761.00 | 332803192 | 99467964 | 49929577 | 0.000000 | 29093667 | 27317742 | 0.000000
09-04-2025 16:42:15000 | -1343163 | 134.3163 | 13812486 | 234792.30 | 332044006 | 99475403 | 49939056 | 0.000000 | 29285442 | 27504535 | 0.000000
09-04-2025 16:42:20000 | -1347457 | 134.7457 | 14141213 | 234797.91 | 333164307 | 99453812 | 49964466 | 0.000000 | 29480513 | 27691500 | 0.000000
09-04-2025 16:42:25000 | -1349934 | 134.9934 | 13996478 | 234726.06 | 333840179 | 99466789 | 49939842 | 0.000000 | 29675198 | 27878824 | 0.000000
09-04-2025 16:42:30000 | -1348200 | 134.82 | 13959683 | 234777.16 | 333339264 | 99468216 | 49940033 | 0.000000 | 29868081 | 28065654 | 0.000000
09-04-2025 16:42:35000 | -1349132 | 134.9132 | 13873962 | 234666.39 | 333695496 | 99475395 | 49933781 | 0.000000 | 30061914 | 28252664 | 0.000000
09-04-2025 16:42:40000 | -1342855 | 134.2855 | 13795798 | 234785.47 | 331976501 | 99476418 | 49928600 | 0.000000 | 30253035 | 28439477 | 0.000000
09-04-2025 16:42:45000 | -1342236 | 134.2236 | 13938602 | 234822.28 | 331805023 | 99465118 | 49956127 | 0.000000 | 30445447 | 28626023 | 0.000000
09-04-2025 16:42:50000 | -1344720 | 134.472 | 13846985 | 234678.63 | 332596680 | 99474007 | 49945984 | 0.000000 | 30640444 | 28813168 | 0.000000
09-04-2025 16:42:55000 | -1343533 | 134.3533 | 14029768 | 234848.95 | 332108673 | 99459198 | 49962662 | 0.000000 | 30833818 | 28999822 | 0.000000
09-04-2025 16:43:00000 | -1352301 | 135.2301 | 14442521 | 234803.08 | 334423004 | 99434525 | 49973892 | 0.000000 | 31032021 | 29187072 | 0.000000
09-04-2025 16:43:05000 | -1348153 | 134.8153 | 14175126 | 234782.59 | 333368469 | 99451767 | 49949669 | 0.000000 | 31230171 | 29374320 | 0.000000
09-04-2025 16:43:10000 | -1341354 | 134.1354 | 13885708 | 234814.63 | 331583191 | 99468445 | 49933971 | 0.000000 | 31422805 | 29560719 | 0.000000
09-04-2025 16:43:15000 | -1343549 | 134.3549 | 13992581 | 234785.48 | 332191162 | 99462051 | 49945221 | 0.000000 | 31617449 | 29747201 | 0.000000
09-04-2025 16:43:20000 | -1346621 | 134.6621 | 13868518 | 234672.13 | 333079376 | 99473862 | 49933739 | 0.000000 | 31812383 | 29934189 | 0.000000
09-04-2025 16:43:25000 | -1345965 | 134.5965 | 13581908 | 234656.28 | 332863495 | 99494728 | 49911812 | 0.000000 | 32002769 | 30121215 | 0.000000
09-04-2025 16:43:30000 | -1342600 | 134.26 | 13527895 | 234728.61 | 331923279 | 99496216 | 49907589 | 0.000000 | 32190869 | 30307914 | 0.000000
09-04-2025 16:43:35000 | -1347014 | 134.7014 | 13541508 | 234603.77 | 333186035 | 99498489 | 49904110 | 0.000000 | 32378853 | 30494428 | 0.000000
09-04-2025 16:43:40000 | -1336659 | 133.6659 | 13217746 | 234682.23 | 330457703 | 99514633 | 49883236 | 0.000000 | 32564509 | 30680736 | 0.000000
09-04-2025 16:43:45000 | -1343972 | 134.3972 | 13486146 | 234624.31 | 332395691 | 99500313 | 49887730 | 0.000000 | 32751201 | 30867137 | 0.000000
09-04-2025 16:43:50000 | -1340053 | 134.0053 | 13724535 | 234782.78 | 331273621 | 99479622 | 49919506 | 0.000000 | 32939478 | 31053209 | 0.000000
09-04-2025 16:43:55000 | -1339234 | 133.9234 | 14329386 | 234939.67 | 331007141 | 99432449 | 49978649 | 0.000000 | 33135037 | 31239313 | 0.000000
09-04-2025 16:44:00000 | -1352234 | 135.2234 | 14751231 | 234899.25 | 334348450 | 99410248 | 50001431 | 0.000000 | 33337749 | 31426457 | 0.000000
09-04-2025 16:44:05000 | -1348898 | 134.8898 | 14393823 | 234799.14 | 333580933 | 99435486 | 49966908 | 0.000000 | 33540874 | 31614076 | 0.000000
09-04-2025 16:44:10000 | -1347300 | 134.73 | 14544318 | 234897.77 | 333093170 | 99422363 | 49974873 | 0.000000 | 33741316 | 31801193 | 0.000000
09-04-2025 16:44:15000 | -1350921 | 135.0921 | 14465765 | 234844.00 | 334032135 | 99431572 | 49970562 | 0.000000 | 33942476 | 31988355 | 0.000000
09-04-2025 16:44:20000 | -1339869 | 133.9869 | 14212163 | 234911.41 | 331169952 | 99442146 | 49974579 | 0.000000 | 34141108 | 32174908 | 0.000000
09-04-2025 16:44:25000 | -1341857 | 134.1857 | 14733912 | 235003.95 | 331662659 | 99402565 | 50009525 | 0.000000 | 34342551 | 32361277 | 0.000000
09-04-2025 16:44:30000 | -1344955 | 134.4955 | 14863029 | 234964.00 | 332511841 | 99394920 | 50021755 | 0.000000 | 34549155 | 32548049 | 0.000000
09-04-2025 16:44:35000 | -1352863 | 135.2863 | 14578943 | 234792.03 | 334610260 | 99424362 | 49991268 | 0.000000 | 34753799 | 32735670 | 0.000000
09-04-2025 16:44:40000 | -1348215 | 134.8215 | 14236455 | 234840.98 | 333315369 | 99447105 | 49953430 | 0.000000 | 34953037 | 32923063 | 0.000000
09-04-2025 16:44:45000 | -1348553 | 134.8553 | 14203938 | 234787.84 | 333465942 | 99449883 | 49948696 | 0.000000 | 35150288 | 33110023 | 0.000000
09-04-2025 16:44:50000 | -1343039 | 134.3039 | 14138282 | 234820.05 | 332062439 | 99450462 | 49936878 | 0.000000 | 35347524 | 33297082 | 0.000000
09-04-2025 16:44:55000 | -1347921 | 134.7921 | 14184774 | 234767.08 | 333333282 | 99450844 | 49934326 | 0.000000 | 35543662 | 33483746 | 0.000000
09-04-2025 16:45:00000 | -1342585 | 134.2585 | 13841160 | 234788.25 | 331913208 | 99472786 | 49917080 | 0.000000 | 35736316 | 33670266 | 0.000000
09-04-2025 16:45:05000 | -1342240 | 134.224 | 13812245 | 234763.42 | 331856964 | 99474701 | 49917202 | 0.000000 | 19251427 | 186570496 | 0.000000
09-04-2025 16:45:10000 | -1347637 | 134.7637 | 13960771 | 234731.02 | 333264954 | 99467690 | 49929947 | 0.000000 | 38443638 | 372961029 | 0.000000
09-04-2025 16:45:15000 | -1343420 | 134.342 | 13960032 | 234789.84 | 332141968 | 99464424 | 49938248 | 0.000000 | 57763763 | 559437195 | 0.000000
09-04-2025 16:45:20000 | -1348196 | 134.8196 | 14052486 | 234758.22 | 333382050 | 99461174 | 49943317 | 0.000000 | 77310608 | 746449829 | 0.000000
09-04-2025 16:45:25000 | -1347810 | 134.781 | 14225140 | 234831.19 | 333231232 | 99447647 | 49952927 | 0.000000 | 96824982 | 933356873 | 0.000000
09-04-2025 16:45:30000 | -1347270 | 134.727 | 14049944 | 234744.05 | 333172760 | 99460632 | 49937988 | 0.000000 | 116471436 | 11205892 | 0.000000
09-04-2025 16:45:35000 | -1339396 | 133.9396 | 13868195 | 234810.14 | 331111420 | 99468239 | 49932465 | 0.000000 | 135853729 | 13073555 | 0.000000
09-04-2025 16:45:40000 | -1348161 | 134.8161 | 14108108 | 234742.05 | 333408081 | 99456909 | 49935661 | 0.000000 | 155311676 | 14940525 | 0.000000
09-04-2025 16:45:45000 | -1344655 | 134.4655 | 14035689 | 234781.36 | 332481964 | 99459641 | 49939247 | 0.000000 | 174848495 | 16808519 | 0.000000
09-04-2025 16:45:50000 | -1346229 | 134.6229 | 14127561 | 234784.02 | 332881836 | 99453865 | 49945965 | 0.000000 | 194256165 | 18674232 | 0.000000
09-04-2025 16:45:55000 | -1341569 | 134.1569 | 13606824 | 234695.97 | 331745453 | 99489586 | 49915047 | 0.000000 | 213439713 | 20539236 | 0.000000
09-04-2025 16:46:00000 | -1346593 | 134.6593 | 13642698 | 234648.31 | 333046326 | 99490707 | 49899834 | 0.000000 | 232469162 | 22406804 | 0.000000
09-04-2025 16:46:05000 | -1342117 | 134.2117 | 13486278 | 234678.78 | 331865234 | 99498932 | 49901276 | 0.000000 | 251298096 | 24270156 | 0.000000
09-04-2025 16:46:10000 | -1340217 | 134.0217 | 13442874 | 234649.69 | 331430573 | 99500725 | 49895504 | 0.000000 | 270101624 | 26135125 | 0.000000
09-04-2025 16:46:15000 | -1337964 | 133.7964 | 13629239 | 234708.59 | 330844666 | 99485176 | 49910210 | 0.000000 | 289021423 | 27996399 | 0.000000
09-04-2025 16:46:20000 | -1340628 | 134.0628 | 13715096 | 234734.70 | 331480988 | 99480774 | 49913414 | 0.000000 | 308012054 | 29861345 | 0.000000
09-04-2025 16:46:25000 | -1342568 | 134.2568 | 13930454 | 234806.08 | 331902863 | 99466003 | 49947933 | 0.000000 | 327234406 | 31726670 | 0.000000
09-04-2025 16:46:30000 | -1352538 | 135.2538 | 14228640 | 234679.77 | 334603210 | 99451202 | 49955437 | 0.000000 | 346981506 | 33597349 | 0.000000
09-04-2025 16:46:35000 | -1341188 | 134.1188 | 13434484 | 234671.27 | 331637512 | 99502060 | 49911041 | 0.000000 | 366045441 | 35465891 | 0.000000
09-04-2025 16:46:40000 | -1336742 | 133.6742 | 13871739 | 234892.09 | 330352997 | 99465874 | 49947178 | 0.000000 | 385007629 | 37325898 | 0.000000
09-04-2025 16:46:45000 | -1338220 | 133.822 | 14185464 | 234914.30 | 330759979 | 99442863 | 49994019 | 0.000000 | 404617310 | 39186995 | 0.000000
09-04-2025 16:46:50000 | -1351629 | 135.1629 | 14526499 | 234797.44 | 334289368 | 99427422 | 49994701 | 0.000000 | 424644135 | 41057749 | 0.000000
09-04-2025 16:46:55000 | -1350879 | 135.0879 | 14258299 | 234727.89 | 334134338 | 99447586 | 49974651 | 0.000000 | 444609924 | 42930308 | 0.000000
09-04-2025 16:47:00000 | -1348003 | 134.8003 | 14028959 | 234825.38 | 333243774 | 99462807 | 49961956 | 0.000000 | 464006226 | 44799902 | 0.000000
09-04-2025 16:47:05000 | -1346775 | 134.6775 | 14301636 | 234829.16 | 332997131 | 99440887 | 49975960 | 0.000000 | 483829773 | 46668926 | 0.000000
09-04-2025 16:47:10000 | -1349564 | 134.9564 | 13818937 | 234622.75 | 333848755 | 99479843 | 49925087 | 0.000000 | 503379669 | 48544482 | 0.000000
09-04-2025 16:47:15000 | -1347286 | 134.7286 | 13763360 | 234720.64 | 333138489 | 99482254 | 49920422 | 0.000000 | 522444519 | 50413247 | 0.000000
09-04-2025 16:47:20000 | -1344803 | 134.4803 | 13997615 | 234806.42 | 332475098 | 99462662 | 49949062 | 0.000000 | 541704712 | 52279141 | 0.000000
09-04-2025 16:47:25000 | -1344420 | 134.442 | 14156447 | 234822.27 | 332393066 | 99450188 | 49973946 | 0.000000 | 561268433 | 54146284 | 0.000000
09-04-2025 16:47:30000 | -1347001 | 134.7001 | 14145886 | 234786.38 | 333074188 | 99453087 | 49977810 | 0.000000 | 580845032 | 56016323 | 0.000000
09-04-2025 16:47:35000 | -1347402 | 134.7402 | 14099694 | 234775.77 | 333171936 | 99456940 | 49977634 | 0.000000 | 600483582 | 57888052 | 0.000000
09-04-2025 16:47:40000 | -1349222 | 134.9222 | 14091339 | 234760.16 | 333644867 | 99459030 | 49956856 | 0.000000 | 620037048 | 59759941 | 0.000000
09-04-2025 16:47:45000 | -1343810 | 134.381 | 13750329 | 234734.28 | 332266602 | 99480568 | 49949867 | 0.000000 | 639266846 | 61624321 | 0.000000
09-04-2025 16:47:50000 | -1343833 | 134.3833 | 13860891 | 234745.00 | 332281250 | 99472267 | 49943142 | 0.000000 | 658589050 | 63492632 | 0.000000
09-04-2025 16:47:55000 | -1342099 | 134.2099 | 13743823 | 234730.73 | 331851990 | 99479744 | 49945526 | 0.000000 | 677761719 | 65358159 | 0.000000
09-04-2025 16:48:00000 | -1340165 | 134.0165 | 13977584 | 234842.78 | 331274811 | 99460503 | 49970600 | 0.000000 | 697046753 | 67221274 | 0.000000
09-04-2025 16:48:05000 | -1342879 | 134.2879 | 13886958 | 234697.39 | 332131531 | 99469551 | 49956161 | 0.000000 | 716461609 | 69087207 | 0.000000
09-04-2025 16:48:10000 | -1343760 | 134.376 | 13700998 | 234673.61 | 332332306 | 99484222 | 49941032 | 0.000000 | 735486206 | 70951606 | 0.000000
09-04-2025 16:48:15000 | -1342591 | 134.2591 | 13847879 | 234726.45 | 332005371 | 99472282 | 49937904 | 0.000000 | 754670898 | 72817495 | 0.000000
09-04-2025 16:48:20000 | -1348630 | 134.863 | 13804479 | 234669.47 | 333554810 | 99480209 | 49932621 | 0.000000 | 773781677 | 74684326 | 0.000000
09-04-2025 16:48:25000 | -1341915 | 134.1915 | 13696598 | 234713.42 | 331816071 | 99483147 | 49923576 | 0.000000 | 792723450 | 76549077 | 0.000000
09-04-2025 16:48:30000 | -1337994 | 133.7994 | 13671595 | 234762.84 | 330786011 | 99482018 | 49934738 | 0.000000 | 811776123 | 78412031 | 0.000000
09-04-2025 16:48:35000 | -1341401 | 134.1401 | 13888962 | 234766.08 | 331674561 | 99468239 | 49964947 | 0.000000 | 830907349 | 80273579 | 0.000000
09-04-2025 16:48:40000 | -1342576 | 134.2576 | 13941102 | 234744.61 | 332004333 | 99465202 | 49978836 | 0.000000 | 850318481 | 82138311 | 0.000000
09-04-2025 16:48:45000 | -1343112 | 134.3112 | 13901263 | 234760.14 | 332096344 | 99468651 | 49964226 | 0.000000 | 869656677 | 84005801 | 0.000000
09-04-2025 16:48:50000 | -1345469 | 134.5469 | 14003504 | 234784.22 | 332672302 | 99462738 | 49972145 | 0.000000 | 888942993 | 85868916 | 0.000000
09-04-2025 16:48:55000 | -1347108 | 134.7108 | 14260654 | 234804.97 | 333108856 | 99444336 | 49985485 | 0.000000 | 908562073 | 87733359 | 0.000000
09-04-2025 16:49:00000 | -1345380 | 134.538 | 13887186 | 234689.59 | 332746582 | 99471489 | 49955379 | 0.000000 | 928159546 | 89603545 | 0.000000
09-04-2025 16:49:05000 | -1339848 | 133.9848 | 13679881 | 234755.52 | 331249695 | 99482819 | 49959053 | 0.000000 | 947139709 | 91464639 | 0.000000
09-04-2025 16:49:10000 | -1339961 | 133.9961 | 13940484 | 234801.38 | 331281860 | 99463173 | 49989010 | 0.000000 | 966386108 | 93324932 | 0.000000
09-04-2025 16:49:15000 | -1338340 | 133.834 | 14097429 | 234865.14 | 330830261 | 99449799 | 49999947 | 0.000000 | 986053772 | 95189199 | 0.000000
09-04-2025 16:49:20000 | -1346520 | 134.652 | 14385738 | 234862.97 | 332907196 | 99434135 | 50006607 | 0.000000 | 10059081 | 97057344 | 0.000000
09-04-2025 16:49:25000 | -1340098 | 134.0098 | 14290237 | 234879.02 | 331287781 | 99436241 | 50028149 | 0.000000 | 10258607 | 98924922 | 0.000000
09-04-2025 16:49:30000 | -1347374 | 134.7374 | 14357699 | 234853.20 | 333128601 | 99437035 | 50032200 | 0.000000 | 10458151 | 10079332 | 0.000000
09-04-2025 16:49:35000 | -1345559 | 134.5559 | 14237496 | 234841.23 | 332665680 | 99444862 | 50024384 | 0.000000 | 10656870 | 10266197 | 0.000000
09-04-2025 16:49:40000 | -1346404 | 134.6404 | 14067874 | 234724.28 | 332996185 | 99458572 | 50003361 | 0.000000 | 10854413 | 10453387 | 0.000000
09-04-2025 16:49:45000 | -1345404 | 134.5404 | 13934703 | 234785.05 | 332634033 | 99467911 | 49978970 | 0.000000 | 11048230 | 10640574 | 0.000000
09-04-2025 16:49:50000 | -1346686 | 134.6686 | 14262164 | 234866.89 | 332909637 | 99443871 | 49989609 | 0.000000 | 11243477 | 10827302 | 0.000000
09-04-2025 16:49:55000 | -1343279 | 134.3279 | 14419979 | 234922.27 | 332039307 | 99428741 | 50013119 | 0.000000 | 11442234 | 11013928 | 0.000000
09-04-2025 16:50:00000 | -1350841 | 135.0841 | 14409386 | 234783.83 | 334081146 | 99435890 | 50012966 | 0.000000 | 11642310 | 11200845 | 0.000000
09-04-2025 16:50:05000 | -1347087 | 134.7087 | 14073403 | 234733.89 | 333149109 | 99458694 | 49972767 | 0.000000 | 11840103 | 11388072 | 0.000000
09-04-2025 16:50:10000 | -1344056 | 134.4056 | 13770280 | 234714.28 | 332368286 | 99479263 | 49943356 | 0.000000 | 12033383 | 11575066 | 0.000000
09-04-2025 16:50:15000 | -1337861 | 133.7861 | 13763395 | 234831.80 | 330680359 | 99474991 | 49950233 | 0.000000 | 12223516 | 11761149 | 0.000000
09-04-2025 16:50:20000 | -1338892 | 133.8892 | 13847029 | 234780.39 | 331024445 | 99469452 | 49969578 | 0.000000 | 12417258 | 11947518 | 0.000000
09-04-2025 16:50:25000 | -1340280 | 134.028 | 13855291 | 234783.02 | 331358795 | 99469917 | 49966751 | 0.000000 | 12610173 | 12133824 | 0.000000
09-04-2025 16:50:30000 | -1343134 | 134.3134 | 13999610 | 234835.86 | 332030243 | 99461182 | 49983841 | 0.000000 | 12801824 | 12319879 | 0.000000
09-04-2025 16:50:35000 | -1343028 | 134.3028 | 14302304 | 234874.72 | 332018616 | 99437744 | 50009018 | 0.000000 | 12998781 | 12506258 | 0.000000
09-04-2025 16:50:40000 | -1347879 | 134.7879 | 14403473 | 234817.23 | 333313538 | 99433891 | 50004936 | 0.000000 | 13198101 | 12693059 | 0.000000
09-04-2025 16:50:45000 | -1339554 | 133.9554 | 14062143 | 234837.83 | 331154053 | 99453514 | 49999485 | 0.000000 | 13394462 | 12879257 | 0.000000
09-04-2025 16:50:50000 | -1341109 | 134.1109 | 14257052 | 234868.09 | 331545563 | 99439674 | 50004520 | 0.000000 | 13592402 | 13065789 | 0.000000
09-04-2025 16:50:55000 | -1341978 | 134.1978 | 14215814 | 234833.88 | 331807007 | 99443604 | 50003307 | 0.000000 | 13790789 | 13252355 | 0.000000
09-04-2025 16:51:00000 | -1342164 | 134.2164 | 14051718 | 234794.56 | 331855286 | 99456421 | 49989876 | 0.000000 | 13987843 | 13439134 | 0.000000
09-04-2025 16:51:05000 | -1342683 | 134.2683 | 13905021 | 234767.06 | 331980164 | 99468025 | 49960716 | 0.000000 | 14182529 | 13625945 | 0.000000
09-04-2025 16:51:10000 | -1341718 | 134.1718 | 14025939 | 234851.50 | 331662079 | 99458038 | 49978146 | 0.000000 | 14375050 | 13811928 | 0.000000
09-04-2025 16:51:15000 | -1347988 | 134.7988 | 14289032 | 234780.39 | 333363525 | 99442863 | 49995899 | 0.000000 | 14571940 | 13998318 | 0.000000
09-04-2025 16:51:20000 | -1344742 | 134.4742 | 14090945 | 234753.28 | 332553162 | 99455482 | 49985126 | 0.000000 | 14768459 | 14185109 | 0.000000
09-04-2025 16:51:25000 | -1344211 | 134.4211 | 14129558 | 234785.89 | 332390015 | 99452087 | 49986454 | 0.000000 | 14963350 | 14371605 | 0.000000
09-04-2025 16:51:30000 | -1339692 | 133.9692 | 13879733 | 234785.52 | 331220551 | 99467590 | 49980640 | 0.000000 | 15158173 | 14558230 | 0.000000
09-04-2025 16:51:35000 | -1341557 | 134.1557 | 14040756 | 234823.09 | 331667206 | 99456772 | 49980892 | 0.000000 | 15352581 | 14744702 | 0.000000
09-04-2025 16:51:40000 | -1342631 | 134.2631 | 14051255 | 234803.64 | 331961975 | 99456825 | 49982662 | 0.000000 | 15547200 | 14931001 | 0.000000
09-04-2025 16:51:45000 | -1340141 | 134.0141 | 13901428 | 234815.94 | 331295319 | 99466293 | 49984051 | 0.000000 | 15741090 | 15117282 | 0.000000
09-04-2025 16:51:50000 | -1342153 | 134.2153 | 13966244 | 234786.53 | 331854340 | 99462952 | 49964783 | 0.000000 | 15933071 | 15303345 | 0.000000
09-04-2025 16:51:55000 | -1339551 | 133.9551 | 14029586 | 234841.77 | 331143555 | 99456017 | 49993103 | 0.000000 | 16125504 | 15488830 | 0.000000
09-04-2025 16:52:00000 | -1343049 | 134.3049 | 14152483 | 234748.70 | 332160217 | 99449379 | 49991894 | 0.000000 | 16322576 | 15675241 | 0.000000
09-04-2025 16:52:05000 | -1340245 | 134.0245 | 14166136 | 234904.00 | 331257904 | 99446030 | 50007748 | 0.000000 | 16517909 | 15861291 | 0.000000
09-04-2025 16:52:10000 | -1343268 | 134.3268 | 14153595 | 234778.03 | 332177277 | 99449471 | 49996128 | 0.000000 | 16715349 | 16047718 | 0.000000
09-04-2025 16:52:15000 | -1343961 | 134.3961 | 14327469 | 234850.38 | 332287079 | 99436554 | 49994122 | 0.000000 | 16913330 | 16234161 | 0.000000
09-04-2025 16:52:20000 | -1346860 | 134.686 | 14156530 | 234763.45 | 333070648 | 99452156 | 49980885 | 0.000000 | 17110454 | 16420631 | 0.000000
09-04-2025 16:52:25000 | -1332405 | 133.2405 | 13760600 | 234835.41 | 329334869 | 99470924 | 49967323 | 0.000000 | 17304646 | 16606811 | 0.000000
09-04-2025 16:52:30000 | -1341733 | 134.1733 | 14890456 | 235057.50 | 331595245 | 99389809 | 50032948 | 0.000000 | 17504266 | 16792633 | 0.000000
09-04-2025 16:52:35000 | -1344359 | 134.4359 | 15040157 | 235036.02 | 332310974 | 99380005 | 50070950 | 0.000000 | 17711838 | 16979014 | 0.000000
09-04-2025 16:52:40000 | -1350684 | 135.0684 | 15096349 | 234946.41 | 333998962 | 99381187 | 50064800 | 0.000000 | 17922051 | 17166229 | 0.000000
09-04-2025 16:52:45000 | -1349838 | 134.9838 | 14787320 | 234888.78 | 333788055 | 99405296 | 50028046 | 0.000000 | 18128092 | 17353510 | 0.000000
09-04-2025 16:52:50000 | -1343426 | 134.3426 | 14604671 | 234984.55 | 332043030 | 99414268 | 50023655 | 0.000000 | 18329647 | 17540086 | 0.000000
09-04-2025 16:52:55000 | -1342266 | 134.2266 | 14958625 | 235067.44 | 331736298 | 99384750 | 50070522 | 0.000000 | 18535302 | 17726506 | 0.000000
09-04-2025 16:53:00000 | -1352175 | 135.2175 | 15031397 | 234938.19 | 334356781 | 99387787 | 50062191 | 0.000000 | 18743807 | 17913762 | 0.000000
09-04-2025 16:53:05000 | -1344069 | 134.4069 | 14664338 | 234967.47 | 332237518 | 99410080 | 50032780 | 0.000000 | 18948665 | 18100715 | 0.000000
09-04-2025 16:53:10000 | -1340141 | 134.0141 | 14825783 | 235042.77 | 331220062 | 99393623 | 50052742 | 0.000000 | 19153765 | 18287051 | 0.000000
09-04-2025 16:53:15000 | -1340067 | 134.0067 | 14983819 | 235061.59 | 331208740 | 99380684 | 50065498 | 0.000000 | 19361765 | 18473361 | 0.000000
09-04-2025 16:53:20000 | -1342881 | 134.2881 | 14797671 | 234958.70 | 331994232 | 99398346 | 50040745 | 0.000000 | 19569398 | 18660027 | 0.000000
09-04-2025 16:53:25000 | -1342430 | 134.243 | 14681466 | 234949.27 | 331862244 | 99407280 | 50006027 | 0.000000 | 19774619 | 18846852 | 0.000000
09-04-2025 16:53:30000 | -1342076 | 134.2076 | 14393879 | 234862.28 | 331824463 | 99429779 | 50008675 | 0.000000 | 19976790 | 19033105 | 0.000000
09-04-2025 16:53:35000 | -1343385 | 134.3385 | 14404572 | 234838.59 | 332184021 | 99430038 | 50000195 | 0.000000 | 20176664 | 19219367 | 0.000000
09-04-2025 16:53:40000 | -1345881 | 134.5881 | 14114168 | 234687.00 | 332930878 | 99454613 | 49951225 | 0.000000 | 20374272 | 19405992 | 0.000000
09-04-2025 16:53:45000 | -1333075 | 133.3075 | 13587466 | 234820.56 | 329477112 | 99484573 | 49945778 | 0.000000 | 20563799 | 19591656 | 0.000000
09-04-2025 16:53:50000 | -1336473 | 133.6473 | 14076838 | 234838.88 | 330410522 | 99449875 | 49977188 | 0.000000 | 20757622 | 19777473 | 0.000000
09-04-2025 16:53:55000 | -1340108 | 134.0108 | 14002366 | 234747.08 | 331410187 | 99458557 | 49985931 | 0.000000 | 20954119 | 19963695 | 0.000000
09-04-2025 16:54:00000 | -1342679 | 134.2679 | 13987676 | 234770.47 | 332004669 | 99461731 | 49983498 | 0.000000 | 21148728 | 20150000 | 0.000000
09-04-2025 16:54:05000 | -1343328 | 134.3328 | 14022063 | 234817.30 | 332101959 | 99459618 | 49971542 | 0.000000 | 21342683 | 20336367 | 0.000000
09-04-2025 16:54:10000 | -1342552 | 134.2552 | 13992614 | 234818.52 | 331906250 | 99461250 | 49966404 | 0.000000 | 21537141 | 20522660 | 0.000000
09-04-2025 16:54:15000 | -1337863 | 133.7863 | 14518246 | 235060.11 | 330551025 | 99416336 | 50014027 | 0.000000 | 21734189 | 20708373 | 0.000000
09-04-2025 16:54:20000 | -1346229 | 134.6229 | 15126866 | 235019.13 | 332814087 | 99374626 | 50074345 | 0.000000 | 21941130 | 20894586 | 0.000000
09-04-2025 16:54:25000 | -1346435 | 134.6435 | 15015581 | 234976.13 | 332895325 | 99383896 | 50060101 | 0.000000 | 22150820 | 21081662 | 0.000000
09-04-2025 16:54:30000 | -1339726 | 133.9726 | 14742012 | 234967.91 | 331205231 | 99400032 | 50054638 | 0.000000 | 22358987 | 21268459 | 0.000000
09-04-2025 16:54:35000 | -1338641 | 133.8641 | 14820258 | 235015.17 | 330885559 | 99392731 | 50050724 | 0.000000 | 22565935 | 21454949 | 0.000000
09-04-2025 16:54:40000 | -1346282 | 134.6282 | 15046611 | 235006.66 | 332830719 | 99381226 | 50038078 | 0.000000 | 22773621 | 21641791 | 0.000000
09-04-2025 16:54:45000 | -1345130 | 134.513 | 15029722 | 235007.17 | 332535950 | 99381554 | 50026081 | 0.000000 | 22982285 | 21828586 | 0.000000
09-04-2025 16:54:50000 | -1347406 | 134.7406 | 15160811 | 235052.98 | 333063568 | 99372925 | 50044113 | 0.000000 | 23191274 | 22015375 | 0.000000
09-04-2025 16:54:55000 | -1341371 | 134.1371 | 14890580 | 235009.86 | 331581390 | 99389473 | 50031551 | 0.000000 | 23399873 | 22202152 | 0.000000
09-04-2025 16:55:00000 | -1342695 | 134.2695 | 14927115 | 235043.25 | 331864105 | 99387703 | 50036697 | 0.000000 | 23608323 | 22389084 | 0.000000
09-04-2025 16:55:05000 | -1347877 | 134.7877 | 15201983 | 235039.69 | 333209961 | 99369987 | 50053646 | 0.000000 | 23818303 | 22575955 | 0.000000
09-04-2025 16:55:10000 | -1348933 | 134.8933 | 15048656 | 234948.89 | 333557983 | 99383469 | 50030693 | 0.000000 | 24028420 | 22763230 | 0.000000
09-04-2025 16:55:15000 | -1341462 | 134.1462 | 14417490 | 234902.30 | 331635376 | 99427399 | 49992615 | 0.000000 | 24234055 | 22950543 | 0.000000
09-04-2025 16:55:20000 | -1346835 | 134.6835 | 14425663 | 234856.55 | 333007385 | 99431282 | 49974850 | 0.000000 | 24434807 | 23137570 | 0.000000
09-04-2025 16:55:25000 | -1339925 | 133.9925 | 14588040 | 235050.00 | 331086456 | 99412560 | 49994949 | 0.000000 | 24635940 | 23324156 | 0.000000
09-04-2025 16:55:30000 | -1345080 | 134.508 | 15071423 | 235036.53 | 332494690 | 99378105 | 50046738 | 0.000000 | 24843474 | 23510588 | 0.000000
09-04-2025 16:55:35000 | -1345189 | 134.5189 | 14928273 | 234957.66 | 332597137 | 99389854 | 50052048 | 0.000000 | 25052798 | 23697459 | 0.000000
09-04-2025 16:55:40000 | -1343545 | 134.3545 | 14823505 | 235003.67 | 332098755 | 99396851 | 50037495 | 0.000000 | 25259836 | 23884441 | 0.000000
09-04-2025 16:55:45000 | -1349692 | 134.9692 | 14946682 | 234975.58 | 333675262 | 99392403 | 50045048 | 0.000000 | 25466094 | 24071213 | 0.000000
09-04-2025 16:55:50000 | -1344808 | 134.4808 | 15135929 | 235101.89 | 332351990 | 99372574 | 50068695 | 0.000000 | 25674661 | 24258092 | 0.000000
09-04-2025 16:55:55000 | -1351780 | 135.178 | 15311534 | 235006.98 | 334244873 | 99364609 | 50086716 | 0.000000 | 25887097 | 24445254 | 0.000000
09-04-2025 16:56:00000 | -1348218 | 134.8218 | 14978786 | 234984.30 | 333311218 | 99388489 | 50051609 | 0.000000 | 26096921 | 24632904 | 0.000000
09-04-2025 16:56:05000 | -1347745 | 134.7745 | 15029117 | 235042.89 | 333122833 | 99383980 | 50056194 | 0.000000 | 26304878 | 24820189 | 0.000000
09-04-2025 16:56:10000 | -1345276 | 134.5276 | 14988415 | 235061.63 | 332484650 | 99385056 | 50073299 | 0.000000 | 26513821 | 25007416 | 0.000000
09-04-2025 16:56:15000 | -1350173 | 135.0173 | 15378955 | 235090.33 | 333744843 | 99357544 | 50097687 | 0.000000 | 26725249 | 25194533 | 0.000000
09-04-2025 16:56:20000 | -1346879 | 134.6879 | 15123653 | 235080.75 | 332890656 | 99375488 | 50082481 | 0.000000 | 26938054 | 25382244 | 0.000000
09-04-2025 16:56:25000 | -1352689 | 135.2689 | 15533701 | 235145.69 | 334321442 | 99347092 | 50114201 | 0.000000 | 27150354 | 25569508 | 0.000000
09-04-2025 16:56:30000 | -1351780 | 135.178 | 15454614 | 235068.52 | 334191650 | 99352791 | 50101768 | 0.000000 | 27364819 | 25757014 | 0.000000
09-04-2025 16:56:35000 | -1346308 | 134.6308 | 15217471 | 235079.55 | 332775024 | 99367256 | 50084721 | 0.000000 | 27578323 | 25944674 | 0.000000
09-04-2025 16:56:40000 | -1348545 | 134.8545 | 15138881 | 235040.22 | 333350708 | 99375771 | 50071651 | 0.000000 | 27788623 | 26132006 | 0.000000
09-04-2025 16:56:45000 | -1353304 | 135.3304 | 15250555 | 235030.05 | 334562469 | 99371017 | 50075878 | 0.000000 | 27998491 | 26319227 | 0.000000
09-04-2025 16:56:50000 | -1351040 | 135.104 | 15138652 | 235010.36 | 334005493 | 99378067 | 50057049 | 0.000000 | 28209124 | 26506848 | 0.000000
09-04-2025 16:56:55000 | -1350040 | 135.004 | 15037979 | 235006.47 | 333737671 | 99385338 | 50063389 | 0.000000 | 28417954 | 26694299 | 0.000000
09-04-2025 16:57:00000 | -1349464 | 134.9464 | 15172179 | 235067.88 | 333548889 | 99373894 | 50075825 | 0.000000 | 28628103 | 26881783 | 0.000000
09-04-2025 16:57:05000 | -1352256 | 135.2256 | 15124315 | 234988.19 | 334325653 | 99380341 | 50065277 | 0.000000 | 28839846 | 27069721 | 0.000000
09-04-2025 16:57:10000 | -1351012 | 135.1012 | 14994218 | 235032.56 | 333924530 | 99389748 | 50062763 | 0.000000 | 29048108 | 27257418 | 0.000000
09-04-2025 16:57:15000 | -1350641 | 135.0641 | 15306192 | 235082.95 | 333850128 | 99363991 | 50084064 | 0.000000 | 29258379 | 27444963 | 0.000000
09-04-2025 16:57:20000 | -1354279 | 135.4279 | 15242607 | 235013.22 | 334819366 | 99372566 | 50084438 | 0.000000 | 29470781 | 27632838 | 0.000000
09-04-2025 16:57:25000 | -1353210 | 135.321 | 15203373 | 235044.27 | 334500793 | 99374779 | 50073399 | 0.000000 | 29681091 | 27820617 | 0.000000
09-04-2025 16:57:30000 | -1346606 | 134.6606 | 15178439 | 235050.27 | 332879852 | 99370743 | 50086655 | 0.000000 | 29893037 | 28008162 | 0.000000
09-04-2025 16:57:35000 | -1353242 | 135.3242 | 15115255 | 234979.00 | 334583771 | 99381973 | 50057240 | 0.000000 | 30104480 | 28196377 | 0.000000
09-04-2025 16:57:40000 | -1351190 | 135.119 | 14970330 | 235040.78 | 333955658 | 99391830 | 50054974 | 0.000000 | 30312126 | 28383773 | 0.000000
09-04-2025 16:57:45000 | -1351282 | 135.1282 | 14850940 | 234963.11 | 334053162 | 99401489 | 50044231 | 0.000000 | 30520229 | 28571463 | 0.000000
09-04-2025 16:57:50000 | -1349937 | 134.9937 | 14945782 | 235016.47 | 333672272 | 99392693 | 50050343 | 0.000000 | 30727251 | 28758951 | 0.000000
09-04-2025 16:57:55000 | -1351549 | 135.1549 | 14444002 | 234807.63 | 334232391 | 99433784 | 50003590 | 0.000000 | 30931638 | 28946840 | 0.000000
09-04-2025 16:58:00000 | -1343211 | 134.3211 | 14366909 | 234966.33 | 331951813 | 99432846 | 50016872 | 0.000000 | 31131177 | 29133904 | 0.000000
09-04-2025 16:58:05000 | -1350452 | 135.0452 | 14770978 | 234910.09 | 333902527 | 99407135 | 50036507 | 0.000000 | 31335862 | 29321449 | 0.000000
09-04-2025 16:58:10000 | -1352492 | 135.2492 | 14869882 | 234951.91 | 334371307 | 99401039 | 50042606 | 0.000000 | 31540327 | 29508705 | 0.000000
09-04-2025 16:58:15000 | -1353430 | 135.343 | 14876464 | 234946.86 | 334612244 | 99401337 | 50044491 | 0.000000 | 31746633 | 29696471 | 0.000000
09-04-2025 16:58:20000 | -1348998 | 134.8998 | 14493975 | 234870.58 | 333534241 | 99427757 | 50022942 | 0.000000 | 31950022 | 29884199 | 0.000000
09-04-2025 16:58:25000 | -1345299 | 134.5299 | 14392652 | 234948.30 | 332489288 | 99432579 | 50052414 | 0.000000 | 32150686 | 30071342 | 0.000000
09-04-2025 16:58:30000 | -1353435 | 135.3435 | 14647267 | 234858.44 | 334676575 | 99419487 | 50066467 | 0.000000 | 32355405 | 30259152 | 0.000000
09-04-2025 16:58:35000 | -1348828 | 134.8828 | 14451034 | 234896.19 | 333441620 | 99430969 | 50047359 | 0.000000 | 32557249 | 30447098 | 0.000000
09-04-2025 16:58:40000 | -1349032 | 134.9032 | 14579083 | 234927.05 | 333485291 | 99421104 | 50054840 | 0.000000 | 32758613 | 30634420 | 0.000000
09-04-2025 16:58:45000 | -1348278 | 134.8278 | 14500481 | 234902.92 | 333314026 | 99426636 | 50053680 | 0.000000 | 32961172 | 30821910 | 0.000000
09-04-2025 16:58:50000 | -1353390 | 135.339 | 14778316 | 234907.97 | 334626373 | 99409103 | 50064095 | 0.000000 | 33165789 | 31009512 | 0.000000
09-04-2025 16:58:55000 | -1346924 | 134.6924 | 14565820 | 234934.08 | 332953918 | 99420349 | 50052498 | 0.000000 | 33369043 | 31196867 | 0.000000
09-04-2025 16:59:00000 | -1353042 | 135.3042 | 14691240 | 234878.95 | 334562347 | 99415688 | 50044579 | 0.000000 | 33572568 | 31384553 | 0.000000
09-04-2025 16:59:05000 | -1352455 | 135.2455 | 14620639 | 234859.03 | 334429810 | 99420746 | 50042488 | 0.000000 | 33775435 | 31572086 | 0.000000
09-04-2025 16:59:10000 | -1351083 | 135.1083 | 14243599 | 234784.77 | 334107239 | 99448883 | 50009342 | 0.000000 | 33974949 | 31759863 | 0.000000
09-04-2025 16:59:15000 | -1350102 | 135.0102 | 14426951 | 234870.33 | 333788574 | 99433907 | 50008793 | 0.000000 | 34174321 | 31947385 | 0.000000
09-04-2025 16:59:20000 | -1350079 | 135.0079 | 14690887 | 234954.95 | 333726654 | 99413170 | 50050701 | 0.000000 | 34375112 | 32134383 | 0.000000
09-04-2025 16:59:25000 | -1352330 | 135.233 | 14657227 | 234878.77 | 334378540 | 99417763 | 50032024 | 0.000000 | 34579683 | 32322172 | 0.000000
09-04-2025 16:59:30000 | -1351607 | 135.1607 | 14530147 | 234848.30 | 334213501 | 99427116 | 50005455 | 0.000000 | 34782432 | 32509898 | 0.000000
09-04-2025 16:59:35000 | -1347720 | 134.772 | 14398211 | 234888.72 | 333169708 | 99434166 | 50007294 | 0.000000 | 34982344 | 32697139 | 0.000000
09-04-2025 16:59:40000 | -1349864 | 134.9864 | 14683845 | 234929.66 | 333712036 | 99413544 | 50031494 | 0.000000 | 35184177 | 32884348 | 0.000000
09-04-2025 16:59:45000 | -1349757 | 134.9757 | 14535764 | 234887.36 | 333710602 | 99425117 | 50029701 | 0.000000 | 35386499 | 33071410 | 0.000000
09-04-2025 16:59:50000 | -1344719 | 134.4719 | 14614660 | 234957.44 | 332394745 | 99414597 | 50036644 | 0.000000 | 35588547 | 33258289 | 0.000000
09-04-2025 16:59:55000 | -1351045 | 135.1045 | 15056935 | 235008.17 | 333989594 | 99384712 | 50079826 | 0.000000 | 35794607 | 33445285 | 0.000000
09-04-2025 17:00:00000 | -1352616 | 135.2616 | 15123085 | 234956.25 | 334460632 | 99380768 | 50068428 | 0.000000 | 36005542 | 33632938 | 0.000000
09-04-2025 17:00:05000 | -1348154 | 134.8154 | 14810144 | 234985.02 | 333244690 | 99402000 | 50030945 | 0.000000 | 20764811 | 187779999 | 0.000000
09-04-2025 17:00:10000 | -1347472 | 134.7472 | 14826488 | 235006.97 | 333055176 | 99400093 | 50035969 | 0.000000 | 41420143 | 375197418 | 0.000000
09-04-2025 17:00:15000 | -1350155 | 135.0155 | 14984236 | 235009.19 | 333751831 | 99389786 | 50037544 | 0.000000 | 62198288 | 562692017 | 0.000000
09-04-2025 17:00:20000 | -1350207 | 135.0207 | 14787723 | 234914.17 | 333841278 | 99405594 | 50028023 | 0.000000 | 82856644 | 750356995 | 0.000000
09-04-2025 17:00:25000 | -1346064 | 134.6064 | 14406941 | 234865.64 | 332797791 | 99432098 | 50001266 | 0.000000 | 103116180 | 937778442 | 0.000000
09-04-2025 17:00:30000 | -1341915 | 134.1915 | 14314765 | 234915.22 | 331694153 | 99435844 | 49997818 | 0.000000 | 123005653 | 11245089 | 0.000000
09-04-2025 17:00:35000 | -1335949 | 133.5949 | 14635217 | 235080.59 | 330087616 | 99405296 | 50033772 | 0.000000 | 143255112 | 13111559 | 0.000000
09-04-2025 17:00:40000 | -1350456 | 135.0456 | 15075624 | 234948.27 | 333935150 | 99382660 | 50048454 | 0.000000 | 164135559 | 14984064 | 0.000000
09-04-2025 17:00:45000 | -1354960 | 135.496 | 14347537 | 234675.69 | 335231110 | 99444046 | 49985527 | 0.000000 | 184543518 | 16863057 | 0.000000
09-04-2025 17:00:50000 | -1344683 | 134.4683 | 13495802 | 234696.89 | 332471344 | 99500122 | 49907524 | 0.000000 | 203707016 | 18737928 | 0.000000
09-04-2025 17:00:55000 | -1341543 | 134.1543 | 13686656 | 234799.53 | 331609558 | 99483604 | 49938335 | 0.000000 | 222534439 | 20600000 | 0.000000
09-04-2025 17:01:00000 | -1343035 | 134.3035 | 14255588 | 234868.38 | 332021545 | 99441383 | 49992844 | 0.000000 | 242054520 | 22462700 | 0.000000
09-04-2025 17:01:05000 | -1347309 | 134.7309 | 14486522 | 234893.91 | 333084869 | 99426918 | 49997765 | 0.000000 | 261999695 | 24332031 | 0.000000
09-04-2025 17:01:10000 | -1344860 | 134.486 | 14414146 | 234896.16 | 332464050 | 99430527 | 49998569 | 0.000000 | 281977966 | 26201096 | 0.000000
09-04-2025 17:01:15000 | -1342120 | 134.212 | 14534142 | 234936.23 | 331773956 | 99418747 | 50012482 | 0.000000 | 302211365 | 28070430 | 0.000000
09-04-2025 17:01:20000 | -1345713 | 134.5713 | 14540682 | 234896.50 | 332705322 | 99421303 | 50021103 | 0.000000 | 322499603 | 29940098 | 0.000000
09-04-2025 17:01:25000 | -1349739 | 134.9739 | 14886703 | 234984.86 | 333661041 | 99397263 | 50033356 | 0.000000 | 342881592 | 31807268 | 0.000000
09-04-2025 17:01:30000 | -1345158 | 134.5158 | 14795281 | 234955.09 | 332555481 | 99400551 | 50027027 | 0.000000 | 363670990 | 33679978 | 0.000000
09-04-2025 17:01:35000 | -1351454 | 135.1454 | 14798241 | 234884.03 | 334196716 | 99405838 | 50010674 | 0.000000 | 384249390 | 35553901 | 0.000000
09-04-2025 17:01:40000 | -1350947 | 135.0947 | 14607044 | 234877.39 | 334033569 | 99420532 | 49975594 | 0.000000 | 404601257 | 37428303 | 0.000000
09-04-2025 17:01:45000 | -1347458 | 134.7458 | 14181131 | 234770.16 | 333214172 | 99450745 | 49937366 | 0.000000 | 424613037 | 39302668 | 0.000000
09-04-2025 17:01:50000 | -1345046 | 134.5046 | 14176635 | 234804.39 | 332581696 | 99449142 | 49936066 | 0.000000 | 444258087 | 41169502 | 0.000000
09-04-2025 17:01:55000 | -1341100 | 134.11 | 13761357 | 234723.03 | 331624207 | 99477654 | 49912968 | 0.000000 | 463647888 | 43034863 | 0.000000
09-04-2025 17:02:00000 | -1343909 | 134.3909 | 13745664 | 234695.73 | 332346008 | 99480995 | 49901333 | 0.000000 | 482746521 | 44902051 | 0.000000
09-04-2025 17:02:05000 | -1343537 | 134.3537 | 13612535 | 234682.30 | 332242615 | 99490646 | 49896065 | 0.000000 | 501578400 | 46763813 | 0.000000
09-04-2025 17:02:10000 | -1340738 | 134.0738 | 13645727 | 234702.48 | 331534088 | 99486053 | 49918114 | 0.000000 | 520460571 | 48623242 | 0.000000
09-04-2025 17:02:15000 | -1342335 | 134.2335 | 13823033 | 234710.86 | 331957520 | 99473961 | 49921043 | 0.000000 | 539578064 | 50485332 | 0.000000
09-04-2025 17:02:20000 | -1338188 | 133.8188 | 13658895 | 234762.75 | 330834808 | 99483124 | 49922279 | 0.000000 | 558670837 | 52345566 | 0.000000
09-04-2025 17:02:25000 | -1344775 | 134.4775 | 13960497 | 234731.86 | 332558899 | 99465462 | 49899067 | 0.000000 | 578092590 | 54213687 | 0.000000
09-04-2025 17:02:30000 | -1342285 | 134.2285 | 13830485 | 234766.11 | 331867279 | 99473358 | 49895626 | 0.000000 | 597351624 | 56078330 | 0.000000
09-04-2025 17:02:35000 | -1340588 | 134.0588 | 13897372 | 234797.89 | 331421570 | 99466957 | 49916672 | 0.000000 | 616633667 | 57941099 | 0.000000
09-04-2025 17:02:40000 | -1340690 | 134.069 | 14050844 | 234864.69 | 331393341 | 99455299 | 49937164 | 0.000000 | 636100952 | 59804663 | 0.000000
09-04-2025 17:02:45000 | -1342414 | 134.2414 | 14199654 | 234836.83 | 331897705 | 99445213 | 49952438 | 0.000000 | 655747131 | 61669507 | 0.000000
09-04-2025 17:02:50000 | -1338986 | 133.8986 | 14105854 | 234875.70 | 330976471 | 99449677 | 49964851 | 0.000000 | 675476135 | 63534399 | 0.000000
09-04-2025 17:02:55000 | -1348565 | 134.8565 | 14301952 | 234777.63 | 333511597 | 99442337 | 49954128 | 0.000000 | 695280823 | 65401392 | 0.000000
09-04-2025 17:03:00000 | -1344535 | 134.4535 | 14239344 | 234890.64 | 332343170 | 99443878 | 49947044 | 0.000000 | 714992126 | 67267593 | 0.000000
09-04-2025 17:03:05000 | -1345764 | 134.5764 | 14237478 | 234847.17 | 332708099 | 99445030 | 49949200 | 0.000000 | 734833557 | 69135181 | 0.000000
09-04-2025 17:03:10000 | -1343213 | 134.3213 | 14094015 | 234813.98 | 332105225 | 99454018 | 49936913 | 0.000000 | 754530334 | 71003369 | 0.000000
09-04-2025 17:03:15000 | -1341756 | 134.1756 | 14081907 | 234795.41 | 331764343 | 99453766 | 49931389 | 0.000000 | 774094238 | 72866553 | 0.000000
09-04-2025 17:03:20000 | -1343092 | 134.3092 | 14093713 | 234803.67 | 332084412 | 99453941 | 49936394 | 0.000000 | 793629822 | 74729482 | 0.000000
09-04-2025 17:03:25000 | -1344798 | 134.4798 | 13868104 | 234710.11 | 332572693 | 99472473 | 49910610 | 0.000000 | 813035217 | 76595928 | 0.000000
09-04-2025 17:03:30000 | -1339370 | 133.937 | 13691118 | 234767.23 | 331124298 | 99481606 | 49894634 | 0.000000 | 832205872 | 78460400 | 0.000000
09-04-2025 17:03:35000 | -1342380 | 134.238 | 14098118 | 234816.19 | 331892029 | 99453026 | 49925823 | 0.000000 | 851539734 | 80320366 | 0.000000
09-04-2025 17:03:40000 | -1340004 | 134.0004 | 14004016 | 234813.53 | 331286926 | 99458344 | 49924328 | 0.000000 | 871106750 | 82183428 | 0.000000
09-04-2025 17:03:45000 | -1343737 | 134.3737 | 14185166 | 234770.50 | 332312378 | 99447418 | 49933331 | 0.000000 | 890844666 | 84048467 | 0.000000
09-04-2025 17:03:50000 | -1342267 | 134.2267 | 14204871 | 234849.67 | 331840485 | 99444687 | 49926071 | 0.000000 | 910503723 | 85912529 | 0.000000
09-04-2025 17:03:55000 | -1338798 | 133.8798 | 14273205 | 234913.09 | 330923645 | 99436493 | 49957458 | 0.000000 | 930256958 | 87773262 | 0.000000
09-04-2025 17:04:00000 | -1347820 | 134.782 | 14488189 | 234816.23 | 333320831 | 99427216 | 49940918 | 0.000000 | 950313293 | 89641992 | 0.000000
09-04-2025 17:04:05000 | -1341515 | 134.1515 | 14260379 | 234856.83 | 331664459 | 99439751 | 49924358 | 0.000000 | 970152161 | 91506113 | 0.000000
09-04-2025 17:04:10000 | -1341278 | 134.1278 | 14265714 | 234908.48 | 331536255 | 99439140 | 49935047 | 0.000000 | 989904907 | 93367861 | 0.000000
09-04-2025 17:04:15000 | -1341107 | 134.1107 | 14058156 | 234744.70 | 331674316 | 99455070 | 49910805 | 0.000000 | 10096582 | 95232725 | 0.000000
09-04-2025 17:04:20000 | -1336414 | 133.6414 | 13998520 | 234856.78 | 330349182 | 99455879 | 49901966 | 0.000000 | 10290027 | 97089990 | 0.000000
09-04-2025 17:04:25000 | -1337382 | 133.7382 | 14247608 | 234874.67 | 330620697 | 99437317 | 49914101 | 0.000000 | 10487311 | 98950068 | 0.000000
09-04-2025 17:04:30000 | -1340777 | 134.0777 | 14250518 | 234829.36 | 331521851 | 99439911 | 49912731 | 0.000000 | 10685558 | 10081150 | 0.000000
09-04-2025 17:04:35000 | -1340804 | 134.0804 | 14077178 | 234749.52 | 331594635 | 99453362 | 49891949 | 0.000000 | 10881578 | 10267389 | 0.000000
09-04-2025 17:04:40000 | -1344024 | 134.4024 | 13937025 | 234741.50 | 332359924 | 99466652 | 49854927 | 0.000000 | 11075339 | 10453699 | 0.000000
09-04-2025 17:04:45000 | -1338031 | 133.8031 | 13819104 | 234798.73 | 330777557 | 99470894 | 49854332 | 0.000000 | 11266554 | 10639469 | 0.000000
09-04-2025 17:04:50000 | -1332415 | 133.2415 | 13931988 | 234883.39 | 329316650 | 99457779 | 49877014 | 0.000000 | 11459363 | 10824937 | 0.000000
09-04-2025 17:04:55000 | -1340799 | 134.0799 | 14170547 | 234772.95 | 331578857 | 99446144 | 49870892 | 0.000000 | 11656880 | 11011173 | 0.000000
09-04-2025 17:05:00000 | -1333245 | 133.3245 | 13961112 | 234901.80 | 329498444 | 99456200 | 49878365 | 0.000000 | 11849967 | 11196599 | 0.000000
09-04-2025 17:05:05000 | -1342081 | 134.2081 | 14715724 | 234975.09 | 331757202 | 99404228 | 49940178 | 0.000000 | 12049700 | 11382148 | 0.000000
09-04-2025 17:05:10000 | -1348180 | 134.818 | 14658323 | 234836.27 | 333424774 | 99414116 | 49926720 | 0.000000 | 12253423 | 11568748 | 0.000000
09-04-2025 17:05:15000 | -1340997 | 134.0997 | 14230870 | 234891.14 | 331478851 | 99441620 | 49907433 | 0.000000 | 12452765 | 11755151 | 0.000000
09-04-2025 17:05:20000 | -1342576 | 134.2576 | 14373508 | 234872.00 | 331926270 | 99431793 | 49927216 | 0.000000 | 12651803 | 11941365 | 0.000000
09-04-2025 17:05:25000 | -1341388 | 134.1388 | 14334253 | 234910.47 | 331579254 | 99433876 | 49915676 | 0.000000 | 12850610 | 12127734 | 0.000000
09-04-2025 17:05:30000 | -1338822 | 133.8822 | 14519197 | 234991.44 | 330880432 | 99417091 | 49943481 | 0.000000 | 13050908 | 12313760 | 0.000000
09-04-2025 17:05:35000 | -1345222 | 134.5222 | 14904947 | 234973.86 | 332575378 | 99391769 | 49957912 | 0.000000 | 13256080 | 12500254 | 0.000000
09-04-2025 17:05:40000 | -1346183 | 134.6183 | 15080021 | 235024.02 | 332791016 | 99378410 | 49974209 | 0.000000 | 13463796 | 12686785 | 0.000000
09-04-2025 17:05:45000 | -1347079 | 134.7079 | 14907724 | 234951.91 | 333062225 | 99393211 | 49963402 | 0.000000 | 13671036 | 12873626 | 0.000000
09-04-2025 17:05:50000 | -1347040 | 134.704 | 14697092 | 234912.11 | 333054565 | 99410049 | 49941570 | 0.000000 | 13875507 | 13060483 | 0.000000
09-04-2025 17:05:55000 | -1333633 | 133.3633 | 14586967 | 235122.58 | 329448761 | 99407143 | 49940197 | 0.000000 | 14077714 | 13246741 | 0.000000
09-04-2025 17:06:00000 | -1339703 | 133.9703 | 15257230 | 235119.17 | 331119873 | 99357750 | 50007671 | 0.000000 | 14286057 | 13432522 | 0.000000
09-04-2025 17:06:05000 | -1346108 | 134.6108 | 15653434 | 235153.45 | 332743439 | 99330650 | 50028629 | 0.000000 | 14501088 | 13619164 | 0.000000
09-04-2025 17:06:10000 | -1346259 | 134.6259 | 15495551 | 235096.56 | 332819183 | 99344101 | 50016884 | 0.000000 | 14717108 | 13806200 | 0.000000
09-04-2025 17:06:15000 | -1349602 | 134.9602 | 15544387 | 235094.50 | 333648163 | 99343231 | 50007717 | 0.000000 | 14933152 | 13993439 | 0.000000
09-04-2025 17:06:20000 | -1347357 | 134.7357 | 15101184 | 234980.81 | 333139740 | 99377762 | 49962460 | 0.000000 | 15144763 | 14180621 | 0.000000
09-04-2025 17:06:25000 | -1343123 | 134.3123 | 14863661 | 235028.11 | 331973999 | 99393234 | 49933170 | 0.000000 | 15351694 | 14367473 | 0.000000
09-04-2025 17:06:30000 | -1343387 | 134.3387 | 14957000 | 235013.14 | 332086182 | 99385895 | 49922363 | 0.000000 | 15559227 | 14554116 | 0.000000
09-04-2025 17:06:35000 | -1344637 | 134.4637 | 14799444 | 234937.73 | 332450897 | 99399757 | 49904076 | 0.000000 | 15765378 | 14740697 | 0.000000
09-04-2025 17:06:40000 | -1337327 | 133.7327 | 14639211 | 235035.55 | 330485382 | 99406189 | 49907417 | 0.000000 | 15969025 | 14926682 | 0.000000
09-04-2025 17:06:45000 | -1339167 | 133.9167 | 14834937 | 235026.75 | 331002350 | 99392006 | 49922043 | 0.000000 | 16174636 | 15112601 | 0.000000
09-04-2025 17:06:50000 | -1342348 | 134.2348 | 14924022 | 235029.44 | 331798126 | 99387634 | 49920425 | 0.000000 | 16381125 | 15298575 | 0.000000
09-04-2025 17:06:55000 | -1338843 | 133.8843 | 15091311 | 235084.11 | 330909637 | 99370712 | 49946365 | 0.000000 | 16590419 | 15484629 | 0.000000
09-04-2025 17:07:00000 | -1346233 | 134.6233 | 15011263 | 234974.44 | 332844788 | 99384064 | 49934952 | 0.000000 | 16798907 | 15670977 | 0.000000
09-04-2025 17:07:05000 | -1342699 | 134.2699 | 14903709 | 234957.53 | 331976868 | 99389603 | 49905788 | 0.000000 | 17006466 | 15857478 | 0.000000
09-04-2025 17:07:10000 | -1339815 | 133.9815 | 14838392 | 235058.20 | 331124573 | 99392311 | 49921558 | 0.000000 | 17212128 | 16043630 | 0.000000
09-04-2025 17:07:15000 | -1341695 | 134.1695 | 14965360 | 235037.23 | 331645020 | 99383675 | 49931870 | 0.000000 | 17420042 | 16229883 | 0.000000
09-04-2025 17:07:20000 | -1340268 | 134.0268 | 14727100 | 234960.00 | 331334961 | 99401711 | 49923580 | 0.000000 | 17625995 | 16416109 | 0.000000
09-04-2025 17:07:25000 | -1339227 | 133.9227 | 14514188 | 234912.66 | 331089142 | 99417839 | 49908382 | 0.000000 | 17829608 | 16602498 | 0.000000
09-04-2025 17:07:30000 | -1338977 | 133.8977 | 14412462 | 234862.34 | 331078339 | 99425690 | 49888618 | 0.000000 | 18030117 | 16788682 | 0.000000
09-04-2025 17:07:35000 | -1334125 | 133.4125 | 14296528 | 234955.06 | 329728210 | 99430733 | 49893398 | 0.000000 | 18229097 | 16974377 | 0.000000
09-04-2025 17:07:40000 | -1341619 | 134.1619 | 14720675 | 234962.59 | 331663269 | 99403419 | 49906570 | 0.000000 | 18431180 | 17160164 | 0.000000
09-04-2025 17:07:45000 | -1337848 | 133.7848 | 14532944 | 234974.23 | 330673065 | 99415154 | 49923599 | 0.000000 | 18632926 | 17345684 | 0.000000
09-04-2025 17:07:50000 | -1339209 | 133.9209 | 14833768 | 235037.88 | 330995575 | 99392143 | 49946613 | 0.000000 | 18836337 | 17531391 | 0.000000
09-04-2025 17:07:55000 | -1343121 | 134.3121 | 14824618 | 234935.25 | 332090851 | 99396385 | 49951946 | 0.000000 | 19042059 | 17717434 | 0.000000
09-04-2025 17:08:00000 | -1336308 | 133.6308 | 14601956 | 234996.59 | 330281464 | 99408287 | 49952991 | 0.000000 | 19245580 | 17903371 | 0.000000
09-04-2025 17:08:05000 | -1339185 | 133.9185 | 14920922 | 235014.86 | 331045746 | 99385025 | 49975849 | 0.000000 | 19451898 | 18089297 | 0.000000
09-04-2025 17:08:10000 | -1342073 | 134.2073 | 14853154 | 235005.20 | 331746368 | 99393143 | 49973568 | 0.000000 | 19657537 | 18275371 | 0.000000
09-04-2025 17:08:15000 | -1338443 | 133.8443 | 14818257 | 235019.17 | 330828186 | 99392715 | 49964653 | 0.000000 | 19864606 | 18461523 | 0.000000
09-04-2025 17:08:20000 | -1337483 | 133.7483 | 14941436 | 235072.84 | 330549774 | 99381790 | 49975471 | 0.000000 | 20071166 | 18647291 | 0.000000
09-04-2025 17:08:25000 | -1339775 | 133.9775 | 14885236 | 235005.91 | 331189178 | 99388466 | 49971783 | 0.000000 | 20278854 | 18833352 | 0.000000
09-04-2025 17:08:30000 | -1341436 | 134.1436 | 14857909 | 234971.97 | 331636566 | 99392181 | 49957146 | 0.000000 | 20485815 | 19019611 | 0.000000
09-04-2025 17:08:35000 | -1338548 | 133.8548 | 14721161 | 234976.34 | 330885468 | 99400665 | 49943623 | 0.000000 | 20690205 | 19205545 | 0.000000
09-04-2025 17:08:40000 | -1337029 | 133.7029 | 14725311 | 235030.70 | 330440582 | 99398979 | 49957462 | 0.000000 | 20893591 | 19391105 | 0.000000
09-04-2025 17:08:45000 | -1336402 | 133.6402 | 14761357 | 235018.13 | 330317047 | 99395500 | 49973869 | 0.000000 | 21099485 | 19576865 | 0.000000
09-04-2025 17:08:50000 | -1333168 | 133.3168 | 14672763 | 235024.81 | 329495331 | 99399796 | 49963520 | 0.000000 | 21304094 | 19762537 | 0.000000
09-04-2025 17:08:55000 | -1337197 | 133.7197 | 14766274 | 234942.48 | 330620514 | 99395813 | 49952782 | 0.000000 | 21508862 | 19948002 | 0.000000
09-04-2025 17:09:00000 | -1335527 | 133.5527 | 14374303 | 234904.34 | 330159271 | 99425774 | 49919540 | 0.000000 | 21710598 | 20133854 | 0.000000
09-04-2025 17:09:05000 | -1335372 | 133.5372 | 14313282 | 234915.83 | 330095642 | 99430466 | 49921734 | 0.000000 | 21909858 | 20319230 | 0.000000
09-04-2025 17:09:10000 | -1333601 | 133.3601 | 14483578 | 234956.09 | 329649017 | 99415413 | 49938236 | 0.000000 | 22110540 | 20504404 | 0.000000
09-04-2025 17:09:15000 | -1330009 | 133.0009 | 14446451 | 234969.13 | 328741302 | 99415260 | 49939091 | 0.000000 | 22312737 | 20689611 | 0.000000
09-04-2025 17:09:20000 | -1333315 | 133.3315 | 14599884 | 234984.17 | 329567566 | 99405815 | 49935883 | 0.000000 | 22515515 | 20874895 | 0.000000
09-04-2025 17:09:25000 | -1329633 | 132.9633 | 14733551 | 235090.30 | 328558685 | 99391663 | 49969055 | 0.000000 | 22717368 | 21059342 | 0.000000
09-04-2025 17:09:30000 | -1334696 | 133.4696 | 14798843 | 234964.42 | 329984619 | 99390915 | 49952969 | 0.000000 | 22923137 | 21244570 | 0.000000
09-04-2025 17:09:35000 | -1336507 | 133.6507 | 14819863 | 235011.89 | 330374329 | 99390839 | 49934196 | 0.000000 | 23126541 | 21429711 | 0.000000
09-04-2025 17:09:40000 | -1333637 | 133.3637 | 14805941 | 234964.53 | 329731201 | 99389374 | 49921013 | 0.000000 | 23334326 | 21615064 | 0.000000
09-04-2025 17:09:45000 | -1333728 | 133.3728 | 14701913 | 234994.09 | 329682404 | 99397926 | 49911034 | 0.000000 | 23538672 | 21800352 | 0.000000
09-04-2025 17:09:50000 | -1332512 | 133.2512 | 14618469 | 234993.88 | 329363556 | 99403603 | 49905617 | 0.000000 | 23741709 | 21985422 | 0.000000
09-04-2025 17:09:55000 | -1335850 | 133.585 | 14636873 | 234911.13 | 330300293 | 99405075 | 49887085 | 0.000000 | 23946367 | 22171000 | 0.000000
09-04-2025 17:10:00000 | -1337162 | 133.7162 | 14492766 | 234912.48 | 330581757 | 99417763 | 49865578 | 0.000000 | 24147588 | 22356574 | 0.000000
09-04-2025 17:10:05000 | -1333507 | 133.3507 | 14189830 | 234899.78 | 329626953 | 99438614 | 49845524 | 0.000000 | 24345308 | 22541678 | 0.000000
09-04-2025 17:10:10000 | -1329605 | 132.9605 | 14539876 | 235014.34 | 328608887 | 99407387 | 49882965 | 0.000000 | 24545159 | 22726521 | 0.000000
09-04-2025 17:10:15000 | -1335233 | 133.5233 | 14762438 | 234963.42 | 330112061 | 99394363 | 49899879 | 0.000000 | 24749353 | 22911771 | 0.000000
09-04-2025 17:10:20000 | -1335624 | 133.5624 | 14698658 | 234930.48 | 330236847 | 99399887 | 49894096 | 0.000000 | 24953936 | 23097232 | 0.000000
09-04-2025 17:10:25000 | -1338594 | 133.8594 | 14748580 | 234980.97 | 330903412 | 99398491 | 49870434 | 0.000000 | 25157583 | 23282969 | 0.000000
09-04-2025 17:10:30000 | -1334486 | 133.4486 | 14792274 | 235059.36 | 329804962 | 99391258 | 49895809 | 0.000000 | 25361926 | 23468264 | 0.000000
09-04-2025 17:10:35000 | -1337122 | 133.7122 | 14888897 | 235011.81 | 330534760 | 99385757 | 49922501 | 0.000000 | 25569238 | 23653939 | 0.000000
09-04-2025 17:10:40000 | -1337966 | 133.7966 | 14842286 | 234973.25 | 330784363 | 99390327 | 49911636 | 0.000000 | 25777419 | 23840135 | 0.000000
09-04-2025 17:10:45000 | -1342658 | 134.2658 | 14796554 | 234963.94 | 331931030 | 99398239 | 49899696 | 0.000000 | 25982534 | 24026242 | 0.000000
09-04-2025 17:10:50000 | -1331133 | 133.1133 | 14332947 | 234978.16 | 328976318 | 99425301 | 49883568 | 0.000000 | 26183843 | 24211781 | 0.000000
09-04-2025 17:10:55000 | -1337355 | 133.7355 | 14723344 | 234991.19 | 330578705 | 99399429 | 49891090 | 0.000000 | 26387402 | 24397623 | 0.000000
09-04-2025 17:11:00000 | -1339751 | 133.9751 | 14586378 | 234920.22 | 331226715 | 99412544 | 49883595 | 0.000000 | 26590813 | 24583555 | 0.000000
09-04-2025 17:11:05000 | -1337431 | 133.7431 | 14470036 | 234923.23 | 330627777 | 99419807 | 49855213 | 0.000000 | 26792847 | 24769713 | 0.000000
09-04-2025 17:11:10000 | -1332763 | 133.2763 | 14444930 | 235009.09 | 329361206 | 99417778 | 49872314 | 0.000000 | 26993062 | 24955174 | 0.000000
09-04-2025 17:11:15000 | -1339299 | 133.9299 | 15128727 | 235103.59 | 331004547 | 99368042 | 49926445 | 0.000000 | 27198606 | 25140500 | 0.000000
09-04-2025 17:11:20000 | -1342172 | 134.2172 | 15129386 | 235005.30 | 331846191 | 99370667 | 49932335 | 0.000000 | 27410115 | 25326863 | 0.000000
09-04-2025 17:11:25000 | -1340222 | 134.0222 | 14836375 | 234979.78 | 331327972 | 99392838 | 49910919 | 0.000000 | 27618040 | 25513154 | 0.000000
09-04-2025 17:11:30000 | -1341002 | 134.1002 | 14662831 | 234944.41 | 331516663 | 99407516 | 49883297 | 0.000000 | 27823188 | 25699559 | 0.000000
09-04-2025 17:11:35000 | -1340512 | 134.0512 | 14680417 | 235015.72 | 331306061 | 99405678 | 49882423 | 0.000000 | 28026289 | 25885607 | 0.000000
09-04-2025 17:11:40000 | -1338616 | 133.8616 | 14849103 | 235003.23 | 330902954 | 99390358 | 49912888 | 0.000000 | 28230776 | 26071105 | 0.000000
09-04-2025 17:11:45000 | -1337656 | 133.7656 | 14538443 | 234900.55 | 330729858 | 99414551 | 49896477 | 0.000000 | 28434980 | 26257150 | 0.000000
09-04-2025 17:11:50000 | -1338205 | 133.8205 | 14435220 | 234911.13 | 330824127 | 99423233 | 49879074 | 0.000000 | 28635579 | 26442984 | 0.000000
09-04-2025 17:11:55000 | -1339986 | 133.9986 | 14487482 | 234916.41 | 331264374 | 99420616 | 49870483 | 0.000000 | 28835842 | 26628699 | 0.000000
09-04-2025 17:12:00000 | -1341941 | 134.1941 | 14594901 | 234902.67 | 331790680 | 99413765 | 49870468 | 0.000000 | 29037490 | 26814850 | 0.000000
09-04-2025 17:12:05000 | -1339696 | 133.9696 | 14158272 | 234851.47 | 331196899 | 99446190 | 49879761 | 0.000000 | 29236287 | 27000789 | 0.000000
09-04-2025 17:12:10000 | -1340913 | 134.0913 | 14002153 | 234741.05 | 331617737 | 99459213 | 49872070 | 0.000000 | 29431470 | 27186785 | 0.000000
09-04-2025 17:12:15000 | -1340056 | 134.0056 | 13816676 | 234691.53 | 331430511 | 99472664 | 49843338 | 0.000000 | 29624729 | 27372957 | 0.000000
09-04-2025 17:12:20000 | -1332546 | 133.2546 | 13732535 | 234823.92 | 329391571 | 99473175 | 49851425 | 0.000000 | 29814800 | 27558262 | 0.000000
09-04-2025 17:12:25000 | -1335964 | 133.5964 | 13793811 | 234733.88 | 330357697 | 99471199 | 49850708 | 0.000000 | 30006594 | 27743777 | 0.000000
09-04-2025 17:12:30000 | -1336637 | 133.6637 | 13951412 | 234800.45 | 330471863 | 99459686 | 49842693 | 0.000000 | 30199038 | 27929559 | 0.000000
09-04-2025 17:12:35000 | -1337043 | 133.7043 | 13923428 | 234805.13 | 330553619 | 99462158 | 49855354 | 0.000000 | 30391838 | 28115020 | 0.000000
09-04-2025 17:12:40000 | -1338302 | 133.8302 | 13791740 | 234719.91 | 330952148 | 99473183 | 49841187 | 0.000000 | 30584438 | 28300979 | 0.000000
09-04-2025 17:12:45000 | -1341547 | 134.1547 | 13487889 | 234607.52 | 331824524 | 99498390 | 49815838 | 0.000000 | 30773240 | 28486986 | 0.000000
09-04-2025 17:12:50000 | -1333628 | 133.3628 | 13399656 | 234738.31 | 329682953 | 99499023 | 49815662 | 0.000000 | 30959702 | 28672533 | 0.000000
09-04-2025 17:12:55000 | -1338800 | 133.88 | 13643509 | 234680.64 | 331101013 | 99484741 | 49816921 | 0.000000 | 31149568 | 28858357 | 0.000000
09-04-2025 17:13:00000 | -1338229 | 133.8229 | 13744457 | 234717.11 | 330926514 | 99476707 | 49795612 | 0.000000 | 31340183 | 29044203 | 0.000000
09-04-2025 17:13:05000 | -1335182 | 133.5182 | 13631438 | 234743.81 | 330115540 | 99482880 | 49809525 | 0.000000 | 31529719 | 29229791 | 0.000000
09-04-2025 17:13:10000 | -1334580 | 133.458 | 13744093 | 234807.20 | 329906799 | 99473892 | 49817520 | 0.000000 | 31718979 | 29415100 | 0.000000
09-04-2025 17:13:15000 | -1343835 | 134.3835 | 14080059 | 234716.81 | 332385834 | 99455589 | 49835209 | 0.000000 | 31912202 | 29600822 | 0.000000
09-04-2025 17:13:20000 | -1338903 | 133.8903 | 13667149 | 234689.27 | 331111633 | 99483047 | 49811577 | 0.000000 | 32104004 | 29787051 | 0.000000
09-04-2025 17:13:25000 | -1334451 | 133.4451 | 13707677 | 234786.52 | 329896118 | 99476555 | 49821884 | 0.000000 | 32293223 | 29972545 | 0.000000
09-04-2025 17:13:30000 | -1335994 | 133.5994 | 13865987 | 234819.63 | 330262207 | 99465714 | 49832638 | 0.000000 | 32486155 | 30158316 | 0.000000
09-04-2025 17:13:35000 | -1335456 | 133.5456 | 13518578 | 234697.83 | 330219666 | 99491547 | 49804409 | 0.000000 | 32676416 | 30344393 | 0.000000
09-04-2025 17:13:40000 | -1331868 | 133.1868 | 13730644 | 234835.75 | 329200043 | 99472786 | 49812164 | 0.000000 | 32866289 | 30529813 | 0.000000
09-04-2025 17:13:45000 | -1342055 | 134.2055 | 13937990 | 234719.28 | 331903259 | 99465027 | 49820377 | 0.000000 | 33058936 | 30715688 | 0.000000
09-04-2025 17:13:50000 | -1337031 | 133.7031 | 13688476 | 234724.16 | 330608673 | 99480003 | 49789642 | 0.000000 | 33250164 | 30901758 | 0.000000
09-04-2025 17:13:55000 | -1337170 | 133.717 | 13640387 | 234695.92 | 330668579 | 99483727 | 49788132 | 0.000000 | 33439651 | 31087330 | 0.000000
09-04-2025 17:14:00000 | -1331012 | 133.1012 | 13084174 | 234633.70 | 329111847 | 99520302 | 49749889 | 0.000000 | 33625022 | 31273008 | 0.000000
09-04-2025 17:14:05000 | -1331911 | 133.1911 | 13346048 | 234701.61 | 329302216 | 99501724 | 49754475 | 0.000000 | 33808865 | 31458223 | 0.000000
09-04-2025 17:14:10000 | -1330865 | 133.0865 | 13268670 | 234720.52 | 328996826 | 99506676 | 49759418 | 0.000000 | 33992800 | 31643326 | 0.000000
09-04-2025 17:14:15000 | -1331951 | 133.1951 | 13302147 | 234678.58 | 329333252 | 99505005 | 49758759 | 0.000000 | 34178389 | 31828623 | 0.000000
09-04-2025 17:14:20000 | -1335860 | 133.586 | 13412277 | 234635.09 | 330375000 | 99499756 | 49770920 | 0.000000 | 34365334 | 32013908 | 0.000000
09-04-2025 17:14:25000 | -1333789 | 133.3789 | 13447048 | 234659.41 | 329849731 | 99495621 | 49777214 | 0.000000 | 34552014 | 32199176 | 0.000000
09-04-2025 17:14:30000 | -1332345 | 133.2345 | 13395787 | 234698.00 | 329422913 | 99498360 | 49769817 | 0.000000 | 34738777 | 32384373 | 0.000000
09-04-2025 17:14:35000 | -1335010 | 133.501 | 13320021 | 234615.39 | 330175201 | 99505936 | 49763218 | 0.000000 | 34924294 | 32569766 | 0.000000
09-04-2025 17:14:40000 | -1328531 | 132.8531 | 13282104 | 234713.95 | 328449493 | 99503960 | 49768070 | 0.000000 | 35108279 | 32754639 | 0.000000
09-04-2025 17:14:45000 | -1333942 | 133.3942 | 13541171 | 234698.89 | 329847290 | 99488708 | 49785233 | 0.000000 | 35295725 | 32939906 | 0.000000
09-04-2025 17:14:50000 | -1336657 | 133.6657 | 13808083 | 234763.61 | 330495056 | 99470657 | 49794514 | 0.000000 | 35484688 | 33125070 | 0.000000
09-04-2025 17:14:55000 | -1337034 | 133.7034 | 13981191 | 234833.48 | 330528656 | 99457710 | 49824863 | 0.000000 | 35676589 | 33310039 | 0.000000
09-04-2025 17:15:00000 | -1335313 | 133.5313 | 13851936 | 234785.73 | 330139557 | 99466248 | 49819473 | 0.000000 | 35870205 | 33495863 | 0.000000
09-04-2025 17:15:05000 | -1336840 | 133.684 | 14011148 | 234866.83 | 330440125 | 99455246 | 49829258 | 0.000000 | 19362041 | 185611679 | 0.000000
09-04-2025 17:15:10000 | -1343361 | 134.3361 | 14120323 | 234753.11 | 332227905 | 99452110 | 49834148 | 0.000000 | 38914600 | 371347168 | 0.000000
09-04-2025 17:15:15000 | -1331832 | 133.1832 | 13240878 | 234646.41 | 329341980 | 99509430 | 49770424 | 0.000000 | 57848087 | 557259155 | 0.000000
09-04-2025 17:15:20000 | -1330904 | 133.0904 | 13153602 | 234698.77 | 329013092 | 99515160 | 49790417 | 0.000000 | 76041153 | 742135681 | 0.000000
09-04-2025 17:15:25000 | -1337827 | 133.7827 | 13299670 | 234630.53 | 330842590 | 99509491 | 49803146 | 0.000000 | 94418076 | 927281616 | 0.000000
09-04-2025 17:15:30000 | -1335129 | 133.5129 | 13315810 | 234652.94 | 330152100 | 99506332 | 49814777 | 0.000000 | 112795906 | 11125421 | 0.000000
09-04-2025 17:15:35000 | -1332058 | 133.2058 | 13031309 | 234594.50 | 329410736 | 99524887 | 49814777 | 0.000000 | 131040192 | 12977913 | 0.000000
09-04-2025 17:15:40000 | -1328611 | 132.8611 | 12819013 | 234552.13 | 328574768 | 99537766 | 49819572 | 0.000000 | 149148560 | 14826279 | 0.000000
09-04-2025 17:15:45000 | -1329000 | 132.9 | 13144415 | 234673.48 | 328584137 | 99514458 | 49858269 | 0.000000 | 167306534 | 16674276 | 0.000000
09-04-2025 17:15:50000 | -1339184 | 133.9184 | 13586375 | 234645.95 | 331214050 | 99489304 | 49879425 | 0.000000 | 185939911 | 18528707 | 0.000000
09-04-2025 17:15:55000 | -1336439 | 133.6439 | 13133624 | 234608.61 | 330487305 | 99520584 | 49867710 | 0.000000 | 204315918 | 20384467 | 0.000000
09-04-2025 17:16:00000 | -1334397 | 133.4397 | 13342335 | 234713.97 | 329892487 | 99503838 | 49879517 | 0.000000 | 222616302 | 22238264 | 0.000000
09-04-2025 17:16:05000 | -1341566 | 134.1566 | 13520659 | 234619.88 | 331827942 | 99495979 | 49907845 | 0.000000 | 241240662 | 24094600 | 0.000000
09-04-2025 17:16:10000 | -1342931 | 134.2931 | 13545293 | 234617.75 | 332173859 | 99495178 | 49913284 | 0.000000 | 260096313 | 25954778 | 0.000000
09-04-2025 17:16:15000 | -1340835 | 134.0835 | 13431309 | 234659.34 | 331571533 | 99502029 | 49901745 | 0.000000 | 278746368 | 27817725 | 0.000000
09-04-2025 17:16:20000 | -1334545 | 133.4545 | 13168983 | 234659.41 | 329964478 | 99516663 | 49899773 | 0.000000 | 297053070 | 29673899 | 0.000000
09-04-2025 17:16:25000 | -1338461 | 133.8461 | 13496316 | 234681.13 | 330968872 | 99495461 | 49918903 | 0.000000 | 315708466 | 31533757 | 0.000000
09-04-2025 17:16:30000 | -1342545 | 134.2545 | 13321295 | 234581.33 | 332069641 | 99511330 | 49887539 | 0.000000 | 334406311 | 33400007 | 0.000000
09-04-2025 17:16:35000 | -1340811 | 134.0811 | 13333618 | 234628.16 | 331581238 | 99509178 | 49894596 | 0.000000 | 352922180 | 35260476 | 0.000000
09-04-2025 17:16:40000 | -1342949 | 134.2949 | 13360626 | 234602.16 | 332151520 | 99508759 | 49901615 | 0.000000 | 371533173 | 37121353 | 0.000000
09-04-2025 17:16:45000 | -1339525 | 133.9525 | 13373132 | 234634.20 | 331265015 | 99505341 | 49904552 | 0.000000 | 390071350 | 38981995 | 0.000000
09-04-2025 17:16:50000 | -1339470 | 133.947 | 13279722 | 234599.50 | 331281036 | 99512138 | 49905914 | 0.000000 | 408566315 | 40843962 | 0.000000
09-04-2025 17:16:55000 | -1337159 | 133.7159 | 13213250 | 234627.45 | 330661591 | 99515320 | 49921513 | 0.000000 | 426993530 | 42704243 | 0.000000
09-04-2025 17:17:00000 | -1343670 | 134.367 | 13710752 | 234713.25 | 332253540 | 99483429 | 49963818 | 0.000000 | 445769836 | 44565146 | 0.000000
09-04-2025 17:17:05000 | -1343843 | 134.3843 | 13443600 | 234599.55 | 332390167 | 99503342 | 49943218 | 0.000000 | 464684479 | 46432803 | 0.000000
09-04-2025 17:17:10000 | -1340437 | 134.0437 | 13459252 | 234709.72 | 331403503 | 99499680 | 49934669 | 0.000000 | 483338562 | 48298960 | 0.000000
09-04-2025 17:17:15000 | -1342175 | 134.2175 | 13945269 | 234807.63 | 331807709 | 99464569 | 49976536 | 0.000000 | 502385162 | 50159824 | 0.000000
09-04-2025 17:17:20000 | -1345096 | 134.5096 | 14167678 | 234813.53 | 332573059 | 99449867 | 50002472 | 0.000000 | 521978333 | 52025615 | 0.000000
09-04-2025 17:17:25000 | -1347149 | 134.7149 | 14361818 | 234826.53 | 333109924 | 99436523 | 50018764 | 0.000000 | 541767334 | 53894561 | 0.000000
09-04-2025 17:17:30000 | -1349522 | 134.9522 | 14795910 | 234930.14 | 333652588 | 99404335 | 50045406 | 0.000000 | 562081238 | 55762661 | 0.000000
09-04-2025 17:17:35000 | -1349237 | 134.9237 | 14658915 | 234927.45 | 333554443 | 99414978 | 50026104 | 0.000000 | 582535278 | 57636504 | 0.000000
09-04-2025 17:17:40000 | -1346425 | 134.6425 | 14735652 | 234932.14 | 332885529 | 99406441 | 50022415 | 0.000000 | 603129211 | 59507407 | 0.000000
09-04-2025 17:17:45000 | -1343582 | 134.3582 | 14766563 | 235006.13 | 332090637 | 99401466 | 50030567 | 0.000000 | 623459595 | 61372534 | 0.000000
09-04-2025 17:17:50000 | -1339636 | 133.9636 | 14393320 | 234888.73 | 331194916 | 99427757 | 50008308 | 0.000000 | 643700684 | 63241978 | 0.000000
09-04-2025 17:17:55000 | -1347180 | 134.718 | 14390178 | 234797.81 | 333161469 | 99434341 | 50020218 | 0.000000 | 663797424 | 65106563 | 0.000000
09-04-2025 17:18:00000 | -1343774 | 134.3774 | 14208570 | 234830.06 | 332237366 | 99445633 | 50018986 | 0.000000 | 683622314 | 66970938 | 0.000000
09-04-2025 17:18:05000 | -1340783 | 134.0783 | 14103993 | 234854.86 | 331446838 | 99451279 | 49992123 | 0.000000 | 703134155 | 68834336 | 0.000000
09-04-2025 17:18:10000 | -1344166 | 134.4166 | 14605503 | 234953.75 | 332264099 | 99414841 | 50034214 | 0.000000 | 722920532 | 70691416 | 0.000000
09-04-2025 17:18:15000 | -1339411 | 133.9411 | 14409873 | 234939.41 | 331077881 | 99426262 | 50016125 | 0.000000 | 743066833 | 72558848 | 0.000000
09-04-2025 17:18:20000 | -1343963 | 134.3963 | 14518479 | 234889.17 | 332280701 | 99421562 | 50001709 | 0.000000 | 763218506 | 74427383 | 0.000000
09-04-2025 17:18:25000 | -1340326 | 134.0326 | 14254169 | 234903.83 | 331302948 | 99439255 | 49980698 | 0.000000 | 783105347 | 76294229 | 0.000000
09-04-2025 17:18:30000 | -1343758 | 134.3758 | 14078299 | 234727.16 | 332344116 | 99455658 | 49960461 | 0.000000 | 803038818 | 78160889 | 0.000000
09-04-2025 17:18:35000 | -1338433 | 133.8433 | 14291054 | 234952.69 | 330780396 | 99434792 | 49960407 | 0.000000 | 822686584 | 80023022 | 0.000000
09-04-2025 17:18:40000 | -1333496 | 133.3496 | 14477300 | 234993.25 | 329567352 | 99415825 | 49996201 | 0.000000 | 842672607 | 81877793 | 0.000000
09-04-2025 17:18:45000 | -1339757 | 133.9757 | 14651656 | 234923.50 | 331245270 | 99407326 | 50025852 | 0.000000 | 863119629 | 83737930 | 0.000000
09-04-2025 17:18:50000 | -1347881 | 134.7881 | 14538554 | 234805.47 | 333365723 | 99423317 | 49977722 | 0.000000 | 883427307 | 85607842 | 0.000000
09-04-2025 17:18:55000 | -1343401 | 134.3401 | 14350320 | 234917.14 | 332057953 | 99434303 | 49932312 | 0.000000 | 903198425 | 87473779 | 0.000000
09-04-2025 17:19:00000 | -1340430 | 134.043 | 14314823 | 234912.13 | 331335938 | 99434593 | 49936325 | 0.000000 | 923096497 | 89336426 | 0.000000
09-04-2025 17:19:05000 | -1345202 | 134.5202 | 14308438 | 234801.77 | 332657898 | 99439064 | 49944458 | 0.000000 | 942959534 | 91196777 | 0.000000
09-04-2025 17:19:10000 | -1338800 | 133.88 | 13846890 | 234812.05 | 330955933 | 99469391 | 49909092 | 0.000000 | 962304993 | 93058955 | 0.000000
09-04-2025 17:19:15000 | -1338489 | 133.8489 | 14194144 | 234931.52 | 330797668 | 99442413 | 49934361 | 0.000000 | 981792419 | 94919121 | 0.000000
09-04-2025 17:19:20000 | -1340376 | 134.0376 | 14050840 | 234775.16 | 331442383 | 99455048 | 49948280 | 0.000000 | 10014417 | 96781289 | 0.000000
09-04-2025 17:19:25000 | -1339616 | 133.9616 | 13908030 | 234807.61 | 331173218 | 99465378 | 49948036 | 0.000000 | 10209160 | 98647119 | 0.000000
09-04-2025 17:19:30000 | -1340984 | 134.0984 | 14232887 | 234880.97 | 331493256 | 99441452 | 49973625 | 0.000000 | 10405117 | 10051153 | 0.000000
09-04-2025 17:19:35000 | -1347353 | 134.7353 | 14200336 | 234746.70 | 333231964 | 99449188 | 49966228 | 0.000000 | 10603815 | 10238147 | 0.000000
09-04-2025 17:19:40000 | -1342860 | 134.286 | 14412275 | 234946.58 | 331902039 | 99428993 | 49975376 | 0.000000 | 10801729 | 10424806 | 0.000000
09-04-2025 17:19:45000 | -1346864 | 134.6864 | 14811320 | 234999.78 | 332912964 | 99400772 | 50022060 | 0.000000 | 11004666 | 10611557 | 0.000000
09-04-2025 17:19:50000 | -1349383 | 134.9383 | 14723913 | 234950.28 | 333582764 | 99409950 | 50029419 | 0.000000 | 11208058 | 10798650 | 0.000000
09-04-2025 17:19:55000 | -1344423 | 134.4423 | 14829268 | 235026.00 | 332283447 | 99397171 | 50046341 | 0.000000 | 11412328 | 10985302 | 0.000000
09-04-2025 17:20:00000 | -1347333 | 134.7333 | 14917521 | 234967.83 | 333103027 | 99392647 | 50052567 | 0.000000 | 11620116 | 11172750 | 0.000000
09-04-2025 17:20:05000 | -1346870 | 134.687 | 14787815 | 234950.23 | 332977539 | 99402657 | 50046833 | 0.000000 | 11826340 | 11359914 | 0.000000
09-04-2025 17:20:10000 | -1348372 | 134.8372 | 14740032 | 234934.56 | 333352814 | 99407791 | 50036423 | 0.000000 | 12032621 | 11547442 | 0.000000
09-04-2025 17:20:15000 | -1347185 | 134.7185 | 14499469 | 234879.61 | 333077698 | 99425797 | 49994556 | 0.000000 | 12235527 | 11735092 | 0.000000
09-04-2025 17:20:20000 | -1347841 | 134.7841 | 14213965 | 234769.11 | 333319763 | 99448532 | 49967789 | 0.000000 | 12433807 | 11921970 | 0.000000
09-04-2025 17:20:25000 | -1340237 | 134.0237 | 14065613 | 234880.64 | 331263245 | 99453796 | 49957802 | 0.000000 | 12629100 | 12108593 | 0.000000
09-04-2025 17:20:30000 | -1339653 | 133.9653 | 14100509 | 234858.42 | 331163513 | 99450630 | 49968948 | 0.000000 | 12824344 | 12294813 | 0.000000
09-04-2025 17:20:35000 | -1344348 | 134.4348 | 14223684 | 234806.38 | 332414673 | 99444939 | 49986591 | 0.000000 | 13021232 | 12481310 | 0.000000
09-04-2025 17:20:40000 | -1345754 | 134.5754 | 14242366 | 234852.52 | 332700836 | 99444641 | 49998234 | 0.000000 | 13219049 | 12668141 | 0.000000
09-04-2025 17:20:45000 | -1343803 | 134.3803 | 14877832 | 235103.88 | 332040955 | 99392693 | 50055882 | 0.000000 | 13420605 | 12854621 | 0.000000
09-04-2025 17:20:50000 | -1348648 | 134.8648 | 15095359 | 235024.67 | 333389038 | 99379410 | 50087830 | 0.000000 | 13629204 | 13041688 | 0.000000
09-04-2025 17:20:55000 | -1345563 | 134.5563 | 15140912 | 235094.25 | 332555054 | 99372856 | 50094063 | 0.000000 | 13838728 | 13229024 | 0.000000
09-04-2025 17:21:00000 | -1348873 | 134.8873 | 15460681 | 235154.36 | 333358093 | 99349525 | 50113415 | 0.000000 | 14052397 | 13416335 | 0.000000
09-04-2025 17:21:05000 | -1347810 | 134.781 | 15630287 | 235187.08 | 333101593 | 99334274 | 50134293 | 0.000000 | 14269792 | 13603818 | 0.000000
09-04-2025 17:21:10000 | -1355404 | 135.5404 | 15823125 | 235105.09 | 335123566 | 99325462 | 50138847 | 0.000000 | 14489344 | 13791610 | 0.000000
09-04-2025 17:21:15000 | -1352659 | 135.2659 | 15525645 | 235173.06 | 334274353 | 99347733 | 50104675 | 0.000000 | 14706218 | 13979731 | 0.000000
09-04-2025 17:21:20000 | -1350561 | 135.0561 | 15757694 | 235245.55 | 333727142 | 99326218 | 50109547 | 0.000000 | 14923617 | 14167299 | 0.000000
09-04-2025 17:21:25000 | -1349995 | 134.9995 | 15752875 | 235219.45 | 333623505 | 99326065 | 50124264 | 0.000000 | 15142330 | 14354922 | 0.000000
09-04-2025 17:21:30000 | -1354134 | 135.4134 | 15797206 | 235131.19 | 334769226 | 99326401 | 50133324 | 0.000000 | 15362109 | 14542726 | 0.000000
09-04-2025 17:21:35000 | -1354003 | 135.4003 | 15489346 | 235065.27 | 334747589 | 99352020 | 50091549 | 0.000000 | 15578981 | 14730905 | 0.000000
09-04-2025 17:21:40000 | -1347017 | 134.7017 | 15252723 | 235095.78 | 332931122 | 99365013 | 50073334 | 0.000000 | 15792636 | 14918559 | 0.000000
09-04-2025 17:21:45000 | -1348163 | 134.8163 | 15373663 | 235090.81 | 333256989 | 99356087 | 50083115 | 0.000000 | 16005422 | 15105758 | 0.000000
09-04-2025 17:21:50000 | -1345318 | 134.5318 | 15086962 | 235035.22 | 332558746 | 99377052 | 50059906 | 0.000000 | 16216725 | 15292918 | 0.000000
09-04-2025 17:21:55000 | -1347246 | 134.7246 | 15109635 | 235034.39 | 333034821 | 99376968 | 50062855 | 0.000000 | 16426805 | 15480071 | 0.000000
09-04-2025 17:22:00000 | -1348755 | 134.8755 | 14938931 | 234938.92 | 333491302 | 99392189 | 50062141 | 0.000000 | 16634680 | 15667040 | 0.000000
09-04-2025 17:22:05000 | -1347167 | 134.7167 | 15060165 | 235058.58 | 332967957 | 99380928 | 50077282 | 0.000000 | 16842001 | 15854096 | 0.000000
09-04-2025 17:22:10000 | -1352224 | 135.2224 | 15092910 | 234976.89 | 334326691 | 99382858 | 50081944 | 0.000000 | 17052241 | 16041767 | 0.000000
09-04-2025 17:22:15000 | -1347857 | 134.7857 | 15207313 | 235153.75 | 333041321 | 99369530 | 50085041 | 0.000000 | 17260662 | 16229149 | 0.000000
09-04-2025 17:22:20000 | -1348993 | 134.8993 | 15629445 | 235144.08 | 333451202 | 99335503 | 50131462 | 0.000000 | 17476752 | 16416545 | 0.000000
09-04-2025 17:22:25000 | -1353706 | 135.3706 | 15765860 | 235173.36 | 334595703 | 99328621 | 50114296 | 0.000000 | 17695042 | 16604580 | 0.000000
09-04-2025 17:22:30000 | -1350414 | 135.0414 | 15561643 | 235146.53 | 333774445 | 99342575 | 50084229 | 0.000000 | 17913409 | 16792486 | 0.000000
09-04-2025 17:22:35000 | -1350545 | 135.0545 | 16130924 | 235292.38 | 333763916 | 99294243 | 50062263 | 0.000000 | 18135269 | 16980066 | 0.000000
09-04-2025 17:22:40000 | -1350744 | 135.0744 | 16354432 | 235318.28 | 333841522 | 99274979 | 50091789 | 0.000000 | 18361718 | 17167209 | 0.000000
09-04-2025 17:22:45000 | -1344480 | 134.448 | 15892039 | 235267.30 | 332251312 | 99308647 | 50073746 | 0.000000 | 18584320 | 17354541 | 0.000000
09-04-2025 17:22:50000 | -1350587 | 135.0587 | 16200661 | 235243.17 | 333867310 | 99288239 | 50082699 | 0.000000 | 18807960 | 17541809 | 0.000000
09-04-2025 17:22:55000 | -1354239 | 135.4239 | 15746867 | 235050.16 | 334896423 | 99330750 | 50047672 | 0.000000 | 19029581 | 17729438 | 0.000000
09-04-2025 17:23:00000 | -1346250 | 134.625 | 15595518 | 235203.48 | 332693756 | 99335686 | 50036030 | 0.000000 | 19246207 | 17916668 | 0.000000
09-04-2025 17:23:05000 | -1347702 | 134.7702 | 15490262 | 235119.39 | 333133484 | 99345932 | 50033043 | 0.000000 | 19462996 | 18103598 | 0.000000
09-04-2025 17:23:10000 | -1346306 | 134.6306 | 15039271 | 234987.94 | 332853119 | 99381851 | 50002201 | 0.000000 | 19674390 | 18290514 | 0.000000
09-04-2025 17:23:15000 | -1345231 | 134.5231 | 15024736 | 234983.61 | 332594971 | 99382057 | 49974804 | 0.000000 | 19884037 | 18477441 | 0.000000
09-04-2025 17:23:20000 | -1339982 | 133.9982 | 15105990 | 235137.00 | 331126862 | 99370560 | 49993549 | 0.000000 | 20092128 | 18663332 | 0.000000
09-04-2025 17:23:25000 | -1342165 | 134.2165 | 14772531 | 234971.91 | 331799866 | 99399734 | 50013920 | 0.000000 | 20297690 | 18849621 | 0.000000
09-04-2025 17:23:30000 | -1347009 | 134.7009 | 15082156 | 235004.72 | 333014221 | 99378998 | 50034336 | 0.000000 | 20505815 | 19036352 | 0.000000
09-04-2025 17:23:35000 | -1345628 | 134.5628 | 15358632 | 235162.92 | 332536011 | 99354927 | 50044384 | 0.000000 | 20714731 | 19223178 | 0.000000
09-04-2025 17:23:40000 | -1346511 | 134.6511 | 15634359 | 235124.27 | 332886932 | 99332664 | 50072769 | 0.000000 | 20932285 | 19410166 | 0.000000
09-04-2025 17:23:45000 | -1348764 | 134.8764 | 15533505 | 235094.08 | 333453552 | 99343338 | 50049557 | 0.000000 | 21148533 | 19597664 | 0.000000
09-04-2025 17:23:50000 | -1346063 | 134.6063 | 14658896 | 234853.48 | 332884369 | 99412239 | 50050900 | 0.000000 | 21360422 | 19784908 | 0.000000
09-04-2025 17:23:55000 | -1346215 | 134.6215 | 14226445 | 234828.20 | 332842926 | 99446251 | 50046425 | 0.000000 | 21560327 | 19972215 | 0.000000
09-04-2025 17:24:00000 | -1345726 | 134.5726 | 14265724 | 234887.27 | 332650208 | 99442810 | 50055557 | 0.000000 | 21757705 | 20159143 | 0.000000
09-04-2025 17:24:05000 | -1341651 | 134.1651 | 14393797 | 234940.70 | 331610199 | 99429428 | 50068275 | 0.000000 | 21957859 | 20346162 | 0.000000
09-04-2025 17:24:10000 | -1350003 | 135.0003 | 14726840 | 234898.11 | 333802979 | 99410255 | 50091408 | 0.000000 | 22159634 | 20533021 | 0.000000
09-04-2025 17:24:15000 | -1355319 | 135.5319 | 14484844 | 234717.67 | 335295410 | 99433746 | 50058075 | 0.000000 | 22362463 | 20720518 | 0.000000
09-04-2025 17:24:20000 | -1347520 | 134.752 | 14574754 | 234886.11 | 333173035 | 99420158 | 50046532 | 0.000000 | 22564448 | 20907775 | 0.000000
09-04-2025 17:24:25000 | -1343491 | 134.3491 | 14890354 | 235079.69 | 332017181 | 99391403 | 50079010 | 0.000000 | 22766724 | 21094443 | 0.000000
09-04-2025 17:24:30000 | -1345860 | 134.586 | 14749572 | 234935.63 | 332743561 | 99404831 | 50083023 | 0.000000 | 22973931 | 21281654 | 0.000000
09-04-2025 17:24:35000 | -1342420 | 134.242 | 14038219 | 234772.05 | 331958740 | 99457657 | 50027805 | 0.000000 | 23173040 | 21468949 | 0.000000
09-04-2025 17:24:40000 | -1344473 | 134.4473 | 14452389 | 234905.78 | 332364594 | 99427200 | 50043659 | 0.000000 | 23371411 | 21655486 | 0.000000
09-04-2025 17:24:45000 | -1346685 | 134.6685 | 14585434 | 234902.70 | 332953613 | 99418594 | 50075123 | 0.000000 | 23573511 | 21842150 | 0.000000
09-04-2025 17:24:50000 | -1348585 | 134.8585 | 14329425 | 234802.36 | 333490784 | 99440224 | 50051495 | 0.000000 | 23775339 | 22029643 | 0.000000
09-04-2025 17:24:55000 | -1349319 | 134.9319 | 14075763 | 234744.66 | 333685547 | 99460297 | 50016705 | 0.000000 | 23973835 | 22216975 | 0.000000
09-04-2025 17:25:00000 | -1342109 | 134.2109 | 14088530 | 234881.33 | 331725098 | 99453545 | 50009285 | 0.000000 | 24169031 | 22403600 | 0.000000
09-04-2025 17:25:05000 | -1340994 | 134.0994 | 14050614 | 234842.06 | 331504822 | 99455559 | 50017040 | 0.000000 | 24365005 | 22590121 | 0.000000
09-04-2025 17:25:10000 | -1343418 | 134.3418 | 14330596 | 234849.70 | 332160309 | 99435860 | 50042938 | 0.000000 | 24562939 | 22776686 | 0.000000
09-04-2025 17:25:15000 | -1348743 | 134.8743 | 14396021 | 234783.58 | 333575958 | 99435188 | 50043682 | 0.000000 | 24763376 | 22963861 | 0.000000
09-04-2025 17:25:20000 | -1342460 | 134.246 | 14402302 | 234919.81 | 331839966 | 99429436 | 50061058 | 0.000000 | 24961658 | 23150438 | 0.000000
09-04-2025 17:25:25000 | -1348528 | 134.8528 | 14860368 | 235017.17 | 333310394 | 99398308 | 50086063 | 0.000000 | 25164895 | 23337508 | 0.000000
09-04-2025 17:25:30000 | -1351284 | 135.1284 | 14791737 | 234914.92 | 334108887 | 99406212 | 50073383 | 0.000000 | 25371401 | 23525217 | 0.000000
09-04-2025 17:25:35000 | -1350969 | 135.0969 | 14691131 | 234913.63 | 334017181 | 99413918 | 50066891 | 0.000000 | 25575576 | 23712699 | 0.000000
09-04-2025 17:25:40000 | -1344919 | 134.4919 | 14726668 | 235002.09 | 332422241 | 99405838 | 50059093 | 0.000000 | 25781147 | 23900193 | 0.000000
09-04-2025 17:25:45000 | -1350352 | 135.0352 | 14597675 | 234881.11 | 333874115 | 99420761 | 50036587 | 0.000000 | 25985708 | 24087791 | 0.000000
09-04-2025 17:25:50000 | -1348323 | 134.8323 | 14484879 | 234863.64 | 333379181 | 99427902 | 50020481 | 0.000000 | 26188694 | 24275156 | 0.000000
09-04-2025 17:25:55000 | -1346732 | 134.6732 | 14547962 | 234902.73 | 332950989 | 99421593 | 50013420 | 0.000000 | 26391228 | 24462375 | 0.000000
09-04-2025 17:26:00000 | -1347788 | 134.7788 | 14545564 | 234933.59 | 333169556 | 99422684 | 50007042 | 0.000000 | 26591772 | 24649234 | 0.000000
09-04-2025 17:26:05000 | -1342206 | 134.2206 | 14810480 | 235036.17 | 331722107 | 99396713 | 50040936 | 0.000000 | 26795352 | 24835402 | 0.000000
09-04-2025 17:26:10000 | -1340035 | 134.0035 | 14783573 | 235025.45 | 331209625 | 99396950 | 50052280 | 0.000000 | 27001494 | 25021877 | 0.000000
09-04-2025 17:26:15000 | -1345392 | 134.5392 | 14801017 | 234955.30 | 332616699 | 99400299 | 50036877 | 0.000000 | 27207629 | 25208934 | 0.000000
09-04-2025 17:26:20000 | -1341712 | 134.1712 | 14991366 | 235076.94 | 331594360 | 99381569 | 50050873 | 0.000000 | 27414639 | 25395527 | 0.000000
09-04-2025 17:26:25000 | -1352908 | 135.2908 | 15146968 | 234885.09 | 334650696 | 99379097 | 50044174 | 0.000000 | 27625212 | 25582656 | 0.000000
09-04-2025 17:26:30000 | -1346099 | 134.6099 | 14777820 | 234987.52 | 332735962 | 99402786 | 50003204 | 0.000000 | 27831418 | 25769742 | 0.000000
09-04-2025 17:26:35000 | -1348330 | 134.833 | 14790887 | 234903.80 | 333408661 | 99403694 | 49997417 | 0.000000 | 28036865 | 25956477 | 0.000000
09-04-2025 17:26:40000 | -1343386 | 134.3386 | 14680999 | 234965.11 | 332082092 | 99408150 | 49972496 | 0.000000 | 28240537 | 26143094 | 0.000000
09-04-2025 17:26:45000 | -1337035 | 133.7035 | 14552850 | 234976.78 | 330485657 | 99412857 | 50000160 | 0.000000 | 28443689 | 26328887 | 0.000000
09-04-2025 17:26:50000 | -1336829 | 133.6829 | 14854134 | 235057.55 | 330397034 | 99388336 | 50034435 | 0.000000 | 28649919 | 26514688 | 0.000000
09-04-2025 17:26:55000 | -1339413 | 133.9413 | 15022969 | 235054.19 | 331079285 | 99376869 | 50061634 | 0.000000 | 28859143 | 26700869 | 0.000000
09-04-2025 17:27:00000 | -1349697 | 134.9697 | 15361082 | 235051.73 | 333682953 | 99358574 | 50082310 | 0.000000 | 29070176 | 26887424 | 0.000000
09-04-2025 17:27:05000 | -1345254 | 134.5254 | 14958518 | 235020.23 | 332532379 | 99387459 | 50056759 | 0.000000 | 29280193 | 27074502 | 0.000000
09-04-2025 17:27:10000 | -1346999 | 134.6999 | 15362212 | 235137.48 | 332898743 | 99355934 | 50066475 | 0.000000 | 29490889 | 27261234 | 0.000000
09-04-2025 17:27:15000 | -1346488 | 134.6488 | 15641549 | 235186.20 | 332796082 | 99332031 | 50117672 | 0.000000 | 29706228 | 27447852 | 0.000000
09-04-2025 17:27:20000 | -1341524 | 134.1524 | 15441736 | 235220.19 | 331472839 | 99344040 | 50122459 | 0.000000 | 29921545 | 27634760 | 0.000000
09-04-2025 17:27:25000 | -1341770 | 134.177 | 15563423 | 235194.69 | 331619934 | 99334007 | 50140636 | 0.000000 | 30137993 | 27821482 | 0.000000
09-04-2025 17:27:30000 | -1346411 | 134.6411 | 15669161 | 235172.13 | 332798523 | 99329620 | 50150551 | 0.000000 | 30355857 | 28008682 | 0.000000
09-04-2025 17:27:35000 | -1346896 | 134.6896 | 15521572 | 235180.64 | 332858826 | 99342537 | 50122368 | 0.000000 | 30572593 | 28196262 | 0.000000
09-04-2025 17:27:40000 | -1347944 | 134.7944 | 16073199 | 235322.25 | 333076996 | 99296555 | 50148060 | 0.000000 | 30792400 | 28383211 | 0.000000
09-04-2025 17:27:45000 | -1349871 | 134.9871 | 16117167 | 235309.84 | 333582703 | 99294739 | 50171692 | 0.000000 | 31017131 | 28570607 | 0.000000
09-04-2025 17:27:50000 | -1355137 | 135.5137 | 16145899 | 235219.48 | 334998688 | 99297684 | 50154408 | 0.000000 | 31240391 | 28758521 | 0.000000
09-04-2025 17:27:55000 | -1346888 | 134.6888 | 16067107 | 235349.63 | 332780548 | 99295990 | 50145054 | 0.000000 | 31462756 | 28946053 | 0.000000
09-04-2025 17:28:00000 | -1350184 | 135.0184 | 15832818 | 235230.69 | 333682312 | 99319466 | 50128117 | 0.000000 | 31684092 | 29133887 | 0.000000
09-04-2025 17:28:05000 | -1352117 | 135.2117 | 16116152 | 235234.67 | 334226990 | 99297142 | 50140541 | 0.000000 | 31905493 | 29321271 | 0.000000
09-04-2025 17:28:10000 | -1353151 | 135.3151 | 15955100 | 235206.42 | 334486145 | 99312019 | 50154804 | 0.000000 | 32126934 | 29508805 | 0.000000
09-04-2025 17:28:15000 | -1350558 | 135.0558 | 15849708 | 235214.19 | 333797211 | 99318405 | 50155247 | 0.000000 | 32347375 | 29696627 | 0.000000
09-04-2025 17:28:20000 | -1351218 | 135.1218 | 15591226 | 235111.34 | 334039520 | 99340874 | 50126163 | 0.000000 | 32566301 | 29884523 | 0.000000
09-04-2025 17:28:25000 | -1348092 | 134.8092 | 15507129 | 235169.14 | 333168335 | 99344894 | 50121613 | 0.000000 | 32781951 | 30071918 | 0.000000
09-04-2025 17:28:30000 | -1345450 | 134.545 | 15727690 | 235276.38 | 332435394 | 99323700 | 50121597 | 0.000000 | 32998394 | 30259158 | 0.000000
09-04-2025 17:28:35000 | -1351653 | 135.1653 | 15970660 | 235252.17 | 334045807 | 99309181 | 50148403 | 0.000000 | 33217700 | 30446311 | 0.000000
09-04-2025 17:28:40000 | -1351494 | 135.1494 | 16101678 | 235285.06 | 333993744 | 99297752 | 50158737 | 0.000000 | 33440054 | 30633779 | 0.000000
09-04-2025 17:28:45000 | -1354240 | 135.424 | 16090712 | 235200.19 | 334784698 | 99301514 | 50156857 | 0.000000 | 33664011 | 30821748 | 0.000000
09-04-2025 17:28:50000 | -1351797 | 135.1797 | 15637592 | 235144.55 | 334137238 | 99337547 | 50118504 | 0.000000 | 33882852 | 31009773 | 0.000000
09-04-2025 17:28:55000 | -1351120 | 135.112 | 15755587 | 235217.08 | 333904358 | 99326950 | 50109509 | 0.000000 | 34100659 | 31197553 | 0.000000
09-04-2025 17:29:00000 | -1353266 | 135.3266 | 14650434 | 234747.02 | 334793854 | 99419090 | 50123768 | 0.000000 | 34314790 | 31385109 | 0.000000
09-04-2025 17:29:05000 | -1346856 | 134.6856 | 14084443 | 234839.75 | 332949402 | 99457672 | 50140869 | 0.000000 | 34511926 | 31572457 | 0.000000
09-04-2025 17:29:10000 | -1341181 | 134.1181 | 13995741 | 234837.59 | 331538025 | 99459923 | 50172527 | 0.000000 | 34707739 | 31759613 | 0.000000
09-04-2025 17:29:15000 | -1353137 | 135.3137 | 14294477 | 234751.94 | 334666779 | 99446640 | 50159756 | 0.000000 | 34905923 | 31947459 | 0.000000
09-04-2025 17:29:20000 | -1348628 | 134.8628 | 14069396 | 234782.75 | 333461426 | 99460228 | 50151981 | 0.000000 | 35102805 | 32135160 | 0.000000
09-04-2025 17:29:25000 | -1356750 | 135.675 | 14247036 | 234751.13 | 335550476 | 99453178 | 50145092 | 0.000000 | 35299795 | 32323129 | 0.000000
09-04-2025 17:29:30000 | -1352022 | 135.2022 | 14068775 | 234782.33 | 334293243 | 99462959 | 50138432 | 0.000000 | 35494182 | 32510686 | 0.000000
09-04-2025 17:29:35000 | -1353271 | 135.3271 | 14152534 | 234786.53 | 334609955 | 99457596 | 50142193 | 0.000000 | 35690115 | 32698307 | 0.000000
09-04-2025 17:29:40000 | -1346297 | 134.6297 | 14363481 | 234918.70 | 332776703 | 99435684 | 50161266 | 0.000000 | 35888445 | 32885738 | 0.000000
09-04-2025 17:29:45000 | -1349753 | 134.9753 | 14459456 | 234896.89 | 333672668 | 99431084 | 50180779 | 0.000000 | 36086924 | 33073023 | 0.000000
09-04-2025 17:29:50000 | -1351922 | 135.1922 | 14693033 | 234865.05 | 334312164 | 99414589 | 50197865 | 0.000000 | 36291550 | 33260754 | 0.000000
09-04-2025 17:29:55000 | -1355850 | 135.585 | 14525549 | 234765.70 | 335364197 | 99431023 | 50156441 | 0.000000 | 36494583 | 33448984 | 0.000000
09-04-2025 17:30:00000 | -1347454 | 134.7454 | 14119652 | 234839.91 | 333103180 | 99455460 | 50129230 | 0.000000 | 36692292 | 33636563 | 0.000000
09-04-2025 17:30:05000 | -1348912 | 134.8912 | 13993744 | 234772.45 | 333522736 | 99466194 | 50141232 | 0.000000 | 19420750 | 187358810 | 0.000000
09-04-2025 17:30:10000 | -1350420 | 135.042 | 13904022 | 234731.73 | 333929047 | 99474129 | 50137352 | 0.000000 | 38691608 | 374888794 | 0.000000
09-04-2025 17:30:15000 | -1350911 | 135.0911 | 13853097 | 234687.02 | 334097717 | 99478325 | 50128422 | 0.000000 | 57961441 | 562418396 | 0.000000
09-04-2025 17:30:20000 | -1353724 | 135.3724 | 13883174 | 234697.42 | 334776794 | 99478233 | 50124180 | 0.000000 | 77202248 | 749996155 | 0.000000
09-04-2025 17:30:25000 | -1348314 | 134.8314 | 14077624 | 234806.11 | 333346924 | 99459351 | 50160076 | 0.000000 | 96659904 | 937003662 | 0.000000
09-04-2025 17:30:30000 | -1353982 | 135.3982 | 13788616 | 234623.42 | 334922180 | 99485458 | 50130638 | 0.000000 | 116052834 | 11252029 | 0.000000
09-04-2025 17:30:35000 | -1352275 | 135.2275 | 13698468 | 234691.05 | 334387726 | 99490837 | 50109699 | 0.000000 | 135034729 | 13129619 | 0.000000
09-04-2025 17:30:40000 | -1347305 | 134.7305 | 13640448 | 234706.70 | 333130493 | 99491402 | 50105320 | 0.000000 | 153921188 | 15002651 | 0.000000
09-04-2025 17:30:45000 | -1347792 | 134.7792 | 13368961 | 234584.11 | 333358429 | 99511650 | 50081970 | 0.000000 | 172690170 | 16875669 | 0.000000
09-04-2025 17:30:50000 | -1348011 | 134.8011 | 13513810 | 234672.67 | 333323334 | 99501251 | 50081829 | 0.000000 | 191273499 | 18746660 | 0.000000
09-04-2025 17:30:55000 | -1347484 | 134.7484 | 13637463 | 234679.08 | 333216400 | 99491760 | 50102036 | 0.000000 | 210037415 | 20613904 | 0.000000
09-04-2025 17:31:00000 | -1346711 | 134.6711 | 13857344 | 234771.50 | 332949097 | 99474770 | 50152054 | 0.000000 | 229119446 | 22479558 | 0.000000
09-04-2025 17:31:05000 | -1354586 | 135.4586 | 14022798 | 234654.19 | 335086487 | 99468437 | 50142376 | 0.000000 | 248561844 | 24355085 | 0.000000
09-04-2025 17:31:10000 | -1349971 | 134.9971 | 13722777 | 234657.25 | 333877808 | 99487312 | 50119026 | 0.000000 | 267857697 | 26233206 | 0.000000
09-04-2025 17:31:15000 | -1348017 | 134.8017 | 13729453 | 234703.91 | 333335236 | 99485336 | 50105419 | 0.000000 | 286992401 | 28108989 | 0.000000
09-04-2025 17:31:20000 | -1348151 | 134.8151 | 13983194 | 234787.73 | 333315674 | 99466400 | 50132809 | 0.000000 | 306254852 | 29981445 | 0.000000
09-04-2025 17:31:25000 | -1352990 | 135.299 | 14122991 | 234744.69 | 334597992 | 99459618 | 50148731 | 0.000000 | 325880981 | 31859602 | 0.000000
09-04-2025 17:31:30000 | -1348175 | 134.8175 | 13883892 | 234751.83 | 333342957 | 99473907 | 50146729 | 0.000000 | 345359039 | 33737151 | 0.000000
09-04-2025 17:31:35000 | -1351896 | 135.1896 | 14211094 | 234835.48 | 334221741 | 99452026 | 50159966 | 0.000000 | 364833954 | 35610876 | 0.000000
09-04-2025 17:31:40000 | -1358678 | 135.8678 | 14183123 | 234684.55 | 336087463 | 99459557 | 50159157 | 0.000000 | 384558838 | 37491042 | 0.000000
09-04-2025 17:31:45000 | -1354306 | 135.4306 | 13687945 | 234617.61 | 334985992 | 99493126 | 50103382 | 0.000000 | 403687622 | 39372507 | 0.000000
09-04-2025 17:31:50000 | -1344952 | 134.4952 | 13601356 | 234751.97 | 332478699 | 99492538 | 50091915 | 0.000000 | 422648529 | 41246133 | 0.000000
09-04-2025 17:31:55000 | -1347638 | 134.7638 | 13629425 | 234647.86 | 333296478 | 99492470 | 50106144 | 0.000000 | 441737122 | 43119375 | 0.000000
09-04-2025 17:32:00000 | -1347739 | 134.7739 | 13601759 | 234683.08 | 333265533 | 99494591 | 50099628 | 0.000000 | 460625305 | 44993438 | 0.000000
09-04-2025 17:32:05000 | -1346738 | 134.6738 | 13390990 | 234660.34 | 333004700 | 99509293 | 50091122 | 0.000000 | 479467224 | 46867856 | 0.000000
09-04-2025 17:32:10000 | -1353017 | 135.3017 | 13853115 | 234627.52 | 334704590 | 99479935 | 50111176 | 0.000000 | 498556824 | 48740244 | 0.000000
09-04-2025 17:32:15000 | -1345518 | 134.5518 | 13383321 | 234656.00 | 332706757 | 99508965 | 50090420 | 0.000000 | 517234436 | 50609722 | 0.000000
09-04-2025 17:32:20000 | -1341584 | 134.1584 | 13497557 | 234733.50 | 331664093 | 99497704 | 50098640 | 0.000000 | 536094360 | 52478999 | 0.000000
09-04-2025 17:32:25000 | -1349442 | 134.9442 | 14084313 | 234776.08 | 333671082 | 99459740 | 50140316 | 0.000000 | 555502197 | 54350391 | 0.000000
09-04-2025 17:32:30000 | -1355034 | 135.5034 | 14217162 | 234715.80 | 335157196 | 99454079 | 50142887 | 0.000000 | 575139038 | 56227803 | 0.000000
09-04-2025 17:32:35000 | -1351218 | 135.1218 | 13925622 | 234702.38 | 334170593 | 99473129 | 50122005 | 0.000000 | 594580872 | 58106313 | 0.000000
09-04-2025 17:32:40000 | -1353492 | 135.3492 | 14015234 | 234711.00 | 334734802 | 99468155 | 50117027 | 0.000000 | 614022156 | 59984067 | 0.000000
09-04-2025 17:32:45000 | -1350948 | 135.0948 | 13924375 | 234737.02 | 334058228 | 99473015 | 50111935 | 0.000000 | 633365906 | 61861621 | 0.000000
09-04-2025 17:32:50000 | -1348473 | 134.8473 | 14028641 | 234759.72 | 333446442 | 99463203 | 50123226 | 0.000000 | 652898193 | 63738472 | 0.000000
09-04-2025 17:32:55000 | -1351528 | 135.1528 | 13980118 | 234715.81 | 334239563 | 99469269 | 50128735 | 0.000000 | 672455261 | 65615420 | 0.000000
09-04-2025 17:33:00000 | -1352263 | 135.2263 | 14025471 | 234730.66 | 334409790 | 99466423 | 50128582 | 0.000000 | 691874939 | 67489238 | 0.000000
09-04-2025 17:33:05000 | -1352348 | 135.2348 | 13921743 | 234697.63 | 334459778 | 99474289 | 50088997 | 0.000000 | 711373596 | 69368931 | 0.000000
09-04-2025 17:33:10000 | -1350812 | 135.0812 | 13807620 | 234708.00 | 334036469 | 99481644 | 50086014 | 0.000000 | 730536255 | 71241812 | 0.000000
09-04-2025 17:33:15000 | -1350538 | 135.0538 | 13733350 | 234611.63 | 334086578 | 99486954 | 50096371 | 0.000000 | 749716980 | 73111572 | 0.000000
09-04-2025 17:33:20000 | -1345887 | 134.5887 | 13565975 | 234667.16 | 332825897 | 99495850 | 50071125 | 0.000000 | 768719055 | 74986401 | 0.000000
09-04-2025 17:33:25000 | -1347110 | 134.711 | 13620473 | 234716.39 | 333067902 | 99492737 | 50081833 | 0.000000 | 787517761 | 76858027 | 0.000000
09-04-2025 17:33:30000 | -1351218 | 135.1218 | 13731742 | 234676.14 | 334162170 | 99487587 | 50096386 | 0.000000 | 806542175 | 78733452 | 0.000000
09-04-2025 17:33:35000 | -1357012 | 135.7012 | 13515954 | 234497.64 | 335785828 | 99507645 | 50070210 | 0.000000 | 825396606 | 80614937 | 0.000000
09-04-2025 17:33:40000 | -1348616 | 134.8616 | 13093732 | 234576.14 | 333510010 | 99531982 | 50024475 | 0.000000 | 843687378 | 82491982 | 0.000000
09-04-2025 17:33:45000 | -1344330 | 134.433 | 13428177 | 234685.30 | 332392578 | 99504829 | 50068275 | 0.000000 | 862203674 | 84360830 | 0.000000
09-04-2025 17:33:50000 | -1349244 | 134.9244 | 13546943 | 234603.83 | 333734497 | 99499733 | 50084316 | 0.000000 | 881053345 | 86232676 | 0.000000
09-04-2025 17:33:55000 | -1351489 | 135.1489 | 13521478 | 234600.03 | 334279053 | 99503242 | 50074360 | 0.000000 | 899791260 | 88107051 | 0.000000
09-04-2025 17:34:00000 | -1355040 | 135.504 | 13462910 | 234590.75 | 335149872 | 99510063 | 50074986 | 0.000000 | 918520020 | 89984561 | 0.000000
09-04-2025 17:34:05000 | -1355591 | 135.5591 | 13743295 | 234651.84 | 335268097 | 99490013 | 50076744 | 0.000000 | 937310852 | 91861914 | 0.000000
09-04-2025 17:34:10000 | -1349360 | 134.936 | 13748697 | 234737.80 | 333622284 | 99484924 | 50095348 | 0.000000 | 956244568 | 93735176 | 0.000000
09-04-2025 17:34:15000 | -1352120 | 135.212 | 13624288 | 234592.83 | 334473236 | 99496178 | 50072559 | 0.000000 | 975266602 | 95611846 | 0.000000
09-04-2025 17:34:20000 | -1353422 | 135.3422 | 13440207 | 234574.77 | 334773041 | 99510536 | 50029987 | 0.000000 | 994096863 | 97492139 | 0.000000
09-04-2025 17:34:25000 | -1346024 | 134.6024 | 13266736 | 234631.14 | 332834381 | 99517784 | 50036633 | 0.000000 | 10126819 | 99364541 | 0.000000
09-04-2025 17:34:30000 | -1349213 | 134.9213 | 13482925 | 234592.14 | 333720032 | 99504395 | 50041668 | 0.000000 | 10313544 | 10123740 | 0.000000
09-04-2025 17:34:35000 | -1348533 | 134.8533 | 13170917 | 234536.48 | 333569550 | 99526428 | 50029064 | 0.000000 | 10498748 | 10311168 | 0.000000
09-04-2025 17:34:40000 | -1350986 | 135.0986 | 13375203 | 234594.55 | 334126495 | 99513489 | 50039845 | 0.000000 | 10683173 | 10498500 | 0.000000
09-04-2025 17:34:45000 | -1348260 | 134.826 | 13167591 | 234569.39 | 333444885 | 99526474 | 50028248 | 0.000000 | 10866876 | 10686005 | 0.000000
09-04-2025 17:34:50000 | -1348398 | 134.8398 | 13331245 | 234649.52 | 333409607 | 99514816 | 50036438 | 0.000000 | 11050096 | 10873062 | 0.000000
09-04-2025 17:34:55000 | -1348596 | 134.8596 | 13530995 | 234661.16 | 333486572 | 99500427 | 50058769 | 0.000000 | 11236256 | 11060126 | 0.000000
09-04-2025 17:35:00000 | -1350377 | 135.0377 | 13477076 | 234595.00 | 334005890 | 99505661 | 50071964 | 0.000000 | 11424469 | 11247478 | 0.000000
09-04-2025 17:35:05000 | -1346398 | 134.6398 | 13216917 | 234562.67 | 333011932 | 99521637 | 50030003 | 0.000000 | 11610023 | 11434862 | 0.000000
09-04-2025 17:35:10000 | -1346090 | 134.609 | 13466239 | 234686.00 | 332826355 | 99503326 | 50042953 | 0.000000 | 11794606 | 11621579 | 0.000000
09-04-2025 17:35:15000 | -1349008 | 134.9008 | 13629191 | 234624.78 | 333670013 | 99493507 | 50051689 | 0.000000 | 11983488 | 11808898 | 0.000000
09-04-2025 17:35:20000 | -1351146 | 135.1146 | 13447929 | 234594.89 | 334182068 | 99508339 | 50040188 | 0.000000 | 12171023 | 11996410 | 0.000000
09-04-2025 17:35:25000 | -1348601 | 134.8601 | 13689247 | 234733.70 | 333430542 | 99488762 | 50061546 | 0.000000 | 12360050 | 12183755 | 0.000000
09-04-2025 17:35:30000 | -1355284 | 135.5284 | 13859263 | 234633.97 | 335246033 | 99481201 | 50077213 | 0.000000 | 12551547 | 12371269 | 0.000000
09-04-2025 17:35:35000 | -1352213 | 135.2213 | 13529941 | 234603.83 | 334458984 | 99503151 | 50049553 | 0.000000 | 12740299 | 12559137 | 0.000000
09-04-2025 17:35:40000 | -1345431 | 134.5431 | 13554007 | 234756.83 | 332579315 | 99496391 | 50048397 | 0.000000 | 12926145 | 12746309 | 0.000000
09-04-2025 17:35:45000 | -1349112 | 134.9112 | 13832892 | 234719.08 | 333606628 | 99478455 | 50070717 | 0.000000 | 13115966 | 12933316 | 0.000000
09-04-2025 17:35:50000 | -1349132 | 134.9132 | 13689739 | 234647.63 | 333672424 | 99489128 | 50061958 | 0.000000 | 13307103 | 13120862 | 0.000000
09-04-2025 17:35:55000 | -1351839 | 135.1839 | 13609023 | 234631.30 | 334342285 | 99497093 | 50045052 | 0.000000 | 13495123 | 13308317 | 0.000000
09-04-2025 17:36:00000 | -1351028 | 135.1028 | 13250042 | 234519.73 | 334216736 | 99522522 | 50009354 | 0.000000 | 13681013 | 13495839 | 0.000000
09-04-2025 17:36:05000 | -1341022 | 134.1022 | 13521734 | 234795.16 | 331437988 | 99495491 | 50024448 | 0.000000 | 13865986 | 13682574 | 0.000000
09-04-2025 17:36:10000 | -1347244 | 134.7244 | 13873720 | 234725.63 | 333149750 | 99473953 | 50077538 | 0.000000 | 14057390 | 13869276 | 0.000000
09-04-2025 17:36:15000 | -1348422 | 134.8422 | 13621668 | 234648.78 | 333484833 | 99493629 | 50088741 | 0.000000 | 14248197 | 14056520 | 0.000000
09-04-2025 17:36:20000 | -1349649 | 134.9649 | 13477352 | 234590.03 | 333830109 | 99505112 | 50055294 | 0.000000 | 14437190 | 14243931 | 0.000000
09-04-2025 17:36:25000 | -1345624 | 134.5624 | 13716900 | 234750.84 | 332679230 | 99484459 | 50054928 | 0.000000 | 14624568 | 14430767 | 0.000000
09-04-2025 17:36:30000 | -1343030 | 134.303 | 13780490 | 234749.86 | 332063507 | 99477707 | 50068268 | 0.000000 | 14815352 | 14617216 | 0.000000
09-04-2025 17:36:35000 | -1344467 | 134.4467 | 14034918 | 234795.67 | 332409424 | 99459549 | 50093124 | 0.000000 | 15009645 | 14804276 | 0.000000
09-04-2025 17:36:40000 | -1351448 | 135.1448 | 14131461 | 234716.00 | 334256317 | 99457748 | 50104179 | 0.000000 | 15206309 | 14991638 | 0.000000
09-04-2025 17:36:45000 | -1346881 | 134.6881 | 14089943 | 234779.25 | 333042206 | 99457268 | 50094814 | 0.000000 | 15402515 | 15178991 | 0.000000
09-04-2025 17:36:50000 | -1353011 | 135.3011 | 13935938 | 234662.53 | 334664612 | 99473740 | 50064636 | 0.000000 | 15598002 | 15366922 | 0.000000
09-04-2025 17:36:55000 | -1348543 | 134.8543 | 13597411 | 234644.86 | 333516357 | 99495506 | 50015636 | 0.000000 | 15788671 | 15554487 | 0.000000
09-04-2025 17:37:00000 | -1350866 | 135.0866 | 13703664 | 234669.83 | 334078003 | 99489395 | 50022003 | 0.000000 | 15978273 | 15741556 | 0.000000
09-04-2025 17:37:05000 | -1351141 | 135.1141 | 13926100 | 234719.48 | 334127686 | 99473030 | 50030666 | 0.000000 | 16169799 | 15928729 | 0.000000
09-04-2025 17:37:10000 | -1351855 | 135.1855 | 13790280 | 234652.39 | 334366028 | 99483727 | 50029305 | 0.000000 | 16361375 | 16116020 | 0.000000
09-04-2025 17:37:15000 | -1348454 | 134.8454 | 13733167 | 234679.27 | 333474670 | 99485390 | 50031437 | 0.000000 | 16552842 | 16303367 | 0.000000
09-04-2025 17:37:20000 | -1349220 | 134.922 | 13357240 | 234558.94 | 333739288 | 99513527 | 50000206 | 0.000000 | 16741232 | 16490963 | 0.000000
09-04-2025 17:37:25000 | -1346005 | 134.6005 | 13357851 | 234650.48 | 332825714 | 99511169 | 49994335 | 0.000000 | 16926608 | 16678172 | 0.000000
09-04-2025 17:37:30000 | -1347690 | 134.769 | 13213537 | 234567.64 | 333321320 | 99522789 | 49993114 | 0.000000 | 17111166 | 16865229 | 0.000000
09-04-2025 17:37:35000 | -1345203 | 134.5203 | 13199861 | 234631.45 | 332613800 | 99522018 | 49997692 | 0.000000 | 17293866 | 17052252 | 0.000000
09-04-2025 17:37:40000 | -1342316 | 134.2316 | 14089592 | 234875.39 | 331791504 | 99453629 | 50097515 | 0.000000 | 17485911 | 17238414 | 0.000000
09-04-2025 17:37:45000 | -1352153 | 135.2153 | 14342932 | 234772.81 | 334401978 | 99442108 | 50112759 | 0.000000 | 17684088 | 17425982 | 0.000000
09-04-2025 17:37:50000 | -1349043 | 134.9043 | 14361591 | 234915.22 | 333450867 | 99438110 | 50121777 | 0.000000 | 17883451 | 17613672 | 0.000000
09-04-2025 17:37:55000 | -1353199 | 135.3199 | 14598576 | 234894.89 | 334562622 | 99423103 | 50143162 | 0.000000 | 18085065 | 17801289 | 0.000000
09-04-2025 17:38:00000 | -1359672 | 135.9672 | 14713654 | 234830.53 | 336254303 | 99419571 | 50133923 | 0.000000 | 18288094 | 17989525 | 0.000000
09-04-2025 17:38:05000 | -1348657 | 134.8657 | 14378238 | 234899.47 | 333377350 | 99436501 | 50104214 | 0.000000 | 18488744 | 18177650 | 0.000000
09-04-2025 17:38:10000 | -1347838 | 134.7838 | 14662404 | 234955.58 | 333171265 | 99413498 | 50121937 | 0.000000 | 18692092 | 18365229 | 0.000000
09-04-2025 17:38:15000 | -1352868 | 135.2868 | 14604587 | 234885.05 | 334490204 | 99422356 | 50124058 | 0.000000 | 18895531 | 18552939 | 0.000000
09-04-2025 17:38:20000 | -1356323 | 135.6323 | 14719393 | 234869.70 | 335382629 | 99416275 | 50111969 | 0.000000 | 19100461 | 18741207 | 0.000000
09-04-2025 17:38:25000 | -1356672 | 135.6672 | 14649955 | 234882.23 | 335430359 | 99422020 | 50083511 | 0.000000 | 19303656 | 18929508 | 0.000000
09-04-2025 17:38:30000 | -1347130 | 134.713 | 14253879 | 234895.81 | 332974915 | 99444878 | 50066246 | 0.000000 | 19503354 | 19117006 | 0.000000
09-04-2025 17:38:35000 | -1349394 | 134.9394 | 14275784 | 234827.09 | 333633484 | 99445038 | 50067944 | 0.000000 | 19702301 | 19304291 | 0.000000
09-04-2025 17:38:40000 | -1355088 | 135.5088 | 14189608 | 234709.02 | 335172424 | 99456223 | 50039543 | 0.000000 | 19900150 | 19492199 | 0.000000
09-04-2025 17:38:45000 | -1346607 | 134.6607 | 13971482 | 234821.66 | 332885956 | 99466072 | 50041233 | 0.000000 | 20093484 | 19679482 | 0.000000
09-04-2025 17:38:50000 | -1349846 | 134.9846 | 14315567 | 234826.63 | 333752930 | 99442337 | 50083920 | 0.000000 | 20291312 | 19866861 | 0.000000
09-04-2025 17:38:55000 | -1355692 | 135.5692 | 14163512 | 234676.08 | 335358063 | 99458679 | 50065556 | 0.000000 | 20488843 | 20054955 | 0.000000
09-04-2025 17:39:00000 | -1350134 | 135.0134 | 13754949 | 234724.78 | 333827606 | 99485046 | 50038692 | 0.000000 | 20681582 | 20242814 | 0.000000
09-04-2025 17:39:05000 | -1347844 | 134.7844 | 14194572 | 234868.11 | 333178741 | 99450027 | 50058578 | 0.000000 | 20876228 | 20430215 | 0.000000
09-04-2025 17:39:10000 | -1349460 | 134.946 | 14417738 | 234890.44 | 333601379 | 99434090 | 50098312 | 0.000000 | 21075483 | 20617594 | 0.000000
09-04-2025 17:39:15000 | -1352182 | 135.2182 | 14774057 | 234949.11 | 334275146 | 99408394 | 50131649 | 0.000000 | 21278728 | 20805240 | 0.000000
09-04-2025 17:39:20000 | -1356826 | 135.6826 | 14686636 | 234833.30 | 335548157 | 99419273 | 50117134 | 0.000000 | 21482119 | 20993168 | 0.000000
09-04-2025 17:39:25000 | -1347545 | 134.7545 | 14346552 | 234912.25 | 333081451 | 99438042 | 50085155 | 0.000000 | 21682886 | 21181133 | 0.000000
09-04-2025 17:39:30000 | -1350283 | 135.0283 | 14714924 | 234925.42 | 333831482 | 99411438 | 50112640 | 0.000000 | 21886321 | 21368703 | 0.000000
09-04-2025 17:39:35000 | -1349490 | 134.949 | 14390250 | 234799.44 | 333734192 | 99436256 | 50104893 | 0.000000 | 22089106 | 21556582 | 0.000000
09-04-2025 17:39:40000 | -1350763 | 135.0763 | 14198738 | 234745.41 | 334066254 | 99452065 | 50065525 | 0.000000 | 22288740 | 21744408 | 0.000000
09-04-2025 17:39:45000 | -1346666 | 134.6666 | 13964457 | 234796.42 | 332933563 | 99466652 | 50023705 | 0.000000 | 22484304 | 21932010 | 0.000000
09-04-2025 17:39:50000 | -1349345 | 134.9345 | 14163481 | 234831.67 | 333583466 | 99453621 | 50036789 | 0.000000 | 22679856 | 22119061 | 0.000000
09-04-2025 17:39:55000 | -1348598 | 134.8598 | 14054341 | 234742.66 | 333504395 | 99461349 | 50035992 | 0.000000 | 22876711 | 22306488 | 0.000000
09-04-2025 17:40:00000 | -1353284 | 135.3284 | 14169461 | 234767.63 | 334650116 | 99456314 | 50036007 | 0.000000 | 23073135 | 22493912 | 0.000000
09-04-2025 17:40:05000 | -1350290 | 135.029 | 13798462 | 234704.36 | 333907623 | 99481926 | 50009037 | 0.000000 | 23265540 | 22681443 | 0.000000
09-04-2025 17:40:10000 | -1348111 | 134.8111 | 13760385 | 234693.59 | 333380737 | 99483109 | 50009941 | 0.000000 | 23457178 | 22868646 | 0.000000
09-04-2025 17:40:15000 | -1348607 | 134.8607 | 13621082 | 234641.63 | 333546356 | 99493805 | 49992756 | 0.000000 | 23646611 | 23055764 | 0.000000
09-04-2025 17:40:20000 | -1340578 | 134.0578 | 13352093 | 234643.44 | 331504333 | 99507660 | 49994717 | 0.000000 | 23833293 | 23242160 | 0.000000
09-04-2025 17:40:25000 | -1335530 | 133.553 | 13401901 | 234701.47 | 330199554 | 99500275 | 50014114 | 0.000000 | 24019661 | 23428281 | 0.000000
09-04-2025 17:40:30000 | -1342328 | 134.2328 | 13626983 | 234709.75 | 331913483 | 99488655 | 50032677 | 0.000000 | 24207703 | 23614570 | 0.000000
09-04-2025 17:40:35000 | -1342073 | 134.2073 | 13773442 | 234750.91 | 331825806 | 99477493 | 50049881 | 0.000000 | 24398857 | 23801092 | 0.000000
09-04-2025 17:40:40000 | -1347803 | 134.7803 | 14247224 | 234849.38 | 333207611 | 99445938 | 50073463 | 0.000000 | 24594202 | 23987941 | 0.000000
09-04-2025 17:40:45000 | -1350027 | 135.0027 | 14241295 | 234813.41 | 333800751 | 99448204 | 50073814 | 0.000000 | 24791550 | 24175123 | 0.000000
09-04-2025 17:40:50000 | -1346992 | 134.6992 | 14239891 | 234820.36 | 333045990 | 99445847 | 50064190 | 0.000000 | 24989304 | 24362285 | 0.000000
09-04-2025 17:40:55000 | -1346980 | 134.698 | 14285877 | 234826.52 | 333049377 | 99442284 | 50055252 | 0.000000 | 25188350 | 24549504 | 0.000000
09-04-2025 17:41:00000 | -1346913 | 134.6913 | 14449748 | 234896.14 | 332973022 | 99429466 | 50075272 | 0.000000 | 25387739 | 24736381 | 0.000000
09-04-2025 17:41:05000 | -1350693 | 135.0693 | 14382126 | 234768.56 | 334070465 | 99437881 | 50062069 | 0.000000 | 25588906 | 24923906 | 0.000000
09-04-2025 17:41:10000 | -1348785 | 134.8785 | 13878715 | 234737.81 | 333512634 | 99474770 | 50012794 | 0.000000 | 25782939 | 25111357 | 0.000000
09-04-2025 17:41:15000 | -1345520 | 134.552 | 14080313 | 234849.27 | 332608917 | 99456917 | 50023445 | 0.000000 | 25976187 | 25297826 | 0.000000
09-04-2025 17:41:20000 | -1345030 | 134.503 | 14384527 | 234906.52 | 332484009 | 99432991 | 50059311 | 0.000000 | 26174771 | 25484443 | 0.000000
09-04-2025 17:41:25000 | -1350341 | 135.0341 | 14405969 | 234812.83 | 333919189 | 99435738 | 50056896 | 0.000000 | 26374561 | 25671414 | 0.000000
09-04-2025 17:41:30000 | -1343027 | 134.3027 | 14240035 | 234867.20 | 332023529 | 99442581 | 50058922 | 0.000000 | 26573657 | 25858438 | 0.000000
09-04-2025 17:41:35000 | -1347494 | 134.7494 | 14552041 | 234890.77 | 333148254 | 99421921 | 50072647 | 0.000000 | 26774937 | 26045496 | 0.000000
09-04-2025 17:41:40000 | -1351521 | 135.1521 | 14274490 | 234757.48 | 334255371 | 99446869 | 50058067 | 0.000000 | 26974426 | 26232762 | 0.000000
09-04-2025 17:41:45000 | -1347335 | 134.7335 | 13936559 | 234718.22 | 333205963 | 99469284 | 50020454 | 0.000000 | 27169692 | 26419914 | 0.000000
09-04-2025 17:41:50000 | -1340998 | 134.0998 | 14191216 | 234940.11 | 331402954 | 99444702 | 50021770 | 0.000000 | 27363977 | 26606537 | 0.000000
09-04-2025 17:41:55000 | -1345221 | 134.5221 | 14236911 | 234786.41 | 332661896 | 99444626 | 50044975 | 0.000000 | 27562988 | 26793182 | 0.000000
09-04-2025 17:42:00000 | -1341321 | 134.1321 | 14096420 | 234843.59 | 331590057 | 99452301 | 50039005 | 0.000000 | 27759480 | 26979783 | 0.000000
09-04-2025 17:42:05000 | -1350124 | 135.0124 | 14395415 | 234786.69 | 333908569 | 99436378 | 50044579 | 0.000000 | 27958479 | 27166592 | 0.000000
09-04-2025 17:42:10000 | -1345564 | 134.5564 | 14125453 | 234813.92 | 332679260 | 99453491 | 50031528 | 0.000000 | 28154836 | 27353412 | 0.000000
09-04-2025 17:42:15000 | -1343334 | 134.3334 | 14208892 | 234870.44 | 332072479 | 99445251 | 50056252 | 0.000000 | 28351423 | 27539832 | 0.000000
09-04-2025 17:42:20000 | -1347276 | 134.7276 | 14250577 | 234789.56 | 333161285 | 99445251 | 50054939 | 0.000000 | 28549260 | 27726779 | 0.000000
09-04-2025 17:42:25000 | -1348117 | 134.8117 | 14033848 | 234759.19 | 333362000 | 99462524 | 50026722 | 0.000000 | 28745425 | 27914176 | 0.000000
09-04-2025 17:42:30000 | -1347938 | 134.7938 | 14399841 | 234883.50 | 333232422 | 99434219 | 50055698 | 0.000000 | 28942700 | 28100957 | 0.000000
09-04-2025 17:42:35000 | -1346349 | 134.6349 | 14296574 | 234837.39 | 332878479 | 99440933 | 50070133 | 0.000000 | 29140957 | 28287916 | 0.000000
09-04-2025 17:42:40000 | -1342960 | 134.296 | 14222472 | 234885.64 | 331966583 | 99443893 | 50086773 | 0.000000 | 29339255 | 28474910 | 0.000000
09-04-2025 17:42:45000 | -1346587 | 134.6587 | 14471651 | 234885.48 | 332919373 | 99427475 | 50103607 | 0.000000 | 29538945 | 28661953 | 0.000000
09-04-2025 17:42:50000 | -1347104 | 134.7104 | 14385555 | 234849.05 | 333072357 | 99434639 | 50105637 | 0.000000 | 29739250 | 28848885 | 0.000000
09-04-2025 17:42:55000 | -1349848 | 134.9848 | 14305358 | 234790.69 | 333803070 | 99443123 | 50085556 | 0.000000 | 29939155 | 29036074 | 0.000000
09-04-2025 17:43:00000 | -1350189 | 135.0189 | 14290083 | 234787.69 | 333893829 | 99444580 | 50062222 | 0.000000 | 30137419 | 29223189 | 0.000000
09-04-2025 17:43:05000 | -1345558 | 134.5558 | 13809302 | 234718.33 | 332728577 | 99477493 | 50042446 | 0.000000 | 30331157 | 29409865 | 0.000000
09-04-2025 17:43:10000 | -1343314 | 134.3314 | 14114920 | 234870.77 | 332046143 | 99452492 | 50059261 | 0.000000 | 30525227 | 29596508 | 0.000000
09-04-2025 17:43:15000 | -1344782 | 134.4782 | 14253808 | 234848.55 | 332472595 | 99442955 | 50077271 | 0.000000 | 30723416 | 29783424 | 0.000000
09-04-2025 17:43:20000 | -1350696 | 135.0696 | 14164857 | 234724.09 | 334073639 | 99454597 | 50062191 | 0.000000 | 30921577 | 29970752 | 0.000000
09-04-2025 17:43:25000 | -1347539 | 134.7539 | 13663727 | 234673.52 | 333243195 | 99489853 | 50008869 | 0.000000 | 31114119 | 30158357 | 0.000000
09-04-2025 17:43:30000 | -1344368 | 134.4368 | 13767671 | 234738.66 | 332399048 | 99479698 | 50008728 | 0.000000 | 31305063 | 30345100 | 0.000000
09-04-2025 17:43:35000 | -1340309 | 134.0309 | 13814538 | 234816.19 | 331316101 | 99473022 | 50045498 | 0.000000 | 31496189 | 30531508 | 0.000000
09-04-2025 17:43:40000 | -1342000 | 134.2 | 13870955 | 234772.42 | 331799652 | 99470078 | 50080704 | 0.000000 | 31690552 | 30718074 | 0.000000
09-04-2025 17:43:45000 | -1349066 | 134.9066 | 13725353 | 234616.00 | 333711060 | 99486435 | 50054008 | 0.000000 | 31882683 | 30905209 | 0.000000
09-04-2025 17:43:50000 | -1343274 | 134.3274 | 13257798 | 234622.45 | 332171661 | 99516472 | 49997910 | 0.000000 | 32068240 | 31092262 | 0.000000
09-04-2025 17:43:55000 | -1346127 | 134.6127 | 13361137 | 234548.47 | 332998871 | 99511024 | 49979527 | 0.000000 | 32253157 | 31278895 | 0.000000
09-04-2025 17:44:00000 | -1342681 | 134.2681 | 13117742 | 234594.52 | 332032318 | 99526146 | 49956997 | 0.000000 | 32435669 | 31465613 | 0.000000
09-04-2025 17:44:05000 | -1339710 | 133.971 | 13250325 | 234582.97 | 331351257 | 99514458 | 49980892 | 0.000000 | 32620500 | 31651969 | 0.000000
09-04-2025 17:44:10000 | -1346343 | 134.6343 | 13187042 | 234492.22 | 333095886 | 99523743 | 49965363 | 0.000000 | 32804656 | 31838789 | 0.000000
09-04-2025 17:44:15000 | -1341556 | 134.1556 | 13106975 | 234605.09 | 331743622 | 99526131 | 49964119 | 0.000000 | 32985979 | 32025133 | 0.000000
09-04-2025 17:44:20000 | -1344897 | 134.4897 | 13197971 | 234630.41 | 332549530 | 99521942 | 49963554 | 0.000000 | 33168709 | 32211723 | 0.000000
09-04-2025 17:44:25000 | -1341672 | 134.1672 | 13340074 | 234657.84 | 331754883 | 99509331 | 49989426 | 0.000000 | 33353525 | 32398133 | 0.000000
09-04-2025 17:44:30000 | -1341892 | 134.1892 | 13627040 | 234721.20 | 331788696 | 99488327 | 50013542 | 0.000000 | 33541987 | 32584779 | 0.000000
09-04-2025 17:44:35000 | -1347818 | 134.7818 | 13709084 | 234652.59 | 333355133 | 99486702 | 50034386 | 0.000000 | 33731619 | 32771590 | 0.000000
09-04-2025 17:44:40000 | -1345558 | 134.5558 | 13371101 | 234586.59 | 332814331 | 99509888 | 50033146 | 0.000000 | 33918735 | 32958539 | 0.000000
09-04-2025 17:44:45000 | -1346843 | 134.6843 | 13661461 | 234692.55 | 333045685 | 99489502 | 50058754 | 0.000000 | 34107070 | 33145438 | 0.000000
09-04-2025 17:44:50000 | -1349868 | 134.9868 | 13684169 | 234637.61 | 333868225 | 99490089 | 50067478 | 0.000000 | 34296233 | 33332617 | 0.000000
09-04-2025 17:44:55000 | -1351453 | 135.1453 | 13301376 | 234527.55 | 334321045 | 99519135 | 50038475 | 0.000000 | 34483091 | 33520324 | 0.000000
09-04-2025 17:45:00000 | -1341932 | 134.1932 | 13618676 | 234800.88 | 331682617 | 99488976 | 50040173 | 0.000000 | 34669412 | 33707488 | 0.000000
09-04-2025 17:45:05000 | -1349755 | 134.9755 | 14149658 | 234778.91 | 333757599 | 99455009 | 50067520 | 0.000000 | 19483784 | 187162598 | 0.000000
09-04-2025 17:45:10000 | -1350127 | 135.0127 | 14367279 | 234857.23 | 333792877 | 99438560 | 50095001 | 0.000000 | 39249634 | 374206909 | 0.000000
09-04-2025 17:45:15000 | -1350615 | 135.0615 | 14422189 | 234839.53 | 333955750 | 99434708 | 50103752 | 0.000000 | 59254551 | 561796326 | 0.000000
09-04-2025 17:45:20000 | -1352947 | 135.2947 | 14408067 | 234804.69 | 334571655 | 99437729 | 50108929 | 0.000000 | 79295952 | 749368530 | 0.000000
09-04-2025 17:45:25000 | -1350725 | 135.0725 | 14376291 | 234873.56 | 333919067 | 99438354 | 50089931 | 0.000000 | 99269653 | 937048584 | 0.000000
09-04-2025 17:45:30000 | -1344644 | 134.4644 | 14389147 | 234916.92 | 332379059 | 99432304 | 50100155 | 0.000000 | 119372360 | 11242607 | 0.000000
09-04-2025 17:45:35000 | -1348855 | 134.8855 | 14485277 | 234930.58 | 333412079 | 99428314 | 50115273 | 0.000000 | 139412476 | 13113452 | 0.000000
09-04-2025 17:45:40000 | -1350036 | 135.0036 | 14687844 | 234931.47 | 333750183 | 99413376 | 50119312 | 0.000000 | 159793488 | 14989526 | 0.000000
09-04-2025 17:45:45000 | -1348819 | 134.8819 | 14694555 | 234919.70 | 333474670 | 99411789 | 50122105 | 0.000000 | 180280991 | 16866023 | 0.000000
09-04-2025 17:45:50000 | -1350520 | 135.052 | 14733396 | 234913.09 | 333907898 | 99410179 | 50115692 | 0.000000 | 200799500 | 18742273 | 0.000000
09-04-2025 17:45:55000 | -1351185 | 135.1185 | 14590758 | 234877.59 | 334084808 | 99422012 | 50097527 | 0.000000 | 221178864 | 20618740 | 0.000000
09-04-2025 17:46:00000 | -1352226 | 135.2226 | 14625881 | 234929.70 | 334276031 | 99420135 | 50076847 | 0.000000 | 241465530 | 22497161 | 0.000000
09-04-2025 17:46:05000 | -1346814 | 134.6814 | 14666493 | 235003.86 | 332854980 | 99412285 | 50099983 | 0.000000 | 261904755 | 24371074 | 0.000000
09-04-2025 17:46:10000 | -1352953 | 135.2953 | 14860006 | 234900.27 | 334551910 | 99402229 | 50122353 | 0.000000 | 282547394 | 26248003 | 0.000000
09-04-2025 17:46:15000 | -1349304 | 134.9304 | 14582789 | 234925.16 | 333557770 | 99421043 | 50109425 | 0.000000 | 302922516 | 28125283 | 0.000000
09-04-2025 17:46:20000 | -1344035 | 134.4035 | 14275520 | 234863.80 | 332281189 | 99440659 | 50104355 | 0.000000 | 323095734 | 29998174 | 0.000000
09-04-2025 17:46:25000 | -1351137 | 135.1137 | 14875318 | 234959.27 | 334040710 | 99399414 | 50117157 | 0.000000 | 343511780 | 31873137 | 0.000000
09-04-2025 17:46:30000 | -1353335 | 135.3335 | 14682954 | 234842.80 | 334683411 | 99416595 | 50104683 | 0.000000 | 364001007 | 33750068 | 0.000000
09-04-2025 17:46:35000 | -1351908 | 135.1908 | 14468760 | 234843.94 | 334275238 | 99432159 | 50073601 | 0.000000 | 384166809 | 35629395 | 0.000000
09-04-2025 17:46:40000 | -1350540 | 135.054 | 14608592 | 234924.73 | 333862274 | 99420059 | 50072063 | 0.000000 | 404370758 | 37505452 | 0.000000
09-04-2025 17:46:45000 | -1345771 | 134.5771 | 14284611 | 234871.31 | 332690216 | 99441383 | 50069069 | 0.000000 | 424309784 | 39374893 | 0.000000
09-04-2025 17:46:50000 | -1347837 | 134.7837 | 14337872 | 234836.22 | 333256042 | 99438957 | 50061424 | 0.000000 | 444339661 | 41249590 | 0.000000
09-04-2025 17:46:55000 | -1347853 | 134.7853 | 14147011 | 234804.44 | 333259338 | 99453682 | 50041786 | 0.000000 | 464145111 | 43125391 | 0.000000
09-04-2025 17:47:00000 | -1344513 | 134.4513 | 14192340 | 234903.08 | 332315979 | 99447495 | 50053150 | 0.000000 | 483765472 | 44993438 | 0.000000
09-04-2025 17:47:05000 | -1349614 | 134.9614 | 14271632 | 234806.31 | 333719696 | 99445534 | 50061722 | 0.000000 | 503527771 | 46864126 | 0.000000
09-04-2025 17:47:10000 | -1347978 | 134.7978 | 14181636 | 234780.47 | 333332092 | 99451126 | 50058578 | 0.000000 | 523315430 | 48738623 | 0.000000
09-04-2025 17:47:15000 | -1351792 | 135.1792 | 14324043 | 234808.81 | 334258789 | 99443275 | 50063038 | 0.000000 | 543069519 | 50612524 | 0.000000
09-04-2025 17:47:20000 | -1348583 | 134.8583 | 14025168 | 234739.70 | 333500885 | 99463554 | 50056362 | 0.000000 | 562845337 | 52487095 | 0.000000
09-04-2025 17:47:25000 | -1345582 | 134.5582 | 14349254 | 234946.83 | 332553772 | 99436203 | 50075928 | 0.000000 | 582489868 | 54356958 | 0.000000
09-04-2025 17:47:30000 | -1353609 | 135.3609 | 14588987 | 234892.69 | 334653992 | 99424202 | 50101303 | 0.000000 | 602665527 | 56233081 | 0.000000
09-04-2025 17:47:35000 | -1355352 | 135.5352 | 14497293 | 234804.95 | 335180725 | 99432808 | 50090851 | 0.000000 | 622821716 | 58113389 | 0.000000
09-04-2025 17:47:40000 | -1355015 | 135.5015 | 14506662 | 234836.38 | 335054871 | 99431801 | 50091984 | 0.000000 | 642957520 | 59992529 | 0.000000
09-04-2025 17:47:45000 | -1350934 | 135.0934 | 14224602 | 234813.02 | 334017944 | 99450218 | 50077415 | 0.000000 | 662888184 | 61871387 | 0.000000
09-04-2025 17:47:50000 | -1353480 | 135.348 | 14403729 | 234835.72 | 334655701 | 99438507 | 50082703 | 0.000000 | 682860596 | 63750210 | 0.000000
09-04-2025 17:47:55000 | -1351077 | 135.1077 | 14396217 | 234836.23 | 334062866 | 99437103 | 50091541 | 0.000000 | 702917847 | 65627910 | 0.000000
09-04-2025 17:48:00000 | -1352452 | 135.2452 | 14455659 | 234878.58 | 334357117 | 99433632 | 50102276 | 0.000000 | 722955322 | 67506279 | 0.000000
09-04-2025 17:48:05000 | -1351246 | 135.1246 | 14527463 | 234897.80 | 334052094 | 99427025 | 50113171 | 0.000000 | 743124451 | 69385322 | 0.000000
09-04-2025 17:48:10000 | -1361644 | 136.1644 | 14521531 | 234750.92 | 336803864 | 99436127 | 50102825 | 0.000000 | 763236816 | 71266953 | 0.000000
09-04-2025 17:48:15000 | -1352912 | 135.2912 | 14176005 | 234795.69 | 334517181 | 99455521 | 50077053 | 0.000000 | 782932983 | 73145830 | 0.000000
09-04-2025 17:48:20000 | -1352984 | 135.2984 | 14272701 | 234853.31 | 334474335 | 99448189 | 50076073 | 0.000000 | 802619995 | 75023062 | 0.000000
09-04-2025 17:48:25000 | -1352964 | 135.2964 | 14460074 | 234869.72 | 334504456 | 99433716 | 50097462 | 0.000000 | 822594971 | 76899243 | 0.000000
09-04-2025 17:48:30000 | -1354258 | 135.4258 | 14620183 | 234879.06 | 334843567 | 99422310 | 50096897 | 0.000000 | 842833313 | 78780200 | 0.000000
09-04-2025 17:48:35000 | -1354261 | 135.4261 | 14663573 | 234889.63 | 334839233 | 99418907 | 50115540 | 0.000000 | 863114258 | 80659468 | 0.000000
09-04-2025 17:48:40000 | -1357634 | 135.7634 | 14529890 | 234806.52 | 335750000 | 99432167 | 50103714 | 0.000000 | 883415344 | 82542598 | 0.000000
09-04-2025 17:48:45000 | -1353269 | 135.3269 | 14405953 | 234861.06 | 334568390 | 99438156 | 50088497 | 0.000000 | 903486694 | 84425391 | 0.000000
09-04-2025 17:48:50000 | -1351460 | 135.146 | 14389202 | 234882.73 | 334097412 | 99437965 | 50098644 | 0.000000 | 923505981 | 86303809 | 0.000000
09-04-2025 17:48:55000 | -1353685 | 135.3685 | 14310810 | 234777.64 | 334767151 | 99445831 | 50105988 | 0.000000 | 943687012 | 88184912 | 0.000000
09-04-2025 17:49:00000 | -1350282 | 135.0282 | 14267009 | 234843.08 | 333828613 | 99446434 | 50089554 | 0.000000 | 963517395 | 90063672 | 0.000000
09-04-2025 17:49:05000 | -1354260 | 135.426 | 14744861 | 234920.59 | 334815857 | 99412498 | 50093903 | 0.000000 | 983781860 | 91942275 | 0.000000
09-04-2025 17:49:10000 | -1356932 | 135.6932 | 14685614 | 234900.19 | 335488007 | 99419449 | 50112743 | 0.000000 | 10042126 | 93824033 | 0.000000
09-04-2025 17:49:15000 | -1358792 | 135.8792 | 14693421 | 234846.34 | 336013733 | 99420410 | 50112473 | 0.000000 | 10245764 | 95707334 | 0.000000
09-04-2025 17:49:20000 | -1360704 | 136.0704 | 14429703 | 234737.61 | 336570526 | 99442413 | 50084141 | 0.000000 | 10448020 | 97592305 | 0.000000
09-04-2025 17:49:25000 | -1346588 | 134.6588 | 13995705 | 234817.36 | 332894653 | 99464218 | 50042980 | 0.000000 | 10644816 | 99475596 | 0.000000
09-04-2025 17:49:30000 | -1349100 | 134.91 | 14319370 | 234855.47 | 333536865 | 99441429 | 50066631 | 0.000000 | 10843575 | 10135273 | 0.000000
09-04-2025 17:49:35000 | -1351793 | 135.1793 | 14462214 | 234862.22 | 334220825 | 99432571 | 50086979 | 0.000000 | 11044210 | 10322982 | 0.000000
09-04-2025 17:49:40000 | -1355499 | 135.5499 | 14460198 | 234812.94 | 335202576 | 99435799 | 50079723 | 0.000000 | 11244995 | 10510970 | 0.000000
09-04-2025 17:49:45000 | -1357799 | 135.7799 | 14052724 | 234666.44 | 335865601 | 99468689 | 50049973 | 0.000000 | 11442150 | 10699000 | 0.000000
09-04-2025 17:49:50000 | -1351097 | 135.1097 | 13702208 | 234718.94 | 334065216 | 99489677 | 50018723 | 0.000000 | 11634700 | 10887124 | 0.000000
09-04-2025 17:49:55000 | -1350397 | 135.0397 | 14014670 | 234778.02 | 333886169 | 99465775 | 50043682 | 0.000000 | 11828402 | 11074772 | 0.000000
09-04-2025 17:50:00000 | -1356364 | 135.6364 | 13903627 | 234615.83 | 335550262 | 99478722 | 50039688 | 0.000000 | 12021732 | 11262827 | 0.000000
09-04-2025 17:50:05000 | -1352667 | 135.2667 | 13602294 | 234687.48 | 334468384 | 99498199 | 50018032 | 0.000000 | 12211132 | 11450979 | 0.000000
09-04-2025 17:50:10000 | -1351099 | 135.1099 | 13382413 | 234617.80 | 334126465 | 99513054 | 50024242 | 0.000000 | 12398618 | 11638646 | 0.000000
09-04-2025 17:50:15000 | -1352039 | 135.2039 | 13607840 | 234677.55 | 334338898 | 99497330 | 50034695 | 0.000000 | 12585066 | 11825938 | 0.000000
09-04-2025 17:50:20000 | -1347918 | 134.7918 | 13384447 | 234621.69 | 333343872 | 99510620 | 50028831 | 0.000000 | 12772119 | 12013352 | 0.000000
09-04-2025 17:50:25000 | -1348213 | 134.8213 | 13471915 | 234677.52 | 333355591 | 99504463 | 50026066 | 0.000000 | 12958191 | 12200810 | 0.000000
09-04-2025 17:50:30000 | -1351678 | 135.1678 | 13798374 | 234722.33 | 334222107 | 99482986 | 50054386 | 0.000000 | 13149227 | 12388445 | 0.000000
09-04-2025 17:50:35000 | -1353697 | 135.3697 | 13913106 | 234680.25 | 334810242 | 99475975 | 50078022 | 0.000000 | 13342704 | 12576399 | 0.000000
09-04-2025 17:50:40000 | -1355075 | 135.5075 | 13876038 | 234656.52 | 335164673 | 99479797 | 50060066 | 0.000000 | 13534618 | 12764429 | 0.000000
09-04-2025 17:50:45000 | -1350334 | 135.0334 | 13832721 | 234784.22 | 333814636 | 99479401 | 50058315 | 0.000000 | 13725739 | 12952135 | 0.000000
09-04-2025 17:50:50000 | -1351650 | 135.165 | 14038383 | 234784.94 | 334183716 | 99464966 | 50086700 | 0.000000 | 13919784 | 13139865 | 0.000000
09-04-2025 17:50:55000 | -1357024 | 135.7024 | 13731261 | 234581.53 | 335713257 | 99491959 | 50068439 | 0.000000 | 14112756 | 13328121 | 0.000000
09-04-2025 17:51:00000 | -1350558 | 135.0558 | 13374926 | 234638.58 | 333962524 | 99513206 | 50042320 | 0.000000 | 14300566 | 13516205 | 0.000000
09-04-2025 17:51:05000 | -1348729 | 134.8729 | 13534399 | 234671.05 | 333512054 | 99500275 | 50055187 | 0.000000 | 14488796 | 13703688 | 0.000000
09-04-2025 17:51:10000 | -1347292 | 134.7292 | 13543248 | 234671.44 | 333163818 | 99498566 | 50084908 | 0.000000 | 14677012 | 13890731 | 0.000000
09-04-2025 17:51:15000 | -1352882 | 135.2882 | 13211074 | 234436.98 | 334778168 | 99526596 | 50065723 | 0.000000 | 14864845 | 14078649 | 0.000000
09-04-2025 17:51:20000 | -1353295 | 135.3295 | 13163013 | 234542.50 | 334719238 | 99530289 | 50059135 | 0.000000 | 15047288 | 14266609 | 0.000000
09-04-2025 17:51:25000 | -1353560 | 135.356 | 13036926 | 234477.97 | 334847961 | 99539368 | 50062965 | 0.000000 | 15228468 | 14454426 | 0.000000
09-04-2025 17:51:30000 | -1351179 | 135.1179 | 12726634 | 234429.95 | 334258881 | 99559349 | 50034149 | 0.000000 | 15407198 | 14642434 | 0.000000
09-04-2025 17:51:35000 | -1349030 | 134.903 | 12905412 | 234549.17 | 333598999 | 99545532 | 50040173 | 0.000000 | 15584231 | 14829892 | 0.000000
09-04-2025 17:51:40000 | -1347046 | 134.7046 | 12985765 | 234550.80 | 333136017 | 99538551 | 50060955 | 0.000000 | 15764927 | 15017364 | 0.000000
09-04-2025 17:51:45000 | -1348650 | 134.865 | 12999089 | 234492.23 | 333614746 | 99538696 | 50067688 | 0.000000 | 15946310 | 15204699 | 0.000000
09-04-2025 17:51:50000 | -1352678 | 135.2678 | 12903240 | 234422.86 | 334675232 | 99548119 | 50049599 | 0.000000 | 16125624 | 15392297 | 0.000000
09-04-2025 17:51:55000 | -1348067 | 134.8067 | 12603905 | 234467.59 | 333412354 | 99565765 | 50037388 | 0.000000 | 16301837 | 15579724 | 0.000000
09-04-2025 17:52:00000 | -1349568 | 134.9568 | 12839207 | 234472.33 | 333831238 | 99550507 | 50062256 | 0.000000 | 16479104 | 15766888 | 0.000000
09-04-2025 17:52:05000 | -1347411 | 134.7411 | 12718027 | 234475.63 | 333262970 | 99557495 | 50063667 | 0.000000 | 16655253 | 15954047 | 0.000000
09-04-2025 17:52:10000 | -1350498 | 135.0498 | 12912869 | 234441.31 | 334118652 | 99545990 | 50071251 | 0.000000 | 16835525 | 16141764 | 0.000000
09-04-2025 17:52:15000 | -1354544 | 135.4544 | 13177408 | 234523.88 | 335065521 | 99530136 | 50071323 | 0.000000 | 17016387 | 16329686 | 0.000000
09-04-2025 17:52:20000 | -1354745 | 135.4745 | 12889021 | 234421.47 | 335179840 | 99550468 | 50058372 | 0.000000 | 17196360 | 16517695 | 0.000000
09-04-2025 17:52:25000 | -1346434 | 134.6434 | 12544094 | 234455.64 | 333013702 | 99568817 | 50036709 | 0.000000 | 17372303 | 16705514 | 0.000000
09-04-2025 17:52:30000 | -1354362 | 135.4362 | 12740998 | 234422.58 | 335049561 | 99560425 | 50031178 | 0.000000 | 17548409 | 16893396 | 0.000000
09-04-2025 17:52:35000 | -1350958 | 135.0958 | 12926446 | 234482.67 | 334174377 | 99545349 | 50050728 | 0.000000 | 17726667 | 17080928 | 0.000000
09-04-2025 17:52:40000 | -1351735 | 135.1735 | 12867024 | 234477.72 | 334358215 | 99550011 | 50057888 | 0.000000 | 17905912 | 17268693 | 0.000000
09-04-2025 17:52:45000 | -1354158 | 135.4158 | 13008896 | 234523.59 | 334936829 | 99541733 | 50057167 | 0.000000 | 18085087 | 17456572 | 0.000000
09-04-2025 17:52:50000 | -1352660 | 135.266 | 12999063 | 234488.45 | 334599243 | 99541412 | 50065018 | 0.000000 | 18265979 | 17644457 | 0.000000
09-04-2025 17:52:55000 | -1352632 | 135.2632 | 12721280 | 234374.22 | 334691437 | 99560661 | 50040451 | 0.000000 | 18445593 | 17832686 | 0.000000
09-04-2025 17:53:00000 | -1352245 | 135.2245 | 12775739 | 234434.81 | 334523865 | 99556664 | 50039371 | 0.000000 | 18621937 | 18020291 | 0.000000
09-04-2025 17:53:05000 | -1353025 | 135.3025 | 12879534 | 234438.39 | 334734406 | 99549995 | 50051594 | 0.000000 | 18800117 | 18207975 | 0.000000
09-04-2025 17:53:10000 | -1356291 | 135.6291 | 12802414 | 234353.20 | 335639130 | 99557457 | 50048450 | 0.000000 | 18979613 | 18396143 | 0.000000
09-04-2025 17:53:15000 | -1353486 | 135.3486 | 12254418 | 234276.70 | 334934265 | 99592628 | 50005440 | 0.000000 | 19153445 | 18584590 | 0.000000
09-04-2025 17:53:20000 | -1348960 | 134.896 | 12428964 | 234403.53 | 333684387 | 99578217 | 50022331 | 0.000000 | 19325629 | 18772148 | 0.000000
09-04-2025 17:53:25000 | -1355758 | 135.5758 | 12609051 | 234385.16 | 335416656 | 99570305 | 50023502 | 0.000000 | 19499618 | 18960270 | 0.000000
09-04-2025 17:53:30000 | -1353730 | 135.373 | 12439312 | 234348.61 | 334937683 | 99580475 | 50018848 | 0.000000 | 19672636 | 19148164 | 0.000000
09-04-2025 17:53:35000 | -1352549 | 135.2549 | 12311871 | 234328.53 | 334641754 | 99588257 | 50018257 | 0.000000 | 19845406 | 19336369 | 0.000000
09-04-2025 17:53:40000 | -1352881 | 135.2881 | 12389225 | 234356.47 | 334702484 | 99583305 | 50019081 | 0.000000 | 20016581 | 19524293 | 0.000000
09-04-2025 17:53:45000 | -1356467 | 135.6467 | 12305303 | 234254.47 | 335709900 | 99591057 | 50011478 | 0.000000 | 20188430 | 19712174 | 0.000000
09-04-2025 17:53:50000 | -1352666 | 135.2666 | 11981384 | 234271.22 | 334683594 | 99610008 | 49979137 | 0.000000 | 20356354 | 19900330 | 0.000000
09-04-2025 17:53:55000 | -1354970 | 135.497 | 12154073 | 234262.97 | 335299072 | 99600105 | 49968632 | 0.000000 | 20524836 | 20088279 | 0.000000
09-04-2025 17:54:00000 | -1349857 | 134.9857 | 12067323 | 234325.88 | 333932434 | 99602791 | 49982113 | 0.000000 | 20693020 | 20276014 | 0.000000
09-04-2025 17:54:05000 | -1351358 | 135.1358 | 12236936 | 234334.36 | 334325256 | 99592514 | 50015469 | 0.000000 | 20862471 | 20463650 | 0.000000
09-04-2025 17:54:10000 | -1355964 | 135.5964 | 12110913 | 234184.55 | 335643433 | 99603508 | 50013672 | 0.000000 | 21032224 | 20651672 | 0.000000
09-04-2025 17:54:15000 | -1353972 | 135.3972 | 12104018 | 234330.11 | 334947205 | 99602791 | 49995003 | 0.000000 | 21199255 | 20839807 | 0.000000
09-04-2025 17:54:20000 | -1349623 | 134.9623 | 12091776 | 234286.78 | 333937500 | 99601051 | 50004272 | 0.000000 | 21368474 | 21027459 | 0.000000
09-04-2025 17:54:25000 | -1347381 | 134.7381 | 12420932 | 234422.17 | 333270508 | 99577782 | 50045162 | 0.000000 | 21540225 | 21214988 | 0.000000
09-04-2025 17:54:30000 | -1354577 | 135.4577 | 12654239 | 234321.27 | 335237305 | 99566483 | 50052578 | 0.000000 | 21715344 | 21403191 | 0.000000
09-04-2025 17:54:35000 | -1352186 | 135.2186 | 12677320 | 234466.39 | 334441498 | 99563385 | 50071793 | 0.000000 | 21889666 | 21590982 | 0.000000
09-04-2025 17:54:40000 | -1354365 | 135.4365 | 12859028 | 234469.41 | 335016571 | 99552299 | 50087994 | 0.000000 | 22068042 | 21779066 | 0.000000
09-04-2025 17:54:45000 | -1357282 | 135.7282 | 12863504 | 234396.50 | 335836090 | 99553894 | 50082241 | 0.000000 | 22247036 | 21967449 | 0.000000
09-04-2025 17:54:50000 | -1357728 | 135.7728 | 12579906 | 234332.66 | 335968109 | 99573502 | 50061989 | 0.000000 | 22422915 | 22155746 | 0.000000
09-04-2025 17:54:55000 | -1347493 | 134.7493 | 12221490 | 234392.22 | 333297272 | 99591217 | 50022903 | 0.000000 | 22594285 | 22343730 | 0.000000
09-04-2025 17:55:00000 | -1352610 | 135.261 | 12382182 | 234326.33 | 334681763 | 99583611 | 50017178 | 0.000000 | 22766616 | 22531428 | 0.000000
09-04-2025 17:55:05000 | -1350521 | 135.0521 | 12434398 | 234379.11 | 334104370 | 99578819 | 50019798 | 0.000000 | 22939612 | 22719102 | 0.000000
09-04-2025 17:55:10000 | -1353243 | 135.3243 | 12497853 | 234335.73 | 334848541 | 99576241 | 50019886 | 0.000000 | 23113420 | 22906996 | 0.000000
09-04-2025 17:55:15000 | -1353935 | 135.3935 | 12451116 | 234357.06 | 334974304 | 99579811 | 50008205 | 0.000000 | 23286008 | 23094938 | 0.000000
09-04-2025 17:55:20000 | -1350787 | 135.0787 | 12120441 | 234277.58 | 334241577 | 99599854 | 50003765 | 0.000000 | 23457385 | 23282662 | 0.000000
09-04-2025 17:55:25000 | -1350389 | 135.0389 | 12283904 | 234344.56 | 334085785 | 99588814 | 50002655 | 0.000000 | 23627068 | 23470363 | 0.000000
09-04-2025 17:55:30000 | -1350478 | 135.0478 | 12792068 | 234484.14 | 334023346 | 99554382 | 50045467 | 0.000000 | 23802134 | 23657717 | 0.000000
09-04-2025 17:55:35000 | -1351890 | 135.189 | 12906730 | 234454.08 | 334441956 | 99547348 | 50068493 | 0.000000 | 23981809 | 23845568 | 0.000000
09-04-2025 17:55:40000 | -1353293 | 135.3293 | 12715087 | 234375.13 | 334854858 | 99561508 | 50029156 | 0.000000 | 24160459 | 24034127 | 0.000000
09-04-2025 17:55:45000 | -1354726 | 135.4726 | 12611610 | 234365.47 | 335193268 | 99569473 | 49999374 | 0.000000 | 24334658 | 24221943 | 0.000000
09-04-2025 17:55:50000 | -1350086 | 135.0086 | 12702035 | 234469.88 | 333927338 | 99560333 | 50006222 | 0.000000 | 24509661 | 24409477 | 0.000000
09-04-2025 17:55:55000 | -1348048 | 134.8048 | 12623736 | 234436.11 | 333458893 | 99564400 | 50019840 | 0.000000 | 24685691 | 24596906 | 0.000000
09-04-2025 17:56:00000 | -1347623 | 134.7623 | 12274166 | 234304.22 | 333470825 | 99587784 | 50006264 | 0.000000 | 24858606 | 24784262 | 0.000000
09-04-2025 17:56:05000 | -1347261 | 134.7261 | 12237102 | 234310.95 | 333357422 | 99590034 | 49988552 | 0.000000 | 25030183 | 24971791 | 0.000000
09-04-2025 17:56:10000 | -1353271 | 135.3271 | 12058462 | 234224.03 | 334920959 | 99605354 | 49960930 | 0.000000 | 25198315 | 25159363 | 0.000000
09-04-2025 17:56:15000 | -1342901 | 134.2901 | 11810047 | 234267.47 | 332253418 | 99615517 | 49939716 | 0.000000 | 25362285 | 25346129 | 0.000000
09-04-2025 17:56:20000 | -1346374 | 134.6374 | 12001548 | 234280.52 | 333128784 | 99605057 | 49954628 | 0.000000 | 25527336 | 25532576 | 0.000000
09-04-2025 17:56:25000 | -1343198 | 134.3198 | 11951398 | 234295.02 | 332318146 | 99606491 | 49968266 | 0.000000 | 25693206 | 25719209 | 0.000000
09-04-2025 17:56:30000 | -1344862 | 134.4862 | 12037032 | 234243.67 | 332818634 | 99601845 | 49987640 | 0.000000 | 25861860 | 25906100 | 0.000000
09-04-2025 17:56:35000 | -1343604 | 134.3604 | 11966878 | 234275.02 | 332447784 | 99605713 | 49975010 | 0.000000 | 26028335 | 26092938 | 0.000000
09-04-2025 17:56:40000 | -1345049 | 134.5049 | 12099396 | 234286.17 | 332819977 | 99597847 | 49979507 | 0.000000 | 26195632 | 26279492 | 0.000000
09-04-2025 17:56:45000 | -1342999 | 134.2999 | 12087647 | 234335.94 | 332242279 | 99597397 | 49977833 | 0.000000 | 26363855 | 26466238 | 0.000000
09-04-2025 17:56:50000 | -1346584 | 134.6584 | 12429803 | 234345.63 | 333186340 | 99576683 | 49997471 | 0.000000 | 26535735 | 26653002 | 0.000000
09-04-2025 17:56:55000 | -1337282 | 133.7282 | 12333444 | 234475.25 | 330702118 | 99577400 | 50023808 | 0.000000 | 26706780 | 26839186 | 0.000000
09-04-2025 17:57:00000 | -1343887 | 134.3887 | 12537619 | 234373.88 | 332509155 | 99567635 | 50043381 | 0.000000 | 26881643 | 27025846 | 0.000000
09-04-2025 17:57:05000 | -1343002 | 134.3002 | 12352030 | 234364.70 | 332261749 | 99579712 | 50024178 | 0.000000 | 27055322 | 27212742 | 0.000000
09-04-2025 17:57:10000 | -1348449 | 134.8449 | 12605341 | 234367.86 | 333647766 | 99565918 | 50037647 | 0.000000 | 27229746 | 27399643 | 0.000000
09-04-2025 17:57:15000 | -1349582 | 134.9582 | 12315938 | 234299.05 | 333960663 | 99586189 | 50007240 | 0.000000 | 27401709 | 27587035 | 0.000000
09-04-2025 17:57:20000 | -1347838 | 134.7838 | 12390492 | 234360.69 | 333458618 | 99580116 | 50008118 | 0.000000 | 27572205 | 27774002 | 0.000000
09-04-2025 17:57:25000 | -1341456 | 134.1456 | 12042855 | 234337.48 | 331851715 | 99599449 | 49998070 | 0.000000 | 27741338 | 27960938 | 0.000000
09-04-2025 17:57:30000 | -1343443 | 134.3443 | 11983225 | 234266.75 | 332425110 | 99604546 | 49978745 | 0.000000 | 27908599 | 28147816 | 0.000000
09-04-2025 17:57:35000 | -1346127 | 134.6127 | 12093731 | 234293.25 | 333072052 | 99598854 | 49986046 | 0.000000 | 28074670 | 28334240 | 0.000000
09-04-2025 17:57:40000 | -1340320 | 134.032 | 11755467 | 234245.06 | 331638733 | 99617584 | 49977097 | 0.000000 | 28239514 | 28520869 | 0.000000
09-04-2025 17:57:45000 | -1340916 | 134.0916 | 11807841 | 234259.14 | 331783447 | 99614532 | 49976753 | 0.000000 | 28403079 | 28707326 | 0.000000
09-04-2025 17:57:50000 | -1342703 | 134.2703 | 11799162 | 234224.58 | 332261597 | 99616112 | 49967030 | 0.000000 | 28567844 | 28894047 | 0.000000
09-04-2025 17:57:55000 | -1343528 | 134.3528 | 11792804 | 234234.39 | 332453125 | 99616989 | 49961777 | 0.000000 | 28732036 | 29080445 | 0.000000
09-04-2025 17:58:00000 | -1345335 | 134.5335 | 11991914 | 234271.30 | 332883820 | 99605080 | 49956928 | 0.000000 | 28896113 | 29266896 | 0.000000
09-04-2025 17:58:05000 | -1339103 | 133.9103 | 11989009 | 234344.67 | 331253052 | 99601608 | 49973171 | 0.000000 | 29063047 | 29453469 | 0.000000
09-04-2025 17:58:10000 | -1344518 | 134.4518 | 12067344 | 234279.52 | 332692596 | 99599648 | 49973267 | 0.000000 | 29230581 | 29640326 | 0.000000
09-04-2025 17:58:15000 | -1347053 | 134.7053 | 12427590 | 234368.05 | 333263153 | 99577126 | 49995323 | 0.000000 | 29400791 | 29827229 | 0.000000
09-04-2025 17:58:20000 | -1346471 | 134.6471 | 12452188 | 234378.83 | 333128510 | 99575096 | 50015522 | 0.000000 | 29573875 | 30014311 | 0.000000
09-04-2025 17:58:25000 | -1348693 | 134.8693 | 12329873 | 234314.11 | 333722076 | 99584709 | 50006020 | 0.000000 | 29746199 | 30201662 | 0.000000
09-04-2025 17:58:30000 | -1352216 | 135.2216 | 12059194 | 234191.30 | 334704773 | 99604691 | 49958775 | 0.000000 | 29915752 | 30389369 | 0.000000
09-04-2025 17:58:35000 | -1343209 | 134.3209 | 11583353 | 234207.31 | 332364105 | 99630226 | 49923573 | 0.000000 | 30079082 | 30576479 | 0.000000
09-04-2025 17:58:40000 | -1344065 | 134.4065 | 11900148 | 234266.38 | 332563263 | 99610336 | 49929516 | 0.000000 | 30242966 | 30763182 | 0.000000
09-04-2025 17:58:45000 | -1343910 | 134.391 | 11991828 | 234314.52 | 332474976 | 99604256 | 49950466 | 0.000000 | 30407769 | 30949689 | 0.000000
09-04-2025 17:58:50000 | -1347306 | 134.7306 | 11994162 | 234208.86 | 333461853 | 99606079 | 49956055 | 0.000000 | 30574614 | 31136908 | 0.000000
09-04-2025 17:58:55000 | -1345344 | 134.5344 | 11772058 | 234218.89 | 332917084 | 99619354 | 49943138 | 0.000000 | 30738860 | 31323994 | 0.000000
09-04-2025 17:59:00000 | -1344951 | 134.4951 | 11752620 | 234243.00 | 332778748 | 99620384 | 49950783 | 0.000000 | 30902253 | 31510939 | 0.000000
09-04-2025 17:59:05000 | -1350768 | 135.0768 | 11977637 | 234185.45 | 334335266 | 99609161 | 49959629 | 0.000000 | 31068040 | 31698021 | 0.000000
09-04-2025 17:59:10000 | -1347441 | 134.7441 | 11876316 | 234237.73 | 333430115 | 99613815 | 49948189 | 0.000000 | 31233037 | 31885135 | 0.000000
09-04-2025 17:59:15000 | -1345605 | 134.5605 | 11749679 | 234231.38 | 332954376 | 99620934 | 49943920 | 0.000000 | 31397805 | 32072180 | 0.000000
09-04-2025 17:59:20000 | -1346275 | 134.6275 | 11872090 | 234226.20 | 333153564 | 99613426 | 49939491 | 0.000000 | 31562556 | 32259264 | 0.000000
09-04-2025 17:59:25000 | -1342940 | 134.294 | 11787727 | 234250.30 | 332279144 | 99616982 | 49948666 | 0.000000 | 31725876 | 32445787 | 0.000000
09-04-2025 17:59:30000 | -1347813 | 134.7813 | 11574133 | 234121.31 | 333615326 | 99633316 | 49929245 | 0.000000 | 31888228 | 32632879 | 0.000000
09-04-2025 17:59:35000 | -1348400 | 134.84 | 11990903 | 234254.64 | 333661041 | 99606934 | 49927254 | 0.000000 | 32051284 | 32819770 | 0.000000
09-04-2025 17:59:40000 | -1344268 | 134.4268 | 11763582 | 234218.06 | 332648834 | 99619293 | 49939545 | 0.000000 | 32215745 | 33006547 | 0.000000
09-04-2025 17:59:45000 | -1343184 | 134.3184 | 11781573 | 234240.30 | 332359894 | 99617523 | 49943676 | 0.000000 | 32379978 | 33193480 | 0.000000
09-04-2025 17:59:50000 | -1344955 | 134.4955 | 11984390 | 234292.97 | 332758301 | 99605354 | 49969944 | 0.000000 | 32546226 | 33380227 | 0.000000
09-04-2025 17:59:55000 | -1344817 | 134.4817 | 11985726 | 234312.50 | 332699921 | 99605186 | 49979382 | 0.000000 | 32712410 | 33567129 | 0.000000
09-04-2025 18:00:00000 | -1354943 | 135.4943 | 12089677 | 234141.33 | 335452911 | 99604294 | 49967415 | 0.000000 | 32880225 | 33754469 | 0.000000
09-04-2025 18:00:05000 | -1345011 | 134.5011 | 11599843 | 234221.58 | 332793488 | 99630165 | 49939129 | 0.000000 | 16201086 | 187030853 | 0.000000
09-04-2025 18:00:10000 | -1350196 | 135.0196 | 11851028 | 234150.95 | 334217316 | 99617012 | 49937881 | 0.000000 | 32575424 | 374094543 | 0.000000
09-04-2025 18:00:15000 | -1346275 | 134.6275 | 11532433 | 234202.92 | 333116486 | 99635109 | 49922848 | 0.000000 | 48614204 | 561223572 | 0.000000
09-04-2025 18:00:20000 | -1342269 | 134.2269 | 11774156 | 234317.69 | 332027649 | 99617485 | 49953453 | 0.000000 | 64825569 | 747937195 | 0.000000
09-04-2025 18:00:25000 | -1346386 | 134.6386 | 11688562 | 234133.00 | 333274078 | 99625282 | 49959297 | 0.000000 | 81289909 | 935059509 | 0.000000
09-04-2025 18:00:30000 | -1349274 | 134.9274 | 11388110 | 234079.75 | 333995728 | 99645706 | 49915321 | 0.000000 | 97271263 | 11225034 | 0.000000
09-04-2025 18:00:35000 | -1342892 | 134.2892 | 11454778 | 234212.08 | 332252289 | 99638176 | 49915695 | 0.000000 | 113086075 | 13092842 | 0.000000
09-04-2025 18:00:40000 | -1349250 | 134.925 | 11514484 | 234099.00 | 333990356 | 99637833 | 49920139 | 0.000000 | 129022690 | 14962625 | 0.000000
09-04-2025 18:00:45000 | -1349592 | 134.9592 | 10666441 | 233817.06 | 334306641 | 99689133 | 49850323 | 0.000000 | 144489120 | 16837776 | 0.000000
09-04-2025 18:00:50000 | -1340055 | 134.0055 | 10240719 | 233875.14 | 331794220 | 99709274 | 49791996 | 0.000000 | 158909348 | 18704059 | 0.000000
09-04-2025 18:00:55000 | -1337438 | 133.7438 | 10227469 | 233949.88 | 331043640 | 99708885 | 49802628 | 0.000000 | 173024170 | 20564292 | 0.000000
09-04-2025 18:01:00000 | -1333929 | 133.3929 | 10444090 | 233997.55 | 330161499 | 99694893 | 49853588 | 0.000000 | 187469498 | 22418008 | 0.000000
09-04-2025 18:01:05000 | -1347229 | 134.7229 | 10448604 | 233784.72 | 333727966 | 99700600 | 49845840 | 0.000000 | 202013718 | 24281763 | 0.000000
09-04-2025 18:01:10000 | -1337578 | 133.7578 | 10412888 | 233963.83 | 331088074 | 99698349 | 49833092 | 0.000000 | 216335922 | 26143687 | 0.000000
09-04-2025 18:01:15000 | -1340396 | 134.0396 | 10612988 | 233942.36 | 331852509 | 99688011 | 49841419 | 0.000000 | 230957352 | 28002480 | 0.000000
09-04-2025 18:01:20000 | -1340177 | 134.0177 | 10483983 | 233924.94 | 331801788 | 99695412 | 49821327 | 0.000000 | 245567764 | 29864863 | 0.000000
09-04-2025 18:01:25000 | -1332514 | 133.2514 | 10837384 | 234135.81 | 329684326 | 99670898 | 49853889 | 0.000000 | 260421875 | 31720525 | 0.000000
09-04-2025 18:01:30000 | -1335458 | 133.5458 | 10836784 | 233990.44 | 330618439 | 99672379 | 49880978 | 0.000000 | 275651733 | 33577988 | 0.000000
09-04-2025 18:01:35000 | -1342610 | 134.261 | 10886036 | 233965.88 | 332426178 | 99672905 | 49869652 | 0.000000 | 290819855 | 35442202 | 0.000000
09-04-2025 18:01:40000 | -1339690 | 133.969 | 10682345 | 233958.70 | 331672150 | 99683601 | 49844864 | 0.000000 | 305674286 | 37303979 | 0.000000
09-04-2025 18:01:45000 | -1342316 | 134.2316 | 10698685 | 233979.50 | 332289551 | 99683876 | 49825607 | 0.000000 | 320505341 | 39168740 | 0.000000
09-04-2025 18:01:50000 | -1342068 | 134.2068 | 10740557 | 233974.20 | 332243286 | 99681290 | 49837711 | 0.000000 | 335404694 | 41030933 | 0.000000
09-04-2025 18:01:55000 | -1342868 | 134.2868 | 10777010 | 233982.45 | 332434418 | 99679512 | 49842064 | 0.000000 | 350333801 | 42894482 | 0.000000
09-04-2025 18:02:00000 | -1339514 | 133.9514 | 10573050 | 233932.28 | 331644928 | 99689934 | 49830017 | 0.000000 | 365249786 | 44759580 | 0.000000
09-04-2025 18:02:05000 | -1344164 | 134.4164 | 10435557 | 233863.30 | 332858307 | 99699989 | 49807507 | 0.000000 | 379812286 | 46626128 | 0.000000
09-04-2025 18:02:10000 | -1337147 | 133.7147 | 10267416 | 233928.33 | 331007996 | 99706490 | 49794498 | 0.000000 | 394243866 | 48488945 | 0.000000
09-04-2025 18:02:15000 | -1338654 | 133.8654 | 10015695 | 233795.83 | 331521118 | 99721275 | 49787052 | 0.000000 | 408407349 | 50349683 | 0.000000
09-04-2025 18:02:20000 | -1340846 | 134.0846 | 10282566 | 233875.28 | 331997925 | 99707245 | 49801128 | 0.000000 | 422460602 | 52207183 | 0.000000
09-04-2025 18:02:25000 | -1337204 | 133.7204 | 99484756 | 233768.16 | 331191864 | 99724396 | 49817680 | 0.000000 | 436502502 | 54062954 | 0.000000
09-04-2025 18:02:30000 | -1335756 | 133.5756 | 10040344 | 233853.20 | 330736053 | 99718697 | 49826523 | 0.000000 | 450509766 | 55922822 | 0.000000
09-04-2025 18:02:35000 | -1347065 | 134.7065 | 10520926 | 233831.55 | 333639709 | 99696388 | 49839939 | 0.000000 | 464846130 | 57783262 | 0.000000
09-04-2025 18:02:40000 | -1340024 | 134.0024 | 10264931 | 233920.95 | 331728882 | 99707886 | 49822338 | 0.000000 | 479113037 | 59647271 | 0.000000
09-04-2025 18:02:45000 | -1344633 | 134.4633 | 10651183 | 233924.52 | 332927185 | 99687737 | 49844810 | 0.000000 | 493705322 | 61511030 | 0.000000
09-04-2025 18:02:50000 | -1346777 | 134.6777 | 10506115 | 233858.67 | 333522400 | 99697105 | 49839676 | 0.000000 | 508358093 | 63377324 | 0.000000
09-04-2025 18:02:55000 | -1340856 | 134.0856 | 10107668 | 233824.78 | 332035919 | 99717079 | 49821201 | 0.000000 | 522711914 | 65246055 | 0.000000
09-04-2025 18:03:00000 | -1341034 | 134.1034 | 10042014 | 233836.39 | 332057861 | 99720802 | 49804756 | 0.000000 | 536657715 | 67108765 | 0.000000
09-04-2025 18:03:05000 | -1339417 | 133.9417 | 10214305 | 233884.72 | 331620178 | 99710487 | 49821556 | 0.000000 | 550760559 | 68968989 | 0.000000
09-04-2025 18:03:10000 | -1340953 | 134.0953 | 10302122 | 233895.83 | 332001038 | 99706184 | 49830109 | 0.000000 | 564922852 | 70830005 | 0.000000
09-04-2025 18:03:15000 | -1346106 | 134.6106 | 10205047 | 233746.75 | 333458618 | 99713860 | 49818428 | 0.000000 | 579118530 | 72696699 | 0.000000
09-04-2025 18:03:20000 | -1342609 | 134.2609 | 99951895 | 233788.16 | 332498718 | 99724037 | 49796619 | 0.000000 | 593056274 | 74562261 | 0.000000
09-04-2025 18:03:25000 | -1340491 | 134.0491 | 98720693 | 233784.94 | 331962769 | 99729919 | 49789574 | 0.000000 | 606744934 | 76425776 | 0.000000
09-04-2025 18:03:30000 | -1338169 | 133.8169 | 10117312 | 233895.98 | 331273865 | 99715408 | 49818195 | 0.000000 | 620669312 | 78285972 | 0.000000
09-04-2025 18:03:35000 | -1339943 | 133.9943 | 10525353 | 233961.13 | 331695526 | 99692909 | 49865856 | 0.000000 | 635132568 | 80148403 | 0.000000
09-04-2025 18:03:40000 | -1348565 | 134.8565 | 10727507 | 233867.39 | 333991638 | 99685104 | 49867695 | 0.000000 | 649959473 | 82017813 | 0.000000
09-04-2025 18:03:45000 | -1350239 | 135.0239 | 10271549 | 233776.05 | 334448303 | 99711899 | 49828365 | 0.000000 | 664389404 | 83890391 | 0.000000
09-04-2025 18:03:50000 | -1344950 | 134.495 | 10404434 | 233888.14 | 333015198 | 99702110 | 49824314 | 0.000000 | 678698181 | 85756924 | 0.000000
09-04-2025 18:03:55000 | -1341470 | 134.147 | 10273009 | 233888.98 | 332132263 | 99708054 | 49833916 | 0.000000 | 693091187 | 87621299 | 0.000000
09-04-2025 18:04:00000 | -1348149 | 134.8149 | 10434523 | 233821.95 | 333898987 | 99701813 | 49844341 | 0.000000 | 707512817 | 89487461 | 0.000000
09-04-2025 18:04:05000 | -1342368 | 134.2368 | 10102262 | 233808.34 | 332434357 | 99718018 | 49815529 | 0.000000 | 721698425 | 91357188 | 0.000000
09-04-2025 18:04:10000 | -1336579 | 133.6579 | 10269471 | 233953.36 | 330834686 | 99706131 | 49829060 | 0.000000 | 735833801 | 93219697 | 0.000000
09-04-2025 18:04:15000 | -1339810 | 133.981 | 10186190 | 233823.25 | 331800873 | 99712242 | 49836205 | 0.000000 | 750072510 | 95083096 | 0.000000
09-04-2025 18:04:20000 | -1344453 | 134.4453 | 10042050 | 233766.02 | 332992615 | 99722214 | 49820984 | 0.000000 | 764171204 | 96951260 | 0.000000
09-04-2025 18:04:25000 | -1344899 | 134.4899 | 10045172 | 233784.92 | 333077759 | 99722229 | 49810101 | 0.000000 | 778025391 | 98818633 | 0.000000
09-04-2025 18:04:30000 | -1345980 | 134.598 | 99608604 | 233751.67 | 333374939 | 99727287 | 49805332 | 0.000000 | 791899658 | 10068513 | 0.000000
09-04-2025 18:04:35000 | -1339379 | 133.9379 | 98969443 | 233839.16 | 331612701 | 99728111 | 49799858 | 0.000000 | 805530334 | 10254974 | 0.000000
09-04-2025 18:04:40000 | -1341870 | 134.187 | 99833223 | 233818.78 | 332274292 | 99724388 | 49796413 | 0.000000 | 819273438 | 10441383 | 0.000000
09-04-2025 18:04:45000 | -1343431 | 134.3431 | 99069160 | 233702.69 | 332816681 | 99729202 | 49794930 | 0.000000 | 833139893 | 10627730 | 0.000000
09-04-2025 18:04:50000 | -1339167 | 133.9167 | 97519238 | 233769.45 | 331638947 | 99735909 | 49778664 | 0.000000 | 846690979 | 10814114 | 0.000000
09-04-2025 18:04:55000 | -1336579 | 133.6579 | 10052487 | 233879.39 | 330902679 | 99718361 | 49822803 | 0.000000 | 860460083 | 10999850 | 0.000000
09-04-2025 18:05:00000 | -1338395 | 133.8395 | 98853574 | 233747.08 | 331502197 | 99728348 | 49844364 | 0.000000 | 874446777 | 11185835 | 0.000000
09-04-2025 18:05:05000 | -1339144 | 133.9144 | 10012694 | 233806.80 | 331638733 | 99721642 | 49825661 | 0.000000 | 888368591 | 11372112 | 0.000000
09-04-2025 18:05:10000 | -1344271 | 134.4271 | 10463183 | 233917.05 | 332820740 | 99698456 | 49848011 | 0.000000 | 902573608 | 11558237 | 0.000000
09-04-2025 18:05:15000 | -1341927 | 134.1927 | 10417310 | 233882.56 | 332278198 | 99700035 | 49846951 | 0.000000 | 917063110 | 11744789 | 0.000000
09-04-2025 18:05:20000 | -1348228 | 134.8228 | 10141263 | 233708.77 | 334026825 | 99718300 | 49821392 | 0.000000 | 931376892 | 11931843 | 0.000000
09-04-2025 18:05:25000 | -1345046 | 134.5046 | 99994619 | 233793.47 | 333094727 | 99724800 | 49797596 | 0.000000 | 945256042 | 12118501 | 0.000000
09-04-2025 18:05:30000 | -1340695 | 134.0695 | 10107735 | 233898.42 | 331896301 | 99717010 | 49812927 | 0.000000 | 959193481 | 12304811 | 0.000000
09-04-2025 18:05:35000 | -1342512 | 134.2512 | 10218886 | 233815.36 | 332476593 | 99711555 | 49845390 | 0.000000 | 973358765 | 12491110 | 0.000000
09-04-2025 18:05:40000 | -1341058 | 134.1058 | 10062104 | 233796.52 | 332117737 | 99719696 | 49836075 | 0.000000 | 987438660 | 12677461 | 0.000000
09-04-2025 18:05:45000 | -1338834 | 133.8834 | 10267933 | 233897.47 | 331467010 | 99707199 | 49855671 | 0.000000 | 10016260 | 12863558 | 0.000000
09-04-2025 18:05:50000 | -1346240 | 134.624 | 10557821 | 233861.11 | 333396637 | 99693893 | 49858284 | 0.000000 | 10162952 | 13050240 | 0.000000
09-04-2025 18:05:55000 | -1344281 | 134.4281 | 10140158 | 233779.53 | 332953522 | 99716713 | 49827274 | 0.000000 | 10306274 | 13237120 | 0.000000
09-04-2025 18:06:00000 | -1340710 | 134.071 | 10157309 | 233895.59 | 331913940 | 99714249 | 49833069 | 0.000000 | 10446184 | 13423664 | 0.000000
09-04-2025 18:06:05000 | -1337110 | 133.711 | 10462572 | 234043.97 | 330871338 | 99695267 | 49882488 | 0.000000 | 10588721 | 13609556 | 0.000000
09-04-2025 18:06:10000 | -1348509 | 134.8509 | 11441996 | 234102.75 | 333789978 | 99641960 | 49990368 | 0.000000 | 10741515 | 13795395 | 0.000000
09-04-2025 18:06:15000 | -1352989 | 135.2989 | 11384100 | 234015.95 | 335002686 | 99647888 | 49964951 | 0.000000 | 10899824 | 13983058 | 0.000000
09-04-2025 18:06:20000 | -1348865 | 134.8865 | 11399186 | 234162.38 | 333782104 | 99644806 | 49958752 | 0.000000 | 11057444 | 14170336 | 0.000000
09-04-2025 18:06:25000 | -1349569 | 134.9569 | 11712612 | 234172.97 | 334001373 | 99625511 | 49955593 | 0.000000 | 11220081 | 14357710 | 0.000000
09-04-2025 18:06:30000 | -1348766 | 134.8766 | 11349143 | 234058.92 | 333903198 | 99647850 | 49942516 | 0.000000 | 11381223 | 14545229 | 0.000000
09-04-2025 18:06:35000 | -1345475 | 134.5475 | 11083061 | 234055.72 | 333035767 | 99662453 | 49926003 | 0.000000 | 11536541 | 14732600 | 0.000000
09-04-2025 18:06:40000 | -1345676 | 134.5676 | 11119830 | 234071.00 | 333070465 | 99660324 | 49935169 | 0.000000 | 11691460 | 14919882 | 0.000000
09-04-2025 18:06:45000 | -1351750 | 135.175 | 11324890 | 234077.31 | 334599365 | 99650887 | 49955688 | 0.000000 | 11847307 | 15107255 | 0.000000
09-04-2025 18:06:50000 | -1347990 | 134.799 | 11098373 | 234005.64 | 333728607 | 99662781 | 49962212 | 0.000000 | 12003223 | 15294491 | 0.000000
09-04-2025 18:06:55000 | -1344484 | 134.4484 | 11067822 | 234069.11 | 332770905 | 99662880 | 49955982 | 0.000000 | 12158329 | 15481861 | 0.000000
09-04-2025 18:07:00000 | -1346028 | 134.6028 | 11586787 | 234185.30 | 333093536 | 99631546 | 49970402 | 0.000000 | 12317391 | 15668937 | 0.000000
09-04-2025 18:07:05000 | -1347923 | 134.7923 | 11483099 | 234112.58 | 333638855 | 99639084 | 49978523 | 0.000000 | 12477517 | 15855906 | 0.000000
09-04-2025 18:07:10000 | -1350306 | 135.0306 | 10982775 | 233971.81 | 334326996 | 99670860 | 49947819 | 0.000000 | 12633849 | 16043610 | 0.000000
09-04-2025 18:07:15000 | -1348139 | 134.8139 | 11002085 | 234012.80 | 333734833 | 99668648 | 49943459 | 0.000000 | 12786521 | 16230749 | 0.000000
09-04-2025 18:07:20000 | -1348643 | 134.8643 | 11250350 | 234105.72 | 333780579 | 99653862 | 49955414 | 0.000000 | 12940291 | 16417842 | 0.000000
09-04-2025 18:07:25000 | -1349816 | 134.9816 | 11474456 | 234160.63 | 334033752 | 99640633 | 49985611 | 0.000000 | 13098090 | 16605014 | 0.000000
09-04-2025 18:07:30000 | -1348300 | 134.83 | 11704099 | 234262.59 | 333570465 | 99625351 | 50015465 | 0.000000 | 13258317 | 16792330 | 0.000000
09-04-2025 18:07:35000 | -1352691 | 135.2691 | 12086405 | 234234.42 | 334769287 | 99603195 | 50044296 | 0.000000 | 13424019 | 16979873 | 0.000000
09-04-2025 18:07:40000 | -1350409 | 135.0409 | 11849818 | 234195.94 | 334208801 | 99617210 | 50033878 | 0.000000 | 13590835 | 17167947 | 0.000000
09-04-2025 18:07:45000 | -1351780 | 135.178 | 11872475 | 234193.88 | 334556122 | 99616524 | 50016228 | 0.000000 | 13756510 | 17355975 | 0.000000
09-04-2025 18:07:50000 | -1351294 | 135.1294 | 12041792 | 234276.41 | 334354004 | 99605293 | 50019360 | 0.000000 | 13921864 | 17543645 | 0.000000
09-04-2025 18:07:55000 | -1352230 | 135.223 | 11693426 | 234113.41 | 334744751 | 99628189 | 50006748 | 0.000000 | 14087906 | 17731576 | 0.000000
09-04-2025 18:08:00000 | -1350749 | 135.0749 | 11807558 | 234226.08 | 334243927 | 99620110 | 50004250 | 0.000000 | 14249050 | 17919121 | 0.000000
09-04-2025 18:08:05000 | -1352258 | 135.2258 | 11543109 | 234075.41 | 334769867 | 99637650 | 50005844 | 0.000000 | 14411350 | 18106395 | 0.000000
09-04-2025 18:08:10000 | -1346398 | 134.6398 | 11676864 | 234260.20 | 333097198 | 99626030 | 50031372 | 0.000000 | 14570845 | 18293260 | 0.000000
09-04-2025 18:08:15000 | -1352209 | 135.2209 | 11967547 | 234153.97 | 334743347 | 99610641 | 50046963 | 0.000000 | 14737440 | 18480828 | 0.000000
09-04-2025 18:08:20000 | -1349365 | 134.9365 | 11694723 | 234172.34 | 333952515 | 99626534 | 50031075 | 0.000000 | 14902157 | 18668699 | 0.000000
09-04-2025 18:08:25000 | -1349621 | 134.9621 | 12071424 | 234298.25 | 333919342 | 99602379 | 50066681 | 0.000000 | 15068353 | 18856223 | 0.000000
09-04-2025 18:08:30000 | -1346539 | 134.6539 | 11699252 | 234213.13 | 333208496 | 99624680 | 50081989 | 0.000000 | 15232459 | 19043084 | 0.000000
09-04-2025 18:08:35000 | -1352011 | 135.2011 | 11883537 | 234191.59 | 334614929 | 99615944 | 50048637 | 0.000000 | 15394329 | 19230350 | 0.000000
09-04-2025 18:08:40000 | -1354113 | 135.4113 | 12119997 | 234195.67 | 335188538 | 99601830 | 50052162 | 0.000000 | 15562184 | 19417932 | 0.000000
09-04-2025 18:08:45000 | -1356070 | 135.607 | 11659816 | 234134.44 | 335654419 | 99632385 | 50027435 | 0.000000 | 15724136 | 19605732 | 0.000000
09-04-2025 18:08:50000 | -1346126 | 134.6126 | 11348480 | 234163.95 | 333096558 | 99646523 | 50027740 | 0.000000 | 15880977 | 19793172 | 0.000000
09-04-2025 18:08:55000 | -1344313 | 134.4313 | 11320211 | 234136.13 | 332683502 | 99647324 | 50051991 | 0.000000 | 16038671 | 19980264 | 0.000000
09-04-2025 18:09:00000 | -1337386 | 133.7386 | 11124982 | 234134.02 | 330949005 | 99655800 | 50070900 | 0.000000 | 16192528 | 20165959 | 0.000000
09-04-2025 18:09:05000 | -1324499 | 132.4499 | 10781901 | 234118.16 | 327733856 | 99670311 | 50054176 | 0.000000 | 16344061 | 20350688 | 0.000000
09-04-2025 18:09:10000 | -1316153 | 131.6153 | 10734948 | 234151.44 | 325630371 | 99669022 | 50061234 | 0.000000 | 16493872 | 20534295 | 0.000000
09-04-2025 18:09:15000 | -1311505 | 131.1505 | 10300017 | 234014.50 | 324584808 | 99693024 | 50063778 | 0.000000 | 16639497 | 20716662 | 0.000000
09-04-2025 18:09:20000 | -1298328 | 129.8328 | 95579824 | 233882.13 | 321389160 | 99730118 | 50034248 | 0.000000 | 16778412 | 20897941 | 0.000000
09-04-2025 18:09:25000 | -1287110 | 128.711 | 96940059 | 234075.06 | 318388336 | 99717575 | 50052567 | 0.000000 | 16910311 | 21077195 | 0.000000
09-04-2025 18:09:30000 | -1280670 | 128.067 | 99454258 | 234060.44 | 316876740 | 99699821 | 50071625 | 0.000000 | 17048184 | 21255352 | 0.000000
09-04-2025 18:09:35000 | -1269860 | 126.986 | 95627715 | 234017.42 | 314202362 | 99717651 | 50062332 | 0.000000 | 17183203 | 21432488 | 0.000000
09-04-2025 18:09:40000 | -1263101 | 126.3101 | 97284375 | 234088.03 | 312473633 | 99704704 | 50086205 | 0.000000 | 17317139 | 21607742 | 0.000000
09-04-2025 18:09:45000 | -1255970 | 125.597 | 90598076 | 233893.77 | 310854858 | 99740845 | 50064667 | 0.000000 | 17447996 | 21782469 | 0.000000
09-04-2025 18:09:50000 | -1238387 | 123.8387 | 88500371 | 234031.61 | 306308258 | 99745621 | 50054325 | 0.000000 | 17571395 | 21955385 | 0.000000
09-04-2025 18:09:55000 | -1232313 | 123.2313 | 88169092 | 233988.22 | 304865295 | 99745026 | 50062557 | 0.000000 | 17694650 | 22126766 | 0.000000
09-04-2025 18:10:00000 | -1234742 | 123.4742 | 88951436 | 233918.50 | 305571960 | 99741516 | 50057888 | 0.000000 | 17817598 | 22298195 | 0.000000
09-04-2025 18:10:05000 | -1233659 | 123.3659 | 90980566 | 234047.05 | 305170380 | 99729164 | 50053196 | 0.000000 | 17941903 | 22469484 | 0.000000
09-04-2025 18:10:10000 | -1233886 | 123.3886 | 90580186 | 234005.55 | 305275330 | 99731628 | 50048527 | 0.000000 | 18067599 | 22641037 | 0.000000
09-04-2025 18:10:15000 | -1231558 | 123.1558 | 92084834 | 234098.22 | 304613525 | 99721634 | 50075367 | 0.000000 | 18193870 | 22812205 | 0.000000
09-04-2025 18:10:20000 | -1236244 | 123.6244 | 90879932 | 233928.66 | 305963043 | 99730881 | 50082829 | 0.000000 | 18323381 | 22984219 | 0.000000
09-04-2025 18:10:25000 | -1239479 | 123.9479 | 88210469 | 233879.44 | 306775787 | 99747719 | 50045765 | 0.000000 | 18447665 | 23156623 | 0.000000
09-04-2025 18:10:30000 | -1237645 | 123.7645 | 90817246 | 234033.81 | 306163910 | 99731857 | 50058804 | 0.000000 | 18571765 | 23328338 | 0.000000
09-04-2025 18:10:35000 | -1242367 | 124.2367 | 91168027 | 233950.63 | 307443237 | 99731834 | 50064007 | 0.000000 | 18698615 | 23500691 | 0.000000
09-04-2025 18:10:40000 | -1240965 | 124.0965 | 89029014 | 233870.78 | 307167572 | 99743645 | 50066631 | 0.000000 | 18823423 | 23672973 | 0.000000
09-04-2025 18:10:45000 | -1240555 | 124.0555 | 87082549 | 233846.48 | 307062561 | 99754532 | 50044453 | 0.000000 | 18946194 | 23845541 | 0.000000
09-04-2025 18:10:50000 | -1237658 | 123.7658 | 93947988 | 234201.22 | 306007355 | 99713135 | 50108559 | 0.000000 | 19071270 | 24017264 | 0.000000
09-04-2025 18:10:55000 | -1249069 | 124.9069 | 92966436 | 233850.27 | 309254425 | 99724167 | 50106487 | 0.000000 | 19203202 | 24190098 | 0.000000
09-04-2025 18:11:00000 | -1245976 | 124.5976 | 90078496 | 233908.92 | 308362762 | 99739685 | 50053101 | 0.000000 | 19328917 | 24363295 | 0.000000
09-04-2025 18:11:05000 | -1240277 | 124.0277 | 93230732 | 234079.66 | 306795715 | 99718674 | 50046265 | 0.000000 | 19456587 | 24535787 | 0.000000
09-04-2025 18:11:10000 | -1242205 | 124.2205 | 93406807 | 234063.27 | 307299561 | 99718483 | 50057442 | 0.000000 | 19585563 | 24708283 | 0.000000
09-04-2025 18:11:15000 | -1242344 | 124.2344 | 95089189 | 234103.52 | 307306976 | 99708359 | 50077934 | 0.000000 | 19716631 | 24880670 | 0.000000
09-04-2025 18:11:20000 | -1243234 | 124.3234 | 89794170 | 233868.59 | 307745605 | 99740181 | 50054253 | 0.000000 | 19844495 | 25053559 | 0.000000
09-04-2025 18:11:25000 | -1238996 | 123.8996 | 89552822 | 234007.00 | 306512299 | 99739807 | 50030785 | 0.000000 | 19967252 | 25225977 | 0.000000
09-04-2025 18:11:30000 | -1237282 | 123.7282 | 92260918 | 234077.95 | 306042877 | 99723137 | 50057117 | 0.000000 | 20094268 | 25398080 | 0.000000
09-04-2025 18:11:35000 | -1247157 | 124.7157 | 92285947 | 233929.86 | 308666412 | 99727341 | 50067902 | 0.000000 | 20222594 | 25570600 | 0.000000
09-04-2025 18:11:40000 | -1243404 | 124.3404 | 92035713 | 233971.56 | 307691742 | 99727180 | 50041996 | 0.000000 | 20350010 | 25743533 | 0.000000
09-04-2025 18:11:45000 | -1244858 | 124.4858 | 95218252 | 234101.78 | 307929749 | 99708748 | 50073132 | 0.000000 | 20479204 | 25915926 | 0.000000
09-04-2025 18:11:50000 | -1244475 | 124.4475 | 93157832 | 234003.11 | 307928284 | 99720993 | 50064861 | 0.000000 | 20609722 | 26088809 | 0.000000
09-04-2025 18:11:55000 | -1246949 | 124.6949 | 93724219 | 233949.22 | 308616211 | 99718719 | 50048965 | 0.000000 | 20740474 | 26261848 | 0.000000
09-04-2025 18:12:00000 | -1242575 | 124.2575 | 91469375 | 234028.38 | 307402527 | 99730156 | 50017860 | 0.000000 | 20866799 | 26434676 | 0.000000
09-04-2025 18:12:05000 | -1242523 | 124.2523 | 96550146 | 234165.03 | 307295685 | 99699455 | 50060833 | 0.000000 | 20998157 | 26607096 | 0.000000
09-04-2025 18:12:10000 | -1245531 | 124.5531 | 95381064 | 234016.23 | 308208344 | 99708069 | 50077824 | 0.000000 | 21131687 | 26779832 | 0.000000
09-04-2025 18:12:15000 | -1244855 | 124.4855 | 91852822 | 233954.55 | 308061432 | 99728889 | 50040989 | 0.000000 | 21261675 | 26953160 | 0.000000
09-04-2025 18:12:20000 | -1243262 | 124.3262 | 96326387 | 234165.28 | 307479095 | 99701195 | 50054497 | 0.000000 | 21391782 | 27125826 | 0.000000
09-04-2025 18:12:25000 | -1243888 | 124.3888 | 99344746 | 234190.64 | 307653564 | 99682587 | 50089809 | 0.000000 | 21527654 | 27298439 | 0.000000
09-04-2025 18:12:30000 | -1247774 | 124.7774 | 98950283 | 234134.91 | 308677155 | 99687042 | 50099720 | 0.000000 | 21665647 | 27471525 | 0.000000
09-04-2025 18:12:35000 | -1242761 | 124.2761 | 98182891 | 234150.73 | 307406036 | 99689377 | 50091408 | 0.000000 | 21802820 | 27644500 | 0.000000
09-04-2025 18:12:40000 | -1240908 | 124.0908 | 99865928 | 234251.55 | 306857483 | 99677727 | 50092274 | 0.000000 | 21939934 | 27817211 | 0.000000
09-04-2025 18:12:45000 | -1241963 | 124.1963 | 10177618 | 234272.39 | 307125397 | 99665909 | 50110409 | 0.000000 | 22080364 | 27989885 | 0.000000
09-04-2025 18:12:50000 | -1248312 | 124.8312 | 10211167 | 234188.22 | 308803497 | 99667107 | 50106339 | 0.000000 | 22221958 | 28162760 | 0.000000
09-04-2025 18:12:55000 | -1245198 | 124.5198 | 99554668 | 234130.80 | 308059906 | 99681915 | 50071301 | 0.000000 | 22362375 | 28335906 | 0.000000
09-04-2025 18:13:00000 | -1238876 | 123.8876 | 10069847 | 234279.81 | 306337921 | 99671288 | 50089138 | 0.000000 | 22500618 | 28508170 | 0.000000
09-04-2025 18:13:05000 | -1248528 | 124.8528 | 99733877 | 234113.47 | 308904236 | 99682472 | 50087173 | 0.000000 | 22640220 | 28681111 | 0.000000
09-04-2025 18:13:10000 | -1247951 | 124.7951 | 97389971 | 234068.89 | 308778564 | 99696869 | 50052807 | 0.000000 | 22777046 | 28854408 | 0.000000
09-04-2025 18:13:15000 | -1245034 | 124.5034 | 94908447 | 234058.44 | 308030548 | 99710709 | 50025814 | 0.000000 | 22909756 | 29027396 | 0.000000
09-04-2025 18:13:20000 | -1244073 | 124.4073 | 94955352 | 234047.59 | 307801117 | 99709984 | 50026802 | 0.000000 | 23042324 | 29200207 | 0.000000
09-04-2025 18:13:25000 | -1245821 | 124.5821 | 92814316 | 233937.84 | 308339996 | 99723633 | 50012371 | 0.000000 | 23173030 | 29373090 | 0.000000
09-04-2025 18:13:30000 | -1241539 | 124.1539 | 91566875 | 234024.55 | 307147919 | 99729134 | 50002975 | 0.000000 | 23299917 | 29545717 | 0.000000
09-04-2025 18:13:35000 | -1238240 | 123.824 | 91459053 | 234050.64 | 306300201 | 99728333 | 50030815 | 0.000000 | 23427117 | 29717719 | 0.000000
09-04-2025 18:13:40000 | -1239020 | 123.902 | 94714609 | 234120.75 | 306459778 | 99709099 | 50053299 | 0.000000 | 23556843 | 29889814 | 0.000000
09-04-2025 18:13:45000 | -1241652 | 124.1652 | 96402969 | 234122.06 | 307141968 | 99699951 | 50078194 | 0.000000 | 23690107 | 30062482 | 0.000000
09-04-2025 18:13:50000 | -1246969 | 124.6969 | 99421084 | 234160.55 | 308457458 | 99683662 | 50095341 | 0.000000 | 23825833 | 30235289 | 0.000000
09-04-2025 18:13:55000 | -1243011 | 124.3011 | 98170234 | 234162.05 | 307454224 | 99689575 | 50102425 | 0.000000 | 23962898 | 30407920 | 0.000000
09-04-2025 18:14:00000 | -1246858 | 124.6858 | 10307846 | 234261.98 | 308361877 | 99660019 | 50120056 | 0.000000 | 24102725 | 30580773 | 0.000000
09-04-2025 18:14:05000 | -1243474 | 124.3474 | 10029766 | 234192.36 | 307569519 | 99676285 | 50108330 | 0.000000 | 24244436 | 30753805 | 0.000000
09-04-2025 18:14:10000 | -1245745 | 124.5745 | 10156729 | 234189.44 | 308160461 | 99669281 | 50084732 | 0.000000 | 24386621 | 30927049 | 0.000000
09-04-2025 18:14:15000 | -1247837 | 124.7837 | 10289831 | 234243.81 | 308626923 | 99661728 | 50080250 | 0.000000 | 24529424 | 31100160 | 0.000000
09-04-2025 18:14:20000 | -1246145 | 124.6145 | 10292996 | 234264.55 | 308182739 | 99660606 | 50075897 | 0.000000 | 24672036 | 31273133 | 0.000000
09-04-2025 18:14:25000 | -1248006 | 124.8006 | 10310927 | 234187.31 | 308745026 | 99660439 | 50057381 | 0.000000 | 24816838 | 31446326 | 0.000000
09-04-2025 18:14:30000 | -1244410 | 124.441 | 10207269 | 234274.09 | 307725983 | 99665283 | 50031929 | 0.000000 | 24959016 | 31619412 | 0.000000
09-04-2025 18:14:35000 | -1242444 | 124.2444 | 10328507 | 234321.38 | 307206329 | 99656250 | 50052284 | 0.000000 | 25101836 | 31792014 | 0.000000
09-04-2025 18:14:40000 | -1241393 | 124.1393 | 10258551 | 234301.92 | 306958954 | 99660294 | 50066807 | 0.000000 | 25245488 | 31964813 | 0.000000
09-04-2025 18:14:45000 | -1248681 | 124.8681 | 10491406 | 234240.47 | 308883484 | 99648888 | 50098778 | 0.000000 | 25388469 | 32137250 | 0.000000
09-04-2025 18:14:50000 | -1249001 | 124.9001 | 99941357 | 234054.13 | 309100342 | 99681396 | 50056114 | 0.000000 | 25530413 | 32310645 | 0.000000
09-04-2025 18:14:55000 | -1239556 | 123.9556 | 96356455 | 234158.09 | 306576019 | 99699226 | 50016136 | 0.000000 | 25665737 | 32483557 | 0.000000
09-04-2025 18:15:00000 | -1241794 | 124.1794 | 97655244 | 234153.14 | 307152832 | 99692207 | 50034359 | 0.000000 | 25801572 | 32655951 | 0.000000
09-04-2025 18:15:05000 | -1239201 | 123.9201 | 98968438 | 234223.38 | 306449615 | 99682602 | 50049843 | 0.000000 | 13686594 | 172480927 | 0.000000
09-04-2025 18:15:10000 | -1244848 | 124.4848 | 10411797 | 234303.63 | 307837097 | 99652046 | 50091724 | 0.000000 | 27890331 | 344858551 | 0.000000
09-04-2025 18:15:15000 | -1242254 | 124.2254 | 10381262 | 234275.11 | 307228363 | 99652641 | 50085850 | 0.000000 | 42365326 | 517835815 | 0.000000
09-04-2025 18:15:20000 | -1245489 | 124.5489 | 10463186 | 234274.59 | 308040558 | 99648987 | 50069763 | 0.000000 | 56856895 | 691059998 | 0.000000
09-04-2025 18:15:25000 | -1242147 | 124.2147 | 10455060 | 234338.31 | 307133850 | 99647644 | 50083397 | 0.000000 | 71294800 | 863618225 | 0.000000
09-04-2025 18:15:30000 | -1245175 | 124.5175 | 10539167 | 234307.45 | 307939667 | 99643715 | 50075275 | 0.000000 | 85846626 | 10365787 | 0.000000
09-04-2025 18:15:35000 | -1243416 | 124.3416 | 10751671 | 234414.33 | 307412872 | 99628242 | 50095654 | 0.000000 | 100519531 | 12091580 | 0.000000
09-04-2025 18:15:40000 | -1243326 | 124.3326 | 10731252 | 234345.75 | 307478180 | 99629593 | 50098377 | 0.000000 | 115491859 | 13821219 | 0.000000
09-04-2025 18:15:45000 | -1247387 | 124.7387 | 10786258 | 234365.02 | 308456146 | 99628220 | 50083233 | 0.000000 | 130420242 | 15553773 | 0.000000
09-04-2025 18:15:50000 | -1239699 | 123.9699 | 10772658 | 234442.61 | 306468201 | 99624565 | 50081818 | 0.000000 | 145389206 | 17281989 | 0.000000
09-04-2025 18:15:55000 | -1248525 | 124.8525 | 11006880 | 234382.86 | 308760315 | 99613647 | 50099957 | 0.000000 | 160634003 | 19011744 | 0.000000
09-04-2025 18:16:00000 | -1249519 | 124.9519 | 10859324 | 234360.30 | 309005005 | 99624474 | 50079414 | 0.000000 | 175740585 | 20745215 | 0.000000
09-04-2025 18:16:05000 | -1247384 | 124.7384 | 10726092 | 234349.89 | 308459717 | 99632332 | 50070511 | 0.000000 | 190722504 | 22478140 | 0.000000
09-04-2025 18:16:10000 | -1243676 | 124.3676 | 10506604 | 234305.23 | 307565674 | 99645050 | 50057831 | 0.000000 | 205347321 | 24206453 | 0.000000
09-04-2025 18:16:15000 | -1248481 | 124.8481 | 10526160 | 234226.53 | 308853149 | 99646461 | 50047550 | 0.000000 | 220023865 | 25938660 | 0.000000
09-04-2025 18:16:20000 | -1245775 | 124.5775 | 10413758 | 234294.67 | 308072510 | 99652435 | 50038517 | 0.000000 | 234415024 | 27668628 | 0.000000
09-04-2025 18:16:25000 | -1242889 | 124.2889 | 10262467 | 234259.56 | 307381744 | 99660851 | 50051075 | 0.000000 | 248710052 | 29395303 | 0.000000
09-04-2025 18:16:30000 | -1243573 | 124.3573 | 10370597 | 234287.19 | 307532806 | 99654076 | 50052197 | 0.000000 | 263042816 | 31124966 | 0.000000
09-04-2025 18:16:35000 | -1245587 | 124.5587 | 10245704 | 234241.48 | 308062042 | 99663406 | 50053410 | 0.000000 | 277294739 | 32854492 | 0.000000
09-04-2025 18:16:40000 | -1243662 | 124.3662 | 10179202 | 234268.77 | 307542114 | 99666718 | 50052673 | 0.000000 | 291406647 | 34581958 | 0.000000
09-04-2025 18:16:45000 | -1242330 | 124.233 | 10413070 | 234308.81 | 307211945 | 99650558 | 50070789 | 0.000000 | 305848267 | 36309519 | 0.000000
09-04-2025 18:16:50000 | -1247217 | 124.7217 | 10657290 | 234320.36 | 308443390 | 99636917 | 50082661 | 0.000000 | 320552856 | 38041443 | 0.000000
09-04-2025 18:16:55000 | -1249248 | 124.9248 | 10588086 | 234283.52 | 308982635 | 99642746 | 50083527 | 0.000000 | 335348663 | 39775840 | 0.000000
09-04-2025 18:17:00000 | -1247407 | 124.7407 | 10646452 | 234329.81 | 308479889 | 99637756 | 50070099 | 0.000000 | 350120056 | 41510151 | 0.000000
09-04-2025 18:17:05000 | -1245537 | 124.5537 | 10660471 | 234375.08 | 307967560 | 99635727 | 50071712 | 0.000000 | 364950623 | 43242178 | 0.000000
09-04-2025 18:17:10000 | -1244612 | 124.4612 | 10867155 | 234417.94 | 307724030 | 99620979 | 50097912 | 0.000000 | 379975311 | 44973374 | 0.000000
09-04-2025 18:17:15000 | -1249360 | 124.936 | 10441281 | 234241.58 | 309032074 | 99652596 | 50066051 | 0.000000 | 394744781 | 46708936 | 0.000000
09-04-2025 18:17:20000 | -1249330 | 124.933 | 10609452 | 234324.56 | 308955688 | 99641357 | 50057819 | 0.000000 | 409266632 | 48440464 | 0.000000
09-04-2025 18:17:25000 | -1244789 | 124.4789 | 10498548 | 234378.38 | 307744904 | 99646225 | 50058422 | 0.000000 | 423803711 | 50173613 | 0.000000
09-04-2025 18:17:30000 | -1248436 | 124.8436 | 10703205 | 234315.22 | 308766418 | 99634506 | 50084431 | 0.000000 | 438610199 | 51904575 | 0.000000
09-04-2025 18:17:35000 | -1247787 | 124.7787 | 10424718 | 234226.89 | 308658264 | 99652824 | 50072037 | 0.000000 | 453236267 | 53635918 | 0.000000
09-04-2025 18:17:40000 | -1244326 | 124.4326 | 10243916 | 234267.91 | 307720245 | 99662842 | 50053581 | 0.000000 | 467636505 | 55368721 | 0.000000
09-04-2025 18:17:45000 | -1248490 | 124.849 | 10201954 | 234201.91 | 308821777 | 99667801 | 50039604 | 0.000000 | 481911774 | 57100327 | 0.000000
09-04-2025 18:17:50000 | -1247239 | 124.7239 | 10052708 | 234166.61 | 308529480 | 99676758 | 50021732 | 0.000000 | 495893494 | 58831460 | 0.000000
09-04-2025 18:17:55000 | -1249568 | 124.9568 | 10108403 | 234142.50 | 309146240 | 99674393 | 50012672 | 0.000000 | 509911072 | 60564585 | 0.000000
09-04-2025 18:18:00000 | -1246997 | 124.6997 | 95332041 | 234073.98 | 308498291 | 99709053 | 49976421 | 0.000000 | 523324585 | 62297905 | 0.000000
09-04-2025 18:18:05000 | -1243523 | 124.3523 | 98105645 | 234196.48 | 307535950 | 99690239 | 49993214 | 0.000000 | 536723145 | 64025479 | 0.000000
09-04-2025 18:18:10000 | -1239656 | 123.9656 | 10283533 | 234368.92 | 306446838 | 99657692 | 50063030 | 0.000000 | 550677673 | 65746924 | 0.000000
09-04-2025 18:18:15000 | -1247676 | 124.7676 | 10734732 | 234354.22 | 308532867 | 99631920 | 50107956 | 0.000000 | 565420349 | 67478691 | 0.000000
09-04-2025 18:18:20000 | -1248939 | 124.8939 | 10457653 | 234274.08 | 308890533 | 99651276 | 50112305 | 0.000000 | 580070007 | 69214478 | 0.000000
09-04-2025 18:18:25000 | -1251788 | 125.1788 | 10695831 | 234312.73 | 309587006 | 99636948 | 50109501 | 0.000000 | 594752380 | 70952480 | 0.000000
09-04-2025 18:18:30000 | -1256618 | 125.6618 | 10567449 | 234207.88 | 310883362 | 99648270 | 50071587 | 0.000000 | 609630859 | 72696157 | 0.000000
09-04-2025 18:18:35000 | -1249921 | 124.9921 | 10421456 | 234313.91 | 309067902 | 99654213 | 50055016 | 0.000000 | 624059631 | 74434155 | 0.000000
09-04-2025 18:18:40000 | -1247261 | 124.7261 | 10632123 | 234344.92 | 308418488 | 99638641 | 50070118 | 0.000000 | 638817993 | 76167407 | 0.000000
09-04-2025 18:18:45000 | -1251871 | 125.1871 | 10398196 | 234212.22 | 309681885 | 99656815 | 50054665 | 0.000000 | 653407043 | 77902627 | 0.000000
09-04-2025 18:18:50000 | -1249188 | 124.9188 | 99854785 | 234126.20 | 309054321 | 99682037 | 50024776 | 0.000000 | 667525757 | 79640122 | 0.000000
09-04-2025 18:18:55000 | -1245360 | 124.536 | 10069955 | 234233.91 | 307984436 | 99674683 | 50030357 | 0.000000 | 681364990 | 81370649 | 0.000000
09-04-2025 18:19:00000 | -1248934 | 124.8934 | 10222096 | 234197.47 | 308938965 | 99666733 | 50052750 | 0.000000 | 695490173 | 83103867 | 0.000000
09-04-2025 18:19:05000 | -1250658 | 125.0658 | 10249135 | 234209.17 | 309356445 | 99665894 | 50047508 | 0.000000 | 709646545 | 84839004 | 0.000000
09-04-2025 18:19:10000 | -1248388 | 124.8388 | 10349103 | 234249.94 | 308765137 | 99658142 | 50065941 | 0.000000 | 723882202 | 86571982 | 0.000000
09-04-2025 18:19:15000 | -1252730 | 125.273 | 10434056 | 234238.94 | 309863495 | 99654930 | 50072422 | 0.000000 | 738309509 | 88308564 | 0.000000
09-04-2025 18:19:20000 | -1250299 | 125.0299 | 10097067 | 234169.58 | 309287354 | 99675499 | 50044437 | 0.000000 | 752585388 | 90046279 | 0.000000
09-04-2025 18:19:25000 | -1244821 | 124.4821 | 10378229 | 234337.17 | 307790588 | 99654266 | 50059624 | 0.000000 | 766935852 | 91780391 | 0.000000
09-04-2025 18:19:30000 | -1245490 | 124.549 | 10350520 | 234280.11 | 308016602 | 99656464 | 50060265 | 0.000000 | 781354248 | 93513359 | 0.000000
09-04-2025 18:19:35000 | -1243470 | 124.347 | 10328092 | 234283.31 | 307508514 | 99656837 | 50070896 | 0.000000 | 795730103 | 95243203 | 0.000000
09-04-2025 18:19:40000 | -1248102 | 124.8102 | 10729925 | 234360.42 | 308630432 | 99632492 | 50099480 | 0.000000 | 810410583 | 96975840 | 0.000000
09-04-2025 18:19:45000 | -1250773 | 125.0773 | 10456562 | 234240.27 | 309385864 | 99652367 | 50096897 | 0.000000 | 825161072 | 98712295 | 0.000000
09-04-2025 18:19:50000 | -1252630 | 125.263 | 10495806 | 234235.14 | 309854431 | 99650795 | 50080460 | 0.000000 | 839787781 | 10044989 | 0.000000
09-04-2025 18:19:55000 | -1245840 | 124.584 | 10598126 | 234357.30 | 308051208 | 99640121 | 50084343 | 0.000000 | 854458008 | 10218320 | 0.000000
09-04-2025 18:20:00000 | -1249755 | 124.9755 | 10541437 | 234272.14 | 309106720 | 99646156 | 50074467 | 0.000000 | 869173340 | 10391955 | 0.000000
09-04-2025 18:20:05000 | -1251983 | 125.1983 | 10354580 | 234201.16 | 309711761 | 99659737 | 50051346 | 0.000000 | 883566528 | 10565470 | 0.000000
09-04-2025 18:20:10000 | -1248811 | 124.8811 | 10065693 | 234150.80 | 308940369 | 99676735 | 50013550 | 0.000000 | 897731018 | 10738988 | 0.000000
09-04-2025 18:20:15000 | -1242251 | 124.2251 | 10122824 | 234264.17 | 307192230 | 99669632 | 50017063 | 0.000000 | 911740112 | 10911871 | 0.000000
09-04-2025 18:20:20000 | -1245600 | 124.56 | 10233779 | 234218.45 | 308098389 | 99664192 | 50039730 | 0.000000 | 925937988 | 11084448 | 0.000000
09-04-2025 18:20:25000 | -1245849 | 124.5849 | 10474552 | 234327.30 | 308064178 | 99648430 | 50046803 | 0.000000 | 940298218 | 11257489 | 0.000000
09-04-2025 18:20:30000 | -1245259 | 124.5259 | 10481578 | 234284.36 | 307974213 | 99647629 | 50082489 | 0.000000 | 954913269 | 11430282 | 0.000000
09-04-2025 18:20:35000 | -1247556 | 124.7556 | 10602105 | 234316.53 | 308524597 | 99640839 | 50110653 | 0.000000 | 969404846 | 11602962 | 0.000000
09-04-2025 18:20:40000 | -1247027 | 124.7027 | 10887995 | 234392.36 | 308352448 | 99621002 | 50123692 | 0.000000 | 984355591 | 11776096 | 0.000000
09-04-2025 18:20:45000 | -1248393 | 124.8393 | 10855244 | 234333.48 | 308759674 | 99624084 | 50129417 | 0.000000 | 999589844 | 11949452 | 0.000000
09-04-2025 18:20:50000 | -1250416 | 125.0416 | 10680710 | 234312.25 | 309246368 | 99637177 | 50098301 | 0.000000 | 10144794 | 12123221 | 0.000000
09-04-2025 18:20:55000 | -1250046 | 125.0046 | 10572283 | 234294.84 | 309156219 | 99644257 | 50082497 | 0.000000 | 10292404 | 12296802 | 0.000000
09-04-2025 18:21:00000 | -1251041 | 125.1041 | 10553247 | 234279.22 | 309417572 | 99646095 | 50067261 | 0.000000 | 10439557 | 12470485 | 0.000000
09-04-2025 18:21:05000 | -1249084 | 124.9084 | 10651496 | 234331.80 | 308890442 | 99638382 | 50046562 | 0.000000 | 10586144 | 12643983 | 0.000000
09-04-2025 18:21:10000 | -1242785 | 124.2785 | 10604828 | 234392.59 | 307259918 | 99637909 | 50054905 | 0.000000 | 10734568 | 12817126 | 0.000000
09-04-2025 18:21:15000 | -1244814 | 124.4814 | 10835615 | 234429.69 | 307750488 | 99623291 | 50086384 | 0.000000 | 10883756 | 12989968 | 0.000000
09-04-2025 18:21:20000 | -1247621 | 124.7621 | 10572669 | 234256.50 | 308625854 | 99642860 | 50088314 | 0.000000 | 11033138 | 13163346 | 0.000000
09-04-2025 18:21:25000 | -1247102 | 124.7102 | 10421505 | 234249.66 | 308460876 | 99652657 | 50058540 | 0.000000 | 11179113 | 13336797 | 0.000000
09-04-2025 18:21:30000 | -1243656 | 124.3656 | 10378951 | 234334.50 | 307499512 | 99653572 | 50055374 | 0.000000 | 11322870 | 13509912 | 0.000000
09-04-2025 18:21:35000 | -1254420 | 125.442 | 10335623 | 234163.09 | 310379089 | 99662285 | 50052948 | 0.000000 | 11466023 | 13683225 | 0.000000
09-04-2025 18:21:40000 | -1250358 | 125.0358 | 10129556 | 234194.52 | 309287933 | 99673447 | 50028297 | 0.000000 | 11606124 | 13856693 | 0.000000
09-04-2025 18:21:45000 | -1247447 | 124.7447 | 10007543 | 234167.72 | 308574097 | 99679749 | 50021069 | 0.000000 | 11745833 | 14029931 | 0.000000
09-04-2025 18:21:50000 | -1242937 | 124.2937 | 99931865 | 234230.13 | 307383972 | 99678352 | 50028099 | 0.000000 | 11883881 | 14202768 | 0.000000
09-04-2025 18:21:55000 | -1247206 | 124.7206 | 10292009 | 234269.00 | 308435303 | 99661247 | 50059444 | 0.000000 | 12026364 | 14375802 | 0.000000
09-04-2025 18:22:00000 | -1247228 | 124.7228 | 10326906 | 234260.66 | 308465576 | 99658974 | 50061691 | 0.000000 | 12169623 | 14549225 | 0.000000
09-04-2025 18:22:05000 | -1243928 | 124.3928 | 10392407 | 234318.33 | 307589752 | 99652824 | 50082172 | 0.000000 | 12313132 | 14722157 | 0.000000
09-04-2025 18:22:10000 | -1246760 | 124.676 | 10460754 | 234264.41 | 308365082 | 99649857 | 50084789 | 0.000000 | 12458709 | 14895413 | 0.000000
09-04-2025 18:22:15000 | -1245862 | 124.5862 | 10244303 | 234218.86 | 308163483 | 99663643 | 50063370 | 0.000000 | 12602512 | 15068652 | 0.000000
09-04-2025 18:22:20000 | -1250643 | 125.0643 | 10320083 | 234258.75 | 309307007 | 99661270 | 50056488 | 0.000000 | 12744348 | 15241960 | 0.000000
09-04-2025 18:22:25000 | -1246212 | 124.6212 | 10457440 | 234370.33 | 308095337 | 99649773 | 50057880 | 0.000000 | 12887513 | 15415107 | 0.000000
09-04-2025 18:22:30000 | -1249964 | 124.9964 | 10451043 | 234260.61 | 309163727 | 99652283 | 50068546 | 0.000000 | 13033237 | 15588361 | 0.000000
09-04-2025 18:22:35000 | -1249032 | 124.9032 | 10245447 | 234200.25 | 308970795 | 99665268 | 50064480 | 0.000000 | 13176711 | 15761678 | 0.000000
09-04-2025 18:22:40000 | -1246168 | 124.6168 | 10207387 | 234226.50 | 308230377 | 99666214 | 50061581 | 0.000000 | 13319716 | 15935106 | 0.000000
09-04-2025 18:22:45000 | -1252415 | 125.2415 | 10377760 | 234231.08 | 309781128 | 99658455 | 50058495 | 0.000000 | 13462834 | 16108665 | 0.000000
09-04-2025 18:22:50000 | -1248938 | 124.8938 | 10511418 | 234332.83 | 308832581 | 99647705 | 50073372 | 0.000000 | 13607157 | 16281910 | 0.000000
09-04-2025 18:22:55000 | -1252911 | 125.2911 | 10523417 | 234268.97 | 309894440 | 99649124 | 50082752 | 0.000000 | 13753633 | 16455506 | 0.000000
09-04-2025 18:23:00000 | -1249794 | 124.9794 | 10774684 | 234398.94 | 309000763 | 99630440 | 50098782 | 0.000000 | 13900557 | 16628943 | 0.000000
09-04-2025 18:23:05000 | -1251266 | 125.1266 | 10543357 | 234229.16 | 309541382 | 99646881 | 50097107 | 0.000000 | 14049305 | 16802818 | 0.000000
09-04-2025 18:23:10000 | -1251864 | 125.1864 | 10341518 | 234180.28 | 309709290 | 99660522 | 50081177 | 0.000000 | 14195182 | 16976771 | 0.000000
09-04-2025 18:23:15000 | -1248634 | 124.8634 | 10670297 | 234380.03 | 308720642 | 99636856 | 50084591 | 0.000000 | 14340859 | 17150369 | 0.000000
09-04-2025 18:23:20000 | -1251235 | 125.1235 | 10847802 | 234362.81 | 309417206 | 99626289 | 50103794 | 0.000000 | 14491637 | 17324072 | 0.000000
09-04-2025 18:23:25000 | -1251606 | 125.1606 | 10946439 | 234388.59 | 309494629 | 99619728 | 50112232 | 0.000000 | 14642072 | 17497658 | 0.000000
09-04-2025 18:23:30000 | -1255464 | 125.5464 | 10793203 | 234306.56 | 310519348 | 99632492 | 50098389 | 0.000000 | 14793261 | 17671871 | 0.000000
09-04-2025 18:23:35000 | -1250758 | 125.0758 | 10529521 | 234321.78 | 309287689 | 99647514 | 50080154 | 0.000000 | 14940338 | 17845822 | 0.000000
09-04-2025 18:23:40000 | -1247311 | 124.7311 | 10656407 | 234391.70 | 308379150 | 99637032 | 50092728 | 0.000000 | 15087781 | 18019477 | 0.000000
09-04-2025 18:23:45000 | -1249932 | 124.9932 | 10582310 | 234293.86 | 309136780 | 99643524 | 50080322 | 0.000000 | 15235873 | 18193420 | 0.000000
09-04-2025 18:23:50000 | -1248721 | 124.8721 | 10731952 | 234401.27 | 308733002 | 99632721 | 50095600 | 0.000000 | 15383969 | 18366969 | 0.000000
09-04-2025 18:23:55000 | -1253969 | 125.3969 | 10988798 | 234369.53 | 310115173 | 99618225 | 50108673 | 0.000000 | 15535984 | 18540910 | 0.000000
09-04-2025 18:24:00000 | -1251456 | 125.1456 | 10430834 | 234261.30 | 309519745 | 99654442 | 50087746 | 0.000000 | 15683615 | 18714859 | 0.000000
09-04-2025 18:24:05000 | -1247353 | 124.7353 | 10490429 | 234306.06 | 308467804 | 99648209 | 50086208 | 0.000000 | 15829799 | 18888541 | 0.000000
09-04-2025 18:24:10000 | -1249235 | 124.9235 | 10475177 | 234303.88 | 308922089 | 99650276 | 50091217 | 0.000000 | 15975337 | 19062197 | 0.000000
09-04-2025 18:24:15000 | -1248994 | 124.8994 | 10808870 | 234426.86 | 308782135 | 99627625 | 50119385 | 0.000000 | 16122534 | 19235670 | 0.000000
09-04-2025 18:24:20000 | -1251379 | 125.1379 | 10787127 | 234339.89 | 309472076 | 99630516 | 50140076 | 0.000000 | 16272743 | 19409336 | 0.000000
09-04-2025 18:24:25000 | -1251904 | 125.1904 | 10860680 | 234385.69 | 309555542 | 99625801 | 50130936 | 0.000000 | 16423235 | 19583305 | 0.000000
09-04-2025 18:24:30000 | -1253139 | 125.3139 | 11103738 | 234428.47 | 309851318 | 99609734 | 50147572 | 0.000000 | 16575769 | 19757133 | 0.000000
09-04-2025 18:24:35000 | -1257222 | 125.7222 | 11117162 | 234372.72 | 310930939 | 99611313 | 50138405 | 0.000000 | 16730540 | 19931498 | 0.000000
09-04-2025 18:24:40000 | -1256551 | 125.6551 | 11138362 | 234433.53 | 310693298 | 99609428 | 50151131 | 0.000000 | 16883914 | 20105490 | 0.000000
09-04-2025 18:24:45000 | -1253682 | 125.3682 | 10983190 | 234373.80 | 310033539 | 99618439 | 50145638 | 0.000000 | 17037999 | 20279736 | 0.000000
09-04-2025 18:24:50000 | -1252255 | 125.2255 | 10777635 | 234326.33 | 309701080 | 99631676 | 50124294 | 0.000000 | 17189421 | 20453945 | 0.000000
09-04-2025 18:24:55000 | -1250130 | 125.013 | 10647454 | 234334.42 | 309150879 | 99639259 | 50110794 | 0.000000 | 17337902 | 20627898 | 0.000000
09-04-2025 18:25:00000 | -1252910 | 125.291 | 10691463 | 234366.94 | 309790253 | 99637894 | 50102036 | 0.000000 | 17485887 | 20801904 | 0.000000
09-04-2025 18:25:05000 | -1252390 | 125.239 | 10843679 | 234376.41 | 309682587 | 99627258 | 50123932 | 0.000000 | 17636251 | 20975682 | 0.000000
09-04-2025 18:25:10000 | -1256139 | 125.6139 | 10933434 | 234357.89 | 310657410 | 99623344 | 50147911 | 0.000000 | 17787491 | 21149750 | 0.000000
09-04-2025 18:25:15000 | -1259415 | 125.9415 | 10732964 | 234232.06 | 311579285 | 99638832 | 50134983 | 0.000000 | 17938036 | 21324174 | 0.000000
09-04-2025 18:25:20000 | -1248431 | 124.8431 | 10659194 | 234424.70 | 308611664 | 99637489 | 50119926 | 0.000000 | 18085773 | 21498354 | 0.000000
09-04-2025 18:25:25000 | -1250523 | 125.0523 | 10958575 | 234413.36 | 309209106 | 99618233 | 50144958 | 0.000000 | 18237502 | 21672355 | 0.000000
09-04-2025 18:25:30000 | -1253305 | 125.3305 | 11206572 | 234482.52 | 309843994 | 99602615 | 50169209 | 0.000000 | 18390604 | 21846404 | 0.000000
09-04-2025 18:25:35000 | -1258784 | 125.8784 | 11063096 | 234304.98 | 311397736 | 99616013 | 50152477 | 0.000000 | 18546150 | 22021100 | 0.000000
09-04-2025 18:25:40000 | -1252036 | 125.2036 | 11032673 | 234453.66 | 309538849 | 99614006 | 50124611 | 0.000000 | 18697786 | 22195482 | 0.000000
09-04-2025 18:25:45000 | -1254869 | 125.4869 | 11212793 | 234433.69 | 310293274 | 99603165 | 50151268 | 0.000000 | 18851731 | 22369098 | 0.000000
09-04-2025 18:25:50000 | -1255182 | 125.5182 | 10693191 | 234259.27 | 310486725 | 99639076 | 50116047 | 0.000000 | 19003223 | 22543391 | 0.000000
09-04-2025 18:25:55000 | -1250576 | 125.0576 | 10578615 | 234290.80 | 309295105 | 99644135 | 50102043 | 0.000000 | 19150854 | 22717232 | 0.000000
09-04-2025 18:26:00000 | -1249917 | 124.9917 | 10611996 | 234323.14 | 309097412 | 99641525 | 50108654 | 0.000000 | 19298010 | 22890938 | 0.000000
09-04-2025 18:26:05000 | -1249416 | 124.9416 | 10657526 | 234340.52 | 308962250 | 99638168 | 50125591 | 0.000000 | 19446339 | 23064676 | 0.000000
09-04-2025 18:26:10000 | -1255504 | 125.5504 | 10558214 | 234226.92 | 310582672 | 99648262 | 50113712 | 0.000000 | 19594258 | 23239004 | 0.000000
09-04-2025 18:26:15000 | -1251838 | 125.1838 | 10421196 | 234294.73 | 309569336 | 99655289 | 50098732 | 0.000000 | 19738329 | 23412844 | 0.000000
09-04-2025 18:26:20000 | -1246398 | 124.6398 | 10635650 | 234394.66 | 308147095 | 99637909 | 50120968 | 0.000000 | 19885480 | 23586340 | 0.000000
09-04-2025 18:26:25000 | -1252430 | 125.243 | 10657567 | 234260.34 | 309807281 | 99639893 | 50132896 | 0.000000 | 20034340 | 23760014 | 0.000000
09-04-2025 18:26:30000 | -1254665 | 125.4665 | 10682672 | 234322.72 | 310277954 | 99639488 | 50125877 | 0.000000 | 20181899 | 23933996 | 0.000000
09-04-2025 18:26:35000 | -1249607 | 124.9607 | 10715113 | 234387.75 | 308956665 | 99634377 | 50139389 | 0.000000 | 20330225 | 24107832 | 0.000000
09-04-2025 18:26:40000 | -1249942 | 124.9942 | 10849301 | 234402.91 | 309053894 | 99625420 | 50145000 | 0.000000 | 20481272 | 24281809 | 0.000000
09-04-2025 18:26:45000 | -1251255 | 125.1255 | 10775278 | 234319.97 | 309466644 | 99631256 | 50145065 | 0.000000 | 20632397 | 24455762 | 0.000000
09-04-2025 18:26:50000 | -1250076 | 125.0076 | 10791129 | 234391.30 | 309088745 | 99629478 | 50133087 | 0.000000 | 20782280 | 24629816 | 0.000000
09-04-2025 18:26:55000 | -1253288 | 125.3288 | 10931284 | 234354.36 | 309953400 | 99621780 | 50141750 | 0.000000 | 20934456 | 24803969 | 0.000000
09-04-2025 18:27:00000 | -1253226 | 125.3226 | 10723819 | 234326.69 | 309931030 | 99635887 | 50128662 | 0.000000 | 21083733 | 24978107 | 0.000000
09-04-2025 18:27:05000 | -1255913 | 125.5913 | 10760496 | 234309.50 | 310622131 | 99634964 | 50118896 | 0.000000 | 21233618 | 25152381 | 0.000000
09-04-2025 18:27:10000 | -1252835 | 125.2835 | 10665819 | 234323.03 | 309827698 | 99639572 | 50128376 | 0.000000 | 21382161 | 25326295 | 0.000000
09-04-2025 18:27:15000 | -1254854 | 125.4854 | 10252881 | 234132.77 | 310488190 | 99667870 | 50102852 | 0.000000 | 21527444 | 25500596 | 0.000000
09-04-2025 18:27:20000 | -1251518 | 125.1518 | 10435636 | 234288.64 | 309506348 | 99654160 | 50108841 | 0.000000 | 21671125 | 25674607 | 0.000000
09-04-2025 18:27:25000 | -1249805 | 124.9805 | 10339642 | 234264.72 | 309101410 | 99659531 | 50114662 | 0.000000 | 21815239 | 25848625 | 0.000000
09-04-2025 18:27:30000 | -1254554 | 125.4554 | 10404425 | 234243.84 | 310297424 | 99657867 | 50112583 | 0.000000 | 21959683 | 26022850 | 0.000000
09-04-2025 18:27:35000 | -1255059 | 125.5059 | 10647142 | 234335.45 | 310354095 | 99642090 | 50135666 | 0.000000 | 22105254 | 26196969 | 0.000000
09-04-2025 18:27:40000 | -1255957 | 125.5957 | 10485146 | 234226.16 | 310684845 | 99653336 | 50134418 | 0.000000 | 22252896 | 26371510 | 0.000000
09-04-2025 18:27:45000 | -1250984 | 125.0984 | 10572943 | 234353.55 | 309310059 | 99644745 | 50130852 | 0.000000 | 22399580 | 26545744 | 0.000000
09-04-2025 18:27:50000 | -1255838 | 125.5838 | 11016410 | 234407.84 | 310524658 | 99617455 | 50165447 | 0.000000 | 22550344 | 26719684 | 0.000000
09-04-2025 18:27:55000 | -1258835 | 125.8835 | 10801909 | 234286.38 | 311375977 | 99633865 | 50160553 | 0.000000 | 22702209 | 26894150 | 0.000000
09-04-2025 18:28:00000 | -1256899 | 125.6899 | 11054636 | 234402.09 | 310798187 | 99615456 | 50164303 | 0.000000 | 22854331 | 27068820 | 0.000000
09-04-2025 18:28:05000 | -1260905 | 126.0905 | 11044757 | 234356.34 | 311842072 | 99618561 | 50160984 | 0.000000 | 23007810 | 27243617 | 0.000000
09-04-2025 18:28:10000 | -1258540 | 125.854 | 10479271 | 234212.20 | 311331818 | 99655136 | 50110641 | 0.000000 | 23155999 | 27418748 | 0.000000
09-04-2025 18:28:15000 | -1254991 | 125.4991 | 10348811 | 234283.73 | 310339783 | 99661728 | 50081078 | 0.000000 | 23299529 | 27593191 | 0.000000
09-04-2025 18:28:20000 | -1249052 | 124.9052 | 10805715 | 234435.75 | 308782196 | 99627876 | 50108101 | 0.000000 | 23447097 | 27766934 | 0.000000
09-04-2025 18:28:25000 | -1254854 | 125.4854 | 10950373 | 234372.06 | 310314697 | 99621407 | 50129906 | 0.000000 | 23598958 | 27941148 | 0.000000
09-04-2025 18:28:30000 | -1258005 | 125.8005 | 11123111 | 234415.34 | 311068756 | 99611382 | 50163979 | 0.000000 | 23752507 | 28115391 | 0.000000
09-04-2025 18:28:35000 | -1257993 | 125.7993 | 10801114 | 234278.88 | 311175720 | 99633430 | 50149448 | 0.000000 | 23906182 | 28290324 | 0.000000
09-04-2025 18:28:40000 | -1255834 | 125.5834 | 10381003 | 234233.41 | 310619110 | 99660088 | 50110947 | 0.000000 | 24051763 | 28464908 | 0.000000
09-04-2025 18:28:45000 | -1254034 | 125.4034 | 10340259 | 234252.28 | 310144714 | 99661774 | 50097454 | 0.000000 | 24195298 | 28639414 | 0.000000
09-04-2025 18:28:50000 | -1256871 | 125.6871 | 10457117 | 234249.16 | 310866791 | 99655678 | 50094559 | 0.000000 | 24339485 | 28813838 | 0.000000
09-04-2025 18:28:55000 | -1256916 | 125.6916 | 10254434 | 234179.08 | 310932312 | 99668854 | 50097176 | 0.000000 | 24483230 | 28988064 | 0.000000
09-04-2025 18:29:00000 | -1256120 | 125.612 | 10179739 | 234128.22 | 310786713 | 99673225 | 50081985 | 0.000000 | 24624646 | 29162477 | 0.000000
09-04-2025 18:29:05000 | -1252738 | 125.2738 | 10202373 | 234218.06 | 309843292 | 99670013 | 50081627 | 0.000000 | 24765208 | 29336537 | 0.000000
09-04-2025 18:29:10000 | -1253658 | 125.3658 | 10104218 | 234202.88 | 310079865 | 99676773 | 50092281 | 0.000000 | 24905313 | 29510342 | 0.000000
09-04-2025 18:29:15000 | -1254318 | 125.4318 | 10288301 | 234231.11 | 310236328 | 99665298 | 50109749 | 0.000000 | 25047913 | 29684543 | 0.000000
09-04-2025 18:29:20000 | -1254878 | 125.4878 | 10509557 | 234284.25 | 310348877 | 99651131 | 50139278 | 0.000000 | 25192590 | 29858535 | 0.000000
09-04-2025 18:29:25000 | -1259158 | 125.9158 | 10536610 | 234228.22 | 311481079 | 99651711 | 50133537 | 0.000000 | 25339185 | 30033041 | 0.000000
09-04-2025 18:29:30000 | -1260148 | 126.0148 | 10645189 | 234260.22 | 311696747 | 99645088 | 50128780 | 0.000000 | 25486104 | 30207746 | 0.000000
09-04-2025 18:29:35000 | -1257319 | 125.7319 | 10850934 | 234357.72 | 310918213 | 99629662 | 50139439 | 0.000000 | 25636213 | 30382512 | 0.000000
09-04-2025 18:29:40000 | -1260259 | 126.0259 | 10989449 | 234347.22 | 311682068 | 99621964 | 50154648 | 0.000000 | 25788535 | 30557256 | 0.000000
09-04-2025 18:29:45000 | -1263485 | 126.3485 | 10919719 | 234294.39 | 312533813 | 99628609 | 50146076 | 0.000000 | 25941089 | 30732563 | 0.000000
09-04-2025 18:29:50000 | -1263218 | 126.3218 | 10395065 | 234184.92 | 312511383 | 99663124 | 50104626 | 0.000000 | 26087415 | 30907986 | 0.000000
09-04-2025 18:29:55000 | -1257835 | 125.7835 | 10349866 | 234241.02 | 311098541 | 99663185 | 50097752 | 0.000000 | 26231536 | 31082760 | 0.000000
09-04-2025 18:30:00000 | -1258191 | 125.8191 | 10436295 | 234260.78 | 311170624 | 99657753 | 50104504 | 0.000000 | 26375498 | 31257414 | 0.000000
09-04-2025 18:30:05000 | -1261471 | 126.1471 | 10576782 | 234214.45 | 312069336 | 99650345 | 50126488 | 0.000000 | 14651164 | 174634796 | 0.000000
09-04-2025 18:30:10000 | -1260485 | 126.0485 | 10067382 | 234079.95 | 311905762 | 99682564 | 50079624 | 0.000000 | 28986929 | 349948303 | 0.000000
09-04-2025 18:30:15000 | -1255620 | 125.562 | 99081543 | 234204.28 | 310511688 | 99690102 | 50060070 | 0.000000 | 42724941 | 524689575 | 0.000000
09-04-2025 18:30:20000 | -1259044 | 125.9044 | 10195401 | 234170.56 | 311457367 | 99673737 | 50082066 | 0.000000 | 56807880 | 699150208 | 0.000000
09-04-2025 18:30:25000 | -1255825 | 125.5825 | 97440449 | 234041.50 | 310748047 | 99700333 | 50044617 | 0.000000 | 70686050 | 874132080 | 0.000000
09-04-2025 18:30:30000 | -1252402 | 125.2402 | 98041055 | 234176.70 | 309738708 | 99694992 | 50043980 | 0.000000 | 84362129 | 10487280 | 0.000000
09-04-2025 18:30:35000 | -1256924 | 125.6924 | 10088314 | 234198.91 | 310877533 | 99679451 | 50074482 | 0.000000 | 98308121 | 12230917 | 0.000000
09-04-2025 18:30:40000 | -1258685 | 125.8685 | 10266775 | 234190.39 | 311358368 | 99668991 | 50096638 | 0.000000 | 112474678 | 13977269 | 0.000000
09-04-2025 18:30:45000 | -1260002 | 126.0002 | 10495141 | 234257.69 | 311640961 | 99654892 | 50112213 | 0.000000 | 126921471 | 15725834 | 0.000000
09-04-2025 18:30:50000 | -1263165 | 126.3165 | 10234592 | 234091.05 | 312586273 | 99673370 | 50086853 | 0.000000 | 141455704 | 17481140 | 0.000000
09-04-2025 18:30:55000 | -1256730 | 125.673 | 10438247 | 234305.20 | 310759125 | 99656837 | 50077816 | 0.000000 | 155824020 | 19234082 | 0.000000
09-04-2025 18:31:00000 | -1263555 | 126.3555 | 11045396 | 234395.05 | 312442261 | 99620102 | 50131470 | 0.000000 | 170820511 | 20981875 | 0.000000
09-04-2025 18:31:05000 | -1264721 | 126.4721 | 11261913 | 234412.22 | 312752716 | 99605881 | 50151894 | 0.000000 | 186378387 | 22735291 | 0.000000
09-04-2025 18:31:10000 | -1264375 | 126.4375 | 11131567 | 234343.89 | 312729187 | 99614685 | 50125084 | 0.000000 | 201953583 | 24494060 | 0.000000
09-04-2025 18:31:15000 | -1266379 | 126.6379 | 11319113 | 234405.16 | 313175323 | 99602921 | 50115051 | 0.000000 | 217603073 | 26250549 | 0.000000
09-04-2025 18:31:20000 | -1262990 | 126.299 | 11103313 | 234386.58 | 312321808 | 99615791 | 50079258 | 0.000000 | 233166763 | 28007480 | 0.000000
09-04-2025 18:31:25000 | -1261044 | 126.1044 | 10765045 | 234293.30 | 311905579 | 99637611 | 50037899 | 0.000000 | 248392380 | 29764355 | 0.000000
09-04-2025 18:31:30000 | -1256824 | 125.6824 | 10740245 | 234380.25 | 310743134 | 99636856 | 50034611 | 0.000000 | 263326630 | 31515352 | 0.000000
09-04-2025 18:31:35000 | -1257908 | 125.7908 | 10926696 | 234367.09 | 311065918 | 99624855 | 50050781 | 0.000000 | 278567444 | 33264863 | 0.000000
09-04-2025 18:31:40000 | -1260868 | 126.0868 | 10875719 | 234351.89 | 311805115 | 99630058 | 50036041 | 0.000000 | 293583038 | 35014114 | 0.000000
09-04-2025 18:31:45000 | -1259503 | 125.9503 | 11011219 | 234403.19 | 311425537 | 99620018 | 50042149 | 0.000000 | 308814484 | 36763699 | 0.000000
09-04-2025 18:31:50000 | -1258878 | 125.8878 | 11143218 | 234412.11 | 311295746 | 99610527 | 50074226 | 0.000000 | 324244781 | 38513113 | 0.000000
09-04-2025 18:31:55000 | -1261868 | 126.1868 | 11001754 | 234329.52 | 312105896 | 99622078 | 50060963 | 0.000000 | 339680756 | 40266985 | 0.000000
09-04-2025 18:32:00000 | -1264644 | 126.4644 | 10693524 | 234227.66 | 312854858 | 99644409 | 50016693 | 0.000000 | 354718475 | 42023042 | 0.000000
09-04-2025 18:32:05000 | -1262886 | 126.2886 | 10426040 | 234211.11 | 312394562 | 99660950 | 49961266 | 0.000000 | 369365387 | 43778979 | 0.000000
09-04-2025 18:32:10000 | -1252857 | 125.2857 | 10317362 | 234315.55 | 309769287 | 99662636 | 49973820 | 0.000000 | 383722382 | 45523599 | 0.000000
09-04-2025 18:32:15000 | -1252278 | 125.2278 | 10996527 | 234473.52 | 309557678 | 99616669 | 50040730 | 0.000000 | 398785461 | 47265566 | 0.000000
09-04-2025 18:32:20000 | -1262677 | 126.2677 | 11225736 | 234352.88 | 312317078 | 99607132 | 50084496 | 0.000000 | 414334839 | 49013696 | 0.000000
09-04-2025 18:32:25000 | -1266223 | 126.6223 | 10687067 | 234239.00 | 313225189 | 99645714 | 50058994 | 0.000000 | 429228882 | 50768203 | 0.000000
09-04-2025 18:32:30000 | -1261304 | 126.1304 | 10439746 | 234225.17 | 311986359 | 99659210 | 50024780 | 0.000000 | 443884796 | 52522471 | 0.000000
09-04-2025 18:32:35000 | -1256030 | 125.603 | 10511183 | 234306.86 | 310604614 | 99651665 | 50016876 | 0.000000 | 458481445 | 54272153 | 0.000000
09-04-2025 18:32:40000 | -1257991 | 125.7991 | 10642501 | 234299.47 | 311119324 | 99644058 | 50036324 | 0.000000 | 473276611 | 56020371 | 0.000000
09-04-2025 18:32:45000 | -1258636 | 125.8636 | 10740655 | 234287.20 | 311313843 | 99637871 | 50047817 | 0.000000 | 488257996 | 57770376 | 0.000000
09-04-2025 18:32:50000 | -1261098 | 126.1098 | 10438566 | 234214.86 | 311951416 | 99659180 | 50018917 | 0.000000 | 502876312 | 59523096 | 0.000000
09-04-2025 18:32:55000 | -1263043 | 126.3043 | 10386593 | 234181.59 | 312460236 | 99663582 | 49996933 | 0.000000 | 517327576 | 61274858 | 0.000000
09-04-2025 18:33:00000 | -1258625 | 125.8625 | 98714629 | 234110.00 | 311365936 | 99693848 | 49967140 | 0.000000 | 531304382 | 63025044 | 0.000000
09-04-2025 18:33:05000 | -1255752 | 125.5752 | 10090540 | 234214.13 | 310564941 | 99678711 | 49989555 | 0.000000 | 545238892 | 64770962 | 0.000000
09-04-2025 18:33:10000 | -1256564 | 125.6564 | 10339930 | 234205.41 | 310829834 | 99663147 | 50017647 | 0.000000 | 559587280 | 66516909 | 0.000000
09-04-2025 18:33:15000 | -1256322 | 125.6322 | 10417467 | 234250.05 | 310727264 | 99657974 | 50033318 | 0.000000 | 574122498 | 68265127 | 0.000000
09-04-2025 18:33:20000 | -1264751 | 126.4751 | 10512310 | 234172.00 | 312918488 | 99656349 | 50035942 | 0.000000 | 588724487 | 70018384 | 0.000000
09-04-2025 18:33:25000 | -1264214 | 126.4214 | 10226942 | 234134.27 | 312784027 | 99674393 | 50033325 | 0.000000 | 602919250 | 71768818 | 0.000000
09-04-2025 18:33:30000 | -1259709 | 125.9709 | 10046812 | 234140.25 | 311632477 | 99683464 | 50026848 | 0.000000 | 616963684 | 73520215 | 0.000000
09-04-2025 18:33:35000 | -1260171 | 126.0171 | 10362781 | 234224.55 | 311692230 | 99663589 | 50069321 | 0.000000 | 631264404 | 75268228 | 0.000000
09-04-2025 18:33:40000 | -1262793 | 126.2793 | 10349274 | 234163.41 | 312418121 | 99665848 | 50071404 | 0.000000 | 645591309 | 77020938 | 0.000000
09-04-2025 18:33:45000 | -1264172 | 126.4172 | 10272334 | 234169.52 | 312730164 | 99671486 | 50047825 | 0.000000 | 659887207 | 78778496 | 0.000000
09-04-2025 18:33:50000 | -1262034 | 126.2034 | 10165586 | 234210.45 | 312128662 | 99677162 | 50019943 | 0.000000 | 673991699 | 80534258 | 0.000000
09-04-2025 18:33:55000 | -1257005 | 125.7005 | 10389675 | 234308.28 | 310814575 | 99660156 | 50046951 | 0.000000 | 688334839 | 82282402 | 0.000000
09-04-2025 18:34:00000 | -1264645 | 126.4645 | 10492854 | 234205.92 | 312842072 | 99657562 | 50067669 | 0.000000 | 702950867 | 84035537 | 0.000000
09-04-2025 18:34:05000 | -1266060 | 126.606 | 10269767 | 234107.48 | 313282745 | 99672623 | 50047161 | 0.000000 | 717299255 | 85792373 | 0.000000
09-04-2025 18:34:10000 | -1261189 | 126.1189 | 10071652 | 234119.30 | 312023010 | 99682648 | 50032597 | 0.000000 | 731400879 | 87544551 | 0.000000
09-04-2025 18:34:15000 | -1262923 | 126.2923 | 10040524 | 234063.78 | 312520905 | 99685463 | 50013336 | 0.000000 | 745546265 | 89301641 | 0.000000
09-04-2025 18:34:20000 | -1258366 | 125.8366 | 98535879 | 234118.94 | 311290039 | 99694824 | 50009022 | 0.000000 | 759259888 | 91053066 | 0.000000
09-04-2025 18:34:25000 | -1263159 | 126.3159 | 10314415 | 234210.23 | 312437164 | 99668274 | 50052380 | 0.000000 | 773354553 | 92802422 | 0.000000
09-04-2025 18:34:30000 | -1260589 | 126.0589 | 10426602 | 234281.59 | 311734528 | 99659683 | 50068050 | 0.000000 | 787654724 | 94554951 | 0.000000
09-04-2025 18:34:35000 | -1264951 | 126.4951 | 10676696 | 234269.34 | 312871979 | 99645691 | 50106812 | 0.000000 | 802367737 | 96307109 | 0.000000
09-04-2025 18:34:40000 | -1267136 | 126.7136 | 10705611 | 234204.20 | 313505707 | 99644997 | 50105289 | 0.000000 | 817326111 | 98065977 | 0.000000
09-04-2025 18:34:45000 | -1266374 | 126.6374 | 10232874 | 234115.08 | 313334900 | 99675125 | 50050182 | 0.000000 | 831885254 | 99828555 | 0.000000
09-04-2025 18:34:50000 | -1263368 | 126.3368 | 10143541 | 234189.81 | 312481781 | 99679230 | 50036774 | 0.000000 | 845908386 | 10158534 | 0.000000
09-04-2025 18:34:55000 | -1263429 | 126.3429 | 10499590 | 234261.97 | 312475433 | 99656464 | 50074505 | 0.000000 | 860348022 | 10333903 | 0.000000
09-04-2025 18:35:00000 | -1271752 | 127.1752 | 10617292 | 234173.86 | 314671814 | 99653320 | 50071774 | 0.000000 | 875022644 | 10509985 | 0.000000
09-04-2025 18:35:05000 | -1265360 | 126.536 | 10450027 | 234227.34 | 312986847 | 99660721 | 50040470 | 0.000000 | 889488708 | 10685949 | 0.000000
09-04-2025 18:35:10000 | -1264147 | 126.4147 | 10634396 | 234289.64 | 312637787 | 99648033 | 50067268 | 0.000000 | 904155334 | 10861483 | 0.000000
09-04-2025 18:35:15000 | -1264414 | 126.4414 | 10486886 | 234203.67 | 312792145 | 99657822 | 50064388 | 0.000000 | 918965576 | 11037602 | 0.000000
09-04-2025 18:35:20000 | -1266314 | 126.6314 | 10636485 | 234257.41 | 313219055 | 99649094 | 50067699 | 0.000000 | 933641235 | 11213396 | 0.000000
09-04-2025 18:35:25000 | -1267764 | 126.7764 | 10569178 | 234203.42 | 313629791 | 99654282 | 50070766 | 0.000000 | 948396240 | 11389273 | 0.000000
09-04-2025 18:35:30000 | -1266943 | 126.6943 | 10486996 | 234219.92 | 313396667 | 99659172 | 50054699 | 0.000000 | 962980530 | 11565176 | 0.000000
09-04-2025 18:35:35000 | -1266006 | 126.6006 | 10286704 | 234222.97 | 313112488 | 99671524 | 50019577 | 0.000000 | 977195068 | 11741102 | 0.000000
09-04-2025 18:35:40000 | -1262272 | 126.2272 | 10557748 | 234292.66 | 312160675 | 99652039 | 50045025 | 0.000000 | 991706909 | 11916447 | 0.000000
09-04-2025 18:35:45000 | -1262965 | 126.2965 | 10488695 | 234217.69 | 312417603 | 99656921 | 50055553 | 0.000000 | 10063918 | 12092091 | 0.000000
09-04-2025 18:35:50000 | -1265890 | 126.589 | 10265292 | 234114.44 | 313223755 | 99672821 | 50043289 | 0.000000 | 10208781 | 12267913 | 0.000000
09-04-2025 18:35:55000 | -1266271 | 126.6271 | 10176983 | 234157.30 | 313246368 | 99678589 | 50029907 | 0.000000 | 10349143 | 12443587 | 0.000000
09-04-2025 18:36:00000 | -1268166 | 126.8166 | 10103635 | 234105.63 | 313762054 | 99684128 | 50020306 | 0.000000 | 10489325 | 12619504 | 0.000000
09-04-2025 18:36:05000 | -1263099 | 126.3099 | 10199828 | 234219.69 | 312386597 | 99675537 | 50025620 | 0.000000 | 10629191 | 12794985 | 0.000000
09-04-2025 18:36:10000 | -1258982 | 125.8982 | 10854407 | 234387.06 | 311294525 | 99630402 | 50096584 | 0.000000 | 10776187 | 12969852 | 0.000000
09-04-2025 18:36:15000 | -1266245 | 126.6245 | 10473955 | 234143.41 | 313318512 | 99659645 | 50077450 | 0.000000 | 10925420 | 13146020 | 0.000000
09-04-2025 18:36:20000 | -1266509 | 126.6509 | 10505509 | 234219.91 | 313287506 | 99657745 | 50078312 | 0.000000 | 11071381 | 13322008 | 0.000000
09-04-2025 18:36:25000 | -1268226 | 126.8226 | 10523892 | 234189.45 | 313749268 | 99657471 | 50075024 | 0.000000 | 11216576 | 13497800 | 0.000000
09-04-2025 18:36:30000 | -1268768 | 126.8768 | 10461043 | 234179.91 | 313885803 | 99661819 | 50067760 | 0.000000 | 11361487 | 13673716 | 0.000000
09-04-2025 18:36:35000 | -1265697 | 126.5697 | 10364330 | 234201.41 | 313079590 | 99666405 | 50063702 | 0.000000 | 11505566 | 13849570 | 0.000000
09-04-2025 18:36:40000 | -1267791 | 126.7791 | 10486411 | 234226.81 | 313588318 | 99659668 | 50052353 | 0.000000 | 11650781 | 14025824 | 0.000000
09-04-2025 18:36:45000 | -1285546 | 128.5546 | 10489582 | 233858.27 | 318453217 | 99668755 | 50002651 | 0.000000 | 11796843 | 14202396 | 0.000000
09-04-2025 18:36:50000 | -1263247 | 126.3247 | 90694297 | 233929.14 | 312614532 | 99743271 | 49822048 | 0.000000 | 11926608 | 14379227 | 0.000000
09-04-2025 18:36:55000 | -1251110 | 125.111 | 91964375 | 234090.45 | 309422668 | 99730934 | 49833748 | 0.000000 | 12055377 | 14553846 | 0.000000
09-04-2025 18:37:00000 | -1258953 | 125.8953 | 92475479 | 233944.89 | 311554504 | 99731308 | 49868229 | 0.000000 | 12184387 | 14728495 | 0.000000
09-04-2025 18:37:05000 | -1259868 | 125.9868 | 90312285 | 233886.42 | 311816986 | 99744057 | 49874886 | 0.000000 | 12311143 | 14903320 | 0.000000
09-04-2025 18:37:10000 | -1256859 | 125.6859 | 88968154 | 233908.31 | 311023712 | 99750404 | 49893909 | 0.000000 | 12436360 | 15078301 | 0.000000
09-04-2025 18:37:15000 | -1262395 | 126.2395 | 90172588 | 233794.88 | 312563324 | 99745865 | 49914246 | 0.000000 | 12562009 | 15253079 | 0.000000
09-04-2025 18:37:20000 | -1262840 | 126.284 | 88436826 | 233788.77 | 312650513 | 99755684 | 49898315 | 0.000000 | 12685148 | 15428333 | 0.000000
09-04-2025 18:37:25000 | -1260954 | 126.0954 | 87824717 | 233839.98 | 312109406 | 99758324 | 49885441 | 0.000000 | 12807296 | 15603777 | 0.000000
09-04-2025 18:37:30000 | -1259712 | 125.9712 | 88424199 | 233848.39 | 311804504 | 99754547 | 49908379 | 0.000000 | 12929252 | 15778546 | 0.000000
09-04-2025 18:37:35000 | -1263069 | 126.3069 | 92286201 | 233935.61 | 312578339 | 99734138 | 49915409 | 0.000000 | 13054811 | 15953625 | 0.000000
09-04-2025 18:37:40000 | -1262431 | 126.2431 | 91311318 | 233860.05 | 312506866 | 99739441 | 49914520 | 0.000000 | 13182391 | 16129026 | 0.000000
09-04-2025 18:37:45000 | -1261588 | 126.1588 | 89408301 | 233872.78 | 312261658 | 99749817 | 49931042 | 0.000000 | 13306403 | 16303832 | 0.000000
09-04-2025 18:37:50000 | -1261165 | 126.1165 | 91491865 | 233904.17 | 312144257 | 99737892 | 49944271 | 0.000000 | 13432588 | 16478891 | 0.000000
09-04-2025 18:37:55000 | -1260796 | 126.0796 | 93751621 | 234007.73 | 311949280 | 99724678 | 49964115 | 0.000000 | 13561129 | 16653967 | 0.000000
09-04-2025 18:38:00000 | -1264886 | 126.4886 | 91704941 | 233848.02 | 313128204 | 99738213 | 49939255 | 0.000000 | 13690402 | 16829510 | 0.000000
09-04-2025 18:38:05000 | -1261298 | 126.1298 | 93158164 | 234018.09 | 312044342 | 99728355 | 49911636 | 0.000000 | 13817997 | 17004959 | 0.000000
09-04-2025 18:38:10000 | -1261406 | 126.1406 | 92889775 | 233935.73 | 312177704 | 99729958 | 49910603 | 0.000000 | 13948711 | 17180227 | 0.000000
09-04-2025 18:38:15000 | -1262058 | 126.2058 | 92501943 | 233922.98 | 312345734 | 99732475 | 49933105 | 0.000000 | 14077604 | 17355201 | 0.000000
09-04-2025 18:38:20000 | -1260950 | 126.095 | 89888682 | 233835.03 | 312142944 | 99746880 | 49953243 | 0.000000 | 14204309 | 17530303 | 0.000000
09-04-2025 18:38:25000 | -1261224 | 126.1224 | 88335518 | 233829.30 | 312194672 | 99755623 | 49932228 | 0.000000 | 14327358 | 17705742 | 0.000000
09-04-2025 18:38:30000 | -1263117 | 126.3117 | 88374844 | 233812.75 | 312680420 | 99756134 | 49906498 | 0.000000 | 14449449 | 17881133 | 0.000000
09-04-2025 18:38:35000 | -1259659 | 125.9659 | 88365430 | 233887.34 | 311732483 | 99754852 | 49914803 | 0.000000 | 14571844 | 18056115 | 0.000000
09-04-2025 18:38:40000 | -1258873 | 125.8873 | 89807305 | 233941.48 | 311496063 | 99746498 | 49924431 | 0.000000 | 14694530 | 18230904 | 0.000000
09-04-2025 18:38:45000 | -1259145 | 125.9145 | 96857939 | 234110.08 | 311467743 | 99705444 | 49984150 | 0.000000 | 14823597 | 18405471 | 0.000000
09-04-2025 18:38:50000 | -1264766 | 126.4766 | 94642109 | 233890.47 | 313100800 | 99721199 | 49996658 | 0.000000 | 14957722 | 18580920 | 0.000000
09-04-2025 18:38:55000 | -1264468 | 126.4468 | 91424287 | 233851.30 | 313023071 | 99739639 | 49974010 | 0.000000 | 15086090 | 18756391 | 0.000000
09-04-2025 18:39:00000 | -1262119 | 126.2119 | 92341387 | 233988.52 | 312280945 | 99733421 | 49988338 | 0.000000 | 15212666 | 18931432 | 0.000000
09-04-2025 18:39:05000 | -1260047 | 126.0047 | 93715420 | 233974.78 | 311806244 | 99724564 | 50013687 | 0.000000 | 15343098 | 19106529 | 0.000000
09-04-2025 18:39:10000 | -1263469 | 126.3469 | 94887119 | 233947.53 | 312705292 | 99719185 | 50019207 | 0.000000 | 15474459 | 19281908 | 0.000000
09-04-2025 18:39:15000 | -1262496 | 126.2496 | 94811123 | 233955.22 | 312460907 | 99719200 | 50008606 | 0.000000 | 15606240 | 19457393 | 0.000000
09-04-2025 18:39:20000 | -1262700 | 126.27 | 93455039 | 233904.78 | 312554169 | 99727234 | 49988922 | 0.000000 | 15738209 | 19633133 | 0.000000
09-04-2025 18:39:25000 | -1260927 | 126.0927 | 93990479 | 234006.64 | 311981598 | 99723335 | 49989315 | 0.000000 | 15867705 | 19808293 | 0.000000
09-04-2025 18:39:30000 | -1261915 | 126.1915 | 96164414 | 234035.66 | 312227875 | 99710899 | 50004185 | 0.000000 | 16000121 | 19983457 | 0.000000
09-04-2025 18:39:35000 | -1263560 | 126.356 | 96232412 | 234004.47 | 312681641 | 99711243 | 50017475 | 0.000000 | 16134061 | 20158748 | 0.000000
09-04-2025 18:39:40000 | -1264192 | 126.4192 | 94599111 | 233933.97 | 312895630 | 99721199 | 50000729 | 0.000000 | 16266702 | 20334387 | 0.000000
09-04-2025 18:39:45000 | -1262604 | 126.2604 | 93391865 | 233911.80 | 312519379 | 99727554 | 49977001 | 0.000000 | 16398483 | 20509723 | 0.000000
09-04-2025 18:39:50000 | -1260528 | 126.0528 | 89585996 | 233854.44 | 312015747 | 99748405 | 49922649 | 0.000000 | 16525120 | 20685059 | 0.000000
09-04-2025 18:39:55000 | -1261347 | 126.1347 | 91583672 | 233934.56 | 312142517 | 99737442 | 49909969 | 0.000000 | 16650043 | 20859990 | 0.000000
09-04-2025 18:40:00000 | -1260189 | 126.0189 | 86356602 | 233773.59 | 311982025 | 99766029 | 49899914 | 0.000000 | 16772092 | 21034900 | 0.000000
09-04-2025 18:40:05000 | -1257622 | 125.7622 | 84505869 | 233722.13 | 311384796 | 99775002 | 49895218 | 0.000000 | 16889969 | 21209498 | 0.000000
09-04-2025 18:40:10000 | -1249761 | 124.9761 | 83996182 | 233825.83 | 309305176 | 99774902 | 49918774 | 0.000000 | 17007272 | 21383658 | 0.000000
09-04-2025 18:40:15000 | -1255095 | 125.5095 | 81443125 | 233625.66 | 310839172 | 99790123 | 49911335 | 0.000000 | 17123503 | 21558096 | 0.000000
09-04-2025 18:40:20000 | -1251686 | 125.1686 | 83861875 | 233831.83 | 309763397 | 99776306 | 49923965 | 0.000000 | 17237626 | 21732199 | 0.000000
09-04-2025 18:40:25000 | -1256303 | 125.6303 | 87146426 | 233857.16 | 310927002 | 99760277 | 49944618 | 0.000000 | 17356854 | 21906563 | 0.000000
09-04-2025 18:40:30000 | -1257892 | 125.7892 | 89935781 | 233902.05 | 311313568 | 99745384 | 49972160 | 0.000000 | 17480254 | 22081227 | 0.000000
09-04-2025 18:40:35000 | -1261750 | 126.175 | 95262832 | 234041.55 | 312171295 | 99716194 | 49997768 | 0.000000 | 17606034 | 22255660 | 0.000000
09-04-2025 18:40:40000 | -1259918 | 125.9918 | 94933740 | 234014.80 | 311743713 | 99717331 | 50007915 | 0.000000 | 17737563 | 22430563 | 0.000000
09-04-2025 18:40:45000 | -1257812 | 125.7812 | 95203027 | 234024.36 | 311215607 | 99714783 | 50032928 | 0.000000 | 17870062 | 22605322 | 0.000000
09-04-2025 18:40:50000 | -1265677 | 126.5677 | 93142275 | 233863.31 | 313330444 | 99730316 | 50043377 | 0.000000 | 18000298 | 22780629 | 0.000000
09-04-2025 18:40:55000 | -1264959 | 126.4959 | 87909629 | 233737.02 | 313236023 | 99759384 | 49991268 | 0.000000 | 18125806 | 22956412 | 0.000000
09-04-2025 18:41:00000 | -1257611 | 125.7611 | 88390117 | 233851.06 | 311281799 | 99753922 | 49964504 | 0.000000 | 18248452 | 23131646 | 0.000000
09-04-2025 18:41:05000 | -1261284 | 126.1284 | 89754912 | 233843.63 | 312215088 | 99747757 | 49960102 | 0.000000 | 18372957 | 23306559 | 0.000000
09-04-2025 18:41:10000 | -1256507 | 125.6507 | 88213467 | 233854.22 | 310996368 | 99754471 | 49949215 | 0.000000 | 18495598 | 23481416 | 0.000000
09-04-2025 18:41:15000 | -1262628 | 126.2628 | 90147012 | 233840.42 | 312554993 | 99746101 | 49929077 | 0.000000 | 18619797 | 23656600 | 0.000000
09-04-2025 18:41:20000 | -1256831 | 125.6831 | 88774873 | 233896.00 | 311030579 | 99751472 | 49919376 | 0.000000 | 18743151 | 23831389 | 0.000000
09-04-2025 18:41:25000 | -1255146 | 125.5146 | 87596436 | 233835.31 | 310675903 | 99757355 | 49917973 | 0.000000 | 18866196 | 24006250 | 0.000000
09-04-2025 18:41:30000 | -1254767 | 125.4767 | 88159902 | 233892.73 | 310518616 | 99754089 | 49946297 | 0.000000 | 18987861 | 24180639 | 0.000000
09-04-2025 18:41:35000 | -1259196 | 125.9196 | 87375332 | 233794.61 | 311720825 | 99760117 | 49960777 | 0.000000 | 19110663 | 24355479 | 0.000000
09-04-2025 18:41:40000 | -1260012 | 126.0012 | 91158564 | 233878.86 | 311874847 | 99739319 | 49973167 | 0.000000 | 19236235 | 24530469 | 0.000000
09-04-2025 18:41:45000 | -1258750 | 125.875 | 88138369 | 233837.77 | 311567017 | 99755753 | 49965752 | 0.000000 | 19359733 | 24705416 | 0.000000
09-04-2025 18:41:50000 | -1260390 | 126.039 | 87087568 | 233798.33 | 312006989 | 99762138 | 49948158 | 0.000000 | 19482003 | 24880430 | 0.000000
09-04-2025 18:41:55000 | -1255108 | 125.5108 | 87007715 | 233851.23 | 310632355 | 99760582 | 49956223 | 0.000000 | 19602561 | 25055055 | 0.000000
09-04-2025 18:42:00000 | -1260751 | 126.0751 | 90930967 | 233898.84 | 312029510 | 99740913 | 49991100 | 0.000000 | 19727198 | 25229699 | 0.000000
09-04-2025 18:42:05000 | -1261094 | 126.1094 | 90191035 | 233856.38 | 312156464 | 99745232 | 49964188 | 0.000000 | 19852704 | 25404938 | 0.000000
09-04-2025 18:42:10000 | -1256639 | 125.6639 | 93778154 | 234031.72 | 310891815 | 99722702 | 49980175 | 0.000000 | 19981099 | 25579609 | 0.000000
09-04-2025 18:42:15000 | -1259693 | 125.9693 | 95095391 | 234016.20 | 311691193 | 99716270 | 50007992 | 0.000000 | 20112517 | 25754465 | 0.000000
09-04-2025 18:42:20000 | -1260636 | 126.0636 | 94216016 | 233932.03 | 312016998 | 99721886 | 50016369 | 0.000000 | 20244653 | 25929576 | 0.000000
09-04-2025 18:42:25000 | -1261428 | 126.1428 | 93043115 | 233901.36 | 312228607 | 99729080 | 50010555 | 0.000000 | 20375133 | 26104686 | 0.000000
09-04-2025 18:42:30000 | -1262790 | 126.279 | 88137930 | 233741.44 | 312691559 | 99757309 | 49966129 | 0.000000 | 20501143 | 26280119 | 0.000000
09-04-2025 18:42:35000 | -1258266 | 125.8266 | 89250928 | 233910.50 | 311374023 | 99749382 | 49953857 | 0.000000 | 20623525 | 26455020 | 0.000000
09-04-2025 18:42:40000 | -1257846 | 125.7846 | 89945498 | 233899.59 | 311297699 | 99745308 | 49960857 | 0.000000 | 20748333 | 26629695 | 0.000000
09-04-2025 18:42:45000 | -1257312 | 125.7312 | 93681846 | 234023.03 | 311069305 | 99723564 | 49986565 | 0.000000 | 20876372 | 26804426 | 0.000000
09-04-2025 18:42:50000 | -1261173 | 126.1173 | 95682646 | 234005.09 | 312077637 | 99713440 | 50003098 | 0.000000 | 21008838 | 26979516 | 0.000000
09-04-2025 18:42:55000 | -1263163 | 126.3163 | 92900723 | 233907.03 | 312656342 | 99730644 | 50001053 | 0.000000 | 21140098 | 27154953 | 0.000000
09-04-2025 18:43:00000 | -1265632 | 126.5632 | 89176572 | 233740.89 | 313419952 | 99752686 | 49973267 | 0.000000 | 21266870 | 27330594 | 0.000000
09-04-2025 18:43:05000 | -1263127 | 126.3127 | 83230156 | 233616.69 | 312859711 | 99783615 | 49916275 | 0.000000 | 21385850 | 27506211 | 0.000000
09-04-2025 18:43:10000 | -1252556 | 125.2556 | 82188008 | 233801.75 | 309993958 | 99785416 | 49893829 | 0.000000 | 21499841 | 27681168 | 0.000000
09-04-2025 18:43:15000 | -1258157 | 125.8157 | 86224717 | 233808.88 | 311427368 | 99765991 | 49927967 | 0.000000 | 21618306 | 27855756 | 0.000000
09-04-2025 18:43:20000 | -1257660 | 125.766 | 88448574 | 233875.19 | 311259064 | 99753616 | 49946827 | 0.000000 | 21739102 | 28030594 | 0.000000
09-04-2025 18:43:25000 | -1260790 | 126.079 | 91190498 | 233894.44 | 312053497 | 99739456 | 49951077 | 0.000000 | 21864456 | 28205857 | 0.000000
09-04-2025 18:43:30000 | -1263027 | 126.3027 | 92549014 | 233947.89 | 312563629 | 99732613 | 49966351 | 0.000000 | 21991213 | 28381008 | 0.000000
09-04-2025 18:43:35000 | -1259910 | 125.991 | 94908252 | 234069.83 | 311670929 | 99717476 | 49988228 | 0.000000 | 22118931 | 28555914 | 0.000000
09-04-2025 18:43:40000 | -1262353 | 126.2353 | 95579209 | 233968.11 | 312416046 | 99714584 | 50034912 | 0.000000 | 22252324 | 28730959 | 0.000000
09-04-2025 18:43:45000 | -1266404 | 126.6404 | 94972930 | 233915.98 | 313469452 | 99719971 | 50024414 | 0.000000 | 22382949 | 28906455 | 0.000000
09-04-2025 18:43:50000 | -1263545 | 126.3545 | 91537861 | 233898.73 | 312728851 | 99738609 | 50002335 | 0.000000 | 22512209 | 29082154 | 0.000000
09-04-2025 18:43:55000 | -1261854 | 126.1854 | 90738330 | 233883.39 | 312330353 | 99742455 | 49994667 | 0.000000 | 22639031 | 29257773 | 0.000000
09-04-2025 18:44:00000 | -1265048 | 126.5048 | 89982275 | 233835.81 | 313157745 | 99747986 | 49994797 | 0.000000 | 22764421 | 29433213 | 0.000000
09-04-2025 18:44:05000 | -1264367 | 126.4367 | 87475635 | 233778.75 | 313021942 | 99761528 | 49960106 | 0.000000 | 22887747 | 29608955 | 0.000000
09-04-2025 18:44:10000 | -1263061 | 126.3061 | 87878408 | 233838.02 | 312631470 | 99758835 | 49945202 | 0.000000 | 23008599 | 29784227 | 0.000000
09-04-2025 18:44:15000 | -1261089 | 126.1089 | 90995547 | 233982.78 | 312004944 | 99740685 | 49973789 | 0.000000 | 23132051 | 29959156 | 0.000000
09-04-2025 18:44:20000 | -1260593 | 126.0593 | 92677959 | 233928.80 | 311988190 | 99730835 | 50000996 | 0.000000 | 23260669 | 30134344 | 0.000000
09-04-2025 18:44:25000 | -1261093 | 126.1093 | 93991572 | 234005.98 | 312023315 | 99723404 | 50019863 | 0.000000 | 23388997 | 30309469 | 0.000000
09-04-2025 18:44:30000 | -1263322 | 126.3322 | 95165693 | 234005.05 | 312593292 | 99717476 | 50047649 | 0.000000 | 23520669 | 30484811 | 0.000000
09-04-2025 18:44:35000 | -1264650 | 126.465 | 92583945 | 233898.94 | 313015594 | 99733093 | 50015877 | 0.000000 | 23651255 | 30660906 | 0.000000
09-04-2025 18:44:40000 | -1263193 | 126.3193 | 88739424 | 233794.84 | 312729645 | 99754158 | 49987915 | 0.000000 | 23776409 | 30836578 | 0.000000
09-04-2025 18:44:45000 | -1257251 | 125.7251 | 89572578 | 233929.98 | 311102997 | 99747169 | 49988586 | 0.000000 | 23899365 | 31011924 | 0.000000
09-04-2025 18:44:50000 | -1265828 | 126.5828 | 91333506 | 233837.70 | 313365356 | 99740707 | 50004112 | 0.000000 | 24026240 | 31187236 | 0.000000
09-04-2025 18:44:55000 | -1262865 | 126.2865 | 92211602 | 233952.05 | 312498901 | 99734482 | 50003231 | 0.000000 | 24153396 | 31362588 | 0.000000
09-04-2025 18:45:00000 | -1262969 | 126.2969 | 92947197 | 233926.50 | 312573608 | 99730293 | 50006184 | 0.000000 | 24283228 | 31538025 | 0.000000
09-04-2025 18:45:05000 | -1263196 | 126.3196 | 92335313 | 233894.11 | 312659882 | 99733910 | 49996223 | 0.000000 | 12867197 | 175470963 | 0.000000
09-04-2025 18:45:10000 | -1263854 | 126.3854 | 92836025 | 233900.48 | 312822510 | 99731308 | 50002544 | 0.000000 | 25782022 | 350761780 | 0.000000
09-04-2025 18:45:15000 | -1267207 | 126.7207 | 93608945 | 233889.09 | 313676971 | 99728271 | 49997612 | 0.000000 | 38879852 | 526402039 | 0.000000
09-04-2025 18:45:20000 | -1265219 | 126.5219 | 93684707 | 233925.78 | 313138458 | 99726982 | 49982319 | 0.000000 | 51686775 | 701851501 | 0.000000
09-04-2025 18:45:25000 | -1261929 | 126.1929 | 91339600 | 233896.63 | 312329895 | 99739075 | 49974068 | 0.000000 | 64568306 | 877346985 | 0.000000
09-04-2025 18:45:30000 | -1261285 | 126.1285 | 91390254 | 233887.69 | 312180756 | 99738518 | 49982010 | 0.000000 | 77293945 | 10526609 | 0.000000
09-04-2025 18:45:35000 | -1262726 | 126.2726 | 92247002 | 233916.22 | 312512115 | 99734222 | 49983231 | 0.000000 | 90057724 | 12279794 | 0.000000
09-04-2025 18:45:40000 | -1260258 | 126.0258 | 90074541 | 233887.89 | 311904327 | 99745552 | 49992146 | 0.000000 | 102664017 | 14030659 | 0.000000
09-04-2025 18:45:45000 | -1258623 | 125.8623 | 91478369 | 233931.56 | 311468170 | 99736916 | 50008892 | 0.000000 | 115285103 | 15780356 | 0.000000
09-04-2025 18:45:50000 | -1262328 | 126.2328 | 90704238 | 233864.28 | 312457977 | 99742844 | 50016727 | 0.000000 | 128043259 | 17532699 | 0.000000
09-04-2025 18:45:55000 | -1267577 | 126.7577 | 87731582 | 233697.14 | 313930084 | 99761345 | 49981163 | 0.000000 | 140435150 | 19288590 | 0.000000
09-04-2025 18:46:00000 | -1258239 | 125.8239 | 85707930 | 233803.47 | 311444702 | 99768806 | 49947346 | 0.000000 | 152316742 | 21039285 | 0.000000
09-04-2025 18:46:05000 | -1254683 | 125.4683 | 84513682 | 233801.98 | 310550079 | 99773911 | 49944572 | 0.000000 | 164102249 | 22785928 | 0.000000
09-04-2025 18:46:10000 | -1256770 | 125.677 | 89258379 | 233903.77 | 311012146 | 99748741 | 49974209 | 0.000000 | 176164551 | 24527998 | 0.000000
09-04-2025 18:46:15000 | -1255536 | 125.5536 | 88694863 | 233911.53 | 310687164 | 99751411 | 49987514 | 0.000000 | 188504745 | 26275107 | 0.000000
09-04-2025 18:46:20000 | -1256858 | 125.6858 | 93794980 | 234002.19 | 310986450 | 99722702 | 50029713 | 0.000000 | 201288177 | 28018125 | 0.000000
09-04-2025 18:46:25000 | -1258992 | 125.8992 | 93693896 | 233951.27 | 311572723 | 99724228 | 50042854 | 0.000000 | 214313873 | 29766060 | 0.000000
09-04-2025 18:46:30000 | -1262424 | 126.2424 | 95071504 | 233976.98 | 312410065 | 99717628 | 50041195 | 0.000000 | 227489563 | 31517466 | 0.000000
09-04-2025 18:46:35000 | -1262530 | 126.253 | 93948584 | 233929.36 | 312477539 | 99724281 | 50050568 | 0.000000 | 240625854 | 33268865 | 0.000000
09-04-2025 18:46:40000 | -1263657 | 126.3657 | 94374092 | 233941.70 | 312749939 | 99722282 | 50038803 | 0.000000 | 253688171 | 35021855 | 0.000000
09-04-2025 18:46:45000 | -1260828 | 126.0828 | 93690625 | 233993.56 | 311971680 | 99725052 | 50029461 | 0.000000 | 266704559 | 36773000 | 0.000000
09-04-2025 18:46:50000 | -1262149 | 126.2149 | 95145322 | 233995.13 | 312317261 | 99717072 | 50026825 | 0.000000 | 279864777 | 38524060 | 0.000000
09-04-2025 18:46:55000 | -1261978 | 126.1978 | 91399590 | 233876.84 | 312367615 | 99738754 | 49999737 | 0.000000 | 292675537 | 40276523 | 0.000000
09-04-2025 18:47:00000 | -1256822 | 125.6822 | 87804395 | 233849.86 | 311068878 | 99756851 | 49957394 | 0.000000 | 305100830 | 42027739 | 0.000000
09-04-2025 18:47:05000 | -1252580 | 125.258 | 89455186 | 233960.97 | 309905212 | 99745956 | 49964645 | 0.000000 | 317382233 | 43770190 | 0.000000
09-04-2025 18:47:10000 | -1258659 | 125.8659 | 92237676 | 233884.20 | 311560944 | 99732559 | 49979111 | 0.000000 | 330115295 | 45512695 | 0.000000
09-04-2025 18:47:15000 | -1256933 | 125.6933 | 92197764 | 233943.84 | 311052826 | 99732063 | 49987926 | 0.000000 | 342922180 | 47257485 | 0.000000
09-04-2025 18:47:20000 | -1255255 | 125.5255 | 91719873 | 233912.31 | 310670258 | 99734116 | 49988689 | 0.000000 | 355582428 | 49000454 | 0.000000
09-04-2025 18:47:25000 | -1251670 | 125.167 | 89456660 | 233910.94 | 309748566 | 99745575 | 49986221 | 0.000000 | 368096405 | 50740469 | 0.000000
09-04-2025 18:47:30000 | -1254180 | 125.418 | 91692900 | 233952.48 | 310350677 | 99733818 | 50000515 | 0.000000 | 380686310 | 52481279 | 0.000000
09-04-2025 18:47:35000 | -1253967 | 125.3967 | 90838311 | 233931.38 | 310310486 | 99738647 | 50018219 | 0.000000 | 393370697 | 54222524 | 0.000000
09-04-2025 18:47:40000 | -1254187 | 125.4187 | 91938652 | 233905.25 | 310420685 | 99732391 | 50028477 | 0.000000 | 406148651 | 55964639 | 0.000000
09-04-2025 18:47:45000 | -1258694 | 125.8694 | 89445410 | 233782.31 | 311647766 | 99748459 | 49990803 | 0.000000 | 418587006 | 57710093 | 0.000000
09-04-2025 18:47:50000 | -1250130 | 125.013 | 85746611 | 233807.61 | 309442627 | 99765594 | 49957714 | 0.000000 | 430631775 | 59451978 | 0.000000
09-04-2025 18:47:55000 | -1246199 | 124.6199 | 88208281 | 233963.56 | 308309082 | 99750435 | 49977001 | 0.000000 | 442668488 | 61186182 | 0.000000
09-04-2025 18:48:00000 | -1251586 | 125.1586 | 88267637 | 233859.17 | 309779358 | 99752235 | 49976444 | 0.000000 | 454835022 | 62922319 | 0.000000
09-04-2025 18:48:05000 | -1247774 | 124.7774 | 91466377 | 233999.28 | 308713867 | 99732407 | 50001057 | 0.000000 | 467401642 | 64657935 | 0.000000
09-04-2025 18:48:10000 | -1252600 | 125.26 | 93661982 | 233994.77 | 309941711 | 99721611 | 50011570 | 0.000000 | 480223328 | 66395254 | 0.000000
09-04-2025 18:48:15000 | -1251721 | 125.1721 | 93019199 | 233993.31 | 309719116 | 99725014 | 50029881 | 0.000000 | 493209351 | 68132334 | 0.000000
09-04-2025 18:48:20000 | -1252018 | 125.2018 | 89259541 | 233860.16 | 309908142 | 99746834 | 50027290 | 0.000000 | 505756226 | 69870205 | 0.000000
09-04-2025 18:48:25000 | -1250586 | 125.0586 | 92373467 | 234027.61 | 309380371 | 99728317 | 50053780 | 0.000000 | 518277283 | 71606226 | 0.000000
09-04-2025 18:48:30000 | -1249877 | 124.9877 | 92185332 | 234010.88 | 309223846 | 99729111 | 50079533 | 0.000000 | 531086426 | 73343110 | 0.000000
09-04-2025 18:48:35000 | -1257131 | 125.7131 | 95569199 | 234005.30 | 311083008 | 99712280 | 50085041 | 0.000000 | 544171509 | 75085581 | 0.000000
09-04-2025 18:48:40000 | -1256555 | 125.6555 | 93737002 | 233899.09 | 311044373 | 99722908 | 50072773 | 0.000000 | 557444092 | 76828950 | 0.000000
09-04-2025 18:48:45000 | -1254283 | 125.4283 | 91907637 | 233961.63 | 310368164 | 99732613 | 50040371 | 0.000000 | 570307373 | 78574429 | 0.000000
09-04-2025 18:48:50000 | -1253317 | 125.3317 | 93795000 | 234016.41 | 310091705 | 99721138 | 50031818 | 0.000000 | 583139038 | 80313237 | 0.000000
09-04-2025 18:48:55000 | -1251203 | 125.1203 | 92833223 | 233971.31 | 309613373 | 99725883 | 50037315 | 0.000000 | 596146729 | 82051475 | 0.000000
09-04-2025 18:49:00000 | -1251301 | 125.1301 | 91522188 | 233929.39 | 309669006 | 99733582 | 50034893 | 0.000000 | 608941101 | 83790088 | 0.000000
09-04-2025 18:49:05000 | -1252767 | 125.2767 | 90505156 | 233901.77 | 310050354 | 99740059 | 50023960 | 0.000000 | 621517273 | 85528486 | 0.000000
09-04-2025 18:49:10000 | -1252592 | 125.2592 | 88309805 | 233849.28 | 310037201 | 99752396 | 50004623 | 0.000000 | 633932190 | 87268164 | 0.000000
09-04-2025 18:49:15000 | -1249709 | 124.9709 | 87164248 | 233875.47 | 309272186 | 99757645 | 49988461 | 0.000000 | 646063171 | 89005820 | 0.000000
09-04-2025 18:49:20000 | -1249382 | 124.9382 | 92165488 | 234028.69 | 309077454 | 99729012 | 50025085 | 0.000000 | 658438843 | 90737451 | 0.000000
09-04-2025 18:49:25000 | -1253254 | 125.3254 | 92461201 | 233896.25 | 310211884 | 99728958 | 50046177 | 0.000000 | 671365662 | 92474160 | 0.000000
09-04-2025 18:49:30000 | -1254742 | 125.4742 | 88597500 | 233816.45 | 310617035 | 99751640 | 50000481 | 0.000000 | 683805359 | 94217109 | 0.000000
09-04-2025 18:49:35000 | -1247911 | 124.7911 | 89308037 | 233968.09 | 308743988 | 99744896 | 49992878 | 0.000000 | 696042419 | 95953975 | 0.000000
09-04-2025 18:49:40000 | -1249536 | 124.9536 | 91987334 | 234008.53 | 309139771 | 99730125 | 50029751 | 0.000000 | 708619080 | 97688613 | 0.000000
09-04-2025 18:49:45000 | -1254618 | 125.4618 | 93464443 | 233964.89 | 310477692 | 99723663 | 50047855 | 0.000000 | 721591858 | 99429600 | 0.000000
09-04-2025 18:49:50000 | -1254091 | 125.4091 | 93922744 | 233977.00 | 310337341 | 99720726 | 50047527 | 0.000000 | 734536621 | 10117211 | 0.000000
09-04-2025 18:49:55000 | -1256660 | 125.666 | 92506504 | 233888.77 | 311061493 | 99730156 | 50031445 | 0.000000 | 747518250 | 10291580 | 0.000000
09-04-2025 18:50:00000 | -1253359 | 125.3359 | 92428477 | 233974.36 | 310132813 | 99729187 | 50015213 | 0.000000 | 760329712 | 10465791 | 0.000000
09-04-2025 18:50:05000 | -1252426 | 125.2426 | 91440625 | 233940.98 | 309932648 | 99734535 | 50009315 | 0.000000 | 773157349 | 10639938 | 0.000000
09-04-2025 18:50:10000 | -1251923 | 125.1923 | 92336787 | 233958.95 | 309798401 | 99729111 | 50013729 | 0.000000 | 785920044 | 10813827 | 0.000000
09-04-2025 18:50:15000 | -1253428 | 125.3428 | 93499707 | 233987.31 | 310151367 | 99722931 | 50026592 | 0.000000 | 798684387 | 10987688 | 0.000000
09-04-2025 18:50:20000 | -1252507 | 125.2507 | 90829287 | 233870.33 | 310032837 | 99738091 | 50024372 | 0.000000 | 811512207 | 11161714 | 0.000000
09-04-2025 18:50:25000 | -1253754 | 125.3754 | 89465547 | 233868.72 | 310320709 | 99746368 | 49988213 | 0.000000 | 823937866 | 11335831 | 0.000000
09-04-2025 18:50:30000 | -1248842 | 124.8842 | 85083994 | 233811.25 | 309110138 | 99768715 | 49954727 | 0.000000 | 835925293 | 11509524 | 0.000000
09-04-2025 18:50:35000 | -1244989 | 124.4989 | 86830498 | 233959.69 | 307993561 | 99757675 | 49970207 | 0.000000 | 847826965 | 11682632 | 0.000000
09-04-2025 18:50:40000 | -1245389 | 124.5389 | 92010117 | 234043.94 | 308072723 | 99728195 | 50010395 | 0.000000 | 860417236 | 11855546 | 0.000000
09-04-2025 18:50:45000 | -1252691 | 125.2691 | 97131055 | 234034.97 | 309975311 | 99700745 | 50062241 | 0.000000 | 873690552 | 12028886 | 0.000000
09-04-2025 18:50:50000 | -1254927 | 125.4927 | 94091025 | 233910.20 | 310634827 | 99720100 | 50064579 | 0.000000 | 886920471 | 12203056 | 0.000000
09-04-2025 18:50:55000 | -1250452 | 125.0452 | 91273135 | 233919.78 | 309472717 | 99734665 | 50039146 | 0.000000 | 899758667 | 12377050 | 0.000000
09-04-2025 18:51:00000 | -1253246 | 125.3246 | 90650830 | 233914.91 | 310154907 | 99739418 | 50027401 | 0.000000 | 912276001 | 12550985 | 0.000000
09-04-2025 18:51:05000 | -1253005 | 125.3005 | 87957803 | 233834.13 | 310152985 | 99754524 | 50004238 | 0.000000 | 924662781 | 12724876 | 0.000000
09-04-2025 18:51:10000 | -1249090 | 124.909 | 87302559 | 233874.83 | 309123657 | 99756638 | 49968491 | 0.000000 | 936699036 | 12898810 | 0.000000
09-04-2025 18:51:15000 | -1248320 | 124.832 | 89279355 | 233948.75 | 308870300 | 99745224 | 49985264 | 0.000000 | 948795959 | 13072062 | 0.000000
09-04-2025 18:51:20000 | -1247315 | 124.7315 | 88925059 | 233903.06 | 308676941 | 99746826 | 49992867 | 0.000000 | 961179504 | 13245394 | 0.000000
09-04-2025 18:51:25000 | -1249884 | 124.9884 | 89981084 | 233884.20 | 309354767 | 99741867 | 49978016 | 0.000000 | 973659546 | 13419065 | 0.000000
09-04-2025 18:51:30000 | -1247074 | 124.7074 | 88285430 | 233871.27 | 308648804 | 99750351 | 49965481 | 0.000000 | 985983398 | 13592414 | 0.000000
09-04-2025 18:51:35000 | -1249429 | 124.9429 | 85677373 | 233769.80 | 309318481 | 99765709 | 49939396 | 0.000000 | 997979126 | 13765609 | 0.000000
09-04-2025 18:51:40000 | -1244959 | 124.4959 | 85107725 | 233858.59 | 308089569 | 99767151 | 49939537 | 0.000000 | 10097897 | 13938794 | 0.000000
09-04-2025 18:51:45000 | -1243090 | 124.309 | 87613584 | 233924.28 | 307586548 | 99752548 | 49993576 | 0.000000 | 10218468 | 14111347 | 0.000000
09-04-2025 18:51:50000 | -1244388 | 124.4388 | 90420771 | 233966.89 | 307898865 | 99737045 | 50023155 | 0.000000 | 10342982 | 14284353 | 0.000000
09-04-2025 18:51:55000 | -1249678 | 124.9678 | 94226816 | 234023.73 | 309195679 | 99716942 | 50063782 | 0.000000 | 10470841 | 14457449 | 0.000000
09-04-2025 18:52:00000 | -1249062 | 124.9062 | 95369678 | 234036.72 | 309046906 | 99709778 | 50080379 | 0.000000 | 10602407 | 14630891 | 0.000000
09-04-2025 18:52:05000 | -1252521 | 125.2521 | 92071475 | 233877.31 | 310051422 | 99730911 | 50034630 | 0.000000 | 10733010 | 14805205 | 0.000000
09-04-2025 18:52:10000 | -1251415 | 125.1415 | 92132432 | 233950.39 | 309681152 | 99730080 | 50011433 | 0.000000 | 10860280 | 14978862 | 0.000000
09-04-2025 18:52:15000 | -1250332 | 125.0332 | 92075449 | 233986.95 | 309370056 | 99729950 | 50001762 | 0.000000 | 10986953 | 15152262 | 0.000000
09-04-2025 18:52:20000 | -1246077 | 124.6077 | 92067031 | 234054.02 | 308229309 | 99728157 | 49997570 | 0.000000 | 11114661 | 15325734 | 0.000000
09-04-2025 18:52:25000 | -1247554 | 124.7554 | 93598408 | 234002.09 | 308689911 | 99719742 | 50005444 | 0.000000 | 11244220 | 15499129 | 0.000000
09-04-2025 18:52:30000 | -1249322 | 124.9322 | 92531211 | 233970.47 | 309149170 | 99726837 | 50005119 | 0.000000 | 11374231 | 15672770 | 0.000000
09-04-2025 18:52:35000 | -1249189 | 124.9189 | 92188408 | 233963.92 | 309117462 | 99728798 | 50001495 | 0.000000 | 11502104 | 15846217 | 0.000000
09-04-2025 18:52:40000 | -1247672 | 124.7672 | 90227832 | 233934.83 | 308745941 | 99739532 | 49997852 | 0.000000 | 11628239 | 16019447 | 0.000000
09-04-2025 18:52:45000 | -1249488 | 124.9488 | 89076826 | 233856.75 | 309277283 | 99746849 | 49974945 | 0.000000 | 11753513 | 16193221 | 0.000000
09-04-2025 18:52:50000 | -1245224 | 124.5224 | 89124805 | 233963.89 | 308085754 | 99744843 | 49970623 | 0.000000 | 11876951 | 16366516 | 0.000000
09-04-2025 18:52:55000 | -1244862 | 124.4862 | 92349414 | 234076.30 | 307906860 | 99725967 | 50011879 | 0.000000 | 12003105 | 16539375 | 0.000000
09-04-2025 18:53:00000 | -1252830 | 125.283 | 91392354 | 233902.02 | 310080444 | 99734978 | 50015053 | 0.000000 | 12130995 | 16713162 | 0.000000
09-04-2025 18:53:05000 | -1250922 | 125.0922 | 91037930 | 233954.72 | 309534332 | 99736221 | 50003387 | 0.000000 | 12257417 | 16887020 | 0.000000
09-04-2025 18:53:10000 | -1249013 | 124.9013 | 91992451 | 233986.95 | 309039337 | 99729866 | 50006451 | 0.000000 | 12384670 | 17060680 | 0.000000
09-04-2025 18:53:15000 | -1252723 | 125.2723 | 10646240 | 234325.16 | 309786682 | 99640823 | 50018669 | 0.000000 | 12525985 | 17234379 | 0.000000
09-04-2025 18:53:20000 | -1246884 | 124.6884 | 10368391 | 234281.16 | 308351837 | 99656052 | 49995430 | 0.000000 | 12671616 | 17408037 | 0.000000
09-04-2025 18:53:25000 | -1248732 | 124.8732 | 10761411 | 234398.63 | 308735046 | 99630714 | 50009796 | 0.000000 | 12819136 | 17581549 | 0.000000
09-04-2025 18:53:30000 | -1246696 | 124.6696 | 10974448 | 234450.50 | 308211060 | 99614792 | 50061268 | 0.000000 | 12970585 | 17754813 | 0.000000
09-04-2025 18:53:35000 | -1257272 | 125.7272 | 10999341 | 234301.14 | 311009460 | 99619492 | 50074821 | 0.000000 | 13123276 | 17928773 | 0.000000
09-04-2025 18:53:40000 | -1255652 | 125.5652 | 10951198 | 234362.06 | 310519775 | 99621834 | 50033901 | 0.000000 | 13275665 | 18103189 | 0.000000
09-04-2025 18:53:45000 | -1253941 | 125.3941 | 10648896 | 234266.50 | 310162048 | 99641342 | 49998604 | 0.000000 | 13426392 | 18277504 | 0.000000
09-04-2025 18:53:50000 | -1252467 | 125.2467 | 10717955 | 234385.41 | 309656799 | 99635849 | 49981636 | 0.000000 | 13573293 | 18451543 | 0.000000
09-04-2025 18:53:55000 | -1252806 | 125.2806 | 10949646 | 234406.48 | 309762573 | 99620232 | 49999023 | 0.000000 | 13724817 | 18625354 | 0.000000
09-04-2025 18:54:00000 | -1252166 | 125.2166 | 10822419 | 234357.38 | 309642883 | 99628578 | 49992554 | 0.000000 | 13875880 | 18799391 | 0.000000
09-04-2025 18:54:05000 | -1253623 | 125.3623 | 11122217 | 234453.23 | 309938507 | 99608742 | 50004604 | 0.000000 | 14027994 | 18973143 | 0.000000
09-04-2025 18:54:10000 | -1254141 | 125.4141 | 11136004 | 234438.44 | 310088379 | 99608101 | 50020531 | 0.000000 | 14182521 | 19147039 | 0.000000
09-04-2025 18:54:15000 | -1254592 | 125.4592 | 10710845 | 234261.55 | 310343506 | 99637550 | 50000683 | 0.000000 | 14334073 | 19321459 | 0.000000
09-04-2025 18:54:20000 | -1250329 | 125.0329 | 10628034 | 234342.86 | 309169586 | 99640678 | 49987801 | 0.000000 | 14481693 | 19495219 | 0.000000
09-04-2025 18:54:25000 | -1249841 | 124.9841 | 10663366 | 234376.33 | 309013855 | 99638016 | 49979504 | 0.000000 | 14630466 | 19669141 | 0.000000
09-04-2025 18:54:30000 | -1255374 | 125.5374 | 10964341 | 234368.20 | 310446625 | 99620758 | 50005829 | 0.000000 | 14781100 | 19843131 | 0.000000
09-04-2025 18:54:35000 | -1253428 | 125.3428 | 11343906 | 234517.97 | 309854156 | 99592957 | 50052197 | 0.000000 | 14936544 | 20016932 | 0.000000
09-04-2025 18:54:40000 | -1256567 | 125.6567 | 11080565 | 234330.08 | 310815735 | 99613457 | 50046730 | 0.000000 | 15092042 | 20191373 | 0.000000
09-04-2025 18:54:45000 | -1258570 | 125.857 | 10802189 | 234275.59 | 311321594 | 99633690 | 49994404 | 0.000000 | 15244362 | 20366191 | 0.000000
09-04-2025 18:54:50000 | -1247924 | 124.7924 | 10374164 | 234335.61 | 308536133 | 99656242 | 49960796 | 0.000000 | 15390328 | 20540166 | 0.000000
09-04-2025 18:54:55000 | -1246949 | 124.6949 | 11282495 | 234604.78 | 308138702 | 99593155 | 49990303 | 0.000000 | 15541553 | 20713758 | 0.000000
09-04-2025 18:55:00000 | -1252346 | 125.2346 | 11657282 | 234590.72 | 309567017 | 99569565 | 50023853 | 0.000000 | 15701917 | 20887527 | 0.000000
09-04-2025 18:55:05000 | -1253839 | 125.3839 | 12134792 | 234687.39 | 309910736 | 99534935 | 50045235 | 0.000000 | 15866465 | 21061406 | 0.000000
09-04-2025 18:55:10000 | -1255157 | 125.5157 | 11977956 | 234613.88 | 310296570 | 99547745 | 50051750 | 0.000000 | 16034540 | 21235695 | 0.000000
09-04-2025 18:55:15000 | -1257617 | 125.7617 | 11751572 | 234547.52 | 310935791 | 99566254 | 50038750 | 0.000000 | 16199343 | 21410354 | 0.000000
09-04-2025 18:55:20000 | -1254597 | 125.4597 | 11543403 | 234534.38 | 310164093 | 99579384 | 50031590 | 0.000000 | 16359645 | 21584533 | 0.000000
09-04-2025 18:55:25000 | -1252240 | 125.224 | 11640778 | 234584.72 | 309539551 | 99570702 | 50055031 | 0.000000 | 16521444 | 21758496 | 0.000000
09-04-2025 18:55:30000 | -1259164 | 125.9164 | 11503324 | 234448.53 | 311388000 | 99585289 | 50055019 | 0.000000 | 16681299 | 21932721 | 0.000000
09-04-2025 18:55:35000 | -1254339 | 125.4339 | 11515477 | 234541.11 | 310085999 | 99581238 | 50045254 | 0.000000 | 16841794 | 22107123 | 0.000000
09-04-2025 18:55:40000 | -1261122 | 126.1122 | 11443728 | 234415.08 | 311900085 | 99590813 | 50020390 | 0.000000 | 17001813 | 22281947 | 0.000000
09-04-2025 18:55:45000 | -1255497 | 125.5497 | 11271306 | 234450.67 | 310433075 | 99599434 | 49980888 | 0.000000 | 17159258 | 22456531 | 0.000000
09-04-2025 18:55:50000 | -1250928 | 125.0928 | 11277351 | 234516.73 | 309226868 | 99596092 | 49989166 | 0.000000 | 17315710 | 22630572 | 0.000000
09-04-2025 18:55:55000 | -1254011 | 125.4011 | 11293451 | 234471.23 | 310049072 | 99596924 | 50001041 | 0.000000 | 17471315 | 22804734 | 0.000000
09-04-2025 18:56:00000 | -1251283 | 125.1283 | 11259515 | 234512.42 | 309316681 | 99597588 | 50011036 | 0.000000 | 17628573 | 22978900 | 0.000000
09-04-2025 18:56:05000 | -1259116 | 125.9116 | 11230522 | 234409.59 | 311366455 | 99604584 | 50007206 | 0.000000 | 17785952 | 23153572 | 0.000000
09-04-2025 18:56:10000 | -1253435 | 125.3435 | 11032214 | 234450.73 | 309875793 | 99614899 | 49998486 | 0.000000 | 17939606 | 23328037 | 0.000000
09-04-2025 18:56:15000 | -1254483 | 125.4483 | 11432100 | 234550.36 | 310088074 | 99587334 | 50022518 | 0.000000 | 18096641 | 23502258 | 0.000000
09-04-2025 18:56:20000 | -1258737 | 125.8737 | 11515208 | 234498.64 | 311219025 | 99584160 | 50046459 | 0.000000 | 18255839 | 23676727 | 0.000000
09-04-2025 18:56:25000 | -1256434 | 125.6434 | 11345170 | 234506.38 | 310605133 | 99594803 | 50043510 | 0.000000 | 18413969 | 23851344 | 0.000000
09-04-2025 18:56:30000 | -1258285 | 125.8285 | 11760832 | 234585.28 | 311050232 | 99566032 | 50057266 | 0.000000 | 18575966 | 24026111 | 0.000000
09-04-2025 18:56:35000 | -1257680 | 125.768 | 11768595 | 234562.97 | 310930878 | 99565048 | 50067471 | 0.000000 | 18739302 | 24200850 | 0.000000
09-04-2025 18:56:40000 | -1260231 | 126.0231 | 11721188 | 234528.92 | 311590637 | 99570259 | 50062126 | 0.000000 | 18902679 | 24375824 | 0.000000
09-04-2025 18:56:45000 | -1257506 | 125.7506 | 11657357 | 234597.66 | 310818939 | 99573067 | 50041992 | 0.000000 | 19064694 | 24550654 | 0.000000
09-04-2025 18:56:50000 | -1257037 | 125.7037 | 12249959 | 234746.33 | 310643768 | 99528519 | 50072132 | 0.000000 | 19231644 | 24725045 | 0.000000
09-04-2025 18:56:55000 | -1264219 | 126.4219 | 12178795 | 234536.88 | 312665833 | 99539185 | 50074780 | 0.000000 | 19402603 | 24900260 | 0.000000
09-04-2025 18:57:00000 | -1263209 | 126.3209 | 12015043 | 234600.20 | 312293457 | 99550705 | 50053284 | 0.000000 | 19569368 | 25075582 | 0.000000
09-04-2025 18:57:05000 | -1259224 | 125.9224 | 11658684 | 234538.13 | 311318298 | 99574127 | 50026272 | 0.000000 | 19732733 | 25250721 | 0.000000
09-04-2025 18:57:10000 | -1260359 | 126.0359 | 11611667 | 234487.53 | 311653748 | 99578285 | 50006516 | 0.000000 | 19893635 | 25425613 | 0.000000
09-04-2025 18:57:15000 | -1259520 | 125.952 | 11451357 | 234471.66 | 311433746 | 99589233 | 49995171 | 0.000000 | 20053258 | 25600502 | 0.000000
09-04-2025 18:57:20000 | -1259400 | 125.94 | 11605961 | 234503.92 | 311395355 | 99578064 | 49993298 | 0.000000 | 20212034 | 25775148 | 0.000000
09-04-2025 18:57:25000 | -1256638 | 125.6638 | 11578714 | 234552.81 | 310646851 | 99578194 | 50013287 | 0.000000 | 20372014 | 25949484 | 0.000000
09-04-2025 18:57:30000 | -1260058 | 126.0058 | 11514643 | 234472.97 | 311576202 | 99585068 | 50007057 | 0.000000 | 20532136 | 26124492 | 0.000000
09-04-2025 18:57:35000 | -1257616 | 125.7616 | 11589299 | 234577.97 | 310854279 | 99578079 | 50024273 | 0.000000 | 20692280 | 26299184 | 0.000000
09-04-2025 18:57:40000 | -1257634 | 125.7634 | 11591706 | 234564.05 | 310878540 | 99577919 | 50059158 | 0.000000 | 20853489 | 26473871 | 0.000000
09-04-2025 18:57:45000 | -1259076 | 125.9076 | 11691571 | 234561.13 | 311258942 | 99571632 | 50068741 | 0.000000 | 21014893 | 26648598 | 0.000000
09-04-2025 18:57:50000 | -1262151 | 126.2151 | 11558071 | 234438.27 | 312146484 | 99583328 | 50045219 | 0.000000 | 21176907 | 26823697 | 0.000000
09-04-2025 18:57:55000 | -1260889 | 126.0889 | 11435470 | 234465.16 | 311772552 | 99591255 | 50007946 | 0.000000 | 21336663 | 26998967 | 0.000000
09-04-2025 18:58:00000 | -1258775 | 125.8775 | 11370734 | 234509.67 | 311182098 | 99594490 | 50012661 | 0.000000 | 21494111 | 27173682 | 0.000000
09-04-2025 18:58:05000 | -1256203 | 125.6203 | 11529318 | 234576.80 | 310497681 | 99581474 | 50032837 | 0.000000 | 21653210 | 27348334 | 0.000000
09-04-2025 18:58:10000 | -1261244 | 126.1244 | 11667049 | 234514.28 | 311846710 | 99574875 | 50051731 | 0.000000 | 21814607 | 27523111 | 0.000000
09-04-2025 18:58:15000 | -1260282 | 126.0282 | 11481189 | 234469.84 | 311627777 | 99587601 | 50035057 | 0.000000 | 21974873 | 27698301 | 0.000000
09-04-2025 18:58:20000 | -1256751 | 125.6751 | 11600744 | 234569.28 | 310664154 | 99576668 | 50043476 | 0.000000 | 22136375 | 27873250 | 0.000000
09-04-2025 18:58:25000 | -1262388 | 126.2388 | 11408816 | 234441.64 | 312168396 | 99594101 | 50020550 | 0.000000 | 22297156 | 28048510 | 0.000000
09-04-2025 18:58:30000 | -1258202 | 125.8202 | 10860806 | 234364.09 | 311124146 | 99629509 | 49969730 | 0.000000 | 22451633 | 28223887 | 0.000000
09-04-2025 18:58:35000 | -1258327 | 125.8327 | 11155035 | 234456.95 | 311095398 | 99609360 | 49982769 | 0.000000 | 22605110 | 28398549 | 0.000000
09-04-2025 18:58:40000 | -1259878 | 125.9878 | 11393137 | 234469.00 | 311511078 | 99593605 | 50003426 | 0.000000 | 22761797 | 28573256 | 0.000000
09-04-2025 18:58:45000 | -1258304 | 125.8304 | 11393313 | 234493.66 | 311091919 | 99592583 | 50013096 | 0.000000 | 22920315 | 28748178 | 0.000000
09-04-2025 18:58:50000 | -1259063 | 125.9063 | 11583001 | 234556.09 | 311236908 | 99579498 | 50026295 | 0.000000 | 23080266 | 28923271 | 0.000000
09-04-2025 18:58:55000 | -1265123 | 126.5123 | 11467743 | 234404.78 | 312899811 | 99591682 | 50030758 | 0.000000 | 23241333 | 29098639 | 0.000000
09-04-2025 18:59:00000 | -1258469 | 125.8469 | 11103637 | 234434.73 | 311153015 | 99613022 | 50016991 | 0.000000 | 23396538 | 29273824 | 0.000000
09-04-2025 18:59:05000 | -1259647 | 125.9647 | 11632159 | 234558.56 | 311389160 | 99576332 | 50065147 | 0.000000 | 23554700 | 29448492 | 0.000000
09-04-2025 18:59:10000 | -1263891 | 126.3891 | 11614629 | 234441.73 | 312579742 | 99580414 | 50073605 | 0.000000 | 23717356 | 29623910 | 0.000000
09-04-2025 18:59:15000 | -1262869 | 126.2869 | 11596476 | 234537.75 | 312197998 | 99581039 | 50055111 | 0.000000 | 23877480 | 29799508 | 0.000000
09-04-2025 18:59:20000 | -1262361 | 126.2361 | 11357086 | 234436.78 | 312154602 | 99597740 | 50043953 | 0.000000 | 24038198 | 29975029 | 0.000000
09-04-2025 18:59:25000 | -1260930 | 126.093 | 11475837 | 234520.80 | 311720306 | 99588409 | 50040966 | 0.000000 | 24197395 | 30150572 | 0.000000
09-04-2025 18:59:30000 | -1260579 | 126.0579 | 11739421 | 234596.59 | 311590363 | 99569168 | 50059986 | 0.000000 | 24358821 | 30325727 | 0.000000
09-04-2025 18:59:35000 | -1266591 | 126.6591 | 11491672 | 234409.00 | 313259735 | 99590935 | 50040512 | 0.000000 | 24520632 | 30501455 | 0.000000
09-04-2025 18:59:40000 | -1262236 | 126.2236 | 11410873 | 234491.45 | 312064148 | 99593864 | 50012630 | 0.000000 | 24677700 | 30676941 | 0.000000
09-04-2025 18:59:45000 | -1259319 | 125.9319 | 11600495 | 234581.56 | 311271790 | 99578400 | 50024250 | 0.000000 | 24837822 | 30851898 | 0.000000
09-04-2025 18:59:50000 | -1262048 | 126.2048 | 11453806 | 234441.38 | 312093109 | 99590698 | 50019508 | 0.000000 | 24999678 | 31027271 | 0.000000
09-04-2025 18:59:55000 | -1265368 | 126.5368 | 11432359 | 234419.22 | 312932068 | 99594345 | 49995289 | 0.000000 | 25157686 | 31202592 | 0.000000
09-04-2025 19:00:00000 | -1258422 | 125.8422 | 11315139 | 234528.72 | 311057037 | 99598198 | 49984303 | 0.000000 | 25314282 | 31377506 | 0.000000
09-04-2025 19:00:05000 | -1257975 | 125.7975 | 11410900 | 234497.97 | 311010620 | 99591118 | 49998104 | 0.000000 | 15893103 | 174868591 | 0.000000
09-04-2025 19:00:10000 | -1258145 | 125.8145 | 97783691 | 234053.38 | 311303589 | 99699341 | 50038303 | 0.000000 | 30285202 | 349311920 | 0.000000
09-04-2025 19:00:15000 | -1263194 | 126.3194 | 93437744 | 233892.53 | 312680695 | 99727547 | 50044918 | 0.000000 | 43570026 | 524587585 | 0.000000
09-04-2025 19:00:20000 | -1265607 | 126.5607 | 92893691 | 233904.39 | 313251617 | 99731720 | 50044701 | 0.000000 | 56374020 | 700054565 | 0.000000
09-04-2025 19:00:25000 | -1260902 | 126.0902 | 89004619 | 233846.58 | 312096161 | 99751793 | 50050228 | 0.000000 | 68908859 | 875333923 | 0.000000
09-04-2025 19:00:30000 | -1262478 | 126.2478 | 89737881 | 233855.86 | 312485138 | 99748329 | 50054970 | 0.000000 | 81368187 | 10508163 | 0.000000
09-04-2025 19:00:35000 | -1265934 | 126.5934 | 94566045 | 233970.59 | 313268738 | 99722153 | 50092285 | 0.000000 | 94095871 | 12260483 | 0.000000
09-04-2025 19:00:40000 | -1264416 | 126.4416 | 95368418 | 233979.27 | 312903992 | 99716759 | 50097446 | 0.000000 | 107298256 | 14017576 | 0.000000
09-04-2025 19:00:45000 | -1268992 | 126.8992 | 92589951 | 233828.06 | 314176575 | 99734879 | 50089024 | 0.000000 | 120393372 | 15779597 | 0.000000
09-04-2025 19:00:50000 | -1269981 | 126.9981 | 91842646 | 233845.67 | 314382965 | 99739525 | 50063927 | 0.000000 | 133096924 | 17539783 | 0.000000
09-04-2025 19:00:55000 | -1264680 | 126.468 | 87525547 | 233814.20 | 313046539 | 99761375 | 50038197 | 0.000000 | 145452957 | 19298268 | 0.000000
09-04-2025 19:01:00000 | -1263931 | 126.3931 | 89030967 | 233853.45 | 312839874 | 99752831 | 50038826 | 0.000000 | 157724319 | 21053596 | 0.000000
09-04-2025 19:01:05000 | -1266515 | 126.6515 | 91088984 | 233868.91 | 313485168 | 99742371 | 50061619 | 0.000000 | 170172653 | 22807649 | 0.000000
09-04-2025 19:01:10000 | -1262506 | 126.2506 | 90301719 | 233932.06 | 312399048 | 99745178 | 50073860 | 0.000000 | 182695633 | 24563892 | 0.000000
09-04-2025 19:01:15000 | -1266068 | 126.6068 | 91200840 | 233888.23 | 313351044 | 99741554 | 50077953 | 0.000000 | 195355347 | 26322866 | 0.000000
09-04-2025 19:01:20000 | -1266899 | 126.6899 | 93336289 | 233927.56 | 313541077 | 99729713 | 50091991 | 0.000000 | 208209732 | 28080178 | 0.000000
09-04-2025 19:01:25000 | -1266106 | 126.6106 | 92483408 | 233904.69 | 313364624 | 99734283 | 50096874 | 0.000000 | 221119507 | 29840098 | 0.000000
09-04-2025 19:01:30000 | -1268275 | 126.8275 | 93529678 | 233906.72 | 313915131 | 99729187 | 50092785 | 0.000000 | 234118286 | 31600559 | 0.000000
09-04-2025 19:01:35000 | -1266456 | 126.6456 | 91594209 | 233901.63 | 313435181 | 99739487 | 50079838 | 0.000000 | 246873291 | 33361501 | 0.000000
09-04-2025 19:01:40000 | -1265808 | 126.5808 | 92668193 | 233936.20 | 313249084 | 99733093 | 50080715 | 0.000000 | 259645325 | 35119358 | 0.000000
09-04-2025 19:01:45000 | -1266970 | 126.697 | 93895391 | 233978.44 | 313502869 | 99726509 | 50095997 | 0.000000 | 272579681 | 36876084 | 0.000000
09-04-2025 19:01:50000 | -1264105 | 126.4105 | 91936084 | 233940.55 | 312812469 | 99736572 | 50119183 | 0.000000 | 285492126 | 38633438 | 0.000000
09-04-2025 19:01:55000 | -1268020 | 126.802 | 93872529 | 233932.69 | 313820526 | 99727097 | 50150677 | 0.000000 | 298505096 | 40390918 | 0.000000
09-04-2025 19:02:00000 | -1268783 | 126.8783 | 94968750 | 233937.67 | 314021088 | 99721046 | 50160892 | 0.000000 | 311586884 | 42150508 | 0.000000
09-04-2025 19:02:05000 | -1266253 | 126.6253 | 93635586 | 233918.17 | 313404297 | 99727707 | 50150448 | 0.000000 | 324707947 | 43912505 | 0.000000
09-04-2025 19:02:10000 | -1268775 | 126.8775 | 92446211 | 233857.03 | 314082642 | 99735603 | 50133602 | 0.000000 | 337667145 | 45673896 | 0.000000
09-04-2025 19:02:15000 | -1264122 | 126.4122 | 89868281 | 233880.27 | 312859680 | 99748253 | 50137020 | 0.000000 | 350246094 | 47431001 | 0.000000
09-04-2025 19:02:20000 | -1266108 | 126.6108 | 93690625 | 233943.09 | 313332581 | 99727325 | 50160934 | 0.000000 | 363064453 | 49186724 | 0.000000
09-04-2025 19:02:25000 | -1267797 | 126.7797 | 92856836 | 233914.13 | 313774078 | 99732849 | 50143681 | 0.000000 | 376018585 | 50949482 | 0.000000
09-04-2025 19:02:30000 | -1266983 | 126.6983 | 93539795 | 233932.20 | 313559784 | 99728577 | 50164772 | 0.000000 | 388933197 | 52705874 | 0.000000
09-04-2025 19:02:35000 | -1269756 | 126.9756 | 94821572 | 233964.27 | 314222290 | 99722328 | 50141491 | 0.000000 | 401937073 | 54468174 | 0.000000
09-04-2025 19:02:40000 | -1265153 | 126.5153 | 99456182 | 234149.61 | 312928772 | 99692436 | 50148373 | 0.000000 | 415487091 | 56226738 | 0.000000
09-04-2025 19:02:45000 | -1263855 | 126.3855 | 10201522 | 234180.34 | 312618774 | 99675819 | 50169731 | 0.000000 | 429501282 | 57983828 | 0.000000
09-04-2025 19:02:50000 | -1269891 | 126.9891 | 10049448 | 234062.11 | 314237579 | 99688339 | 50153557 | 0.000000 | 443553314 | 59745664 | 0.000000
09-04-2025 19:02:55000 | -1264665 | 126.4665 | 10388536 | 234279.69 | 312728363 | 99664314 | 50156929 | 0.000000 | 457704193 | 61504316 | 0.000000
09-04-2025 19:03:00000 | -1272316 | 127.2316 | 10471205 | 234128.38 | 314828949 | 99663040 | 50158405 | 0.000000 | 472233948 | 63264844 | 0.000000
09-04-2025 19:03:05000 | -1265306 | 126.5306 | 10340526 | 234259.66 | 312901703 | 99667725 | 50127541 | 0.000000 | 486364319 | 65024414 | 0.000000
09-04-2025 19:03:10000 | -1264225 | 126.4225 | 10375273 | 234246.45 | 312656799 | 99664932 | 50138481 | 0.000000 | 500669006 | 66779912 | 0.000000
09-04-2025 19:03:15000 | -1268407 | 126.8407 | 10520623 | 234182.88 | 313799591 | 99657784 | 50150467 | 0.000000 | 515221191 | 68536616 | 0.000000
09-04-2025 19:03:20000 | -1264703 | 126.4703 | 10492668 | 234243.52 | 312801025 | 99657600 | 50166042 | 0.000000 | 529796692 | 70292510 | 0.000000
09-04-2025 19:03:25000 | -1266919 | 126.6919 | 10825679 | 234325.83 | 313319031 | 99636909 | 50183418 | 0.000000 | 544632263 | 72051948 | 0.000000
09-04-2025 19:03:30000 | -1268308 | 126.8308 | 10944113 | 234325.17 | 313671478 | 99629776 | 50195602 | 0.000000 | 559781067 | 73810933 | 0.000000
09-04-2025 19:03:35000 | -1269611 | 126.9611 | 11026617 | 234347.16 | 313979218 | 99624969 | 50166306 | 0.000000 | 575025940 | 75575776 | 0.000000
09-04-2025 19:03:40000 | -1269868 | 126.9868 | 11315761 | 234420.41 | 314006592 | 99605324 | 50183365 | 0.000000 | 590584351 | 77338721 | 0.000000
09-04-2025 19:03:45000 | -1270192 | 127.0192 | 11125601 | 234371.84 | 314111938 | 99618591 | 50197838 | 0.000000 | 605993164 | 79099224 | 0.000000
09-04-2025 19:03:50000 | -1268738 | 126.8738 | 11081070 | 234376.25 | 313740784 | 99620758 | 50191486 | 0.000000 | 621520325 | 80863394 | 0.000000
09-04-2025 19:03:55000 | -1268180 | 126.818 | 11196976 | 234371.44 | 313632690 | 99612495 | 50190327 | 0.000000 | 637120789 | 82626016 | 0.000000
09-04-2025 19:04:00000 | -1270900 | 127.09 | 11047341 | 234330.56 | 314324158 | 99624329 | 50174763 | 0.000000 | 652490662 | 84389160 | 0.000000
09-04-2025 19:04:05000 | -1267787 | 126.7787 | 10710826 | 234261.73 | 313589264 | 99645020 | 50140194 | 0.000000 | 667676758 | 86155000 | 0.000000
09-04-2025 19:04:10000 | -1265379 | 126.5379 | 10817061 | 234374.83 | 312861664 | 99636612 | 50145752 | 0.000000 | 682684998 | 87915303 | 0.000000
09-04-2025 19:04:15000 | -1262442 | 126.2442 | 11146492 | 234483.06 | 312067444 | 99612480 | 50196484 | 0.000000 | 698010986 | 89671992 | 0.000000
09-04-2025 19:04:20000 | -1271130 | 127.113 | 11278431 | 234380.73 | 314363190 | 99608681 | 50206589 | 0.000000 | 713684204 | 91435840 | 0.000000
09-04-2025 19:04:25000 | -1266114 | 126.6114 | 11181983 | 234444.45 | 313030945 | 99612267 | 50206928 | 0.000000 | 729257935 | 93198721 | 0.000000
09-04-2025 19:04:30000 | -1271357 | 127.1357 | 11475312 | 234446.19 | 314375549 | 99595123 | 50217918 | 0.000000 | 745164795 | 94963877 | 0.000000
09-04-2025 19:04:35000 | -1272843 | 127.2843 | 11049396 | 234311.48 | 314827484 | 99625328 | 50188126 | 0.000000 | 760762756 | 96730283 | 0.000000
09-04-2025 19:04:40000 | -1264460 | 126.446 | 10967433 | 234411.58 | 312617462 | 99625954 | 50164875 | 0.000000 | 776006104 | 98490977 | 0.000000
09-04-2025 19:04:45000 | -1264056 | 126.4056 | 11416538 | 234526.47 | 312463013 | 99594620 | 50195385 | 0.000000 | 791585022 | 10024707 | 0.000000
09-04-2025 19:04:50000 | -1265319 | 126.5319 | 11245683 | 234393.80 | 312914490 | 99607376 | 50214317 | 0.000000 | 807319519 | 10200436 | 0.000000
09-04-2025 19:04:55000 | -1271595 | 127.1595 | 11082406 | 234254.92 | 314606049 | 99622360 | 50181881 | 0.000000 | 822913757 | 10377051 | 0.000000
09-04-2025 19:05:00000 | -1267854 | 126.7854 | 11503081 | 234530.25 | 313411774 | 99590935 | 50169720 | 0.000000 | 838572083 | 10553149 | 0.000000
09-04-2025 19:05:05000 | -1267233 | 126.7233 | 11592096 | 234478.45 | 313348663 | 99584221 | 50200024 | 0.000000 | 854665588 | 10729117 | 0.000000
09-04-2025 19:05:10000 | -1269434 | 126.9434 | 11707112 | 234533.14 | 313839783 | 99577438 | 50215286 | 0.000000 | 870821289 | 10905372 | 0.000000
09-04-2025 19:05:15000 | -1270144 | 127.0144 | 11807747 | 234507.61 | 314072968 | 99570663 | 50231613 | 0.000000 | 887110291 | 11081619 | 0.000000
09-04-2025 19:05:20000 | -1271667 | 127.1667 | 11754790 | 234487.31 | 314458649 | 99575500 | 50226707 | 0.000000 | 903498352 | 11258149 | 0.000000
09-04-2025 19:05:25000 | -1271558 | 127.1558 | 11456820 | 234434.89 | 314434662 | 99596550 | 50216675 | 0.000000 | 919558655 | 11434818 | 0.000000
09-04-2025 19:05:30000 | -1274770 | 127.477 | 11515724 | 234418.86 | 315261108 | 99594452 | 50219410 | 0.000000 | 935427795 | 11611372 | 0.000000
09-04-2025 19:05:35000 | -1270821 | 127.0821 | 11475438 | 234447.27 | 314241730 | 99594780 | 50218098 | 0.000000 | 951306274 | 11787792 | 0.000000
09-04-2025 19:05:40000 | -1272249 | 127.2249 | 11461063 | 234409.36 | 314640808 | 99596687 | 50192448 | 0.000000 | 967324585 | 11964674 | 0.000000
09-04-2025 19:05:45000 | -1268310 | 126.831 | 11342844 | 234453.06 | 313588928 | 99602470 | 50176319 | 0.000000 | 983075928 | 12141030 | 0.000000
09-04-2025 19:05:50000 | -1270688 | 127.0688 | 11355882 | 234402.83 | 314242188 | 99603043 | 50170231 | 0.000000 | 998875366 | 12317404 | 0.000000
09-04-2025 19:05:55000 | -1269263 | 126.9263 | 11326680 | 234424.33 | 313861908 | 99604187 | 50171013 | 0.000000 | 10146446 | 12493789 | 0.000000
09-04-2025 19:06:00000 | -1267249 | 126.7249 | 11204787 | 234426.86 | 313338013 | 99611389 | 50170891 | 0.000000 | 10303051 | 12669959 | 0.000000
09-04-2025 19:06:05000 | -1268326 | 126.8326 | 11207031 | 234419.72 | 313610748 | 99611893 | 50176601 | 0.000000 | 10459154 | 12846431 | 0.000000
09-04-2025 19:06:10000 | -1270181 | 127.0181 | 11364540 | 234429.42 | 314092773 | 99602127 | 50186310 | 0.000000 | 10616398 | 13022911 | 0.000000
09-04-2025 19:06:15000 | -1270332 | 127.0332 | 11312159 | 234437.02 | 314099640 | 99605858 | 50167892 | 0.000000 | 10772836 | 13199667 | 0.000000
09-04-2025 19:06:20000 | -1271179 | 127.1179 | 11439555 | 234442.22 | 314328644 | 99597519 | 50161068 | 0.000000 | 10931075 | 13376362 | 0.000000
09-04-2025 19:06:25000 | -1266587 | 126.6587 | 11419257 | 234511.91 | 313107178 | 99596039 | 50184559 | 0.000000 | 11089355 | 13552587 | 0.000000
09-04-2025 19:06:30000 | -1271148 | 127.1148 | 11342059 | 234407.34 | 314347443 | 99604286 | 50211998 | 0.000000 | 11247743 | 13729003 | 0.000000
09-04-2025 19:06:35000 | -1272965 | 127.2965 | 11164712 | 234318.81 | 314871216 | 99617584 | 50189445 | 0.000000 | 11404327 | 13905931 | 0.000000
09-04-2025 19:06:40000 | -1270388 | 127.0388 | 11065357 | 234347.86 | 314181702 | 99622803 | 50178291 | 0.000000 | 11559319 | 14082629 | 0.000000
09-04-2025 19:06:45000 | -1269102 | 126.9102 | 10838587 | 234281.63 | 313912903 | 99637291 | 50159702 | 0.000000 | 11711881 | 14259291 | 0.000000
09-04-2025 19:06:50000 | -1269076 | 126.9076 | 11076030 | 234370.67 | 313828583 | 99621307 | 50153534 | 0.000000 | 11864883 | 14435984 | 0.000000
09-04-2025 19:06:55000 | -1270695 | 127.0695 | 11082150 | 234383.39 | 314211395 | 99621849 | 50161633 | 0.000000 | 12018157 | 14612415 | 0.000000
09-04-2025 19:07:00000 | -1270070 | 127.007 | 11294561 | 234398.50 | 314083344 | 99606918 | 50166943 | 0.000000 | 12174875 | 14789061 | 0.000000
09-04-2025 19:07:05000 | -1273244 | 127.3244 | 11354019 | 234420.97 | 314843903 | 99604759 | 50188213 | 0.000000 | 12331947 | 14965724 | 0.000000
09-04-2025 19:07:10000 | -1274431 | 127.4431 | 11165702 | 234305.28 | 315250427 | 99618393 | 50192799 | 0.000000 | 12489010 | 15142673 | 0.000000
09-04-2025 19:07:15000 | -1272849 | 127.2849 | 11083552 | 234335.69 | 314803223 | 99623024 | 50184845 | 0.000000 | 12643805 | 15319669 | 0.000000
09-04-2025 19:07:20000 | -1278526 | 127.8526 | 10832833 | 234206.23 | 316318634 | 99642967 | 50156719 | 0.000000 | 12795498 | 15496789 | 0.000000
09-04-2025 19:07:25000 | -1269692 | 126.9692 | 10526334 | 234251.73 | 314025085 | 99658104 | 50133469 | 0.000000 | 12943699 | 15673753 | 0.000000
09-04-2025 19:07:30000 | -1275876 | 127.5876 | 10545413 | 234152.92 | 315679688 | 99660172 | 50132065 | 0.000000 | 13089696 | 15850350 | 0.000000
09-04-2025 19:07:35000 | -1271437 | 127.1437 | 10167468 | 234126.81 | 314548584 | 99681778 | 50094688 | 0.000000 | 13232427 | 16027139 | 0.000000
09-04-2025 19:07:40000 | -1267898 | 126.7898 | 10424720 | 234234.91 | 313584839 | 99663696 | 50108967 | 0.000000 | 13375853 | 16203553 | 0.000000
09-04-2025 19:07:45000 | -1273650 | 127.365 | 10665536 | 234218.63 | 315069824 | 99651215 | 50150806 | 0.000000 | 13522078 | 16379849 | 0.000000
09-04-2025 19:07:50000 | -1270128 | 127.0128 | 10451337 | 234213.83 | 314168457 | 99663162 | 50157932 | 0.000000 | 13667964 | 16556645 | 0.000000
09-04-2025 19:07:55000 | -1270188 | 127.0188 | 10649891 | 234277.14 | 314138062 | 99650345 | 50173729 | 0.000000 | 13816017 | 16733490 | 0.000000
09-04-2025 19:08:00000 | -1274101 | 127.4101 | 11170886 | 234381.14 | 315070587 | 99617844 | 50222115 | 0.000000 | 13967710 | 16910096 | 0.000000
09-04-2025 19:08:05000 | -1277837 | 127.7837 | 11061414 | 234301.75 | 316075256 | 99627426 | 50214317 | 0.000000 | 14122498 | 17087582 | 0.000000
09-04-2025 19:08:10000 | -1275442 | 127.5442 | 11160344 | 234356.66 | 315440216 | 99619354 | 50214890 | 0.000000 | 14276761 | 17264803 | 0.000000
09-04-2025 19:08:15000 | -1274362 | 127.4362 | 10963868 | 234304.97 | 315197205 | 99631950 | 50202068 | 0.000000 | 14431300 | 17442098 | 0.000000
09-04-2025 19:08:20000 | -1273439 | 127.3439 | 11093420 | 234363.61 | 314912262 | 99622704 | 50199390 | 0.000000 | 14584915 | 17619156 | 0.000000
09-04-2025 19:08:25000 | -1273199 | 127.3199 | 11217843 | 234404.95 | 314829468 | 99614098 | 50211124 | 0.000000 | 14739781 | 17796154 | 0.000000
09-04-2025 19:08:30000 | -1274843 | 127.4843 | 11229426 | 234343.50 | 315312866 | 99614296 | 50226486 | 0.000000 | 14897119 | 17973307 | 0.000000
09-04-2025 19:08:35000 | -1278062 | 127.8062 | 11339638 | 234383.94 | 316074890 | 99608704 | 50235191 | 0.000000 | 15053427 | 18150529 | 0.000000
09-04-2025 19:08:40000 | -1278382 | 127.8382 | 10968627 | 234256.59 | 316243530 | 99633934 | 50208149 | 0.000000 | 15209016 | 18328076 | 0.000000
09-04-2025 19:08:45000 | -1275012 | 127.5012 | 10776949 | 234267.20 | 315362091 | 99644684 | 50186996 | 0.000000 | 15360826 | 18505500 | 0.000000
09-04-2025 19:08:50000 | -1276791 | 127.6791 | 10844302 | 234283.06 | 315790894 | 99641251 | 50187222 | 0.000000 | 15510538 | 18682619 | 0.000000
09-04-2025 19:08:55000 | -1273184 | 127.3184 | 10650959 | 234233.58 | 314935211 | 99651909 | 50174427 | 0.000000 | 15659371 | 18859830 | 0.000000
09-04-2025 19:09:00000 | -1274681 | 127.4681 | 10759004 | 234248.38 | 315302368 | 99645676 | 50158096 | 0.000000 | 15809294 | 19037090 | 0.000000
09-04-2025 19:09:05000 | -1272440 | 127.244 | 10512166 | 234215.86 | 314744263 | 99660484 | 50155815 | 0.000000 | 15956708 | 19213818 | 0.000000
09-04-2025 19:09:10000 | -1271931 | 127.1931 | 10712909 | 234300.53 | 314546692 | 99647179 | 50176548 | 0.000000 | 16103668 | 19390424 | 0.000000
09-04-2025 19:09:15000 | -1273516 | 127.3516 | 11181400 | 234393.11 | 314911743 | 99616776 | 50221825 | 0.000000 | 16256732 | 19567201 | 0.000000
09-04-2025 19:09:20000 | -1277834 | 127.7834 | 11236871 | 234342.00 | 316050598 | 99615585 | 50228779 | 0.000000 | 16412559 | 19744400 | 0.000000
09-04-2025 19:09:25000 | -1277259 | 127.7259 | 11130754 | 234282.13 | 315969879 | 99622429 | 50218212 | 0.000000 | 16568423 | 19921834 | 0.000000
09-04-2025 19:09:30000 | -1275210 | 127.521 | 11215644 | 234364.22 | 315375519 | 99615456 | 50211945 | 0.000000 | 16723661 | 20099229 | 0.000000
09-04-2025 19:09:35000 | -1273390 | 127.339 | 10975455 | 234337.31 | 314910858 | 99630615 | 50215576 | 0.000000 | 16877196 | 20276119 | 0.000000
09-04-2025 19:09:40000 | -1276216 | 127.6216 | 11259063 | 234363.69 | 315630676 | 99613098 | 50227879 | 0.000000 | 17033297 | 20453410 | 0.000000
09-04-2025 19:09:45000 | -1282324 | 128.2324 | 11264275 | 234289.91 | 317234741 | 99616402 | 50218689 | 0.000000 | 17190166 | 20631008 | 0.000000
09-04-2025 19:09:50000 | -1275355 | 127.5355 | 11126464 | 234369.84 | 315381317 | 99621597 | 50201477 | 0.000000 | 17344480 | 20808436 | 0.000000
09-04-2025 19:09:55000 | -1277513 | 127.7513 | 11367217 | 234405.53 | 315919220 | 99606468 | 50225845 | 0.000000 | 17501752 | 20985664 | 0.000000
09-04-2025 19:10:00000 | -1280998 | 128.0998 | 11171707 | 234246.30 | 316944489 | 99621872 | 50215755 | 0.000000 | 17658712 | 21163033 | 0.000000
09-04-2025 19:10:05000 | -1277214 | 127.7214 | 10754020 | 234214.22 | 315972137 | 99647400 | 50167206 | 0.000000 | 17811244 | 21340822 | 0.000000
09-04-2025 19:10:10000 | -1277212 | 127.7212 | 10963619 | 234310.16 | 315886810 | 99633598 | 50185322 | 0.000000 | 17962305 | 21517979 | 0.000000
09-04-2025 19:10:15000 | -1279096 | 127.9096 | 10837341 | 234225.98 | 316434204 | 99642990 | 50184746 | 0.000000 | 18113470 | 21695447 | 0.000000
09-04-2025 19:10:20000 | -1274095 | 127.4095 | 10664734 | 234253.39 | 315131531 | 99651512 | 50179306 | 0.000000 | 18262855 | 21872678 | 0.000000
09-04-2025 19:10:25000 | -1275817 | 127.5817 | 10695180 | 234241.98 | 315579071 | 99650467 | 50176090 | 0.000000 | 18411509 | 22049988 | 0.000000
09-04-2025 19:10:30000 | -1275688 | 127.5688 | 10816679 | 234262.70 | 315548370 | 99642448 | 50193954 | 0.000000 | 18560903 | 22227105 | 0.000000
09-04-2025 19:10:35000 | -1280156 | 128.0156 | 10839726 | 234176.06 | 316763611 | 99643425 | 50195972 | 0.000000 | 18712261 | 22404682 | 0.000000
09-04-2025 19:10:40000 | -1277148 | 127.7148 | 10680841 | 234229.06 | 315918060 | 99652122 | 50182014 | 0.000000 | 18860392 | 22582232 | 0.000000
09-04-2025 19:10:45000 | -1276323 | 127.6323 | 10551710 | 234180.91 | 315754486 | 99660004 | 50186066 | 0.000000 | 19008754 | 22759723 | 0.000000
09-04-2025 19:10:50000 | -1277760 | 127.776 | 10621861 | 234183.52 | 316118256 | 99656258 | 50174919 | 0.000000 | 19156096 | 22937225 | 0.000000
09-04-2025 19:10:55000 | -1274540 | 127.454 | 10474753 | 234223.02 | 315245819 | 99663986 | 50162247 | 0.000000 | 19302244 | 23114535 | 0.000000
09-04-2025 19:11:00000 | -1276232 | 127.6232 | 10861358 | 234295.22 | 315643372 | 99639816 | 50175453 | 0.000000 | 19451000 | 23291754 | 0.000000
09-04-2025 19:11:05000 | -1278999 | 127.8999 | 10872385 | 234243.11 | 316394653 | 99640640 | 50188988 | 0.000000 | 19601962 | 23468996 | 0.000000
09-04-2025 19:11:10000 | -1278733 | 127.8733 | 10820466 | 234248.69 | 316310486 | 99643898 | 50191391 | 0.000000 | 19752543 | 23646447 | 0.000000
09-04-2025 19:11:15000 | -1280671 | 128.0671 | 10672380 | 234169.75 | 316862854 | 99654572 | 50180508 | 0.000000 | 19901704 | 23824059 | 0.000000
09-04-2025 19:11:20000 | -1278204 | 127.8204 | 10477168 | 234176.64 | 316208130 | 99665749 | 50177509 | 0.000000 | 20047644 | 24001412 | 0.000000
09-04-2025 19:11:25000 | -1275916 | 127.5916 | 10324459 | 234131.77 | 315674774 | 99674210 | 50173359 | 0.000000 | 20191914 | 24178639 | 0.000000
09-04-2025 19:11:30000 | -1277127 | 127.7127 | 10102552 | 234046.89 | 316043427 | 99688591 | 50132679 | 0.000000 | 20333549 | 24356166 | 0.000000
09-04-2025 19:11:35000 | -1275356 | 127.5356 | 10045941 | 234079.56 | 315552734 | 99691200 | 50102219 | 0.000000 | 20474214 | 24533598 | 0.000000
09-04-2025 19:11:40000 | -1269333 | 126.9333 | 10150827 | 234185.94 | 313950623 | 99681770 | 50123020 | 0.000000 | 20615181 | 24710318 | 0.000000
09-04-2025 19:11:45000 | -1274602 | 127.4602 | 10416340 | 234163.91 | 315327271 | 99667740 | 50160500 | 0.000000 | 20757905 | 24886893 | 0.000000
09-04-2025 19:11:50000 | -1277353 | 127.7353 | 10312332 | 234069.41 | 316109467 | 99675705 | 50167198 | 0.000000 | 20901602 | 25063963 | 0.000000
09-04-2025 19:11:55000 | -1279528 | 127.9528 | 10302342 | 234127.58 | 316564178 | 99677422 | 50160954 | 0.000000 | 21044497 | 25241402 | 0.000000
09-04-2025 19:12:00000 | -1276276 | 127.6276 | 10460753 | 234190.61 | 315710815 | 99665787 | 50167152 | 0.000000 | 21188635 | 25418484 | 0.000000
09-04-2025 19:12:05000 | -1278441 | 127.8441 | 10436462 | 234125.09 | 316326324 | 99668449 | 50156143 | 0.000000 | 21335029 | 25595965 | 0.000000
09-04-2025 19:12:10000 | -1275393 | 127.5393 | 10326249 | 234173.95 | 315488525 | 99673836 | 50138100 | 0.000000 | 21479124 | 25773465 | 0.000000
09-04-2025 19:12:15000 | -1273641 | 127.3641 | 10399215 | 234219.75 | 315011658 | 99668327 | 50147839 | 0.000000 | 21622986 | 25950510 | 0.000000
09-04-2025 19:12:20000 | -1278067 | 127.8067 | 10492527 | 234161.78 | 316196533 | 99664696 | 50157986 | 0.000000 | 21768918 | 26127715 | 0.000000
09-04-2025 19:12:25000 | -1276729 | 127.6729 | 10455979 | 234180.55 | 315836365 | 99666321 | 50158955 | 0.000000 | 21914512 | 26304945 | 0.000000
09-04-2025 19:12:30000 | -1275055 | 127.5055 | 10326768 | 234120.14 | 315479309 | 99673630 | 50144356 | 0.000000 | 22060356 | 26482404 | 0.000000
09-04-2025 19:12:35000 | -1275898 | 127.5898 | 10508709 | 234224.36 | 315581970 | 99662529 | 50144009 | 0.000000 | 22204446 | 26659693 | 0.000000
09-04-2025 19:12:40000 | -1278058 | 127.8058 | 10448841 | 234147.88 | 316204834 | 99667465 | 50159176 | 0.000000 | 22349990 | 26836893 | 0.000000
09-04-2025 19:12:45000 | -1280868 | 128.0868 | 10197383 | 234032.20 | 317002228 | 99684586 | 50131214 | 0.000000 | 22493770 | 27014689 | 0.000000
09-04-2025 19:12:50000 | -1274307 | 127.4307 | 10176601 | 234169.48 | 315198914 | 99682640 | 50115185 | 0.000000 | 22633464 | 27191943 | 0.000000
09-04-2025 19:12:55000 | -1274335 | 127.4335 | 10325793 | 234166.50 | 315239624 | 99673325 | 50130795 | 0.000000 | 22775740 | 27368697 | 0.000000
09-04-2025 19:13:00000 | -1278310 | 127.831 | 10004991 | 234003.59 | 316380920 | 99695114 | 50101093 | 0.000000 | 22918035 | 27546359 | 0.000000
09-04-2025 19:13:05000 | -1276065 | 127.6065 | 10007046 | 234058.06 | 315749573 | 99693916 | 50089405 | 0.000000 | 23056223 | 27723648 | 0.000000
09-04-2025 19:13:10000 | -1270156 | 127.0156 | 96900137 | 234032.22 | 314272217 | 99710258 | 50085918 | 0.000000 | 23192986 | 27900691 | 0.000000
09-04-2025 19:13:15000 | -1275681 | 127.5681 | 96724316 | 233959.52 | 315723755 | 99713783 | 50077999 | 0.000000 | 23327998 | 28077873 | 0.000000
09-04-2025 19:13:20000 | -1273122 | 127.3122 | 95205615 | 233978.91 | 315040344 | 99721558 | 50065510 | 0.000000 | 23461299 | 28255170 | 0.000000
09-04-2025 19:13:25000 | -1276607 | 127.6607 | 95497607 | 233966.77 | 315919830 | 99721375 | 50062996 | 0.000000 | 23593552 | 28432232 | 0.000000
09-04-2025 19:13:30000 | -1273780 | 127.378 | 96590527 | 234017.23 | 315174988 | 99713722 | 50075687 | 0.000000 | 23727002 | 28609230 | 0.000000
09-04-2025 19:13:35000 | -1277985 | 127.7985 | 96227578 | 233940.42 | 316307404 | 99717720 | 50073196 | 0.000000 | 23860649 | 28786545 | 0.000000
09-04-2025 19:13:40000 | -1275160 | 127.516 | 95668828 | 233983.39 | 315544861 | 99719742 | 50061108 | 0.000000 | 23992134 | 28963768 | 0.000000
09-04-2025 19:13:45000 | -1271656 | 127.1656 | 95012334 | 234018.42 | 314622833 | 99722046 | 50077110 | 0.000000 | 24125334 | 29140590 | 0.000000
09-04-2025 19:13:50000 | -1278738 | 127.8738 | 97159238 | 233947.09 | 316501038 | 99712593 | 50073257 | 0.000000 | 24258989 | 29317895 | 0.000000
09-04-2025 19:13:55000 | -1275892 | 127.5892 | 95400557 | 233944.69 | 315771118 | 99721626 | 50049370 | 0.000000 | 24392517 | 29495432 | 0.000000
09-04-2025 19:14:00000 | -1273184 | 127.3184 | 94615400 | 233974.59 | 315052490 | 99725014 | 50047016 | 0.000000 | 24524097 | 29672438 | 0.000000
09-04-2025 19:14:05000 | -1274939 | 127.4939 | 94218701 | 233916.78 | 315552124 | 99728050 | 50045441 | 0.000000 | 24656719 | 29849732 | 0.000000
09-04-2025 19:14:10000 | -1277409 | 127.7409 | 92476777 | 233875.48 | 316184753 | 99738983 | 50017109 | 0.000000 | 24785237 | 30027129 | 0.000000
09-04-2025 19:14:15000 | -1274103 | 127.4103 | 92333730 | 233914.06 | 315318054 | 99738434 | 50022308 | 0.000000 | 24913093 | 30204031 | 0.000000
09-04-2025 19:14:20000 | -1274519 | 127.4519 | 92684541 | 233880.66 | 315469513 | 99736626 | 50052181 | 0.000000 | 25042051 | 30380914 | 0.000000
09-04-2025 19:14:25000 | -1277176 | 127.7176 | 90646289 | 233811.14 | 316183075 | 99749084 | 50059669 | 0.000000 | 25168052 | 30557908 | 0.000000
09-04-2025 19:14:30000 | -1277225 | 127.7225 | 88915723 | 233749.47 | 316248413 | 99758553 | 50027199 | 0.000000 | 25292351 | 30735438 | 0.000000
09-04-2025 19:14:35000 | -1273556 | 127.3556 | 87964414 | 233802.63 | 315255249 | 99762314 | 50009892 | 0.000000 | 25413948 | 30912621 | 0.000000
09-04-2025 19:14:40000 | -1271316 | 127.1316 | 87469229 | 233799.03 | 314700073 | 99764153 | 50020782 | 0.000000 | 25535691 | 31089373 | 0.000000
09-04-2025 19:14:45000 | -1272642 | 127.2642 | 90507314 | 233870.55 | 314986267 | 99748070 | 50034607 | 0.000000 | 25659788 | 31266307 | 0.000000
09-04-2025 19:14:50000 | -1272156 | 127.2156 | 91270273 | 233901.22 | 314837311 | 99743622 | 50070599 | 0.000000 | 25786851 | 31443158 | 0.000000
09-04-2025 19:14:55000 | -1277848 | 127.7848 | 92866621 | 233849.84 | 316333984 | 99736961 | 50097511 | 0.000000 | 25915032 | 31620297 | 0.000000
09-04-2025 19:15:00000 | -1281816 | 128.1816 | 88829375 | 233739.14 | 317393646 | 99760742 | 50085365 | 0.000000 | 26039180 | 31797834 | 0.000000
09-04-2025 19:15:05000 | -1277585 | 127.7585 | 91029277 | 233849.78 | 316238037 | 99747124 | 50061157 | 0.000000 | 12656870 | 177442810 | 0.000000
09-04-2025 19:15:10000 | -1275344 | 127.5344 | 90216719 | 233845.38 | 315678070 | 99750732 | 50082184 | 0.000000 | 25284992 | 354458435 | 0.000000
09-04-2025 19:15:15000 | -1276293 | 127.6293 | 92455664 | 233855.70 | 315939423 | 99738647 | 50110554 | 0.000000 | 38051899 | 531536987 | 0.000000
09-04-2025 19:15:20000 | -1278333 | 127.8333 | 92271680 | 233818.39 | 316487061 | 99740509 | 50094894 | 0.000000 | 50929695 | 708950256 | 0.000000
09-04-2025 19:15:25000 | -1277710 | 127.771 | 90828076 | 233789.66 | 316347412 | 99748291 | 50058105 | 0.000000 | 63719532 | 886638245 | 0.000000
09-04-2025 19:15:30000 | -1272153 | 127.2153 | 90956270 | 233923.61 | 314798950 | 99745377 | 50048977 | 0.000000 | 76263283 | 10637118 | 0.000000
09-04-2025 19:15:35000 | -1272055 | 127.2055 | 91580674 | 233883.50 | 314843658 | 99741844 | 50065865 | 0.000000 | 89114838 | 12407335 | 0.000000
09-04-2025 19:15:40000 | -1275276 | 127.5276 | 94701602 | 233974.34 | 315569489 | 99725410 | 50090134 | 0.000000 | 102113861 | 14177476 | 0.000000
09-04-2025 19:15:45000 | -1277953 | 127.7953 | 94258418 | 233878.91 | 316346252 | 99729095 | 50090488 | 0.000000 | 115108971 | 15946919 | 0.000000
09-04-2025 19:15:50000 | -1278424 | 127.8424 | 94750225 | 233883.53 | 316464569 | 99726479 | 50081223 | 0.000000 | 128225998 | 17720389 | 0.000000
09-04-2025 19:15:55000 | -1273640 | 127.364 | 92098613 | 233866.81 | 315262939 | 99739578 | 50062458 | 0.000000 | 141094711 | 19492026 | 0.000000
09-04-2025 19:16:00000 | -1276539 | 127.6539 | 90563359 | 233751.86 | 316104797 | 99749290 | 50037773 | 0.000000 | 153863251 | 21266104 | 0.000000
09-04-2025 19:16:05000 | -1274358 | 127.4358 | 88148896 | 233778.42 | 315488892 | 99761620 | 50025127 | 0.000000 | 166112717 | 23036775 | 0.000000
09-04-2025 19:16:10000 | -1274173 | 127.4173 | 85772080 | 233657.25 | 315567505 | 99774193 | 50016338 | 0.000000 | 178248581 | 24807207 | 0.000000
09-04-2025 19:16:15000 | -1276145 | 127.6145 | 86339814 | 233707.50 | 315995819 | 99771912 | 50003426 | 0.000000 | 190205536 | 26579255 | 0.000000
09-04-2025 19:16:20000 | -1272280 | 127.228 | 83953877 | 233697.84 | 315018158 | 99782997 | 49985931 | 0.000000 | 201958618 | 28348655 | 0.000000
09-04-2025 19:16:25000 | -1271473 | 127.1473 | 83691924 | 233704.36 | 314803925 | 99784073 | 49984287 | 0.000000 | 213546661 | 30115530 | 0.000000
09-04-2025 19:16:30000 | -1270873 | 127.0873 | 81192588 | 233637.63 | 314706360 | 99796547 | 50004414 | 0.000000 | 224996521 | 31882419 | 0.000000
09-04-2025 19:16:35000 | -1271288 | 127.1288 | 86587305 | 233789.91 | 314694489 | 99768852 | 50055531 | 0.000000 | 236752808 | 33646724 | 0.000000
09-04-2025 19:16:40000 | -1278057 | 127.8057 | 85632041 | 233619.50 | 316573364 | 99776291 | 50058052 | 0.000000 | 248776520 | 35418789 | 0.000000
09-04-2025 19:16:45000 | -1275427 | 127.5427 | 83758066 | 233656.55 | 315844788 | 99785065 | 50029545 | 0.000000 | 260416321 | 37191675 | 0.000000
09-04-2025 19:16:50000 | -1273628 | 127.3628 | 84833262 | 233697.88 | 315365509 | 99778908 | 50033520 | 0.000000 | 272157379 | 38961826 | 0.000000
09-04-2025 19:16:55000 | -1278355 | 127.8355 | 83179541 | 233586.70 | 316652588 | 99788979 | 50027077 | 0.000000 | 283859650 | 40734004 | 0.000000
09-04-2025 19:17:00000 | -1272678 | 127.2678 | 80869819 | 233643.92 | 315138000 | 99798721 | 49992905 | 0.000000 | 295189819 | 42505864 | 0.000000
09-04-2025 19:17:05000 | -1270932 | 127.0932 | 82726221 | 233711.73 | 314645020 | 99788826 | 50002525 | 0.000000 | 306620544 | 44274116 | 0.000000
09-04-2025 19:17:10000 | -1275553 | 127.5553 | 86128594 | 233709.52 | 315843658 | 99772812 | 50008305 | 0.000000 | 318340393 | 46042729 | 0.000000
09-04-2025 19:17:15000 | -1274180 | 127.418 | 84250488 | 233671.48 | 315526306 | 99782112 | 50013630 | 0.000000 | 330202576 | 47812012 | 0.000000
09-04-2025 19:17:20000 | -1279017 | 127.9017 | 81233003 | 233513.08 | 316885498 | 99798920 | 50015469 | 0.000000 | 341725433 | 49582183 | 0.000000
09-04-2025 19:17:25000 | -1272474 | 127.2474 | 78387861 | 233549.64 | 315176849 | 99810791 | 49994728 | 0.000000 | 352652466 | 51352798 | 0.000000
09-04-2025 19:17:30000 | -1272273 | 127.2273 | 78447334 | 233549.73 | 315127808 | 99810448 | 49977379 | 0.000000 | 363558868 | 53123130 | 0.000000
09-04-2025 19:17:35000 | -1272669 | 127.2669 | 77239453 | 233534.31 | 315231720 | 99816338 | 49979340 | 0.000000 | 374303558 | 54889790 | 0.000000
09-04-2025 19:17:40000 | -1269375 | 126.9375 | 77410420 | 233573.92 | 314364838 | 99814568 | 49982201 | 0.000000 | 385132660 | 56655977 | 0.000000
09-04-2025 19:17:45000 | -1272174 | 127.2174 | 77309346 | 233519.47 | 315127228 | 99815865 | 50005707 | 0.000000 | 395890930 | 58421938 | 0.000000
09-04-2025 19:17:50000 | -1272368 | 127.2368 | 80714473 | 233603.50 | 315116455 | 99799393 | 50023834 | 0.000000 | 406889008 | 60188291 | 0.000000
09-04-2025 19:17:55000 | -1275243 | 127.5243 | 78799219 | 233517.69 | 315913452 | 99809639 | 50012585 | 0.000000 | 417865753 | 61960762 | 0.000000
09-04-2025 19:18:00000 | -1275944 | 127.5944 | 77969492 | 233515.97 | 316077576 | 99813820 | 49996353 | 0.000000 | 428645752 | 63731211 | 0.000000
09-04-2025 19:18:05000 | -1271439 | 127.1439 | 77789980 | 233551.55 | 314910217 | 99813354 | 50014832 | 0.000000 | 439478271 | 65499517 | 0.000000
09-04-2025 19:18:10000 | -1276351 | 127.6351 | 79937402 | 233536.84 | 316174164 | 99804451 | 50032543 | 0.000000 | 450441711 | 67268911 | 0.000000
09-04-2025 19:18:15000 | -1274131 | 127.4131 | 77936426 | 233543.08 | 315587769 | 99813446 | 50003269 | 0.000000 | 461358673 | 69039863 | 0.000000
09-04-2025 19:18:20000 | -1276072 | 127.6072 | 78410200 | 233478.41 | 316162109 | 99811752 | 49988102 | 0.000000 | 472369476 | 70812485 | 0.000000
09-04-2025 19:18:25000 | -1275085 | 127.5085 | 77312310 | 233536.52 | 315823547 | 99816689 | 49969532 | 0.000000 | 483074677 | 72582900 | 0.000000
09-04-2025 19:18:30000 | -1269177 | 126.9177 | 76149141 | 233529.78 | 314356903 | 99820488 | 49976276 | 0.000000 | 493749298 | 74350845 | 0.000000
09-04-2025 19:18:35000 | -1272707 | 127.2707 | 79929595 | 233604.81 | 315183228 | 99803375 | 50005070 | 0.000000 | 504759064 | 76117427 | 0.000000
09-04-2025 19:18:40000 | -1272821 | 127.2821 | 80360713 | 233572.19 | 315267303 | 99801285 | 50039341 | 0.000000 | 515971924 | 77885327 | 0.000000
09-04-2025 19:18:45000 | -1276824 | 127.6824 | 81414800 | 233566.55 | 316275909 | 99797325 | 50051228 | 0.000000 | 527217896 | 79657085 | 0.000000
09-04-2025 19:18:50000 | -1279492 | 127.9492 | 78798477 | 233439.16 | 317072052 | 99810898 | 50018944 | 0.000000 | 538334595 | 81432837 | 0.000000
09-04-2025 19:18:55000 | -1274775 | 127.4775 | 76185576 | 233495.22 | 315786072 | 99821892 | 49996033 | 0.000000 | 548951965 | 83204824 | 0.000000
09-04-2025 19:19:00000 | -1271225 | 127.1225 | 75801528 | 233526.48 | 314863037 | 99822693 | 50013466 | 0.000000 | 559549561 | 84971445 | 0.000000
09-04-2025 19:19:05000 | -1274200 | 127.42 | 78534185 | 233568.44 | 315579712 | 99810600 | 50044678 | 0.000000 | 570246094 | 86738965 | 0.000000
09-04-2025 19:19:10000 | -1279715 | 127.9715 | 79576143 | 233477.09 | 317081268 | 99807228 | 50032940 | 0.000000 | 581304260 | 88513281 | 0.000000
09-04-2025 19:19:15000 | -1273570 | 127.357 | 81309961 | 233648.45 | 315359711 | 99796814 | 50039371 | 0.000000 | 592358765 | 90282617 | 0.000000
09-04-2025 19:19:20000 | -1275078 | 127.5078 | 81484443 | 233581.66 | 315824493 | 99796425 | 50058559 | 0.000000 | 603729675 | 92053721 | 0.000000
09-04-2025 19:19:25000 | -1276641 | 127.6641 | 78795850 | 233513.86 | 316259796 | 99810066 | 50036427 | 0.000000 | 614749939 | 93827402 | 0.000000
09-04-2025 19:19:30000 | -1277277 | 127.7277 | 79135747 | 233515.52 | 316419739 | 99808617 | 50023537 | 0.000000 | 625796021 | 95598691 | 0.000000
09-04-2025 19:19:35000 | -1273650 | 127.365 | 78379146 | 233547.52 | 315469910 | 99811180 | 50002174 | 0.000000 | 636687134 | 97372432 | 0.000000
09-04-2025 19:19:40000 | -1275032 | 127.5032 | 79547627 | 233558.92 | 315814423 | 99805946 | 50005871 | 0.000000 | 647702881 | 99143086 | 0.000000
09-04-2025 19:19:45000 | -1275700 | 127.57 | 79216753 | 233546.73 | 315994934 | 99807755 | 50007378 | 0.000000 | 658729004 | 10091450 | 0.000000
09-04-2025 19:19:50000 | -1272938 | 127.2938 | 76434082 | 233508.91 | 315318420 | 99820213 | 49999352 | 0.000000 | 669408386 | 10268395 | 0.000000
09-04-2025 19:19:55000 | -1270325 | 127.0325 | 77438779 | 233571.48 | 314603271 | 99814713 | 50020565 | 0.000000 | 680127014 | 10444833 | 0.000000
09-04-2025 19:20:00000 | -1277977 | 127.7977 | 82348662 | 233588.70 | 316543854 | 99793037 | 50052780 | 0.000000 | 691362976 | 10621774 | 0.000000
09-04-2025 19:20:05000 | -1278467 | 127.8467 | 78398896 | 233467.14 | 316767670 | 99812508 | 50029671 | 0.000000 | 702481995 | 10799179 | 0.000000
09-04-2025 19:20:10000 | -1277558 | 127.7558 | 77335942 | 233503.94 | 316478638 | 99817284 | 50008995 | 0.000000 | 713282166 | 10976613 | 0.000000
09-04-2025 19:20:15000 | -1275532 | 127.5532 | 77851694 | 233575.02 | 315889801 | 99814255 | 50001778 | 0.000000 | 723943420 | 11153782 | 0.000000
09-04-2025 19:20:20000 | -1274363 | 127.4363 | 81681172 | 233680.50 | 315518463 | 99795219 | 50023048 | 0.000000 | 734979309 | 11330816 | 0.000000
09-04-2025 19:20:25000 | -1274674 | 127.4674 | 82220146 | 233653.19 | 315638794 | 99792618 | 50032658 | 0.000000 | 746483887 | 11508089 | 0.000000
09-04-2025 19:20:30000 | -1275651 | 127.5651 | 84559658 | 233711.14 | 315839142 | 99781021 | 50043545 | 0.000000 | 758028198 | 11685363 | 0.000000
09-04-2025 19:20:35000 | -1279354 | 127.9354 | 83799795 | 233585.53 | 316910370 | 99786163 | 50035545 | 0.000000 | 769724060 | 11862984 | 0.000000
09-04-2025 19:20:40000 | -1272711 | 127.2711 | 80946250 | 233643.41 | 315148529 | 99798355 | 50023869 | 0.000000 | 780953125 | 12040104 | 0.000000
09-04-2025 19:20:45000 | -1276984 | 127.6984 | 79542217 | 233516.58 | 316353851 | 99806564 | 50046368 | 0.000000 | 792170227 | 12217154 | 0.000000
09-04-2025 19:20:50000 | -1278767 | 127.8767 | 79670537 | 233542.84 | 316758972 | 99806480 | 50045532 | 0.000000 | 803200439 | 12394651 | 0.000000
09-04-2025 19:20:55000 | -1278892 | 127.8892 | 77080117 | 233469.50 | 316849609 | 99818863 | 50005268 | 0.000000 | 814044495 | 12572428 | 0.000000
09-04-2025 19:21:00000 | -1273937 | 127.3937 | 79888008 | 233637.84 | 315442719 | 99803955 | 50027496 | 0.000000 | 824989807 | 12749457 | 0.000000
09-04-2025 19:21:05000 | -1279281 | 127.9281 | 82836465 | 233592.23 | 316867676 | 99791016 | 50048138 | 0.000000 | 836344238 | 12926732 | 0.000000
09-04-2025 19:21:10000 | -1276852 | 127.6852 | 83170615 | 233651.38 | 316194427 | 99788528 | 50052891 | 0.000000 | 847854248 | 13104112 | 0.000000
09-04-2025 19:21:15000 | -1276069 | 127.6069 | 80948501 | 233567.86 | 316081207 | 99799400 | 50059105 | 0.000000 | 859321411 | 13281609 | 0.000000
09-04-2025 19:21:20000 | -1276117 | 127.6117 | 80915479 | 233612.52 | 316029877 | 99799576 | 50042824 | 0.000000 | 870484924 | 13458971 | 0.000000
09-04-2025 19:21:25000 | -1275765 | 127.5765 | 75852178 | 233467.98 | 316062134 | 99823715 | 50020508 | 0.000000 | 881341309 | 13636371 | 0.000000
09-04-2025 19:21:30000 | -1277979 | 127.7979 | 73088506 | 233328.25 | 316759460 | 99836861 | 49985802 | 0.000000 | 891739563 | 13813896 | 0.000000
09-04-2025 19:21:35000 | -1270888 | 127.0888 | 73097837 | 233466.59 | 314819916 | 99834999 | 49972622 | 0.000000 | 901867310 | 13990765 | 0.000000
09-04-2025 19:21:40000 | -1272477 | 127.2477 | 76254619 | 233485.88 | 315232971 | 99820923 | 49993469 | 0.000000 | 912395691 | 14167423 | 0.000000
09-04-2025 19:21:45000 | -1272735 | 127.2735 | 75023096 | 233430.70 | 315351837 | 99826721 | 49982872 | 0.000000 | 922916748 | 14344221 | 0.000000
09-04-2025 19:21:50000 | -1266780 | 126.678 | 78271875 | 233636.72 | 313654205 | 99809654 | 50009766 | 0.000000 | 933487549 | 14520579 | 0.000000
09-04-2025 19:21:55000 | -1239859 | 123.9859 | 71238711 | 233660.47 | 306879181 | 99835342 | 50064522 | 0.000000 | 943839661 | 14694517 | 0.000000
09-04-2025 19:22:00000 | -1219916 | 121.9916 | 68626045 | 233633.00 | 301961609 | 99842148 | 50086430 | 0.000000 | 953524109 | 14865039 | 0.000000
09-04-2025 19:22:05000 | -1213920 | 121.392 | 65633633 | 233534.08 | 300571136 | 99854156 | 50057186 | 0.000000 | 962757690 | 15033837 | 0.000000
09-04-2025 19:22:10000 | -1218664 | 121.8664 | 70261772 | 233544.38 | 301786072 | 99834213 | 50026100 | 0.000000 | 972260498 | 15202957 | 0.000000
09-04-2025 19:22:15000 | -1219635 | 121.9635 | 71035371 | 233558.75 | 302018555 | 99830818 | 50019287 | 0.000000 | 982158508 | 15372467 | 0.000000
09-04-2025 19:22:20000 | -1215001 | 121.5001 | 70307212 | 233578.67 | 300839752 | 99832993 | 50025150 | 0.000000 | 992064087 | 15541473 | 0.000000
09-04-2025 19:22:25000 | -1200737 | 120.0737 | 67766494 | 233627.75 | 297222534 | 99841118 | 50047520 | 0.000000 | 10016105 | 15708904 | 0.000000
09-04-2025 19:22:30000 | -1176528 | 117.6528 | 64841431 | 233687.83 | 291131805 | 99848473 | 50074696 | 0.000000 | 10106606 | 15873466 | 0.000000
09-04-2025 19:22:35000 | -1175103 | 117.5103 | 63587896 | 233558.98 | 290924774 | 99853912 | 50047443 | 0.000000 | 10194619 | 16036548 | 0.000000
09-04-2025 19:22:40000 | -1180477 | 118.0477 | 68035708 | 233614.13 | 292242279 | 99834328 | 50015671 | 0.000000 | 10286389 | 16200213 | 0.000000
09-04-2025 19:22:45000 | -1173327 | 117.3327 | 68437363 | 233680.53 | 290403748 | 99830330 | 50035389 | 0.000000 | 10381047 | 16363470 | 0.000000
09-04-2025 19:22:50000 | -1158355 | 115.8355 | 65064009 | 233713.73 | 286622101 | 99842621 | 50041573 | 0.000000 | 10472942 | 16525254 | 0.000000
09-04-2025 19:22:55000 | -1142191 | 114.2191 | 61365542 | 233703.67 | 282596985 | 99855988 | 50059460 | 0.000000 | 10560171 | 16684703 | 0.000000
09-04-2025 19:23:00000 | -1143899 | 114.3899 | 60835674 | 233566.13 | 283175476 | 99858879 | 50030621 | 0.000000 | 10645162 | 16843398 | 0.000000
09-04-2025 19:23:05000 | -1151037 | 115.1037 | 62572471 | 233557.63 | 284975861 | 99852570 | 49992977 | 0.000000 | 10730240 | 17002893 | 0.000000
09-04-2025 19:23:10000 | -1143971 | 114.3971 | 60745869 | 233596.53 | 283172852 | 99859314 | 50006592 | 0.000000 | 10816500 | 17162369 | 0.000000
09-04-2025 19:23:15000 | -1136537 | 113.6537 | 56357256 | 233503.00 | 281378754 | 99877281 | 50013096 | 0.000000 | 10897469 | 17320539 | 0.000000
09-04-2025 19:23:20000 | -1132469 | 113.2469 | 58844536 | 233616.81 | 280269257 | 99865273 | 49994476 | 0.000000 | 10976289 | 17478281 | 0.000000
09-04-2025 19:23:25000 | -1118325 | 111.8325 | 55898701 | 233628.00 | 276728302 | 99875313 | 50018703 | 0.000000 | 11055707 | 17634576 | 0.000000
09-04-2025 19:23:30000 | -1101403 | 110.1403 | 53647676 | 233682.50 | 272460419 | 99881584 | 50041821 | 0.000000 | 11131215 | 17788754 | 0.000000
09-04-2025 19:23:35000 | -1082285 | 108.2285 | 48029722 | 233633.14 | 267737122 | 99901672 | 50059502 | 0.000000 | 11201104 | 17940139 | 0.000000
09-04-2025 19:23:40000 | -1072276 | 107.2276 | 47066465 | 233565.44 | 265328857 | 99903809 | 50052753 | 0.000000 | 11267626 | 18089365 | 0.000000
09-04-2025 19:23:45000 | -1076386 | 107.6386 | 49200840 | 233513.27 | 266427734 | 99895699 | 50019127 | 0.000000 | 11334717 | 18238537 | 0.000000
09-04-2025 19:23:50000 | -1082559 | 108.2559 | 51172612 | 233510.27 | 267978943 | 99888466 | 49989140 | 0.000000 | 11405255 | 18388703 | 0.000000
09-04-2025 19:23:55000 | -1080232 | 108.0232 | 50052842 | 233535.77 | 267361786 | 99892822 | 49996471 | 0.000000 | 11476340 | 18539025 | 0.000000
09-04-2025 19:24:00000 | -1058182 | 105.8182 | 49993467 | 233757.45 | 261672333 | 99888580 | 50038631 | 0.000000 | 11545657 | 18687266 | 0.000000
09-04-2025 19:24:05000 | -1042328 | 104.2328 | 47699453 | 233707.88 | 257785706 | 99895454 | 50064316 | 0.000000 | 11613184 | 18832834 | 0.000000
09-04-2025 19:24:10000 | -1043784 | 104.3784 | 51789487 | 233726.72 | 258170044 | 99877136 | 50046852 | 0.000000 | 11681434 | 18977500 | 0.000000
09-04-2025 19:24:15000 | -1053757 | 105.3757 | 52517036 | 233655.84 | 260719116 | 99876038 | 50034004 | 0.000000 | 11754655 | 19123563 | 0.000000
09-04-2025 19:24:20000 | -1061975 | 106.1975 | 51266519 | 233562.33 | 262838409 | 99883682 | 50023804 | 0.000000 | 11827487 | 19270688 | 0.000000
09-04-2025 19:24:25000 | -1067578 | 106.7578 | 52090454 | 233622.03 | 264162323 | 99881172 | 50016666 | 0.000000 | 11898848 | 19418801 | 0.000000
09-04-2025 19:24:30000 | -1073032 | 107.3032 | 51138496 | 233518.30 | 265615448 | 99886627 | 50004848 | 0.000000 | 11971295 | 19567643 | 0.000000
09-04-2025 19:24:35000 | -1078865 | 107.8865 | 53409268 | 233599.14 | 266990326 | 99877686 | 49975170 | 0.000000 | 12043738 | 19717066 | 0.000000
09-04-2025 19:24:40000 | -1078945 | 107.8945 | 51084082 | 233588.81 | 266994781 | 99888107 | 49959652 | 0.000000 | 12115618 | 19867082 | 0.000000
09-04-2025 19:24:45000 | -1058986 | 105.8986 | 48257769 | 233663.61 | 261953705 | 99896332 | 49998447 | 0.000000 | 12184618 | 20015533 | 0.000000
09-04-2025 19:24:50000 | -1042616 | 104.2616 | 42792949 | 233571.88 | 257952637 | 99915878 | 50036598 | 0.000000 | 12247134 | 20160980 | 0.000000
09-04-2025 19:24:55000 | -1041619 | 104.1619 | 44178594 | 233532.72 | 257766418 | 99910179 | 50025887 | 0.000000 | 12307021 | 20305377 | 0.000000
09-04-2025 19:25:00000 | -1048873 | 104.8873 | 45889956 | 233518.42 | 259588440 | 99904427 | 50009346 | 0.000000 | 12370273 | 20450992 | 0.000000
09-04-2025 19:25:05000 | -1058224 | 105.8224 | 45179854 | 233437.20 | 261982849 | 99908989 | 49990932 | 0.000000 | 12433544 | 20597537 | 0.000000
09-04-2025 19:25:10000 | -1062737 | 106.2737 | 48344907 | 233568.91 | 262985260 | 99896690 | 49990368 | 0.000000 | 12499315 | 20745137 | 0.000000
09-04-2025 19:25:15000 | -1058551 | 105.8551 | 45627163 | 233520.36 | 261977203 | 99907234 | 50003662 | 0.000000 | 12565417 | 20892521 | 0.000000
09-04-2025 19:25:20000 | -1053640 | 105.364 | 46619175 | 233630.39 | 260650787 | 99902260 | 50016624 | 0.000000 | 12629330 | 21039223 | 0.000000
09-04-2025 19:25:25000 | -1039671 | 103.9671 | 46948125 | 233692.56 | 257136414 | 99898201 | 50044060 | 0.000000 | 12695212 | 21184324 | 0.000000
09-04-2025 19:25:30000 | -1033856 | 103.3856 | 44654307 | 233601.72 | 255778168 | 99906853 | 50059067 | 0.000000 | 12757561 | 21327795 | 0.000000
09-04-2025 19:25:35000 | -1044774 | 104.4774 | 45736167 | 233520.91 | 258572906 | 99904320 | 50039082 | 0.000000 | 12819258 | 21472094 | 0.000000
09-04-2025 19:25:40000 | -1053485 | 105.3485 | 50252578 | 233619.33 | 260668671 | 99886421 | 50029625 | 0.000000 | 12885276 | 21618041 | 0.000000
09-04-2025 19:25:45000 | -1056743 | 105.6743 | 52001094 | 233645.56 | 261461975 | 99879143 | 50042778 | 0.000000 | 12956301 | 21764652 | 0.000000
09-04-2025 19:25:50000 | -1052403 | 105.2403 | 48800557 | 233610.80 | 260391907 | 99892662 | 50038185 | 0.000000 | 13025032 | 21910943 | 0.000000
09-04-2025 19:25:55000 | -1052879 | 105.2879 | 50112930 | 233685.36 | 260440002 | 99886925 | 50035580 | 0.000000 | 13092787 | 22057260 | 0.000000
09-04-2025 19:26:00000 | -1047282 | 104.7282 | 50181240 | 233682.72 | 259062500 | 99885399 | 50054722 | 0.000000 | 13164045 | 22203152 | 0.000000
09-04-2025 19:26:05000 | -1045989 | 104.5989 | 50098335 | 233691.95 | 258734436 | 99885498 | 50059017 | 0.000000 | 13233160 | 22348490 | 0.000000
09-04-2025 19:26:10000 | -1047234 | 104.7234 | 49229536 | 233665.81 | 259057983 | 99889687 | 50047642 | 0.000000 | 13301257 | 22493939 | 0.000000
09-04-2025 19:26:15000 | -1044450 | 104.445 | 50531523 | 233681.91 | 258368042 | 99883171 | 50062729 | 0.000000 | 13371970 | 22638959 | 0.000000
09-04-2025 19:26:20000 | -1054750 | 105.475 | 51451348 | 233587.34 | 261026520 | 99881233 | 50049179 | 0.000000 | 13442048 | 22784643 | 0.000000
09-04-2025 19:26:25000 | -1063753 | 106.3753 | 55275679 | 233669.09 | 263204285 | 99865265 | 50032951 | 0.000000 | 13516729 | 22931887 | 0.000000
09-04-2025 19:26:30000 | -1067526 | 106.7526 | 54745278 | 233643.14 | 264158752 | 99868767 | 50021896 | 0.000000 | 13593285 | 23080072 | 0.000000
09-04-2025 19:26:35000 | -1064824 | 106.4824 | 52583535 | 233642.44 | 263464966 | 99878288 | 50017063 | 0.000000 | 13668151 | 23228125 | 0.000000
09-04-2025 19:26:40000 | -1075096 | 107.5096 | 49460986 | 233479.33 | 266150543 | 99894341 | 49986206 | 0.000000 | 13738458 | 23377230 | 0.000000
09-04-2025 19:26:45000 | -1069977 | 106.9977 | 51336909 | 233639.61 | 264729309 | 99885094 | 49991020 | 0.000000 | 13809463 | 23526480 | 0.000000
09-04-2025 19:26:50000 | -1059632 | 105.9632 | 48308433 | 233607.09 | 262173279 | 99896240 | 50017719 | 0.000000 | 13879104 | 23674092 | 0.000000
09-04-2025 19:26:55000 | -1062597 | 106.2597 | 47388867 | 233542.75 | 262967438 | 99900703 | 49996983 | 0.000000 | 13943837 | 23821395 | 0.000000
09-04-2025 19:27:00000 | -1058488 | 105.8488 | 50615928 | 233686.53 | 261831146 | 99885864 | 50010086 | 0.000000 | 14010735 | 23968791 | 0.000000
09-04-2025 19:27:05000 | -1049558 | 104.9558 | 46251270 | 233591.92 | 259679626 | 99903046 | 50033302 | 0.000000 | 14077074 | 24114992 | 0.000000
09-04-2025 19:27:10000 | -1044385 | 104.4385 | 48266050 | 233659.30 | 258350555 | 99893379 | 50038948 | 0.000000 | 14142679 | 24260332 | 0.000000
09-04-2025 19:27:15000 | -1040513 | 104.0513 | 48661025 | 233688.16 | 257368439 | 99890823 | 50051613 | 0.000000 | 14209637 | 24404912 | 0.000000
09-04-2025 19:27:20000 | -1037297 | 103.7297 | 48771035 | 233658.89 | 256608521 | 99889648 | 50067650 | 0.000000 | 14277719 | 24549211 | 0.000000
09-04-2025 19:27:25000 | -1039254 | 103.9254 | 50072690 | 233697.44 | 257066345 | 99884132 | 50071255 | 0.000000 | 14345503 | 24693461 | 0.000000
09-04-2025 19:27:30000 | -1047482 | 104.7482 | 50611626 | 233626.25 | 259182007 | 99883476 | 50056137 | 0.000000 | 14415675 | 24838754 | 0.000000
09-04-2025 19:27:35000 | -1053122 | 105.3122 | 51923105 | 233635.39 | 260577026 | 99878677 | 50052227 | 0.000000 | 14488169 | 24985094 | 0.000000
09-04-2025 19:27:40000 | -1058073 | 105.8073 | 50106880 | 233597.33 | 261820587 | 99888054 | 50047703 | 0.000000 | 14557460 | 25131553 | 0.000000
09-04-2025 19:27:45000 | -1072458 | 107.2458 | 51144849 | 233504.23 | 265489441 | 99886482 | 50008904 | 0.000000 | 14627415 | 25279414 | 0.000000
09-04-2025 19:27:50000 | -1078763 | 107.8763 | 54089170 | 233603.45 | 266968262 | 99874535 | 49994682 | 0.000000 | 14700721 | 25429051 | 0.000000
09-04-2025 19:27:55000 | -1070403 | 107.0403 | 50646890 | 233609.03 | 264856995 | 99888252 | 50002125 | 0.000000 | 14773176 | 25578453 | 0.000000
09-04-2025 19:28:00000 | -1057387 | 105.7387 | 46950415 | 233609.36 | 261606201 | 99901566 | 50025414 | 0.000000 | 14841140 | 25726082 | 0.000000
09-04-2025 19:28:05000 | -1056386 | 105.6386 | 46205190 | 233591.97 | 261365692 | 99904480 | 50018513 | 0.000000 | 14904598 | 25872846 | 0.000000
09-04-2025 19:28:10000 | -1046730 | 104.673 | 44800215 | 233587.56 | 258971375 | 99908531 | 50045155 | 0.000000 | 14968365 | 26018609 | 0.000000
09-04-2025 19:28:15000 | -1049031 | 104.9031 | 43031475 | 233436.02 | 259691711 | 99915970 | 50027866 | 0.000000 | 15029681 | 26164180 | 0.000000
09-04-2025 19:28:20000 | -1054757 | 105.4757 | 45471909 | 233522.84 | 261034485 | 99907204 | 50014618 | 0.000000 | 15090623 | 26310338 | 0.000000
09-04-2025 19:28:25000 | -1054332 | 105.4332 | 48799385 | 233634.50 | 260851807 | 99893059 | 50023422 | 0.000000 | 15156083 | 26456633 | 0.000000
09-04-2025 19:28:30000 | -1042280 | 104.228 | 48546133 | 233727.50 | 257763977 | 99891708 | 50051277 | 0.000000 | 15222346 | 26601906 | 0.000000
09-04-2025 19:28:35000 | -1041306 | 104.1306 | 47160967 | 233635.52 | 257604309 | 99897598 | 50056110 | 0.000000 | 15287985 | 26746379 | 0.000000
09-04-2025 19:28:40000 | -1052103 | 105.2103 | 52245371 | 233652.55 | 260312653 | 99876930 | 50044052 | 0.000000 | 15357129 | 26891904 | 0.000000
09-04-2025 19:28:45000 | -1055488 | 105.5488 | 52275835 | 233645.94 | 261154083 | 99877579 | 50038277 | 0.000000 | 15430106 | 27038465 | 0.000000
09-04-2025 19:28:50000 | -1059378 | 105.9378 | 48509448 | 233510.41 | 262221497 | 99895325 | 50030014 | 0.000000 | 15499659 | 27185080 | 0.000000
09-04-2025 19:28:55000 | -1075805 | 107.5805 | 49106162 | 233420.19 | 266390167 | 99895988 | 49989029 | 0.000000 | 15567361 | 27333412 | 0.000000
09-04-2025 19:29:00000 | -1086326 | 108.6326 | 49549604 | 233398.92 | 269019623 | 99896141 | 49951447 | 0.000000 | 15636138 | 27483646 | 0.000000
09-04-2025 19:29:05000 | -1090336 | 109.0336 | 52583159 | 233551.59 | 269867340 | 99883911 | 49944782 | 0.000000 | 15706888 | 27635109 | 0.000000
09-04-2025 19:29:10000 | -1078521 | 107.8521 | 47643584 | 233511.70 | 266939697 | 99902573 | 49970207 | 0.000000 | 15776217 | 27785770 | 0.000000
09-04-2025 19:29:15000 | -1066203 | 106.6203 | 43593335 | 233479.97 | 263888977 | 99916519 | 49972851 | 0.000000 | 15838298 | 27934412 | 0.000000
09-04-2025 19:29:20000 | -1053503 | 105.3503 | 41471187 | 233517.16 | 260690186 | 99922607 | 49987827 | 0.000000 | 15897318 | 28081518 | 0.000000
09-04-2025 19:29:25000 | -1032492 | 103.2492 | 41303403 | 233634.72 | 255368591 | 99920082 | 50036430 | 0.000000 | 15953816 | 28226072 | 0.000000
09-04-2025 19:29:30000 | -1023458 | 102.3458 | 41389102 | 233593.02 | 253188171 | 99918327 | 50053928 | 0.000000 | 16011019 | 28368855 | 0.000000
09-04-2025 19:29:35000 | -1021679 | 102.1679 | 42198257 | 233591.02 | 252755905 | 99914810 | 50059811 | 0.000000 | 16070018 | 28511133 | 0.000000
09-04-2025 19:29:40000 | -1034442 | 103.4442 | 44848921 | 233525.14 | 256006744 | 99906143 | 50043900 | 0.000000 | 16131627 | 28653996 | 0.000000
09-04-2025 19:29:45000 | -1040165 | 104.0165 | 48953887 | 233639.91 | 257338562 | 99889435 | 50047237 | 0.000000 | 16198003 | 28798377 | 0.000000
09-04-2025 19:29:50000 | -1042510 | 104.251 | 49987324 | 233653.05 | 257915436 | 99885246 | 50076538 | 0.000000 | 16267783 | 28942977 | 0.000000
09-04-2025 19:29:55000 | -1039503 | 103.9503 | 48826299 | 233641.16 | 257173859 | 99889870 | 50087048 | 0.000000 | 16336777 | 29087063 | 0.000000
09-04-2025 19:30:00000 | -1052399 | 105.2399 | 49999312 | 233578.42 | 260443115 | 99887329 | 50063267 | 0.000000 | 16405836 | 29232398 | 0.000000
09-04-2025 19:30:05000 | -1065498 | 106.5498 | 54136128 | 233610.14 | 263688263 | 99871178 | 50037941 | 0.000000 | 7305836 | 147357849 | 0.000000
09-04-2025 19:30:10000 | -1075611 | 107.5611 | 51812383 | 233498.09 | 266283020 | 99884186 | 50015045 | 0.000000 | 14657528 | 296126740 | 0.000000
09-04-2025 19:30:15000 | -1086863 | 108.6863 | 50774194 | 233435.16 | 269125244 | 99891060 | 49976639 | 0.000000 | 21729650 | 446396942 | 0.000000
09-04-2025 19:30:20000 | -1088997 | 108.8997 | 50448066 | 233469.11 | 269606720 | 99892868 | 49973476 | 0.000000 | 28755663 | 597522156 | 0.000000
09-04-2025 19:30:25000 | -1087620 | 108.762 | 47314585 | 233434.58 | 269277832 | 99905510 | 49970184 | 0.000000 | 35388115 | 748635376 | 0.000000
09-04-2025 19:30:30000 | -1081566 | 108.1566 | 44527593 | 233422.22 | 267760895 | 99915359 | 49969322 | 0.000000 | 41683266 | 899118958 | 0.000000
09-04-2025 19:30:35000 | -1071397 | 107.1397 | 42413765 | 233443.05 | 265204254 | 99921738 | 49973103 | 0.000000 | 47593010 | 10484828 | 0.000000
09-04-2025 19:30:40000 | -1061763 | 106.1763 | 41465313 | 233459.70 | 262796051 | 99923828 | 49975445 | 0.000000 | 53336445 | 11966389 | 0.000000
09-04-2025 19:30:45000 | -1063565 | 106.3565 | 38916792 | 233318.06 | 263375641 | 99933121 | 49965923 | 0.000000 | 58799870 | 13440090 | 0.000000
09-04-2025 19:30:50000 | -1066039 | 106.6039 | 40636250 | 233338.45 | 263983307 | 99927429 | 49953350 | 0.000000 | 64341881 | 14917906 | 0.000000
09-04-2025 19:30:55000 | -1059802 | 105.9802 | 41965796 | 233462.91 | 262310699 | 99921692 | 49975674 | 0.000000 | 70162102 | 16394893 | 0.000000
09-04-2025 19:31:00000 | -1042691 | 104.2691 | 39373911 | 233498.03 | 258019867 | 99928780 | 50023163 | 0.000000 | 75849731 | 17853182 | 0.000000
09-04-2025 19:31:05000 | -1027844 | 102.7844 | 40342214 | 233593.08 | 254258362 | 99923065 | 50054279 | 0.000000 | 81214622 | 19284672 | 0.000000
09-04-2025 19:31:10000 | -1034682 | 103.4682 | 42515122 | 233519.39 | 256047180 | 99915688 | 50030994 | 0.000000 | 86890755 | 20716492 | 0.000000
09-04-2025 19:31:15000 | -1040934 | 104.0934 | 45301406 | 233537.38 | 257601410 | 99905434 | 50036816 | 0.000000 | 93092987 | 22159810 | 0.000000
09-04-2025 19:31:20000 | -1045082 | 104.5082 | 45462119 | 233516.45 | 258650452 | 99905518 | 50048901 | 0.000000 | 99434593 | 23609163 | 0.000000
09-04-2025 19:31:25000 | -1051894 | 105.1894 | 46156431 | 233491.20 | 260370087 | 99903870 | 50040554 | 0.000000 | 105811005 | 25067451 | 0.000000
09-04-2025 19:31:30000 | -1056564 | 105.6564 | 47459043 | 233513.13 | 261512054 | 99899269 | 50021343 | 0.000000 | 112301399 | 26530825 | 0.000000
09-04-2025 19:31:35000 | -1064114 | 106.4114 | 47566167 | 233475.88 | 263420044 | 99900246 | 50010750 | 0.000000 | 118846703 | 28004556 | 0.000000
09-04-2025 19:31:40000 | -1061188 | 106.1188 | 48542603 | 233565.06 | 262607880 | 99895538 | 50024044 | 0.000000 | 125506210 | 29481660 | 0.000000
09-04-2025 19:31:45000 | -1051244 | 105.1244 | 45115200 | 233549.80 | 260134430 | 99908035 | 50049007 | 0.000000 | 132061096 | 30948594 | 0.000000
09-04-2025 19:31:50000 | -1053018 | 105.3018 | 45899771 | 233555.59 | 260573242 | 99905136 | 50038738 | 0.000000 | 138283768 | 32412400 | 0.000000
09-04-2025 19:31:55000 | -1056400 | 105.64 | 45941235 | 233493.69 | 261479126 | 99905571 | 50036526 | 0.000000 | 144750504 | 33877346 | 0.000000
09-04-2025 19:32:00000 | -1058639 | 105.8639 | 44799873 | 233441.33 | 262077271 | 99910576 | 50022270 | 0.000000 | 151018082 | 35344246 | 0.000000
09-04-2025 19:32:05000 | -1063280 | 106.328 | 44635728 | 233412.39 | 263254242 | 99912003 | 50015957 | 0.000000 | 157322083 | 36818184 | 0.000000
09-04-2025 19:32:10000 | -1065015 | 106.5015 | 47434810 | 233535.00 | 263578217 | 99900963 | 50012993 | 0.000000 | 163732132 | 38297583 | 0.000000
09-04-2025 19:32:15000 | -1061894 | 106.1894 | 47482217 | 233551.17 | 262785828 | 99900177 | 50024807 | 0.000000 | 170298386 | 39775063 | 0.000000
09-04-2025 19:32:20000 | -1065760 | 106.576 | 45142837 | 233428.27 | 263855103 | 99910416 | 50013107 | 0.000000 | 176646667 | 41251455 | 0.000000
09-04-2025 19:32:25000 | -1070669 | 107.0669 | 48562666 | 233506.44 | 265021240 | 99897293 | 50003819 | 0.000000 | 183204865 | 42734380 | 0.000000
09-04-2025 19:32:30000 | -1068601 | 106.8601 | 45161309 | 233416.48 | 264569702 | 99910812 | 49992928 | 0.000000 | 189645782 | 44218726 | 0.000000
09-04-2025 19:32:35000 | -1068897 | 106.8897 | 43548179 | 233407.17 | 264636322 | 99917114 | 49979267 | 0.000000 | 195743210 | 45703721 | 0.000000
09-04-2025 19:32:40000 | -1065167 | 106.5167 | 41015820 | 233364.05 | 263739807 | 99925941 | 49969967 | 0.000000 | 201682129 | 47186182 | 0.000000
09-04-2025 19:32:45000 | -1062746 | 106.2746 | 39726426 | 233361.88 | 263131897 | 99930206 | 49967762 | 0.000000 | 207306198 | 48663047 | 0.000000
09-04-2025 19:32:50000 | -1065158 | 106.5158 | 39265842 | 233325.09 | 263764709 | 99932121 | 49961845 | 0.000000 | 212812500 | 50140059 | 0.000000
09-04-2025 19:32:55000 | -1054693 | 105.4693 | 40091209 | 233465.47 | 261028961 | 99927834 | 49995678 | 0.000000 | 218436020 | 51610659 | 0.000000
09-04-2025 19:33:00000 | -1035396 | 103.5396 | 37421650 | 233471.53 | 256230011 | 99934753 | 50044651 | 0.000000 | 223937897 | 53054941 | 0.000000
09-04-2025 19:33:05000 | -1028576 | 102.8576 | 38647109 | 233511.03 | 254512680 | 99929489 | 50050362 | 0.000000 | 229162445 | 54486333 | 0.000000
09-04-2025 19:33:10000 | -1033877 | 103.3877 | 40433743 | 233418.30 | 255939133 | 99923615 | 50045513 | 0.000000 | 234756058 | 55919395 | 0.000000
09-04-2025 19:33:15000 | -1044904 | 104.4904 | 44256680 | 233465.56 | 258652191 | 99910423 | 50041145 | 0.000000 | 240697678 | 57365850 | 0.000000
09-04-2025 19:33:20000 | -1053988 | 105.3988 | 44352041 | 233385.34 | 260991150 | 99911583 | 50031013 | 0.000000 | 246909576 | 58826914 | 0.000000
09-04-2025 19:33:25000 | -1063057 | 106.3057 | 44962227 | 233454.08 | 263160187 | 99910675 | 50007236 | 0.000000 | 252999329 | 60301538 | 0.000000
09-04-2025 19:33:30000 | -1066897 | 106.6897 | 45064736 | 233452.38 | 264107147 | 99910912 | 50007744 | 0.000000 | 259271210 | 61784175 | 0.000000
09-04-2025 19:33:35000 | -1062612 | 106.2612 | 44137197 | 233476.64 | 263011841 | 99913849 | 50024754 | 0.000000 | 265540558 | 63262490 | 0.000000
09-04-2025 19:33:40000 | -1069218 | 106.9218 | 43015313 | 233369.00 | 264754303 | 99919174 | 50010979 | 0.000000 | 271515228 | 64741045 | 0.000000
09-04-2025 19:33:45000 | -1073838 | 107.3838 | 45186621 | 233443.70 | 265833649 | 99911583 | 49996269 | 0.000000 | 277550323 | 66228315 | 0.000000
09-04-2025 19:33:50000 | -1068730 | 106.873 | 43436553 | 233436.67 | 264562531 | 99917511 | 49996674 | 0.000000 | 283708374 | 67716914 | 0.000000
09-04-2025 19:33:55000 | -1057598 | 105.7598 | 41518208 | 233476.47 | 261747894 | 99923035 | 50017139 | 0.000000 | 289497498 | 69190659 | 0.000000
09-04-2025 19:34:00000 | -1054036 | 105.4036 | 41915190 | 233460.91 | 260887726 | 99921028 | 50017738 | 0.000000 | 295294952 | 70656450 | 0.000000
09-04-2025 19:34:05000 | -1052299 | 105.2299 | 41549600 | 233443.61 | 260474640 | 99922142 | 50017868 | 0.000000 | 301060181 | 72119702 | 0.000000
09-04-2025 19:34:10000 | -1054892 | 105.4892 | 39446133 | 233296.83 | 261260498 | 99930161 | 50009716 | 0.000000 | 306738037 | 73582441 | 0.000000
09-04-2025 19:34:15000 | -1058258 | 105.8258 | 39465940 | 233329.31 | 262056702 | 99930534 | 50012020 | 0.000000 | 312279358 | 75049380 | 0.000000
09-04-2025 19:34:20000 | -1058054 | 105.8054 | 37091277 | 233261.75 | 262059906 | 99938606 | 50005531 | 0.000000 | 317496643 | 76517563 | 0.000000
09-04-2025 19:34:25000 | -1061125 | 106.1125 | 40546770 | 233384.63 | 262713287 | 99927078 | 50006771 | 0.000000 | 322929657 | 77990674 | 0.000000
09-04-2025 19:34:30000 | -1053593 | 105.3593 | 42858604 | 233517.91 | 260729492 | 99917366 | 50031898 | 0.000000 | 328820221 | 79458384 | 0.000000
09-04-2025 19:34:35000 | -1038676 | 103.8676 | 42005034 | 233561.22 | 256986328 | 99918327 | 50056332 | 0.000000 | 334773041 | 80906328 | 0.000000
09-04-2025 19:34:40000 | -1043354 | 104.3354 | 43114058 | 233527.80 | 258188507 | 99914734 | 50052132 | 0.000000 | 340616364 | 82352402 | 0.000000
09-04-2025 19:34:45000 | -1055031 | 105.5031 | 43306450 | 233355.31 | 261266449 | 99915863 | 50029602 | 0.000000 | 346676544 | 83809668 | 0.000000
09-04-2025 19:34:50000 | -1072956 | 107.2956 | 47459385 | 233383.30 | 265709290 | 99902321 | 49991207 | 0.000000 | 353019684 | 85290244 | 0.000000
09-04-2025 19:34:55000 | -1079254 | 107.9254 | 46525820 | 233379.09 | 267260864 | 99907211 | 49974171 | 0.000000 | 359521698 | 86788838 | 0.000000
09-04-2025 19:35:00000 | -1060097 | 106.0097 | 43818081 | 233533.48 | 262324463 | 99914680 | 50021667 | 0.000000 | 365864502 | 88273584 | 0.000000
09-04-2025 19:35:05000 | -1046433 | 104.6433 | 40178237 | 233515.95 | 258931702 | 99926369 | 50049534 | 0.000000 | 371542847 | 89734814 | 0.000000
09-04-2025 19:35:10000 | -1042031 | 104.2031 | 39549736 | 233481.44 | 257877686 | 99928047 | 50046143 | 0.000000 | 377074493 | 91184033 | 0.000000
09-04-2025 19:35:15000 | -1047886 | 104.7886 | 43352710 | 233471.31 | 259372559 | 99914528 | 50035141 | 0.000000 | 382838684 | 92634727 | 0.000000
09-04-2025 19:35:20000 | -1052531 | 105.2531 | 43947554 | 233457.28 | 260541870 | 99912941 | 50030743 | 0.000000 | 388846405 | 94093506 | 0.000000
09-04-2025 19:35:25000 | -1053735 | 105.3735 | 42750273 | 233395.39 | 260897827 | 99917801 | 50029812 | 0.000000 | 394906158 | 95554912 | 0.000000
09-04-2025 19:35:30000 | -1063042 | 106.3042 | 44597310 | 233420.27 | 263186371 | 99912117 | 50005024 | 0.000000 | 400892944 | 97026904 | 0.000000
09-04-2025 19:35:35000 | -1071136 | 107.1136 | 45403887 | 233437.28 | 265177979 | 99910278 | 49985817 | 0.000000 | 407141296 | 98514131 | 0.000000
09-04-2025 19:35:40000 | -1070027 | 107.0027 | 43694131 | 233431.73 | 264893188 | 99916733 | 49984547 | 0.000000 | 413419067 | 10000248 | 0.000000
09-04-2025 19:35:45000 | -1065562 | 106.5562 | 42354116 | 233415.25 | 263794403 | 99921097 | 49983383 | 0.000000 | 419347809 | 10148503 | 0.000000
09-04-2025 19:35:50000 | -1059199 | 105.9199 | 42474141 | 233464.03 | 262166138 | 99919693 | 49998096 | 0.000000 | 425367798 | 10296114 | 0.000000
09-04-2025 19:35:55000 | -1050733 | 105.0733 | 41680122 | 233508.08 | 260020691 | 99921417 | 50017151 | 0.000000 | 431213623 | 10442406 | 0.000000
09-04-2025 19:36:00000 | -1049042 | 104.9042 | 39739072 | 233391.77 | 259710205 | 99928329 | 50008972 | 0.000000 | 436850098 | 10587966 | 0.000000
09-04-2025 19:36:05000 | -1062583 | 106.2583 | 43853979 | 233395.72 | 263093231 | 99914940 | 49978699 | 0.000000 | 442631775 | 10734891 | 0.000000
09-04-2025 19:36:10000 | -1051674 | 105.1674 | 43547271 | 233516.25 | 260260773 | 99914383 | 50007507 | 0.000000 | 448776093 | 10881770 | 0.000000
09-04-2025 19:36:15000 | -1042200 | 104.22 | 38029490 | 233411.97 | 257986328 | 99933495 | 50035011 | 0.000000 | 454423706 | 11027067 | 0.000000
09-04-2025 19:36:20000 | -1057142 | 105.7142 | 37900100 | 233240.63 | 261871582 | 99935799 | 50002205 | 0.000000 | 459785645 | 11173116 | 0.000000
09-04-2025 19:36:25000 | -1070057 | 107.0057 | 42251504 | 233293.06 | 265043304 | 99922134 | 49966427 | 0.000000 | 465351166 | 11321068 | 0.000000
09-04-2025 19:36:30000 | -1068611 | 106.8611 | 43250298 | 233430.80 | 264536957 | 99918198 | 49976662 | 0.000000 | 471327393 | 11469937 | 0.000000
09-04-2025 19:36:35000 | -1057606 | 105.7606 | 37283914 | 233339.73 | 261869965 | 99937920 | 49986591 | 0.000000 | 476779083 | 11617341 | 0.000000
09-04-2025 19:36:40000 | -1048394 | 104.8394 | 37152388 | 233407.25 | 259509644 | 99937271 | 50004433 | 0.000000 | 481951294 | 11763644 | 0.000000
09-04-2025 19:36:45000 | -1042487 | 104.2487 | 36041230 | 233346.23 | 258106812 | 99940292 | 50025707 | 0.000000 | 487107635 | 11908538 | 0.000000
09-04-2025 19:36:50000 | -1049930 | 104.993 | 35706248 | 233274.13 | 260026001 | 99942223 | 50008762 | 0.000000 | 491890015 | 12053710 | 0.000000
09-04-2025 19:36:55000 | -1056128 | 105.6128 | 38919895 | 233337.05 | 261516541 | 99932167 | 49998425 | 0.000000 | 497127075 | 12200174 | 0.000000
09-04-2025 19:37:00000 | -1065980 | 106.598 | 40297073 | 233273.52 | 264037262 | 99928627 | 49979042 | 0.000000 | 502653381 | 12347608 | 0.000000
09-04-2025 19:37:05000 | -1072704 | 107.2704 | 45847798 | 233416.67 | 265591705 | 99908791 | 49959236 | 0.000000 | 508797394 | 12496616 | 0.000000
09-04-2025 19:37:10000 | -1070100 | 107.01 | 43871084 | 233394.44 | 264954041 | 99916069 | 49958599 | 0.000000 | 515058044 | 12645515 | 0.000000
09-04-2025 19:37:15000 | -1067707 | 106.7707 | 42688398 | 233416.78 | 264323578 | 99920174 | 49952446 | 0.000000 | 521029785 | 12793867 | 0.000000
09-04-2025 19:37:20000 | -1064113 | 106.4113 | 45242754 | 233523.09 | 263341034 | 99909737 | 49955181 | 0.000000 | 527171082 | 12941825 | 0.000000
09-04-2025 19:37:25000 | -1065549 | 106.5549 | 42517842 | 233415.58 | 263798462 | 99920486 | 49933277 | 0.000000 | 533043640 | 13089585 | 0.000000
09-04-2025 19:37:30000 | -1060518 | 106.0518 | 42628003 | 233429.14 | 262535950 | 99919312 | 49938160 | 0.000000 | 539080811 | 13237255 | 0.000000
09-04-2025 19:37:35000 | -1058530 | 105.853 | 39513035 | 233380.63 | 262069183 | 99930405 | 49940216 | 0.000000 | 544666321 | 13384193 | 0.000000
09-04-2025 19:37:40000 | -1053848 | 105.3848 | 40092183 | 233439.11 | 260848969 | 99927711 | 49948509 | 0.000000 | 550211304 | 13531106 | 0.000000
09-04-2025 19:37:45000 | -1044961 | 104.4961 | 41219814 | 233529.77 | 258562897 | 99922287 | 49970318 | 0.000000 | 555792908 | 13676919 | 0.000000
09-04-2025 19:37:50000 | -1038898 | 103.8898 | 38486006 | 233450.08 | 257127502 | 99931458 | 49978020 | 0.000000 | 561305908 | 13821602 | 0.000000
09-04-2025 19:37:55000 | -1048357 | 104.8357 | 41379634 | 233402.84 | 259544922 | 99922195 | 49957394 | 0.000000 | 566925293 | 13966686 | 0.000000
09-04-2025 19:38:00000 | -1065878 | 106.5878 | 43621689 | 233364.52 | 263941132 | 99916359 | 49922886 | 0.000000 | 572846863 | 14113938 | 0.000000
09-04-2025 19:38:05000 | -1071668 | 107.1668 | 46449912 | 233416.00 | 265344788 | 99906197 | 49922577 | 0.000000 | 579249634 | 14262543 | 0.000000
09-04-2025 19:38:10000 | -1068486 | 106.8486 | 44247969 | 233437.08 | 264510010 | 99914360 | 49928421 | 0.000000 | 585573608 | 14411154 | 0.000000
09-04-2025 19:38:15000 | -1073533 | 107.3533 | 42219307 | 233355.03 | 265828796 | 99922760 | 49911869 | 0.000000 | 591399475 | 14559590 | 0.000000
09-04-2025 19:38:20000 | -1072137 | 107.2137 | 42950825 | 233409.22 | 265429840 | 99919853 | 49902336 | 0.000000 | 597231628 | 14708544 | 0.000000
09-04-2025 19:38:25000 | -1063872 | 106.3872 | 42851602 | 233444.94 | 263348358 | 99918976 | 49911522 | 0.000000 | 603228516 | 14856781 | 0.000000
09-04-2025 19:38:30000 | -1044834 | 104.4834 | 39135566 | 233485.03 | 258561127 | 99929924 | 49954102 | 0.000000 | 608890503 | 15002870 | 0.000000
09-04-2025 19:38:35000 | -1038454 | 103.8454 | 35938315 | 233364.83 | 257089783 | 99940170 | 49963516 | 0.000000 | 614118774 | 15147208 | 0.000000
09-04-2025 19:38:40000 | -1041646 | 104.1646 | 37965947 | 233384.47 | 257873932 | 99933640 | 49957607 | 0.000000 | 619293091 | 15291645 | 0.000000
09-04-2025 19:38:45000 | -1049261 | 104.9261 | 41148232 | 233417.94 | 259749695 | 99923195 | 49958626 | 0.000000 | 624805908 | 15437072 | 0.000000
09-04-2025 19:38:50000 | -1053052 | 105.3052 | 41775884 | 233396.00 | 260716583 | 99921402 | 49955734 | 0.000000 | 630636353 | 15583438 | 0.000000
09-04-2025 19:38:55000 | -1053427 | 105.3427 | 41235425 | 233428.05 | 260769928 | 99923477 | 49961731 | 0.000000 | 636356140 | 15729580 | 0.000000
09-04-2025 19:39:00000 | -1051995 | 105.1995 | 40724854 | 233412.08 | 260427887 | 99925156 | 49963337 | 0.000000 | 642059509 | 15875580 | 0.000000
09-04-2025 19:39:05000 | -1039278 | 103.9278 | 39407954 | 233488.11 | 257188812 | 99928185 | 49986286 | 0.000000 | 647564636 | 16020583 | 0.000000
09-04-2025 19:39:10000 | -1041374 | 104.1374 | 39298174 | 233415.59 | 257786560 | 99928871 | 49991043 | 0.000000 | 653020569 | 16164841 | 0.000000
09-04-2025 19:39:15000 | -1063486 | 106.3486 | 43317261 | 233302.77 | 263415863 | 99917152 | 49934177 | 0.000000 | 658800293 | 16311299 | 0.000000
09-04-2025 19:39:20000 | -1078207 | 107.8207 | 44582603 | 233310.16 | 267061157 | 99914619 | 49905655 | 0.000000 | 664930847 | 16460777 | 0.000000
09-04-2025 19:39:25000 | -1073924 | 107.3924 | 42981538 | 233371.70 | 265922852 | 99920006 | 49913342 | 0.000000 | 670963257 | 16610377 | 0.000000
09-04-2025 19:39:30000 | -1062631 | 106.2631 | 43294238 | 233516.16 | 262963806 | 99917107 | 49937096 | 0.000000 | 676921814 | 16758842 | 0.000000
09-04-2025 19:39:35000 | -1051351 | 105.1351 | 37532415 | 233370.50 | 260284729 | 99936340 | 49950722 | 0.000000 | 682476929 | 16904959 | 0.000000
09-04-2025 19:39:40000 | -1054687 | 105.4687 | 40532466 | 233419.17 | 261082306 | 99926239 | 49926254 | 0.000000 | 687882690 | 17051195 | 0.000000
09-04-2025 19:39:45000 | -1054511 | 105.4511 | 41432173 | 233451.89 | 261010590 | 99922905 | 49936523 | 0.000000 | 693567993 | 17197670 | 0.000000
09-04-2025 19:39:50000 | -1041096 | 104.1096 | 37576025 | 233408.56 | 257710602 | 99934929 | 49968792 | 0.000000 | 699051086 | 17342939 | 0.000000
09-04-2025 19:39:55000 | -1040692 | 104.0692 | 38881416 | 233428.11 | 257600220 | 99930283 | 49974937 | 0.000000 | 704354919 | 17487367 | 0.000000
09-04-2025 19:40:00000 | -1044251 | 104.4251 | 40024136 | 233404.02 | 258517700 | 99926628 | 49975643 | 0.000000 | 709840576 | 17632078 | 0.000000
09-04-2025 19:40:05000 | -1046930 | 104.693 | 43211025 | 233474.75 | 259130890 | 99914932 | 49984589 | 0.000000 | 715742188 | 17777334 | 0.000000
09-04-2025 19:40:10000 | -1050914 | 105.0914 | 41598486 | 233421.19 | 260159088 | 99921753 | 49978680 | 0.000000 | 721717102 | 17923148 | 0.000000
09-04-2025 19:40:15000 | -1060570 | 106.057 | 44264805 | 233394.67 | 262602417 | 99913017 | 49958790 | 0.000000 | 727718994 | 18069846 | 0.000000
09-04-2025 19:40:20000 | -1072347 | 107.2347 | 48180596 | 233452.39 | 265488220 | 99899216 | 49937073 | 0.000000 | 734181824 | 18218438 | 0.000000
09-04-2025 19:40:25000 | -1067287 | 106.7287 | 43964507 | 233413.30 | 264237427 | 99915268 | 49944195 | 0.000000 | 740583862 | 18366980 | 0.000000
09-04-2025 19:40:30000 | -1066221 | 106.6221 | 40680835 | 233346.19 | 264019440 | 99927292 | 49932877 | 0.000000 | 746378601 | 18514988 | 0.000000
09-04-2025 19:40:35000 | -1062791 | 106.2791 | 40116838 | 233359.91 | 263149506 | 99928833 | 49938393 | 0.000000 | 751933533 | 18662422 | 0.000000
09-04-2025 19:40:40000 | -1059900 | 105.99 | 40114902 | 233399.41 | 262390289 | 99928452 | 49939747 | 0.000000 | 757432922 | 18809824 | 0.000000
09-04-2025 19:40:45000 | -1055860 | 105.586 | 39798989 | 233393.48 | 261394348 | 99929039 | 49948795 | 0.000000 | 763033936 | 18956785 | 0.000000
09-04-2025 19:40:50000 | -1049702 | 104.9702 | 38811021 | 233414.14 | 259841553 | 99931717 | 49956913 | 0.000000 | 768448120 | 19102951 | 0.000000
09-04-2025 19:40:55000 | -1046302 | 104.6302 | 40614126 | 233470.45 | 258954681 | 99924751 | 49966076 | 0.000000 | 773973572 | 19248416 | 0.000000
09-04-2025 19:41:00000 | -1051963 | 105.1963 | 40888074 | 233419.03 | 260413971 | 99924545 | 49952324 | 0.000000 | 779611633 | 19394330 | 0.000000
09-04-2025 19:41:05000 | -1051849 | 105.1849 | 40807988 | 233398.05 | 260408264 | 99924828 | 49954124 | 0.000000 | 785305603 | 19540494 | 0.000000
09-04-2025 19:41:10000 | -1052098 | 105.2098 | 40087459 | 233401.20 | 260460907 | 99927490 | 49955021 | 0.000000 | 790877258 | 19686531 | 0.000000
09-04-2025 19:41:15000 | -1046385 | 104.6385 | 40493574 | 233460.56 | 258984253 | 99925201 | 49964241 | 0.000000 | 796462036 | 19832121 | 0.000000
09-04-2025 19:41:20000 | -1038363 | 103.8363 | 39996533 | 233475.50 | 256981384 | 99925896 | 49978394 | 0.000000 | 801949646 | 19976951 | 0.000000
09-04-2025 19:41:25000 | -1040934 | 104.0934 | 40811572 | 233451.83 | 257651245 | 99923233 | 49989704 | 0.000000 | 807612854 | 20121297 | 0.000000
09-04-2025 19:41:30000 | -1052977 | 105.2977 | 42952036 | 233433.48 | 260669830 | 99916908 | 49969494 | 0.000000 | 813357666 | 20266811 | 0.000000
09-04-2025 19:41:35000 | -1065185 | 106.5185 | 43762842 | 233351.81 | 263787323 | 99915710 | 49938957 | 0.000000 | 819419373 | 20414160 | 0.000000
09-04-2025 19:41:40000 | -1065853 | 106.5853 | 44386582 | 233430.03 | 263870605 | 99913399 | 49936584 | 0.000000 | 825668396 | 20562705 | 0.000000
09-04-2025 19:41:45000 | -1062106 | 106.2106 | 41908867 | 233423.23 | 262925232 | 99922241 | 49943649 | 0.000000 | 831569336 | 20710246 | 0.000000
09-04-2025 19:41:50000 | -1074707 | 107.4707 | 44203579 | 233351.22 | 266143677 | 99915520 | 49907814 | 0.000000 | 837470215 | 20858830 | 0.000000
09-04-2025 19:41:55000 | -1074261 | 107.4261 | 42926128 | 233369.80 | 265999542 | 99920258 | 49906330 | 0.000000 | 843534668 | 21008205 | 0.000000
09-04-2025 19:42:00000 | -1066803 | 106.6803 | 40503789 | 233369.45 | 264132996 | 99928001 | 49912560 | 0.000000 | 849237732 | 21156795 | 0.000000
09-04-2025 19:42:05000 | -1047890 | 104.789 | 38656196 | 233473.19 | 259325348 | 99932030 | 49952084 | 0.000000 | 854695679 | 21303340 | 0.000000
09-04-2025 19:42:10000 | -1039538 | 103.9538 | 36529717 | 233379.42 | 257345551 | 99938316 | 49958771 | 0.000000 | 859864441 | 21447873 | 0.000000
09-04-2025 19:42:15000 | -1045704 | 104.5704 | 40510286 | 233439.03 | 258840027 | 99925049 | 49945072 | 0.000000 | 865190552 | 21592984 | 0.000000
09-04-2025 19:42:20000 | -1047470 | 104.747 | 40557344 | 233386.14 | 259336060 | 99925125 | 49951485 | 0.000000 | 870898804 | 21738479 | 0.000000
09-04-2025 19:42:25000 | -1047412 | 104.7412 | 41250361 | 233434.98 | 259273621 | 99922539 | 49950874 | 0.000000 | 876540771 | 21883992 | 0.000000
09-04-2025 19:42:30000 | -1042564 | 104.2564 | 40071816 | 233449.02 | 258049744 | 99926216 | 49960480 | 0.000000 | 882174805 | 22029133 | 0.000000
09-04-2025 19:42:35000 | -1044284 | 104.4284 | 41576768 | 233465.59 | 258471344 | 99920837 | 49964993 | 0.000000 | 887859619 | 22174018 | 0.000000
09-04-2025 19:42:40000 | -1054187 | 105.4187 | 45142832 | 233486.00 | 260938110 | 99908440 | 49968193 | 0.000000 | 893852844 | 22319604 | 0.000000
09-04-2025 19:42:45000 | -1061246 | 106.1246 | 45493745 | 233422.73 | 262749420 | 99908241 | 49951504 | 0.000000 | 900137207 | 22466338 | 0.000000
09-04-2025 19:42:50000 | -1060742 | 106.0742 | 46002065 | 233504.86 | 262545746 | 99906097 | 49957973 | 0.000000 | 906453064 | 22613656 | 0.000000
09-04-2025 19:42:55000 | -1050897 | 105.0897 | 43876211 | 233524.81 | 260061523 | 99912956 | 49981697 | 0.000000 | 912654602 | 22760135 | 0.000000
09-04-2025 19:43:00000 | -1045783 | 104.5783 | 41025205 | 233451.00 | 258851715 | 99923141 | 49985287 | 0.000000 | 918464539 | 22905350 | 0.000000
09-04-2025 19:43:05000 | -1059507 | 105.9507 | 42480845 | 233356.30 | 262366089 | 99919716 | 49943176 | 0.000000 | 924247620 | 23051486 | 0.000000
09-04-2025 19:43:10000 | -1070930 | 107.093 | 45893218 | 233386.11 | 265190125 | 99908302 | 49925480 | 0.000000 | 930517151 | 23199680 | 0.000000
09-04-2025 19:43:15000 | -1070329 | 107.0329 | 45297617 | 233451.94 | 264959076 | 99910568 | 49921589 | 0.000000 | 936877319 | 23348578 | 0.000000
09-04-2025 19:43:20000 | -1057870 | 105.787 | 43699512 | 233531.14 | 261778137 | 99914787 | 49945091 | 0.000000 | 943072632 | 23496012 | 0.000000
09-04-2025 19:43:25000 | -1046240 | 104.624 | 42990498 | 233558.63 | 258866364 | 99915688 | 49971741 | 0.000000 | 949088074 | 23641668 | 0.000000
09-04-2025 19:43:30000 | -1046400 | 104.64 | 42743389 | 233490.83 | 258978241 | 99916679 | 49969090 | 0.000000 | 954945618 | 23786664 | 0.000000
09-04-2025 19:43:35000 | -1054103 | 105.4103 | 44047666 | 233432.05 | 260962219 | 99912804 | 49954567 | 0.000000 | 960994263 | 23932287 | 0.000000
09-04-2025 19:43:40000 | -1051168 | 105.1168 | 44719463 | 233488.25 | 260177826 | 99909630 | 49957996 | 0.000000 | 967134644 | 24078420 | 0.000000
09-04-2025 19:43:45000 | -1046005 | 104.6005 | 43806206 | 233526.41 | 258853699 | 99912422 | 49969627 | 0.000000 | 973268921 | 24224111 | 0.000000
09-04-2025 19:43:50000 | -1053473 | 105.3473 | 44345425 | 233482.33 | 260751221 | 99911522 | 49952854 | 0.000000 | 979309387 | 24369953 | 0.000000
09-04-2025 19:43:55000 | -1063542 | 106.3542 | 45382095 | 233432.72 | 263305115 | 99909088 | 49931301 | 0.000000 | 985580933 | 24517012 | 0.000000
09-04-2025 19:44:00000 | -1071067 | 107.1067 | 47200044 | 233437.42 | 265181915 | 99903038 | 49910374 | 0.000000 | 992117554 | 24665479 | 0.000000
09-04-2025 19:44:05000 | -1063397 | 106.3397 | 44687627 | 233483.36 | 263207550 | 99911819 | 49924664 | 0.000000 | 998478638 | 24813523 | 0.000000
09-04-2025 19:44:10000 | -1061241 | 106.1241 | 42345181 | 233437.69 | 262701599 | 99920486 | 49930733 | 0.000000 | 10043770 | 24960980 | 0.000000
09-04-2025 19:44:15000 | -1049417 | 104.9417 | 40078398 | 233442.08 | 259750336 | 99927155 | 49951584 | 0.000000 | 10101201 | 25107465 | 0.000000
09-04-2025 19:44:20000 | -1041135 | 104.1135 | 39468997 | 233475.64 | 257661011 | 99928223 | 49965508 | 0.000000 | 10155322 | 25252484 | 0.000000
09-04-2025 19:44:25000 | -1046004 | 104.6004 | 40180193 | 233406.80 | 258947876 | 99926300 | 49955593 | 0.000000 | 10209662 | 25397299 | 0.000000
09-04-2025 19:44:30000 | -1052914 | 105.2914 | 42376899 | 233397.33 | 260687927 | 99919106 | 49943054 | 0.000000 | 10267858 | 25543324 | 0.000000
09-04-2025 19:44:35000 | -1058221 | 105.8221 | 45151377 | 233467.39 | 261948425 | 99909096 | 49936176 | 0.000000 | 10329286 | 25690164 | 0.000000
09-04-2025 19:44:40000 | -1054152 | 105.4152 | 44788848 | 233545.17 | 260852936 | 99909859 | 49947826 | 0.000000 | 10391715 | 25836967 | 0.000000
09-04-2025 19:44:45000 | -1040179 | 104.0179 | 44341831 | 233643.28 | 257289673 | 99909264 | 49988617 | 0.000000 | 10453483 | 25982443 | 0.000000
09-04-2025 19:44:50000 | -1032092 | 103.2092 | 43318755 | 233594.27 | 255335419 | 99912033 | 50014748 | 0.000000 | 10514121 | 26126094 | 0.000000
09-04-2025 19:44:55000 | -1041974 | 104.1974 | 45878447 | 233536.05 | 257867432 | 99903206 | 49988930 | 0.000000 | 10575331 | 26269898 | 0.000000
09-04-2025 19:45:00000 | -1062800 | 106.28 | 47145693 | 233413.59 | 263162201 | 99901756 | 49948925 | 0.000000 | 10639683 | 26416285 | 0.000000
09-04-2025 19:45:05000 | -1072188 | 107.2188 | 47742598 | 233405.92 | 265496979 | 99901009 | 49937687 | 0.000000 | 6664278 | 148322586 | 0.000000
09-04-2025 19:45:10000 | -1075730 | 107.573 | 46589004 | 233421.84 | 266340668 | 99906349 | 49924770 | 0.000000 | 13257364 | 297681488 | 0.000000
09-04-2025 19:45:15000 | -1071385 | 107.1385 | 45286260 | 233474.42 | 265194244 | 99910789 | 49931400 | 0.000000 | 19567034 | 446631683 | 0.000000
09-04-2025 19:45:20000 | -1053959 | 105.3959 | 43013042 | 233594.88 | 260731964 | 99916824 | 49954460 | 0.000000 | 25545366 | 594208313 | 0.000000
09-04-2025 19:45:25000 | -1042885 | 104.2885 | 39573916 | 233473.03 | 258098785 | 99928078 | 49975929 | 0.000000 | 31256231 | 739526733 | 0.000000
09-04-2025 19:45:30000 | -1041799 | 104.1799 | 39119705 | 233440.45 | 257861145 | 99929573 | 49964718 | 0.000000 | 36619610 | 884348938 | 0.000000
09-04-2025 19:45:35000 | -1054070 | 105.407 | 41276338 | 233376.52 | 260987396 | 99923416 | 49953712 | 0.000000 | 42235123 | 10301348 | 0.000000
09-04-2025 19:45:40000 | -1058691 | 105.8691 | 42679727 | 233418.13 | 262094513 | 99918839 | 49954010 | 0.000000 | 48104553 | 11768724 | 0.000000
09-04-2025 19:45:45000 | -1047520 | 104.752 | 42585342 | 233545.89 | 259194611 | 99917465 | 49981678 | 0.000000 | 54018311 | 13232097 | 0.000000
09-04-2025 19:45:50000 | -1037339 | 103.7339 | 40585232 | 233493.92 | 256713501 | 99923553 | 50004559 | 0.000000 | 59773544 | 14677471 | 0.000000
09-04-2025 19:45:55000 | -1039751 | 103.9751 | 42086338 | 233529.50 | 257285065 | 99918182 | 50004482 | 0.000000 | 65407875 | 16118322 | 0.000000
09-04-2025 19:46:00000 | -1043025 | 104.3025 | 43795483 | 233477.58 | 258168823 | 99911964 | 50003086 | 0.000000 | 71321190 | 17564271 | 0.000000
09-04-2025 19:46:05000 | -1053050 | 105.305 | 46061597 | 233485.11 | 260664215 | 99904472 | 49984715 | 0.000000 | 77606361 | 19024337 | 0.000000
09-04-2025 19:46:10000 | -1055735 | 105.5735 | 47887734 | 233544.86 | 261277283 | 99897285 | 49989761 | 0.000000 | 84248413 | 20491787 | 0.000000
09-04-2025 19:46:15000 | -1049113 | 104.9113 | 47236958 | 233618.39 | 259553101 | 99898788 | 50011509 | 0.000000 | 90900749 | 21954690 | 0.000000
09-04-2025 19:46:20000 | -1042754 | 104.2754 | 45611646 | 233625.78 | 257960083 | 99904472 | 50022655 | 0.000000 | 97253220 | 23405366 | 0.000000
09-04-2025 19:46:25000 | -1046021 | 104.6021 | 46554160 | 233568.53 | 258837585 | 99901108 | 50025043 | 0.000000 | 103612930 | 24854885 | 0.000000
09-04-2025 19:46:30000 | -1053800 | 105.38 | 47361211 | 233521.19 | 260821411 | 99899155 | 50007046 | 0.000000 | 110129417 | 26314336 | 0.000000
09-04-2025 19:46:35000 | -1071492 | 107.1492 | 47539346 | 233368.44 | 265365112 | 99901718 | 49964516 | 0.000000 | 116722626 | 27790925 | 0.000000
09-04-2025 19:46:40000 | -1084638 | 108.4638 | 49208652 | 233412.58 | 268582275 | 99897240 | 49928619 | 0.000000 | 123507301 | 29294907 | 0.000000
09-04-2025 19:46:45000 | -1082111 | 108.2111 | 47182002 | 233419.64 | 267927032 | 99905083 | 49939342 | 0.000000 | 130151245 | 30801228 | 0.000000
09-04-2025 19:46:50000 | -1064854 | 106.4854 | 43210215 | 233525.22 | 263504120 | 99917770 | 49963482 | 0.000000 | 136243378 | 32292004 | 0.000000
09-04-2025 19:46:55000 | -1048121 | 104.8121 | 40544370 | 233526.36 | 259341675 | 99925262 | 49998852 | 0.000000 | 142077225 | 33756563 | 0.000000
09-04-2025 19:47:00000 | -1037720 | 103.772 | 40968623 | 233583.23 | 256714386 | 99922157 | 50008656 | 0.000000 | 147633926 | 35203845 | 0.000000
09-04-2025 19:47:05000 | -1034427 | 103.4427 | 42524521 | 233581.48 | 255918045 | 99915611 | 50020359 | 0.000000 | 153511261 | 36642532 | 0.000000
09-04-2025 19:47:10000 | -1032639 | 103.2639 | 42849209 | 233531.31 | 255538559 | 99914017 | 50035755 | 0.000000 | 159559631 | 38075110 | 0.000000
09-04-2025 19:47:15000 | -1050704 | 105.0704 | 44590928 | 233399.02 | 260162811 | 99910065 | 50003990 | 0.000000 | 165563400 | 39521484 | 0.000000
09-04-2025 19:47:20000 | -1061499 | 106.1499 | 47410977 | 233464.59 | 262788269 | 99900406 | 49983391 | 0.000000 | 172089157 | 40991099 | 0.000000
09-04-2025 19:47:25000 | -1062807 | 106.2807 | 47098096 | 233460.39 | 263113678 | 99901955 | 49986309 | 0.000000 | 178855270 | 42468843 | 0.000000
09-04-2025 19:47:30000 | -1067590 | 106.759 | 47293022 | 233494.50 | 264255554 | 99902023 | 49981590 | 0.000000 | 185371918 | 43949639 | 0.000000
09-04-2025 19:47:35000 | -1065684 | 106.5684 | 46773149 | 233510.17 | 263761353 | 99903824 | 49986351 | 0.000000 | 191925430 | 45430234 | 0.000000
09-04-2025 19:47:40000 | -1065195 | 106.5195 | 45904556 | 233488.09 | 263656219 | 99907272 | 49987095 | 0.000000 | 198368729 | 46909927 | 0.000000
09-04-2025 19:47:45000 | -1067164 | 106.7164 | 46635615 | 233482.33 | 264161682 | 99904648 | 49985279 | 0.000000 | 204846130 | 48391328 | 0.000000
09-04-2025 19:47:50000 | -1061895 | 106.1895 | 44716099 | 233505.34 | 262809265 | 99911453 | 49991364 | 0.000000 | 211150864 | 49869932 | 0.000000
09-04-2025 19:47:55000 | -1061328 | 106.1328 | 43021514 | 233444.64 | 262720978 | 99917946 | 49987049 | 0.000000 | 217183777 | 51342793 | 0.000000
09-04-2025 19:48:00000 | -1065623 | 106.5623 | 43928110 | 233406.34 | 263835815 | 99915138 | 49978767 | 0.000000 | 223300491 | 52820220 | 0.000000
09-04-2025 19:48:05000 | -1069090 | 106.909 | 42118296 | 233374.94 | 264708466 | 99922485 | 49965721 | 0.000000 | 229204666 | 54304194 | 0.000000
09-04-2025 19:48:10000 | -1060798 | 106.0798 | 40859812 | 233422.09 | 262593597 | 99925903 | 49967541 | 0.000000 | 234852478 | 55782529 | 0.000000
09-04-2025 19:48:15000 | -1051100 | 105.11 | 40123848 | 233455.36 | 260152863 | 99927223 | 49994503 | 0.000000 | 240502701 | 57248652 | 0.000000
09-04-2025 19:48:20000 | -1040400 | 104.04 | 39303196 | 233505.31 | 257447479 | 99928719 | 50009396 | 0.000000 | 245919525 | 58699810 | 0.000000
09-04-2025 19:48:25000 | -1032438 | 103.2438 | 42284224 | 233573.47 | 255434189 | 99916237 | 50039761 | 0.000000 | 251678894 | 60136758 | 0.000000
09-04-2025 19:48:30000 | -1030235 | 103.0235 | 41348413 | 233529.80 | 254927765 | 99919556 | 50048153 | 0.000000 | 257458893 | 61568252 | 0.000000
09-04-2025 19:48:35000 | -1033497 | 103.3497 | 44710151 | 233560.67 | 255736206 | 99906555 | 50046841 | 0.000000 | 263514069 | 63003647 | 0.000000
09-04-2025 19:48:40000 | -1042863 | 104.2863 | 45960557 | 233538.25 | 258086151 | 99903023 | 50036865 | 0.000000 | 269747925 | 64447119 | 0.000000
09-04-2025 19:48:45000 | -1048758 | 104.8758 | 47382363 | 233544.25 | 259550568 | 99898094 | 50046711 | 0.000000 | 276333221 | 65902051 | 0.000000
09-04-2025 19:48:50000 | -1043545 | 104.3545 | 46220366 | 233604.08 | 258186279 | 99902054 | 50060604 | 0.000000 | 282768738 | 67352373 | 0.000000
09-04-2025 19:48:55000 | -1044910 | 104.491 | 45337578 | 233537.06 | 258585663 | 99906006 | 50055485 | 0.000000 | 289116760 | 68802739 | 0.000000
09-04-2025 19:49:00000 | -1054796 | 105.4796 | 47709370 | 233526.42 | 261065094 | 99897865 | 50037460 | 0.000000 | 295522125 | 70263457 | 0.000000
09-04-2025 19:49:05000 | -1058017 | 105.8017 | 48430996 | 233542.73 | 261851318 | 99895393 | 50039444 | 0.000000 | 302307709 | 71732813 | 0.000000
09-04-2025 19:49:10000 | -1059994 | 105.9994 | 46560186 | 233517.97 | 262348389 | 99903671 | 50041641 | 0.000000 | 308833008 | 73203115 | 0.000000
09-04-2025 19:49:15000 | -1055164 | 105.5164 | 48477129 | 233636.02 | 261043640 | 99894630 | 50053642 | 0.000000 | 315539825 | 74672515 | 0.000000
09-04-2025 19:49:20000 | -1047369 | 104.7369 | 46821436 | 233621.89 | 259115173 | 99900230 | 50065136 | 0.000000 | 322192291 | 76131069 | 0.000000
09-04-2025 19:49:25000 | -1050776 | 105.0776 | 47999229 | 233617.39 | 259980469 | 99895828 | 50056942 | 0.000000 | 328830261 | 77587866 | 0.000000
09-04-2025 19:49:30000 | -1051259 | 105.1259 | 50123516 | 233646.81 | 260085938 | 99886528 | 50058968 | 0.000000 | 335637848 | 79045571 | 0.000000
09-04-2025 19:49:35000 | -1037678 | 103.7678 | 48375962 | 233720.88 | 256631805 | 99891510 | 50083832 | 0.000000 | 342493164 | 80494199 | 0.000000
09-04-2025 19:49:40000 | -1037057 | 103.7057 | 46547358 | 233600.31 | 256591766 | 99899422 | 50094509 | 0.000000 | 349200470 | 81935146 | 0.000000
09-04-2025 19:49:45000 | -1047681 | 104.7681 | 48003955 | 233559.58 | 259275330 | 99895195 | 50078384 | 0.000000 | 355834778 | 83384512 | 0.000000
09-04-2025 19:49:50000 | -1053502 | 105.3502 | 51335938 | 233622.03 | 260681458 | 99881485 | 50071602 | 0.000000 | 362799286 | 84845771 | 0.000000
09-04-2025 19:49:55000 | -1061311 | 106.1311 | 53372534 | 233655.73 | 262595032 | 99873787 | 50058632 | 0.000000 | 370144073 | 86316982 | 0.000000
09-04-2025 19:50:00000 | -1062366 | 106.2366 | 50539854 | 233580.73 | 262910187 | 99887032 | 50050541 | 0.000000 | 377380280 | 87795264 | 0.000000
09-04-2025 19:50:05000 | -1059009 | 105.9009 | 49759937 | 233628.41 | 262014160 | 99889793 | 50078323 | 0.000000 | 384373810 | 89269014 | 0.000000
09-04-2025 19:50:10000 | -1055152 | 105.5152 | 49560352 | 233638.22 | 261049835 | 99889877 | 50087955 | 0.000000 | 391225952 | 90735313 | 0.000000
09-04-2025 19:50:15000 | -1043315 | 104.3315 | 50116807 | 233750.53 | 258009277 | 99884827 | 50105652 | 0.000000 | 398070251 | 92188770 | 0.000000
09-04-2025 19:50:20000 | -1043339 | 104.3339 | 51442627 | 233749.08 | 258035156 | 99878670 | 50114059 | 0.000000 | 405014069 | 93635078 | 0.000000
09-04-2025 19:50:25000 | -1042427 | 104.2427 | 54269380 | 233805.45 | 257782837 | 99864761 | 50118309 | 0.000000 | 412321930 | 95080508 | 0.000000
09-04-2025 19:50:30000 | -1047556 | 104.7556 | 56025693 | 233774.33 | 259102814 | 99857292 | 50116814 | 0.000000 | 420004028 | 96533525 | 0.000000
09-04-2025 19:50:35000 | -1063273 | 106.3273 | 54796025 | 233638.28 | 263119141 | 99867470 | 50087177 | 0.000000 | 427559845 | 98002344 | 0.000000
09-04-2025 19:50:40000 | -1067952 | 106.7952 | 56634629 | 233697.77 | 264231018 | 99859680 | 50077229 | 0.000000 | 435373657 | 99485127 | 0.000000
09-04-2025 19:50:45000 | -1067642 | 106.7642 | 55957471 | 233716.05 | 264121216 | 99862930 | 50069695 | 0.000000 | 443151794 | 10096790 | 0.000000
09-04-2025 19:50:50000 | -1072925 | 107.2925 | 53513496 | 233588.88 | 265539825 | 99875847 | 50052769 | 0.000000 | 450694977 | 10245353 | 0.000000
09-04-2025 19:50:55000 | -1067599 | 106.7599 | 48754912 | 233557.92 | 264203552 | 99895882 | 50043762 | 0.000000 | 457731873 | 10393994 | 0.000000
09-04-2025 19:51:00000 | -1059180 | 105.918 | 46773008 | 233568.36 | 262091736 | 99902641 | 50057045 | 0.000000 | 464328583 | 10541445 | 0.000000
09-04-2025 19:51:05000 | -1059441 | 105.9441 | 46392183 | 233531.14 | 262193237 | 99904266 | 50055061 | 0.000000 | 470785461 | 10688571 | 0.000000
09-04-2025 19:51:10000 | -1063610 | 106.361 | 49215386 | 233571.27 | 263207947 | 99893120 | 50048908 | 0.000000 | 477413910 | 10836186 | 0.000000
09-04-2025 19:51:15000 | -1054327 | 105.4327 | 47567720 | 233592.84 | 260872864 | 99898376 | 50064316 | 0.000000 | 484144287 | 10983121 | 0.000000
09-04-2025 19:51:20000 | -1044840 | 104.484 | 46818320 | 233657.41 | 258453796 | 99899757 | 50091179 | 0.000000 | 490772400 | 11128824 | 0.000000
09-04-2025 19:51:25000 | -1036001 | 103.6001 | 47143862 | 233690.91 | 256239136 | 99896622 | 50113270 | 0.000000 | 497355743 | 11273129 | 0.000000
09-04-2025 19:51:30000 | -1039634 | 103.9634 | 45997158 | 233591.81 | 257230072 | 99902267 | 50106243 | 0.000000 | 503761841 | 11417337 | 0.000000
09-04-2025 19:51:35000 | -1035443 | 103.5443 | 50330703 | 233749.16 | 256073547 | 99882072 | 50132130 | 0.000000 | 510635742 | 11561984 | 0.000000
09-04-2025 19:51:40000 | -1035373 | 103.5373 | 49611372 | 233690.08 | 256112915 | 99885399 | 50156940 | 0.000000 | 517612915 | 11705708 | 0.000000
09-04-2025 19:51:45000 | -1036313 | 103.6313 | 51354741 | 233716.19 | 256337341 | 99877441 | 50158283 | 0.000000 | 524715454 | 11849273 | 0.000000
09-04-2025 19:51:50000 | -1039931 | 103.9931 | 53717393 | 233789.75 | 257175385 | 99866859 | 50162201 | 0.000000 | 532032043 | 11993416 | 0.000000
09-04-2025 19:51:55000 | -1051639 | 105.1639 | 55786138 | 233725.02 | 260164734 | 99859596 | 50149162 | 0.000000 | 539742859 | 12138661 | 0.000000
09-04-2025 19:52:00000 | -1070620 | 107.062 | 57945313 | 233648.13 | 264958466 | 99853859 | 50106258 | 0.000000 | 547745850 | 12286377 | 0.000000
09-04-2025 19:52:05000 | -1081501 | 108.1501 | 57284014 | 233606.27 | 267683044 | 99860016 | 50080021 | 0.000000 | 555833435 | 12436102 | 0.000000
09-04-2025 19:52:10000 | -1076938 | 107.6938 | 54102847 | 233632.77 | 266486115 | 99874046 | 50099213 | 0.000000 | 563613098 | 12586204 | 0.000000
09-04-2025 19:52:15000 | -1071105 | 107.1105 | 50474302 | 233591.19 | 265053009 | 99889153 | 50086170 | 0.000000 | 570767334 | 12735265 | 0.000000
09-04-2025 19:52:20000 | -1070347 | 107.0347 | 49796621 | 233581.11 | 264872375 | 99891953 | 50080227 | 0.000000 | 577810242 | 12883942 | 0.000000
09-04-2025 19:52:25000 | -1060872 | 106.0872 | 49610366 | 233683.91 | 262409332 | 99890839 | 50090298 | 0.000000 | 584752686 | 13031662 | 0.000000
09-04-2025 19:52:30000 | -1045365 | 104.5365 | 50060913 | 233768.88 | 258495178 | 99885529 | 50131973 | 0.000000 | 591721008 | 13177566 | 0.000000
09-04-2025 19:52:35000 | -1033968 | 103.3968 | 50047163 | 233779.50 | 255672333 | 99883064 | 50157089 | 0.000000 | 598651611 | 13321326 | 0.000000
09-04-2025 19:52:40000 | -1035245 | 103.5245 | 49873418 | 233685.20 | 256088745 | 99884155 | 50143951 | 0.000000 | 605578125 | 13464953 | 0.000000
09-04-2025 19:52:45000 | -1052163 | 105.2163 | 53457314 | 233647.89 | 260350555 | 99871185 | 50118729 | 0.000000 | 612892273 | 13610464 | 0.000000
09-04-2025 19:52:50000 | -1060314 | 106.0314 | 55486416 | 233670.06 | 262359039 | 99863358 | 50103748 | 0.000000 | 620485413 | 13757438 | 0.000000
09-04-2025 19:52:55000 | -1060080 | 106.008 | 53206201 | 233658.59 | 262286285 | 99874283 | 50114613 | 0.000000 | 628189941 | 13905087 | 0.000000
09-04-2025 19:53:00000 | -1057827 | 105.7827 | 52687129 | 233745.02 | 261625916 | 99876190 | 50124870 | 0.000000 | 635380493 | 14052289 | 0.000000
09-04-2025 19:53:05000 | -1052662 | 105.2662 | 52804355 | 233720.97 | 260383575 | 99874420 | 50134872 | 0.000000 | 642728333 | 14198854 | 0.000000
09-04-2025 19:53:10000 | -1050317 | 105.0317 | 53976353 | 233785.86 | 259753052 | 99868210 | 50142010 | 0.000000 | 650085999 | 14344890 | 0.000000
09-04-2025 19:53:15000 | -1042167 | 104.2167 | 54219121 | 233834.97 | 257684143 | 99864944 | 50167587 | 0.000000 | 657606750 | 14489786 | 0.000000
09-04-2025 19:53:20000 | -1045049 | 104.5049 | 52776523 | 233685.92 | 258540527 | 99872726 | 50160896 | 0.000000 | 664938782 | 14634463 | 0.000000
09-04-2025 19:53:25000 | -1054799 | 105.4799 | 56253232 | 233747.20 | 260927094 | 99858093 | 50138390 | 0.000000 | 672564880 | 14780600 | 0.000000
09-04-2025 19:53:30000 | -1063120 | 106.312 | 56081606 | 233666.86 | 263063019 | 99861153 | 50128677 | 0.000000 | 680414734 | 14927825 | 0.000000
09-04-2025 19:53:35000 | -1076873 | 107.6873 | 55018618 | 233602.28 | 266516479 | 99869743 | 50089844 | 0.000000 | 688063110 | 15076876 | 0.000000
09-04-2025 19:53:40000 | -1069494 | 106.9494 | 52965713 | 233631.25 | 264639893 | 99877594 | 50102428 | 0.000000 | 695674194 | 15226214 | 0.000000
09-04-2025 19:53:45000 | -1057763 | 105.7763 | 48678135 | 233662.41 | 261655701 | 99894279 | 50130787 | 0.000000 | 702720825 | 15373756 | 0.000000
09-04-2025 19:53:50000 | -1052084 | 105.2084 | 48602427 | 233677.98 | 260236572 | 99893463 | 50130375 | 0.000000 | 709470215 | 15520208 | 0.000000
09-04-2025 19:53:55000 | -1048160 | 104.816 | 49103506 | 233660.56 | 259295410 | 99890450 | 50134888 | 0.000000 | 716324402 | 15666118 | 0.000000
09-04-2025 19:54:00000 | -1048882 | 104.8882 | 48405581 | 233641.50 | 259483917 | 99893677 | 50135002 | 0.000000 | 723044617 | 15811625 | 0.000000
09-04-2025 19:54:05000 | -1053298 | 105.3298 | 50918193 | 233645.95 | 260598236 | 99883362 | 50115669 | 0.000000 | 729968872 | 15957654 | 0.000000
09-04-2025 19:54:10000 | -1051273 | 105.1273 | 53674448 | 233757.69 | 260010498 | 99869919 | 50132359 | 0.000000 | 737230957 | 16103896 | 0.000000
09-04-2025 19:54:15000 | -1046181 | 104.6181 | 51334141 | 233718.58 | 258766724 | 99879829 | 50152271 | 0.000000 | 744421448 | 16249168 | 0.000000
09-04-2025 19:54:20000 | -1048254 | 104.8254 | 52773027 | 233731.53 | 259280640 | 99873512 | 50152660 | 0.000000 | 751681152 | 16394631 | 0.000000
09-04-2025 19:54:25000 | -1051023 | 105.1023 | 53479297 | 233735.88 | 259967987 | 99870796 | 50149319 | 0.000000 | 759077881 | 16540799 | 0.000000
09-04-2025 19:54:30000 | -1045694 | 104.5694 | 52293594 | 233722.61 | 258653198 | 99875191 | 50170143 | 0.000000 | 766514465 | 16686465 | 0.000000
09-04-2025 19:54:35000 | -1048560 | 104.856 | 52662412 | 233687.19 | 259408386 | 99874115 | 50159454 | 0.000000 | 773730896 | 16831904 | 0.000000
09-04-2025 19:54:40000 | -1057307 | 105.7307 | 50887505 | 233589.20 | 261653320 | 99884377 | 50141651 | 0.000000 | 780802979 | 16978027 | 0.000000
09-04-2025 19:54:45000 | -1068785 | 106.8785 | 51942944 | 233567.80 | 264521973 | 99882111 | 50114285 | 0.000000 | 787956116 | 17125650 | 0.000000
09-04-2025 19:54:50000 | -1073785 | 107.3785 | 56987876 | 233729.05 | 265636017 | 99859467 | 50109493 | 0.000000 | 795597107 | 17274723 | 0.000000
09-04-2025 19:54:55000 | -1060734 | 106.0734 | 53144097 | 233715.27 | 262383575 | 99874725 | 50138596 | 0.000000 | 803201782 | 17422492 | 0.000000
09-04-2025 19:55:00000 | -1061122 | 106.1122 | 52042974 | 233635.09 | 262554993 | 99879944 | 50123756 | 0.000000 | 810470764 | 17569865 | 0.000000
09-04-2025 19:55:05000 | -1071710 | 107.171 | 53046440 | 233599.72 | 265226898 | 99877724 | 50104816 | 0.000000 | 817731018 | 17718020 | 0.000000
09-04-2025 19:55:10000 | -1069849 | 106.9849 | 49882002 | 233551.73 | 264781128 | 99891479 | 50095791 | 0.000000 | 824815002 | 17866574 | 0.000000
09-04-2025 19:55:15000 | -1060050 | 106.005 | 49049150 | 233641.95 | 262249634 | 99893120 | 50115177 | 0.000000 | 831716003 | 18014281 | 0.000000
09-04-2025 19:55:20000 | -1050966 | 105.0966 | 46576396 | 233606.16 | 260018463 | 99901939 | 50123898 | 0.000000 | 838262451 | 18160629 | 0.000000
09-04-2025 19:55:25000 | -1043530 | 104.353 | 47988149 | 233664.84 | 258132660 | 99894432 | 50144264 | 0.000000 | 844852783 | 18305996 | 0.000000
09-04-2025 19:55:30000 | -1041360 | 104.136 | 47606035 | 233680.98 | 257574371 | 99895668 | 50141888 | 0.000000 | 851392212 | 18450604 | 0.000000
09-04-2025 19:55:35000 | -1037747 | 103.7747 | 49727505 | 233705.22 | 256681519 | 99885384 | 50152798 | 0.000000 | 858208923 | 18594668 | 0.000000
09-04-2025 19:55:40000 | -1045030 | 104.503 | 51022036 | 233676.86 | 258526184 | 99881027 | 50146267 | 0.000000 | 865173706 | 18739287 | 0.000000
09-04-2025 19:55:45000 | -1054321 | 105.4321 | 53654775 | 233686.30 | 260841339 | 99870758 | 50138390 | 0.000000 | 872520203 | 18885346 | 0.000000
09-04-2025 19:55:50000 | -1056022 | 105.6022 | 52982212 | 233659.38 | 261281708 | 99874382 | 50138538 | 0.000000 | 879880249 | 19031699 | 0.000000
09-04-2025 19:55:55000 | -1058629 | 105.8629 | 51926484 | 233660.97 | 261917206 | 99879921 | 50137543 | 0.000000 | 887149170 | 19178494 | 0.000000
09-04-2025 19:56:00000 | -1062666 | 106.2666 | 53260723 | 233656.97 | 262926575 | 99874634 | 50119091 | 0.000000 | 894357117 | 19326055 | 0.000000
09-04-2025 19:56:05000 | -1067180 | 106.718 | 52897480 | 233625.72 | 264071930 | 99877380 | 50122902 | 0.000000 | 901748840 | 19474063 | 0.000000
09-04-2025 19:56:10000 | -1065107 | 106.5107 | 50788223 | 233628.22 | 263531982 | 99886505 | 50125946 | 0.000000 | 908862122 | 19622078 | 0.000000
09-04-2025 19:56:15000 | -1064519 | 106.4519 | 50216265 | 233609.34 | 263401764 | 99888924 | 50131371 | 0.000000 | 915898621 | 19769783 | 0.000000
09-04-2025 19:56:20000 | -1058551 | 105.8551 | 50873774 | 233664.73 | 261878113 | 99884712 | 50141804 | 0.000000 | 922954529 | 19916900 | 0.000000
09-04-2025 19:56:25000 | -1053742 | 105.3742 | 48868843 | 233637.89 | 260693817 | 99892632 | 50146175 | 0.000000 | 929932312 | 20063619 | 0.000000
09-04-2025 19:56:30000 | -1050359 | 105.0359 | 50341655 | 233668.61 | 259842651 | 99885345 | 50150723 | 0.000000 | 936984070 | 20209791 | 0.000000
09-04-2025 19:56:35000 | -1063699 | 106.3699 | 53961714 | 233641.95 | 263219910 | 99871567 | 50122429 | 0.000000 | 944287781 | 20356813 | 0.000000
09-04-2025 19:56:40000 | -1063200 | 106.32 | 52767476 | 233649.14 | 263064423 | 99877068 | 50114922 | 0.000000 | 951728271 | 20504516 | 0.000000
09-04-2025 19:56:45000 | -1060848 | 106.0848 | 52624912 | 233696.73 | 262427002 | 99877190 | 50127636 | 0.000000 | 959193665 | 20652422 | 0.000000
09-04-2025 19:56:50000 | -1056335 | 105.6335 | 51807568 | 233705.55 | 261291412 | 99879951 | 50141567 | 0.000000 | 966333862 | 20799400 | 0.000000
09-04-2025 19:56:55000 | -1046514 | 104.6514 | 51794404 | 233798.69 | 258764618 | 99877747 | 50161930 | 0.000000 | 973464172 | 20945293 | 0.000000
09-04-2025 19:57:00000 | -1041027 | 104.1027 | 52358682 | 233816.73 | 257403748 | 99873756 | 50175304 | 0.000000 | 980619995 | 21089920 | 0.000000
09-04-2025 19:57:05000 | -1041567 | 104.1567 | 55379263 | 233826.73 | 257562653 | 99858948 | 50175270 | 0.000000 | 988136169 | 21234453 | 0.000000
09-04-2025 19:57:10000 | -1046493 | 104.6493 | 58124429 | 233844.92 | 258793365 | 99846107 | 50178028 | 0.000000 | 996067749 | 21379605 | 0.000000
09-04-2025 19:57:15000 | -1048280 | 104.828 | 59147417 | 233863.84 | 259225922 | 99841202 | 50174664 | 0.000000 | 10041669 | 21525131 | 0.000000
09-04-2025 19:57:20000 | -1053058 | 105.3058 | 58023228 | 233799.25 | 260459351 | 99848549 | 50163502 | 0.000000 | 10122666 | 21671246 | 0.000000
09-04-2025 19:57:25000 | -1057321 | 105.7321 | 58496934 | 233820.55 | 261494507 | 99847305 | 50157192 | 0.000000 | 10203689 | 21817877 | 0.000000
09-04-2025 19:57:30000 | -1055181 | 105.5181 | 57926421 | 233854.75 | 260922302 | 99849655 | 50173363 | 0.000000 | 10285095 | 21964488 | 0.000000
09-04-2025 19:57:35000 | -1053277 | 105.3277 | 55757920 | 233796.11 | 260488708 | 99860176 | 50174316 | 0.000000 | 10363666 | 22110590 | 0.000000
09-04-2025 19:57:40000 | -1058112 | 105.8112 | 55658984 | 233718.81 | 261763947 | 99861938 | 50153572 | 0.000000 | 10440654 | 22257266 | 0.000000
09-04-2025 19:57:45000 | -1066667 | 106.6667 | 58031885 | 233747.56 | 263874237 | 99852333 | 50142338 | 0.000000 | 10518724 | 22404828 | 0.000000
09-04-2025 19:57:50000 | -1075870 | 107.587 | 57358379 | 233676.63 | 266213989 | 99858185 | 50120049 | 0.000000 | 10598230 | 22553563 | 0.000000
09-04-2025 19:57:55000 | -1077733 | 107.7733 | 55340732 | 233624.86 | 266711121 | 99868423 | 50101765 | 0.000000 | 10676572 | 22703279 | 0.000000
09-04-2025 19:58:00000 | -1074735 | 107.4735 | 53548467 | 233666.27 | 265899078 | 99876106 | 50105350 | 0.000000 | 10751414 | 22852822 | 0.000000
09-04-2025 19:58:05000 | -1059208 | 105.9208 | 52398560 | 233770.17 | 261935303 | 99877861 | 50127953 | 0.000000 | 10825413 | 23000738 | 0.000000
09-04-2025 19:58:10000 | -1045880 | 104.588 | 53221504 | 233818.97 | 258609009 | 99870781 | 50154392 | 0.000000 | 10899071 | 23146768 | 0.000000
09-04-2025 19:58:15000 | -1040578 | 104.0578 | 55959082 | 233930.44 | 257212067 | 99855713 | 50167625 | 0.000000 | 10973409 | 23291430 | 0.000000
09-04-2025 19:58:20000 | -1041851 | 104.1851 | 56712852 | 233879.64 | 257594971 | 99852173 | 50170025 | 0.000000 | 11051487 | 23435865 | 0.000000
09-04-2025 19:58:25000 | -1050163 | 105.0163 | 59027012 | 233835.20 | 259718506 | 99842407 | 50159039 | 0.000000 | 11132142 | 23581096 | 0.000000
09-04-2025 19:58:30000 | -1054699 | 105.4699 | 61133179 | 233873.30 | 260827515 | 99832436 | 50153534 | 0.000000 | 11216810 | 23727420 | 0.000000
09-04-2025 19:58:35000 | -1067512 | 106.7512 | 61276387 | 233773.53 | 264096924 | 99835663 | 50129620 | 0.000000 | 11301792 | 23874869 | 0.000000
09-04-2025 19:58:40000 | -1075258 | 107.5258 | 62569028 | 233803.06 | 265992920 | 99831123 | 50106289 | 0.000000 | 11387849 | 24023920 | 0.000000
09-04-2025 19:58:45000 | -1068165 | 106.8165 | 61192334 | 233879.81 | 264140533 | 99836311 | 50113922 | 0.000000 | 11473989 | 24173154 | 0.000000
09-04-2025 19:58:50000 | -1063687 | 106.3687 | 57439189 | 233812.09 | 263058685 | 99854515 | 50129414 | 0.000000 | 11556578 | 24321086 | 0.000000
09-04-2025 19:58:55000 | -1076816 | 107.6816 | 56862817 | 233641.30 | 266483093 | 99860863 | 50089134 | 0.000000 | 11635601 | 24469621 | 0.000000
09-04-2025 19:59:00000 | -1082742 | 108.2742 | 57984824 | 233741.44 | 267848480 | 99856911 | 50065056 | 0.000000 | 11716079 | 24620014 | 0.000000
09-04-2025 19:59:05000 | -1068990 | 106.899 | 52833730 | 233682.30 | 264456116 | 99878090 | 50098343 | 0.000000 | 11794227 | 24769248 | 0.000000
09-04-2025 19:59:10000 | -1057071 | 105.7071 | 49911108 | 233698.66 | 261462189 | 99888718 | 50113434 | 0.000000 | 11864402 | 24916457 | 0.000000
09-04-2025 19:59:15000 | -1049198 | 104.9198 | 50169976 | 233721.77 | 259493408 | 99885872 | 50122509 | 0.000000 | 11933921 | 25062686 | 0.000000
09-04-2025 19:59:20000 | -1053298 | 105.3298 | 52477515 | 233724.92 | 260529846 | 99876122 | 50110989 | 0.000000 | 12004819 | 25208635 | 0.000000
09-04-2025 19:59:25000 | -1046985 | 104.6985 | 54063281 | 233809.30 | 258899261 | 99866943 | 50119915 | 0.000000 | 12078917 | 25354193 | 0.000000
09-04-2025 19:59:30000 | -1043056 | 104.3056 | 55218403 | 233828.66 | 257925232 | 99860168 | 50128132 | 0.000000 | 12154969 | 25499383 | 0.000000
09-04-2025 19:59:35000 | -1042421 | 104.2421 | 57617876 | 233899.67 | 257720642 | 99847595 | 50140194 | 0.000000 | 12233243 | 25644133 | 0.000000
09-04-2025 19:59:40000 | -1045913 | 104.5913 | 57681968 | 233837.63 | 258649689 | 99848274 | 50132973 | 0.000000 | 12313673 | 25789301 | 0.000000
09-04-2025 19:59:45000 | -1052467 | 105.2467 | 58446714 | 233823.91 | 260291687 | 99846161 | 50118954 | 0.000000 | 12394630 | 25935316 | 0.000000
09-04-2025 19:59:50000 | -1060606 | 106.0606 | 60489854 | 233819.34 | 262332123 | 99837753 | 50102463 | 0.000000 | 12478043 | 26082250 | 0.000000
09-04-2025 19:59:55000 | -1065300 | 106.53 | 59960288 | 233791.34 | 263513611 | 99841972 | 50094162 | 0.000000 | 12562659 | 26230104 | 0.000000
09-04-2025 20:00:00000 | -1066467 | 106.6467 | 59827266 | 233824.00 | 263761658 | 99843018 | 50101395 | 0.000000 | 12646262 | 26378076 | 0.000000
09-04-2025 20:00:05000 | -1070155 | 107.0155 | 58897046 | 233767.91 | 264721313 | 99848892 | 50089855 | 0.000000 | 8175614 | 148479660 | 0.000000
09-04-2025 20:00:10000 | -1078010 | 107.801 | 56936904 | 233638.67 | 266780151 | 99860809 | 50066212 | 0.000000 | 16286114 | 297659973 | 0.000000
09-04-2025 20:00:15000 | -1088801 | 108.8801 | 59443008 | 233673.28 | 269436340 | 99851303 | 50032150 | 0.000000 | 24409065 | 448498383 | 0.000000
09-04-2025 20:00:20000 | -1093259 | 109.3259 | 56857070 | 233609.78 | 270579865 | 99865036 | 50015675 | 0.000000 | 32429031 | 600227661 | 0.000000
09-04-2025 20:00:25000 | -1078562 | 107.8562 | 53557148 | 233687.56 | 266819153 | 99876938 | 50032742 | 0.000000 | 40063869 | 750948486 | 0.000000
09-04-2025 20:00:30000 | -1058598 | 105.8598 | 51000220 | 233791.13 | 261745667 | 99884148 | 50068115 | 0.000000 | 47214687 | 899161438 | 0.000000
09-04-2025 20:00:35000 | -1050545 | 105.0545 | 49275757 | 233694.94 | 259846252 | 99890175 | 50078838 | 0.000000 | 54124348 | 10453138 | 0.000000
09-04-2025 20:00:40000 | -1046105 | 104.6105 | 51002783 | 233740.03 | 258726135 | 99881363 | 50069740 | 0.000000 | 61227589 | 11910178 | 0.000000
09-04-2025 20:00:45000 | -1051459 | 105.1459 | 52454614 | 233697.00 | 260106079 | 99875793 | 50064564 | 0.000000 | 68528427 | 13367070 | 0.000000
09-04-2025 20:00:50000 | -1059856 | 105.9856 | 55231841 | 233704.81 | 262206421 | 99864487 | 50040440 | 0.000000 | 76056679 | 14834600 | 0.000000
09-04-2025 20:00:55000 | -1061665 | 106.1665 | 55876890 | 233748.88 | 262609924 | 99861786 | 50049961 | 0.000000 | 83845856 | 16310331 | 0.000000
09-04-2025 20:01:00000 | -1051440 | 105.144 | 54586167 | 233807.77 | 260004669 | 99865509 | 50071354 | 0.000000 | 91464462 | 17776549 | 0.000000
09-04-2025 20:01:05000 | -1051435 | 105.1435 | 54713398 | 233777.02 | 260041016 | 99864883 | 50068680 | 0.000000 | 99041321 | 19236086 | 0.000000
09-04-2025 20:01:10000 | -1059594 | 105.9594 | 54158550 | 233697.86 | 262133209 | 99869629 | 50044373 | 0.000000 | 106612831 | 20703721 | 0.000000
09-04-2025 20:01:15000 | -1060391 | 106.0391 | 56071543 | 233766.97 | 262275909 | 99860489 | 50046486 | 0.000000 | 114385536 | 22176584 | 0.000000
09-04-2025 20:01:20000 | -1059467 | 105.9467 | 56449907 | 233784.02 | 262034210 | 99858353 | 50051701 | 0.000000 | 122283203 | 23649312 | 0.000000
09-04-2025 20:01:25000 | -1054175 | 105.4175 | 55262080 | 233809.31 | 260686676 | 99862877 | 50069996 | 0.000000 | 130044647 | 25116658 | 0.000000
09-04-2025 20:01:30000 | -1042490 | 104.249 | 51938345 | 233755.08 | 257821960 | 99876122 | 50090870 | 0.000000 | 137456558 | 26570566 | 0.000000
09-04-2025 20:01:35000 | -1040987 | 104.0987 | 51069912 | 233743.06 | 257453308 | 99879875 | 50093712 | 0.000000 | 144505188 | 28015002 | 0.000000
09-04-2025 20:01:40000 | -1048897 | 104.8897 | 55754258 | 233769.52 | 259436981 | 99859024 | 50082394 | 0.000000 | 152020737 | 29471523 | 0.000000
09-04-2025 20:01:45000 | -1051278 | 105.1278 | 55794380 | 233810.17 | 259980164 | 99859459 | 50090279 | 0.000000 | 159687332 | 30927959 | 0.000000
09-04-2025 20:01:50000 | -1054729 | 105.4729 | 56429590 | 233760.52 | 260895203 | 99857185 | 50079697 | 0.000000 | 167457031 | 32387778 | 0.000000
09-04-2025 20:01:55000 | -1059802 | 105.9802 | 58099023 | 233755.41 | 262179321 | 99850075 | 50065636 | 0.000000 | 175351685 | 33853604 | 0.000000
09-04-2025 20:02:00000 | -1067614 | 106.7614 | 57691641 | 233704.38 | 264148895 | 99854317 | 50047291 | 0.000000 | 183394897 | 35331631 | 0.000000
09-04-2025 20:02:05000 | -1076819 | 107.6819 | 58073525 | 233693.98 | 266437225 | 99854889 | 50032322 | 0.000000 | 191487534 | 36824546 | 0.000000
09-04-2025 20:02:10000 | -1061854 | 106.1854 | 54701660 | 233776.67 | 262610626 | 99867569 | 50056923 | 0.000000 | 199372894 | 38310405 | 0.000000
09-04-2025 20:02:15000 | -1051500 | 105.15 | 51886235 | 233751.92 | 260050415 | 99878479 | 50077751 | 0.000000 | 206675110 | 39774236 | 0.000000
09-04-2025 20:02:20000 | -1056169 | 105.6169 | 51437798 | 233637.14 | 261323975 | 99881615 | 50051121 | 0.000000 | 213785477 | 41236870 | 0.000000
09-04-2025 20:02:25000 | -1070910 | 107.091 | 54940010 | 233650.20 | 264989014 | 99868660 | 50021191 | 0.000000 | 221223343 | 42718120 | 0.000000
09-04-2025 20:02:30000 | -1071113 | 107.1113 | 54450801 | 233652.70 | 265034027 | 99871033 | 50022591 | 0.000000 | 228833710 | 44206938 | 0.000000
09-04-2025 20:02:35000 | -1062448 | 106.2448 | 51308579 | 233677.28 | 262826080 | 99883591 | 50030693 | 0.000000 | 236115372 | 45687681 | 0.000000
09-04-2025 20:02:40000 | -1051157 | 105.1157 | 50834600 | 233752.94 | 259952545 | 99883270 | 50056282 | 0.000000 | 243213364 | 47154321 | 0.000000
09-04-2025 20:02:45000 | -1044742 | 104.4742 | 49307598 | 233698.08 | 258414886 | 99888809 | 50063587 | 0.000000 | 250093475 | 48609009 | 0.000000
09-04-2025 20:02:50000 | -1051165 | 105.1165 | 52598096 | 233682.72 | 260049347 | 99875046 | 50046017 | 0.000000 | 257321808 | 50067480 | 0.000000
09-04-2025 20:02:55000 | -1056069 | 105.6069 | 53523525 | 233705.66 | 261246307 | 99871811 | 50031292 | 0.000000 | 264656464 | 51531211 | 0.000000
09-04-2025 20:03:00000 | -1061309 | 106.1309 | 53432227 | 233665.81 | 262584167 | 99873505 | 50026966 | 0.000000 | 272122528 | 53001611 | 0.000000
09-04-2025 20:03:05000 | -1061521 | 106.1521 | 53439102 | 233685.06 | 262619812 | 99873528 | 50029095 | 0.000000 | 279520782 | 54476592 | 0.000000
09-04-2025 20:03:10000 | -1057476 | 105.7476 | 48747861 | 233590.02 | 261668671 | 99893913 | 50037373 | 0.000000 | 286601288 | 55948521 | 0.000000
09-04-2025 20:03:15000 | -1066264 | 106.6264 | 49576016 | 233524.13 | 263920166 | 99892082 | 50017895 | 0.000000 | 293411316 | 57426509 | 0.000000
09-04-2025 20:03:20000 | -1067384 | 106.7384 | 48907202 | 233541.67 | 264169891 | 99895195 | 50016243 | 0.000000 | 300282013 | 58910742 | 0.000000
09-04-2025 20:03:25000 | -1054683 | 105.4683 | 46888862 | 233647.39 | 260891174 | 99901321 | 50031265 | 0.000000 | 306878845 | 60383940 | 0.000000
09-04-2025 20:03:30000 | -1033362 | 103.3362 | 47277144 | 233786.78 | 255483856 | 99895508 | 50080685 | 0.000000 | 313511322 | 61832354 | 0.000000
09-04-2025 20:03:35000 | -1022039 | 102.2039 | 49264810 | 233844.30 | 252648071 | 99884026 | 50122501 | 0.000000 | 320280487 | 63255654 | 0.000000
09-04-2025 20:03:40000 | -1029179 | 102.9179 | 47796133 | 233650.91 | 254603317 | 99892334 | 50096680 | 0.000000 | 327120422 | 64677871 | 0.000000
09-04-2025 20:03:45000 | -1038901 | 103.8901 | 52360830 | 233725.28 | 256976227 | 99873230 | 50092274 | 0.000000 | 334065613 | 66114243 | 0.000000
09-04-2025 20:03:50000 | -1039310 | 103.931 | 54497871 | 233776.53 | 257053192 | 99862801 | 50102592 | 0.000000 | 341505127 | 67557861 | 0.000000
09-04-2025 20:03:55000 | -1054306 | 105.4306 | 56475635 | 233719.30 | 260850159 | 99856842 | 50093544 | 0.000000 | 349130890 | 69012222 | 0.000000
09-04-2025 20:04:00000 | -1054919 | 105.4919 | 56164897 | 233759.67 | 260938507 | 99858574 | 50077354 | 0.000000 | 356934753 | 70478003 | 0.000000
09-04-2025 20:04:05000 | -1059863 | 105.9863 | 57057778 | 233763.36 | 262163666 | 99855400 | 50081173 | 0.000000 | 364852814 | 71951016 | 0.000000
09-04-2025 20:04:10000 | -1065146 | 106.5146 | 54635874 | 233650.28 | 263561768 | 99868706 | 50068367 | 0.000000 | 372613556 | 73429351 | 0.000000
09-04-2025 20:04:15000 | -1067852 | 106.7852 | 56844805 | 233734.50 | 264165192 | 99858612 | 50062050 | 0.000000 | 380393677 | 74911162 | 0.000000
09-04-2025 20:04:20000 | -1067361 | 106.7361 | 56052358 | 233717.75 | 264051483 | 99862396 | 50070557 | 0.000000 | 388308533 | 76392393 | 0.000000
09-04-2025 20:04:25000 | -1072866 | 107.2866 | 56460171 | 233703.59 | 265431549 | 99861816 | 50054474 | 0.000000 | 396130981 | 77878770 | 0.000000
09-04-2025 20:04:30000 | -1070535 | 107.0535 | 55154243 | 233732.44 | 264807495 | 99867546 | 50048222 | 0.000000 | 403802826 | 79366299 | 0.000000
09-04-2025 20:04:35000 | -1064317 | 106.4317 | 52922109 | 233685.08 | 263297974 | 99876602 | 50047028 | 0.000000 | 411271362 | 80848120 | 0.000000
09-04-2025 20:04:40000 | -1061419 | 106.1419 | 53077725 | 233740.45 | 262522034 | 99875206 | 50047897 | 0.000000 | 418544220 | 82324570 | 0.000000
09-04-2025 20:04:45000 | -1053478 | 105.3478 | 50650742 | 233678.84 | 260604645 | 99884621 | 50053806 | 0.000000 | 425765411 | 83792773 | 0.000000
09-04-2025 20:04:50000 | -1052401 | 105.2401 | 50987852 | 233690.97 | 260326294 | 99882843 | 50053692 | 0.000000 | 432835541 | 85254443 | 0.000000
09-04-2025 20:04:55000 | -1051021 | 105.1021 | 51673057 | 233690.64 | 259994873 | 99879364 | 50056690 | 0.000000 | 440023529 | 86713975 | 0.000000
09-04-2025 20:05:00000 | -1056466 | 105.6466 | 54599380 | 233729.05 | 261333008 | 99866722 | 50046860 | 0.000000 | 447384827 | 88179902 | 0.000000
09-04-2025 20:05:05000 | -1055290 | 105.529 | 51587656 | 233641.39 | 261102325 | 99880730 | 50043205 | 0.000000 | 454781586 | 89645117 | 0.000000
09-04-2025 20:05:10000 | -1060201 | 106.0201 | 51765098 | 233652.64 | 262303680 | 99881012 | 50035866 | 0.000000 | 461928528 | 91114941 | 0.000000
09-04-2025 20:05:15000 | -1067840 | 106.784 | 52330542 | 233636.23 | 264215973 | 99880135 | 50026314 | 0.000000 | 469056732 | 92592363 | 0.000000
09-04-2025 20:05:20000 | -1058816 | 105.8816 | 52062983 | 233694.38 | 261918671 | 99879326 | 50051311 | 0.000000 | 476306152 | 94067637 | 0.000000
09-04-2025 20:05:25000 | -1043543 | 104.3543 | 47747700 | 233674.97 | 258120422 | 99895485 | 50080883 | 0.000000 | 483165619 | 95526924 | 0.000000
09-04-2025 20:05:30000 | -1040515 | 104.0515 | 47875020 | 233666.61 | 257383545 | 99894318 | 50085773 | 0.000000 | 489700043 | 96970098 | 0.000000
09-04-2025 20:05:35000 | -1044625 | 104.4625 | 52669536 | 233766.14 | 258347107 | 99873138 | 50083420 | 0.000000 | 496638458 | 98420498 | 0.000000
09-04-2025 20:05:40000 | -1040316 | 104.0316 | 52007427 | 233766.97 | 257273224 | 99875275 | 50098484 | 0.000000 | 503928436 | 99866494 | 0.000000
09-04-2025 20:05:45000 | -1052052 | 105.2052 | 54008584 | 233699.83 | 260270874 | 99868492 | 50086239 | 0.000000 | 511349121 | 10132076 | 0.000000
09-04-2025 20:05:50000 | -1056455 | 105.6455 | 54736323 | 233702.67 | 261365326 | 99866051 | 50076252 | 0.000000 | 518958618 | 10278375 | 0.000000
09-04-2025 20:05:55000 | -1062979 | 106.2979 | 54847295 | 233695.92 | 262982086 | 99867149 | 50067268 | 0.000000 | 526579041 | 10425400 | 0.000000
09-04-2025 20:06:00000 | -1067449 | 106.7449 | 57911792 | 233760.23 | 264048340 | 99853157 | 50061844 | 0.000000 | 534471802 | 10573465 | 0.000000
09-04-2025 20:06:05000 | -1064913 | 106.4913 | 55942329 | 233728.42 | 263432281 | 99862305 | 50065063 | 0.000000 | 542253967 | 10721447 | 0.000000
09-04-2025 20:06:10000 | -1053989 | 105.3989 | 52872363 | 233735.13 | 260691467 | 99874413 | 50095642 | 0.000000 | 549760498 | 10868487 | 0.000000
09-04-2025 20:06:15000 | -1046725 | 104.6725 | 51382314 | 233752.56 | 258863586 | 99879730 | 50102161 | 0.000000 | 557010864 | 11014418 | 0.000000
09-04-2025 20:06:20000 | -1044807 | 104.4807 | 50784180 | 233712.84 | 258425873 | 99882080 | 50106228 | 0.000000 | 564085205 | 11159447 | 0.000000
09-04-2025 20:06:25000 | -1048183 | 104.8183 | 50940317 | 233651.31 | 259333099 | 99882118 | 50087799 | 0.000000 | 571326965 | 11304961 | 0.000000
09-04-2025 20:06:30000 | -1057034 | 105.7034 | 53763359 | 233684.88 | 261510712 | 99870903 | 50071262 | 0.000000 | 578684021 | 11451476 | 0.000000
09-04-2025 20:06:35000 | -1063491 | 106.3491 | 56290474 | 233740.14 | 263073822 | 99860214 | 50066093 | 0.000000 | 586315125 | 11599061 | 0.000000
09-04-2025 20:06:40000 | -1062496 | 106.2496 | 53752358 | 233688.45 | 262855194 | 99872276 | 50070118 | 0.000000 | 593957336 | 11746555 | 0.000000
09-04-2025 20:06:45000 | -1061498 | 106.1498 | 54583745 | 233693.33 | 262618073 | 99868050 | 50077900 | 0.000000 | 601503357 | 11893800 | 0.000000
09-04-2025 20:06:50000 | -1058687 | 105.8687 | 54030845 | 233705.22 | 261898926 | 99870018 | 50076622 | 0.000000 | 609089478 | 12041042 | 0.000000
09-04-2025 20:06:55000 | -1063739 | 106.3739 | 54929487 | 233704.64 | 263157562 | 99866943 | 50062645 | 0.000000 | 616629578 | 12188521 | 0.000000
09-04-2025 20:07:00000 | -1067420 | 106.742 | 57675132 | 233760.75 | 264037415 | 99854347 | 50060337 | 0.000000 | 624526184 | 12336668 | 0.000000
09-04-2025 20:07:05000 | -1068804 | 106.8804 | 54315083 | 233652.58 | 264459625 | 99871124 | 50056549 | 0.000000 | 632336121 | 12485062 | 0.000000
09-04-2025 20:07:10000 | -1059052 | 105.9052 | 55417915 | 233831.42 | 261865387 | 99863373 | 50073654 | 0.000000 | 639976196 | 12632954 | 0.000000
09-04-2025 20:07:15000 | -1050642 | 105.0642 | 52295737 | 233744.36 | 259848907 | 99876350 | 50097889 | 0.000000 | 647468201 | 12779049 | 0.000000
09-04-2025 20:07:20000 | -1049239 | 104.9239 | 52392178 | 233730.34 | 259519287 | 99875565 | 50079952 | 0.000000 | 654658630 | 12924697 | 0.000000
09-04-2025 20:07:25000 | -1052297 | 105.2297 | 54833662 | 233753.33 | 260279938 | 99864510 | 50080444 | 0.000000 | 662227722 | 13070659 | 0.000000
09-04-2025 20:07:30000 | -1049443 | 104.9443 | 54645425 | 233773.09 | 259555328 | 99864708 | 50089054 | 0.000000 | 669856262 | 13216481 | 0.000000
09-04-2025 20:07:35000 | -1045454 | 104.5454 | 55474912 | 233797.47 | 258550995 | 99859512 | 50099022 | 0.000000 | 677486755 | 13361631 | 0.000000
09-04-2025 20:07:40000 | -1053214 | 105.3214 | 54833037 | 233690.19 | 260576721 | 99864746 | 50077110 | 0.000000 | 685160400 | 13507552 | 0.000000
09-04-2025 20:07:45000 | -1057891 | 105.7891 | 58798618 | 233818.61 | 261638397 | 99845894 | 50069374 | 0.000000 | 692988892 | 13654233 | 0.000000
09-04-2025 20:07:50000 | -1061281 | 106.1281 | 56047930 | 233723.63 | 262545441 | 99860840 | 50074429 | 0.000000 | 701003052 | 13801429 | 0.000000
09-04-2025 20:07:55000 | -1061784 | 106.1784 | 53720430 | 233660.14 | 262712341 | 99872253 | 50061153 | 0.000000 | 708711792 | 13948990 | 0.000000
09-04-2025 20:08:00000 | -1069331 | 106.9331 | 54703340 | 233630.98 | 264617767 | 99869408 | 50053272 | 0.000000 | 716385498 | 14097198 | 0.000000
09-04-2025 20:08:05000 | -1063778 | 106.3778 | 54831338 | 233753.34 | 263113342 | 99867424 | 50062138 | 0.000000 | 724023254 | 14245525 | 0.000000
09-04-2025 20:08:10000 | -1053673 | 105.3673 | 52753608 | 233764.83 | 260581146 | 99874901 | 50089081 | 0.000000 | 731482239 | 14392394 | 0.000000
09-04-2025 20:08:15000 | -1054563 | 105.4563 | 51256724 | 233667.95 | 260889923 | 99882088 | 50073608 | 0.000000 | 738547119 | 14538504 | 0.000000
09-04-2025 20:08:20000 | -1065564 | 106.5564 | 53260996 | 233625.06 | 263676880 | 99875313 | 50049133 | 0.000000 | 745811340 | 14685822 | 0.000000
09-04-2025 20:08:25000 | -1062154 | 106.2154 | 53464561 | 233742.34 | 262708130 | 99873558 | 50057274 | 0.000000 | 753220520 | 14833569 | 0.000000
09-04-2025 20:08:30000 | -1053159 | 105.3159 | 52159893 | 233769.91 | 260439880 | 99877579 | 50082722 | 0.000000 | 760531555 | 14980354 | 0.000000
09-04-2025 20:08:35000 | -1055479 | 105.5479 | 53991758 | 233730.33 | 261086700 | 99869423 | 50079529 | 0.000000 | 767894409 | 15126647 | 0.000000
09-04-2025 20:08:40000 | -1055604 | 105.5604 | 54900718 | 233764.53 | 261083435 | 99865028 | 50063114 | 0.000000 | 775331665 | 15273040 | 0.000000
09-04-2025 20:08:45000 | -1056814 | 105.6814 | 57495112 | 233807.13 | 261367981 | 99852341 | 50065979 | 0.000000 | 783188599 | 15419964 | 0.000000
09-04-2025 20:08:50000 | -1061726 | 106.1726 | 59100020 | 233837.48 | 262565857 | 99845436 | 50059505 | 0.000000 | 791297546 | 15567313 | 0.000000
09-04-2025 20:08:55000 | -1058248 | 105.8248 | 59774707 | 233884.20 | 261665924 | 99840858 | 50066353 | 0.000000 | 799512390 | 15714540 | 0.000000
09-04-2025 20:09:00000 | -1057104 | 105.7104 | 58941226 | 233849.03 | 261411469 | 99844917 | 50072067 | 0.000000 | 807755371 | 15861378 | 0.000000
09-04-2025 20:09:05000 | -1065512 | 106.5512 | 60298159 | 233801.02 | 263560425 | 99840256 | 50054604 | 0.000000 | 816043640 | 16008602 | 0.000000
09-04-2025 20:09:10000 | -1071207 | 107.1207 | 61906289 | 233848.33 | 264929871 | 99833427 | 50025997 | 0.000000 | 824510132 | 16157107 | 0.000000
09-04-2025 20:09:15000 | -1073862 | 107.3862 | 59877100 | 233760.83 | 265655823 | 99844910 | 50013233 | 0.000000 | 833033081 | 16306332 | 0.000000
09-04-2025 20:09:20000 | -1069968 | 106.9968 | 58843398 | 233829.64 | 264604279 | 99849113 | 50018055 | 0.000000 | 841231140 | 16455127 | 0.000000
09-04-2025 20:09:25000 | -1064136 | 106.4136 | 56650747 | 233805.55 | 263163177 | 99858597 | 50014484 | 0.000000 | 849147827 | 16603184 | 0.000000
09-04-2025 20:09:30000 | -1049191 | 104.9191 | 56339961 | 233895.28 | 259377533 | 99856133 | 50044445 | 0.000000 | 856996155 | 16749666 | 0.000000
09-04-2025 20:09:35000 | -1037685 | 103.7685 | 58911401 | 234008.53 | 256453278 | 99839233 | 50085285 | 0.000000 | 865077881 | 16894119 | 0.000000
09-04-2025 20:09:40000 | -1034055 | 103.4055 | 59536855 | 233994.38 | 255583313 | 99834663 | 50086685 | 0.000000 | 873282227 | 17037559 | 0.000000
09-04-2025 20:09:45000 | -1048880 | 104.888 | 59643799 | 233816.41 | 259430847 | 99838715 | 50066540 | 0.000000 | 881604736 | 17182117 | 0.000000
09-04-2025 20:09:50000 | -1059721 | 105.9721 | 61730239 | 233816.59 | 262133209 | 99830772 | 50037567 | 0.000000 | 890077698 | 17328871 | 0.000000
09-04-2025 20:09:55000 | -1057478 | 105.7478 | 61240889 | 233899.06 | 261481323 | 99832733 | 50058369 | 0.000000 | 898648987 | 17476059 | 0.000000
09-04-2025 20:10:00000 | -1051786 | 105.1786 | 60390889 | 233903.50 | 260061066 | 99835571 | 50074989 | 0.000000 | 907047852 | 17622518 | 0.000000
09-04-2025 20:10:05000 | -1055789 | 105.5789 | 60057310 | 233845.98 | 261107086 | 99838600 | 50058083 | 0.000000 | 915402466 | 17769002 | 0.000000
09-04-2025 20:10:10000 | -1065999 | 106.5999 | 62710430 | 233867.23 | 263636871 | 99827415 | 50032566 | 0.000000 | 923943970 | 17916453 | 0.000000
09-04-2025 20:10:15000 | -1070646 | 107.0646 | 62926885 | 233830.95 | 264826782 | 99827721 | 50030983 | 0.000000 | 932782837 | 18064904 | 0.000000
09-04-2025 20:10:20000 | -1076078 | 107.6078 | 62479199 | 233825.06 | 266165680 | 99831863 | 50010326 | 0.000000 | 941510986 | 18214154 | 0.000000
09-04-2025 20:10:25000 | -1071775 | 107.1775 | 59916777 | 233853.91 | 265038391 | 99844101 | 50016159 | 0.000000 | 949984802 | 18363152 | 0.000000
09-04-2025 20:10:30000 | -1059356 | 105.9356 | 60672104 | 233948.31 | 261880280 | 99836395 | 50033199 | 0.000000 | 958291260 | 18510779 | 0.000000
09-04-2025 20:10:35000 | -1050335 | 105.0335 | 59593682 | 233930.86 | 259662537 | 99839432 | 50054398 | 0.000000 | 966597961 | 18657090 | 0.000000
09-04-2025 20:10:40000 | -1043442 | 104.3442 | 56993599 | 233897.63 | 257964813 | 99851158 | 50057713 | 0.000000 | 974618591 | 18802162 | 0.000000
09-04-2025 20:10:45000 | -1038007 | 103.8007 | 59531455 | 233995.47 | 256552856 | 99835945 | 50065273 | 0.000000 | 982790039 | 18946830 | 0.000000
09-04-2025 20:10:50000 | -1040677 | 104.0677 | 61994868 | 233999.89 | 257242096 | 99823029 | 50070770 | 0.000000 | 991171570 | 19091391 | 0.000000
09-04-2025 20:10:55000 | -1049562 | 104.9562 | 61141133 | 233864.63 | 259567841 | 99830757 | 50055882 | 0.000000 | 999748352 | 19236789 | 0.000000
09-04-2025 20:11:00000 | -1055835 | 105.5835 | 62530986 | 233898.11 | 261095734 | 99825089 | 50043892 | 0.000000 | 10083658 | 19383166 | 0.000000
09-04-2025 20:11:05000 | -1055197 | 105.5197 | 64506270 | 233971.42 | 260885254 | 99813667 | 50051296 | 0.000000 | 10172745 | 19529768 | 0.000000
09-04-2025 20:11:10000 | -1060860 | 106.086 | 63695444 | 233946.33 | 262303497 | 99820236 | 50037781 | 0.000000 | 10261763 | 19677016 | 0.000000
09-04-2025 20:11:15000 | -1063318 | 106.3318 | 63414077 | 233936.97 | 262908630 | 99822639 | 50035534 | 0.000000 | 10350652 | 19824510 | 0.000000
09-04-2025 20:11:20000 | -1068892 | 106.8892 | 62176406 | 233877.33 | 264330688 | 99831245 | 50021675 | 0.000000 | 10437275 | 19972578 | 0.000000
09-04-2025 20:11:25000 | -1077571 | 107.7571 | 62743579 | 233801.58 | 266563934 | 99830910 | 50004974 | 0.000000 | 10524242 | 20121773 | 0.000000
09-04-2025 20:11:30000 | -1078485 | 107.8485 | 61137490 | 233767.89 | 266805817 | 99839706 | 49982403 | 0.000000 | 10610136 | 20271504 | 0.000000
09-04-2025 20:11:35000 | -1062061 | 106.2061 | 59392520 | 233925.27 | 262555145 | 99844002 | 50011982 | 0.000000 | 10694246 | 20420166 | 0.000000
09-04-2025 20:11:40000 | -1051922 | 105.1922 | 57070171 | 233902.83 | 260051208 | 99853157 | 50027508 | 0.000000 | 10774229 | 20567051 | 0.000000
09-04-2025 20:11:45000 | -1050017 | 105.0017 | 54241289 | 233774.08 | 259687744 | 99866844 | 50029232 | 0.000000 | 10851299 | 20712963 | 0.000000
09-04-2025 20:11:50000 | -1055870 | 105.587 | 55875264 | 233780.00 | 261143372 | 99860275 | 50008778 | 0.000000 | 10928430 | 20859285 | 0.000000
09-04-2025 20:11:55000 | -1050353 | 105.0353 | 59912510 | 233930.00 | 259677155 | 99837715 | 50032623 | 0.000000 | 11010708 | 21005693 | 0.000000
09-04-2025 20:12:00000 | -1042227 | 104.2227 | 57737998 | 233920.34 | 257652252 | 99846901 | 50055332 | 0.000000 | 11092892 | 21150688 | 0.000000
09-04-2025 20:12:05000 | -1035544 | 103.5544 | 61953179 | 234108.08 | 255857452 | 99821518 | 50074291 | 0.000000 | 11175469 | 21294680 | 0.000000
09-04-2025 20:12:10000 | -1032013 | 103.2013 | 65306221 | 234101.03 | 255054535 | 99800377 | 50093983 | 0.000000 | 11264977 | 21438270 | 0.000000
09-04-2025 20:12:15000 | -1043337 | 104.3337 | 63445864 | 233928.55 | 257997192 | 99815613 | 50072166 | 0.000000 | 11353833 | 21582426 | 0.000000
09-04-2025 20:12:20000 | -1061737 | 106.1737 | 66567373 | 233923.94 | 262580780 | 99804031 | 50037468 | 0.000000 | 11444753 | 21728979 | 0.000000
09-04-2025 20:12:25000 | -1072295 | 107.2295 | 68753564 | 233972.45 | 265161194 | 99795074 | 50024918 | 0.000000 | 11539528 | 21877406 | 0.000000
09-04-2025 20:12:30000 | -1073943 | 107.3943 | 67677305 | 233973.48 | 265548035 | 99802032 | 50024769 | 0.000000 | 11634921 | 22026596 | 0.000000
09-04-2025 20:12:35000 | -1064597 | 106.4597 | 64002109 | 233984.58 | 263182617 | 99819778 | 50034782 | 0.000000 | 11726053 | 22175021 | 0.000000
09-04-2025 20:12:40000 | -1057745 | 105.7745 | 60958892 | 233947.17 | 261493317 | 99834343 | 50043182 | 0.000000 | 11812008 | 22322098 | 0.000000
09-04-2025 20:12:45000 | -1063568 | 106.3568 | 63350420 | 233927.23 | 262985016 | 99823074 | 50023743 | 0.000000 | 11898413 | 22469242 | 0.000000
09-04-2025 20:12:50000 | -1066171 | 106.6171 | 64611113 | 233958.00 | 263606110 | 99816879 | 50020500 | 0.000000 | 11987136 | 22617170 | 0.000000
09-04-2025 20:12:55000 | -1067673 | 106.7673 | 63627979 | 233930.19 | 263994629 | 99822891 | 50010197 | 0.000000 | 12075254 | 22765541 | 0.000000
09-04-2025 20:13:00000 | -1056004 | 105.6004 | 61982227 | 233987.63 | 261029938 | 99828186 | 50035290 | 0.000000 | 12163108 | 22912930 | 0.000000
09-04-2025 20:13:05000 | -1062185 | 106.2185 | 60659199 | 233797.39 | 262746490 | 99837334 | 50020199 | 0.000000 | 12247845 | 23059975 | 0.000000
09-04-2025 20:13:10000 | -1076368 | 107.6368 | 59484541 | 233717.75 | 266316925 | 99847641 | 49972374 | 0.000000 | 12331320 | 23208973 | 0.000000
09-04-2025 20:13:15000 | -1065302 | 106.5302 | 58673394 | 233841.20 | 263439606 | 99848671 | 50001244 | 0.000000 | 12415421 | 23357762 | 0.000000
09-04-2025 20:13:20000 | -1057459 | 105.7459 | 57350078 | 233850.59 | 261475830 | 99853256 | 50014870 | 0.000000 | 12494482 | 23505049 | 0.000000
09-04-2025 20:13:25000 | -1044379 | 104.4379 | 57127852 | 233916.70 | 258175446 | 99850731 | 50042862 | 0.000000 | 12574657 | 23650711 | 0.000000
09-04-2025 20:13:30000 | -1036975 | 103.6975 | 58366494 | 233949.88 | 256334747 | 99841972 | 50053856 | 0.000000 | 12655331 | 23795000 | 0.000000
09-04-2025 20:13:35000 | -1029226 | 102.9226 | 60605786 | 234067.25 | 254326721 | 99827080 | 50081093 | 0.000000 | 12737477 | 23938264 | 0.000000
09-04-2025 20:13:40000 | -1031505 | 103.1505 | 60238604 | 233923.03 | 255039993 | 99829918 | 50090199 | 0.000000 | 12822208 | 24081131 | 0.000000
09-04-2025 20:13:45000 | -1041925 | 104.1925 | 60895205 | 233907.00 | 257637543 | 99829643 | 50064339 | 0.000000 | 12905632 | 24225068 | 0.000000
09-04-2025 20:13:50000 | -1057058 | 105.7058 | 63350884 | 233850.59 | 261463623 | 99820892 | 50042595 | 0.000000 | 12992996 | 24371289 | 0.000000
09-04-2025 20:13:55000 | -1066074 | 106.6074 | 65189414 | 233888.09 | 263668823 | 99813560 | 50036995 | 0.000000 | 13082734 | 24518793 | 0.000000
09-04-2025 20:14:00000 | -1071878 | 107.1878 | 63739673 | 233836.92 | 265134827 | 99823662 | 50017727 | 0.000000 | 13173418 | 24667521 | 0.000000
09-04-2025 20:14:05000 | -1073890 | 107.389 | 64020010 | 233915.03 | 265549469 | 99822777 | 50002674 | 0.000000 | 13261876 | 24816682 | 0.000000
09-04-2025 20:14:10000 | -1077636 | 107.7636 | 58891240 | 233728.48 | 266612335 | 99851013 | 49983974 | 0.000000 | 13347305 | 24965967 | 0.000000
09-04-2025 20:14:15000 | -1067174 | 106.7174 | 60970439 | 233938.86 | 263821564 | 99837189 | 49997395 | 0.000000 | 13431172 | 25114729 | 0.000000
09-04-2025 20:14:20000 | -1062238 | 106.2238 | 59895410 | 233880.30 | 262655060 | 99841408 | 50001740 | 0.000000 | 13513945 | 25262250 | 0.000000
09-04-2025 20:14:25000 | -1056846 | 105.6846 | 58896279 | 233873.30 | 261320221 | 99845078 | 50003807 | 0.000000 | 13596022 | 25409232 | 0.000000
09-04-2025 20:14:30000 | -1059656 | 105.9656 | 60026489 | 233853.55 | 262050415 | 99839943 | 49994625 | 0.000000 | 13678738 | 25556191 | 0.000000
09-04-2025 20:14:35000 | -1059507 | 105.9507 | 61423433 | 233921.44 | 261957794 | 99832375 | 49993786 | 0.000000 | 13762509 | 25703695 | 0.000000
09-04-2025 20:14:40000 | -1048511 | 104.8511 | 59057124 | 233912.44 | 259225830 | 99841751 | 50028721 | 0.000000 | 13846110 | 25849994 | 0.000000
09-04-2025 20:14:45000 | -1037788 | 103.7788 | 55431772 | 233878.36 | 256572357 | 99857658 | 50050838 | 0.000000 | 13925179 | 25994457 | 0.000000
09-04-2025 20:14:50000 | -1041225 | 104.1225 | 57685649 | 233866.63 | 257462555 | 99846886 | 50042080 | 0.000000 | 14004146 | 26138734 | 0.000000
09-04-2025 20:14:55000 | -1050958 | 105.0958 | 59731357 | 233866.83 | 259894165 | 99838875 | 50041332 | 0.000000 | 14086965 | 26283977 | 0.000000
09-04-2025 20:15:00000 | -1057283 | 105.7283 | 60122466 | 233811.58 | 261513855 | 99838707 | 50032494 | 0.000000 | 14170598 | 26430352 | 0.000000
09-04-2025 20:15:05000 | -1063032 | 106.3032 | 59175127 | 233764.20 | 262971100 | 99845421 | 50012569 | 0.000000 | 8239048 | 147113342 | 0.000000
09-04-2025 20:15:10000 | -1067165 | 106.7165 | 59582344 | 233791.95 | 263964417 | 99844498 | 50005013 | 0.000000 | 16516470 | 295170624 | 0.000000
09-04-2025 20:15:15000 | -1059602 | 105.9602 | 58765537 | 233851.80 | 262022980 | 99846565 | 50030518 | 0.000000 | 24784170 | 442819153 | 0.000000
09-04-2025 20:15:20000 | -1055274 | 105.5274 | 57799082 | 233874.23 | 260917389 | 99850342 | 50041039 | 0.000000 | 32893856 | 589580505 | 0.000000
09-04-2025 20:15:25000 | -1057183 | 105.7183 | 59659453 | 233877.53 | 261409302 | 99841148 | 50028507 | 0.000000 | 41127430 | 736250977 | 0.000000
09-04-2025 20:15:30000 | -1059000 | 105.9 | 59213789 | 233836.06 | 261897186 | 99844040 | 50026508 | 0.000000 | 49491955 | 883270142 | 0.000000
09-04-2025 20:15:35000 | -1061451 | 106.1451 | 61207905 | 233882.38 | 262478699 | 99834152 | 50022461 | 0.000000 | 57935120 | 10307957 | 0.000000
09-04-2025 20:15:40000 | -1059285 | 105.9285 | 61865581 | 233937.95 | 261890656 | 99829887 | 50032757 | 0.000000 | 66442123 | 11783038 | 0.000000
09-04-2025 20:15:45000 | -1055738 | 105.5738 | 60412417 | 233928.38 | 261008606 | 99836678 | 50033699 | 0.000000 | 74866631 | 13251460 | 0.000000
09-04-2025 20:15:50000 | -1057590 | 105.759 | 60853359 | 233914.41 | 261484833 | 99834869 | 50027447 | 0.000000 | 83296211 | 14719828 | 0.000000
09-04-2025 20:15:55000 | -1053084 | 105.3084 | 60913076 | 233952.17 | 260335480 | 99833130 | 50044853 | 0.000000 | 91759575 | 16184241 | 0.000000
09-04-2025 20:16:00000 | -1057023 | 105.7023 | 59902534 | 233857.55 | 261395111 | 99839806 | 50024414 | 0.000000 | 100141258 | 17650276 | 0.000000
09-04-2025 20:16:05000 | -1064967 | 106.4967 | 62264888 | 233831.80 | 263416443 | 99829521 | 50014771 | 0.000000 | 108768387 | 19125627 | 0.000000
09-04-2025 20:16:10000 | -1078979 | 107.8979 | 60753672 | 233690.20 | 267011017 | 99841850 | 49973621 | 0.000000 | 117403404 | 20618049 | 0.000000
09-04-2025 20:16:15000 | -1082854 | 108.2854 | 59878706 | 233735.61 | 267904083 | 99847458 | 49958805 | 0.000000 | 125765343 | 22122405 | 0.000000
09-04-2025 20:16:20000 | -1068341 | 106.8341 | 60282202 | 233904.92 | 264136230 | 99841187 | 49989792 | 0.000000 | 134158417 | 23615393 | 0.000000
09-04-2025 20:16:25000 | -1052976 | 105.2976 | 56838228 | 233890.58 | 260319733 | 99854630 | 50007740 | 0.000000 | 142159790 | 25085552 | 0.000000
09-04-2025 20:16:30000 | -1045498 | 104.5498 | 54264932 | 233864.89 | 258470825 | 99865570 | 50016682 | 0.000000 | 149792618 | 26541702 | 0.000000
09-04-2025 20:16:35000 | -1042081 | 104.2081 | 53879600 | 233816.02 | 257680725 | 99866600 | 50022930 | 0.000000 | 157226700 | 27989968 | 0.000000
09-04-2025 20:16:40000 | -1046120 | 104.612 | 56075098 | 233783.19 | 258738617 | 99856644 | 50024979 | 0.000000 | 164991058 | 29440898 | 0.000000
09-04-2025 20:16:45000 | -1046574 | 104.6574 | 58456338 | 233872.02 | 258784943 | 99844376 | 50032135 | 0.000000 | 172910156 | 30894214 | 0.000000
09-04-2025 20:16:50000 | -1047396 | 104.7396 | 56437983 | 233806.02 | 259032990 | 99855141 | 50022556 | 0.000000 | 180819489 | 32346123 | 0.000000
09-04-2025 20:16:55000 | -1048869 | 104.8869 | 57232241 | 233837.27 | 259376038 | 99851463 | 50034435 | 0.000000 | 188767517 | 33804417 | 0.000000
09-04-2025 20:17:00000 | -1045304 | 104.5304 | 57922368 | 233904.45 | 258428406 | 99846825 | 50052349 | 0.000000 | 196762756 | 35257703 | 0.000000
09-04-2025 20:17:05000 | -1059464 | 105.9464 | 59442920 | 233786.78 | 262073914 | 99842972 | 50027363 | 0.000000 | 204891617 | 36719834 | 0.000000
09-04-2025 20:17:10000 | -1076377 | 107.6377 | 62577314 | 233757.69 | 266320038 | 99831429 | 49996464 | 0.000000 | 213438980 | 38205825 | 0.000000
09-04-2025 20:17:15000 | -1080760 | 108.076 | 59536450 | 233701.61 | 267419006 | 99848610 | 49972397 | 0.000000 | 221956406 | 39703870 | 0.000000
09-04-2025 20:17:20000 | -1083478 | 108.3478 | 58050405 | 233701.23 | 268070526 | 99856781 | 49956757 | 0.000000 | 230076477 | 41208765 | 0.000000
09-04-2025 20:17:25000 | -1079362 | 107.9362 | 57182666 | 233736.58 | 267006592 | 99859962 | 49956276 | 0.000000 | 238060455 | 42710674 | 0.000000
09-04-2025 20:17:30000 | -1074079 | 107.4079 | 56086772 | 233734.27 | 265691010 | 99863937 | 49951694 | 0.000000 | 245888382 | 44204683 | 0.000000
09-04-2025 20:17:35000 | -1062886 | 106.2886 | 55478394 | 233825.00 | 262817688 | 99864059 | 49967010 | 0.000000 | 253643890 | 45687871 | 0.000000
09-04-2025 20:17:40000 | -1052242 | 105.2242 | 53480771 | 233820.16 | 260173126 | 99871086 | 49980793 | 0.000000 | 261119293 | 47156133 | 0.000000
09-04-2025 20:17:45000 | -1050312 | 105.0312 | 52214854 | 233752.20 | 259757172 | 99876656 | 49977131 | 0.000000 | 268408691 | 48616060 | 0.000000
09-04-2025 20:17:50000 | -1043246 | 104.3246 | 54949429 | 233848.81 | 257942902 | 99861572 | 49990566 | 0.000000 | 275907074 | 50069761 | 0.000000
09-04-2025 20:17:55000 | -1030970 | 103.097 | 54160098 | 233901.00 | 254848877 | 99862297 | 50027649 | 0.000000 | 283433685 | 51507061 | 0.000000
09-04-2025 20:18:00000 | -1036865 | 103.6865 | 53214839 | 233747.48 | 256459167 | 99868561 | 50023491 | 0.000000 | 290831390 | 52938057 | 0.000000
09-04-2025 20:18:05000 | -1050977 | 105.0977 | 57632573 | 233744.02 | 260001923 | 99849983 | 49995667 | 0.000000 | 298639252 | 54387192 | 0.000000
09-04-2025 20:18:10000 | -1052564 | 105.2564 | 58497603 | 233794.64 | 260352722 | 99845924 | 50001400 | 0.000000 | 306818298 | 55851450 | 0.000000
09-04-2025 20:18:15000 | -1056901 | 105.6901 | 56269185 | 233740.86 | 261451752 | 99858574 | 49993694 | 0.000000 | 314748749 | 57319038 | 0.000000
09-04-2025 20:18:20000 | -1068164 | 106.8164 | 58877876 | 233754.17 | 264246490 | 99848434 | 49963535 | 0.000000 | 322707520 | 58800093 | 0.000000
09-04-2025 20:18:25000 | -1061393 | 106.1393 | 57980566 | 233809.75 | 262501495 | 99851128 | 49988384 | 0.000000 | 330998169 | 60277256 | 0.000000
09-04-2025 20:18:30000 | -1058883 | 105.8883 | 57034600 | 233788.69 | 261893555 | 99855255 | 49989025 | 0.000000 | 338887024 | 61748325 | 0.000000
09-04-2025 20:18:35000 | -1061450 | 106.145 | 58900757 | 233830.58 | 262503235 | 99846390 | 49974739 | 0.000000 | 346936890 | 63223027 | 0.000000
09-04-2025 20:18:40000 | -1061169 | 106.1169 | 57380493 | 233787.73 | 262465729 | 99854126 | 49981712 | 0.000000 | 355007141 | 64698423 | 0.000000
09-04-2025 20:18:45000 | -1055997 | 105.5997 | 56346211 | 233789.72 | 261171967 | 99857948 | 49993702 | 0.000000 | 362871735 | 66167144 | 0.000000
09-04-2025 20:18:50000 | -1052955 | 105.2955 | 56366069 | 233822.63 | 260383698 | 99857025 | 49994801 | 0.000000 | 370689423 | 67632402 | 0.000000
09-04-2025 20:18:55000 | -1055514 | 105.5514 | 55518350 | 233752.50 | 261081879 | 99861954 | 49983017 | 0.000000 | 378433838 | 69098701 | 0.000000
09-04-2025 20:19:00000 | -1057377 | 105.7377 | 53145952 | 233684.23 | 261590332 | 99873924 | 49987095 | 0.000000 | 386022278 | 70566152 | 0.000000
09-04-2025 20:19:05000 | -1047399 | 104.7399 | 54445791 | 233831.56 | 258987183 | 99865166 | 50006981 | 0.000000 | 393513885 | 72025928 | 0.000000
09-04-2025 20:19:10000 | -1037102 | 103.7102 | 55616440 | 233904.13 | 256375793 | 99856522 | 50043144 | 0.000000 | 401206238 | 73470313 | 0.000000
09-04-2025 20:19:15000 | -1034603 | 103.4603 | 55756797 | 233854.03 | 255816391 | 99855095 | 50054859 | 0.000000 | 408943909 | 74906211 | 0.000000
09-04-2025 20:19:20000 | -1049030 | 104.903 | 57250718 | 233742.83 | 259517456 | 99851410 | 50030148 | 0.000000 | 416841187 | 76353428 | 0.000000
09-04-2025 20:19:25000 | -1065493 | 106.5493 | 60470830 | 233758.56 | 263605133 | 99839340 | 49994270 | 0.000000 | 424981873 | 77825283 | 0.000000
09-04-2025 20:19:30000 | -1074662 | 107.4662 | 60580781 | 233736.92 | 265890961 | 99841492 | 49985695 | 0.000000 | 433448120 | 79310220 | 0.000000
09-04-2025 20:19:35000 | -1075676 | 107.5676 | 61030225 | 233779.78 | 266103516 | 99839432 | 49977577 | 0.000000 | 441946869 | 80803511 | 0.000000
09-04-2025 20:19:40000 | -1071839 | 107.1839 | 59844053 | 233835.89 | 265070862 | 99844498 | 49970894 | 0.000000 | 450201385 | 82296270 | 0.000000
09-04-2025 20:19:45000 | -1059208 | 105.9208 | 57843853 | 233865.52 | 261897888 | 99851219 | 49991226 | 0.000000 | 458431580 | 83774805 | 0.000000
09-04-2025 20:19:50000 | -1051982 | 105.1982 | 56217646 | 233864.22 | 260096649 | 99857513 | 50000149 | 0.000000 | 466246796 | 85238555 | 0.000000
09-04-2025 20:19:55000 | -1048750 | 104.875 | 54942852 | 233820.95 | 259330780 | 99863052 | 49999676 | 0.000000 | 474002106 | 86695557 | 0.000000
09-04-2025 20:20:00000 | -1046586 | 104.6586 | 55543711 | 233828.66 | 258795868 | 99859467 | 50007927 | 0.000000 | 481771271 | 88149287 | 0.000000
09-04-2025 20:20:05000 | -1045723 | 104.5723 | 54608750 | 233801.97 | 258600342 | 99863930 | 50001087 | 0.000000 | 489388245 | 89601426 | 0.000000
09-04-2025 20:20:10000 | -1046881 | 104.6881 | 56171089 | 233787.44 | 258922791 | 99856361 | 50001896 | 0.000000 | 497204834 | 91055615 | 0.000000
09-04-2025 20:20:15000 | -1048966 | 104.8966 | 54910181 | 233752.48 | 259459625 | 99863274 | 49999245 | 0.000000 | 504874359 | 92508477 | 0.000000
09-04-2025 20:20:20000 | -1048083 | 104.8083 | 57054800 | 233859.52 | 259159393 | 99852158 | 50000019 | 0.000000 | 512651978 | 93963252 | 0.000000
09-04-2025 20:20:25000 | -1046310 | 104.631 | 56071865 | 233801.03 | 258764923 | 99856712 | 50011139 | 0.000000 | 520472351 | 95416406 | 0.000000
09-04-2025 20:20:30000 | -1047262 | 104.7262 | 56422368 | 233807.83 | 258997284 | 99855186 | 50009686 | 0.000000 | 528383057 | 96867383 | 0.000000
09-04-2025 20:20:35000 | -1057585 | 105.7585 | 60068149 | 233820.34 | 261581451 | 99839088 | 49986835 | 0.000000 | 536558472 | 98332666 | 0.000000
09-04-2025 20:20:40000 | -1064051 | 106.4051 | 61394297 | 233859.53 | 263149139 | 99833961 | 49983135 | 0.000000 | 545039490 | 99809570 | 0.000000
09-04-2025 20:20:45000 | -1054026 | 105.4026 | 59204473 | 233917.91 | 260581146 | 99842621 | 50009346 | 0.000000 | 553433167 | 10127908 | 0.000000
09-04-2025 20:20:50000 | -1048541 | 104.8541 | 56425991 | 233830.88 | 259288208 | 99855515 | 50025833 | 0.000000 | 561340942 | 10273764 | 0.000000
09-04-2025 20:20:55000 | -1047411 | 104.7411 | 54892520 | 233801.53 | 259021118 | 99862953 | 50013996 | 0.000000 | 569083313 | 10419245 | 0.000000
09-04-2025 20:21:00000 | -1050854 | 105.0854 | 56464707 | 233827.09 | 259862610 | 99855957 | 50003582 | 0.000000 | 576792236 | 10565042 | 0.000000
09-04-2025 20:21:05000 | -1044039 | 104.4039 | 53575313 | 233754.89 | 258224365 | 99868599 | 50022778 | 0.000000 | 584614319 | 10710443 | 0.000000
09-04-2025 20:21:10000 | -1036958 | 103.6958 | 53114023 | 233810.81 | 256411621 | 99869080 | 50032833 | 0.000000 | 592003479 | 10854975 | 0.000000
09-04-2025 20:21:15000 | -1047269 | 104.7269 | 55004434 | 233791.80 | 259003845 | 99862358 | 50014660 | 0.000000 | 599430969 | 10999912 | 0.000000
09-04-2025 20:21:20000 | -1050108 | 105.0108 | 57532114 | 233798.73 | 259724365 | 99850258 | 50019642 | 0.000000 | 607446350 | 11145733 | 0.000000
09-04-2025 20:21:25000 | -1056802 | 105.6802 | 55909771 | 233691.39 | 261478485 | 99860352 | 50000690 | 0.000000 | 615317749 | 11292033 | 0.000000
09-04-2025 20:21:30000 | -1069129 | 106.9129 | 57174019 | 233688.45 | 264533661 | 99857315 | 49976219 | 0.000000 | 623217102 | 11439978 | 0.000000
09-04-2025 20:21:35000 | -1072923 | 107.2923 | 53902510 | 233637.95 | 265485596 | 99874039 | 49964630 | 0.000000 | 630830505 | 11589200 | 0.000000
09-04-2025 20:21:40000 | -1068143 | 106.8143 | 52284229 | 233652.30 | 264274292 | 99880417 | 49969082 | 0.000000 | 638266724 | 11737944 | 0.000000
09-04-2025 20:21:45000 | -1061885 | 106.1885 | 52573574 | 233742.55 | 262627380 | 99877663 | 49973263 | 0.000000 | 645519836 | 11885882 | 0.000000
09-04-2025 20:21:50000 | -1049536 | 104.9536 | 51740098 | 233789.70 | 259520508 | 99878708 | 50003216 | 0.000000 | 652761047 | 12032303 | 0.000000
09-04-2025 20:21:55000 | -1038051 | 103.8051 | 49954082 | 233753.20 | 256708282 | 99884407 | 50021629 | 0.000000 | 659858826 | 12177086 | 0.000000
09-04-2025 20:22:00000 | -1043238 | 104.3238 | 50947500 | 233726.28 | 258026642 | 99880966 | 50010197 | 0.000000 | 666873230 | 12321717 | 0.000000
09-04-2025 20:22:05000 | -1042137 | 104.2137 | 53974531 | 233790.64 | 257721161 | 99866150 | 50038925 | 0.000000 | 674241089 | 12466628 | 0.000000
09-04-2025 20:22:10000 | -1047893 | 104.7893 | 54511680 | 233766.41 | 259176331 | 99864967 | 50037041 | 0.000000 | 681802734 | 12611711 | 0.000000
09-04-2025 20:22:15000 | -1064238 | 106.4238 | 56448516 | 233673.48 | 263337708 | 99859627 | 49996109 | 0.000000 | 689569458 | 12758521 | 0.000000
09-04-2025 20:22:20000 | -1075246 | 107.5246 | 60068198 | 233734.61 | 266031342 | 99844322 | 49980797 | 0.000000 | 697765076 | 12907245 | 0.000000
09-04-2025 20:22:25000 | -1073406 | 107.3406 | 56837715 | 233696.50 | 265576019 | 99860107 | 49979847 | 0.000000 | 705943359 | 13056601 | 0.000000
09-04-2025 20:22:30000 | -1063457 | 106.3457 | 53773364 | 233722.48 | 263053650 | 99872406 | 49990948 | 0.000000 | 713611328 | 13204886 | 0.000000
09-04-2025 20:22:35000 | -1051802 | 105.1802 | 54951221 | 233872.27 | 260026215 | 99863800 | 50012417 | 0.000000 | 721145508 | 13351702 | 0.000000
09-04-2025 20:22:40000 | -1031782 | 103.1782 | 53505664 | 233931.78 | 255009674 | 99865807 | 50061237 | 0.000000 | 728662781 | 13496104 | 0.000000
09-04-2025 20:22:45000 | -1041352 | 104.1352 | 53310298 | 233725.64 | 257593445 | 99869217 | 50044086 | 0.000000 | 735999817 | 13639757 | 0.000000
09-04-2025 20:22:50000 | -1059282 | 105.9282 | 55940063 | 233652.42 | 262129395 | 99860847 | 49998020 | 0.000000 | 743568176 | 13785689 | 0.000000
09-04-2025 20:22:55000 | -1076232 | 107.6232 | 58441416 | 233651.98 | 266344788 | 99852890 | 49968197 | 0.000000 | 751585999 | 13934545 | 0.000000
09-04-2025 20:23:00000 | -1071064 | 107.1064 | 56372998 | 233700.00 | 264990845 | 99861778 | 49991833 | 0.000000 | 759687439 | 14083940 | 0.000000
09-04-2025 20:23:05000 | -1059168 | 105.9168 | 53126616 | 233746.36 | 261962067 | 99874443 | 50009975 | 0.000000 | 767133057 | 14231589 | 0.000000
09-04-2025 20:23:10000 | -1056666 | 105.6666 | 53567861 | 233724.73 | 261373596 | 99871750 | 50007736 | 0.000000 | 774581665 | 14378405 | 0.000000
09-04-2025 20:23:15000 | -1058090 | 105.809 | 56570693 | 233808.94 | 261667816 | 99857384 | 49993561 | 0.000000 | 782251831 | 14525235 | 0.000000
09-04-2025 20:23:20000 | -1049370 | 104.937 | 57971724 | 233886.31 | 259450562 | 99847755 | 50020809 | 0.000000 | 790357666 | 14671757 | 0.000000
09-04-2025 20:23:25000 | -1039706 | 103.9706 | 53856431 | 233821.56 | 257085602 | 99866112 | 50037346 | 0.000000 | 797997131 | 14816718 | 0.000000
09-04-2025 20:23:30000 | -1041224 | 104.1224 | 53761489 | 233809.92 | 257474060 | 99866966 | 50033710 | 0.000000 | 805434814 | 14961035 | 0.000000
09-04-2025 20:23:35000 | -1050676 | 105.0676 | 56364854 | 233758.27 | 259894531 | 99856415 | 50028034 | 0.000000 | 813164368 | 15106393 | 0.000000
09-04-2025 20:23:40000 | -1062556 | 106.2556 | 57955557 | 233710.58 | 262904724 | 99851578 | 49997215 | 0.000000 | 821145203 | 15253346 | 0.000000
09-04-2025 20:23:45000 | -1068740 | 106.874 | 57463340 | 233690.33 | 264442749 | 99855766 | 49989243 | 0.000000 | 829395081 | 15401596 | 0.000000
09-04-2025 20:23:50000 | -1064059 | 106.4059 | 58261621 | 233823.94 | 263145264 | 99850433 | 49994434 | 0.000000 | 837513672 | 15549750 | 0.000000
09-04-2025 20:23:55000 | -1059146 | 105.9146 | 56182744 | 233781.58 | 261954712 | 99859604 | 49996983 | 0.000000 | 845450439 | 15696991 | 0.000000
09-04-2025 20:24:00000 | -1056670 | 105.667 | 57411655 | 233866.48 | 261264862 | 99852722 | 50000771 | 0.000000 | 853353760 | 15843948 | 0.000000
09-04-2025 20:24:05000 | -1056100 | 105.61 | 57583569 | 233853.56 | 261142273 | 99851685 | 50001495 | 0.000000 | 861327087 | 15990767 | 0.000000
09-04-2025 20:24:10000 | -1046284 | 104.6284 | 54489536 | 233793.95 | 258747070 | 99864662 | 50027416 | 0.000000 | 869178284 | 16136675 | 0.000000
09-04-2025 20:24:15000 | -1042072 | 104.2072 | 52611055 | 233775.39 | 257705414 | 99872795 | 50030907 | 0.000000 | 876574097 | 16281453 | 0.000000
09-04-2025 20:24:20000 | -1045172 | 104.5172 | 54814067 | 233772.95 | 258500122 | 99862762 | 50037712 | 0.000000 | 884123291 | 16426328 | 0.000000
09-04-2025 20:24:25000 | -1045130 | 104.513 | 53295073 | 233743.02 | 258502563 | 99870232 | 50034180 | 0.000000 | 891656860 | 16571547 | 0.000000
09-04-2025 20:24:30000 | -1052268 | 105.2268 | 56109517 | 233757.27 | 260291718 | 99858139 | 50020535 | 0.000000 | 899281860 | 16717285 | 0.000000
09-04-2025 20:24:35000 | -1061519 | 106.1519 | 58865679 | 233792.47 | 262563202 | 99846596 | 50004314 | 0.000000 | 907261230 | 16864207 | 0.000000
09-04-2025 20:24:40000 | -1072301 | 107.2301 | 57653154 | 233668.50 | 265347168 | 99855774 | 49980450 | 0.000000 | 915260620 | 17012475 | 0.000000
09-04-2025 20:24:45000 | -1079800 | 107.98 | 58997910 | 233701.59 | 267176392 | 99851067 | 49955196 | 0.000000 | 923490967 | 17162100 | 0.000000
09-04-2025 20:24:50000 | -1081726 | 108.1726 | 58594443 | 233770.73 | 267567688 | 99853615 | 49951469 | 0.000000 | 931583130 | 17312377 | 0.000000
09-04-2025 20:24:55000 | -1065004 | 106.5004 | 56375283 | 233847.77 | 263326599 | 99860191 | 49983402 | 0.000000 | 939582336 | 17461482 | 0.000000
09-04-2025 20:25:00000 | -1050950 | 105.095 | 52722144 | 233786.56 | 259883209 | 99874405 | 50001129 | 0.000000 | 947090088 | 17608045 | 0.000000
09-04-2025 20:25:05000 | -1047668 | 104.7668 | 52308564 | 233744.20 | 259115448 | 99875587 | 49998787 | 0.000000 | 954369751 | 17753783 | 0.000000
09-04-2025 20:25:10000 | -1054649 | 105.4649 | 53282783 | 233673.50 | 260927856 | 99872620 | 49975822 | 0.000000 | 961641602 | 17899832 | 0.000000
09-04-2025 20:25:15000 | -1061730 | 106.173 | 55899058 | 233706.88 | 262671448 | 99861694 | 49961926 | 0.000000 | 969378601 | 18046881 | 0.000000
09-04-2025 20:25:20000 | -1070045 | 107.0045 | 54410933 | 233618.98 | 264803497 | 99870972 | 49948143 | 0.000000 | 977065613 | 18194756 | 0.000000
09-04-2025 20:25:25000 | -1068509 | 106.8509 | 56898066 | 233801.17 | 264251343 | 99858521 | 49948662 | 0.000000 | 984702942 | 18343377 | 0.000000
09-04-2025 20:25:30000 | -1054500 | 105.45 | 52744678 | 233793.70 | 260753082 | 99875137 | 49994709 | 0.000000 | 992307251 | 18490932 | 0.000000
09-04-2025 20:25:35000 | -1036281 | 103.6281 | 49919131 | 233776.75 | 256247284 | 99884178 | 50029247 | 0.000000 | 999492065 | 18635641 | 0.000000
09-04-2025 20:25:40000 | -1035032 | 103.5032 | 52389766 | 233825.77 | 255909409 | 99872147 | 50031807 | 0.000000 | 10065283 | 18779621 | 0.000000
09-04-2025 20:25:45000 | -1037267 | 103.7267 | 53059087 | 233749.44 | 256552582 | 99869423 | 50043682 | 0.000000 | 10138830 | 18923301 | 0.000000
09-04-2025 20:25:50000 | -1044642 | 104.4642 | 56999575 | 233831.27 | 258333221 | 99851471 | 50037556 | 0.000000 | 10214959 | 19067902 | 0.000000
09-04-2025 20:25:55000 | -1059238 | 105.9238 | 57655454 | 233733.28 | 262051086 | 99852188 | 50019630 | 0.000000 | 10293965 | 19214258 | 0.000000
09-04-2025 20:26:00000 | -1066805 | 106.6805 | 60180454 | 233788.25 | 263888947 | 99841263 | 50013935 | 0.000000 | 10376681 | 19362090 | 0.000000
09-04-2025 20:26:05000 | -1060883 | 106.0883 | 60779106 | 233876.05 | 262338470 | 99836288 | 50031193 | 0.000000 | 10461129 | 19509783 | 0.000000
09-04-2025 20:26:10000 | -1057366 | 105.7366 | 58120562 | 233832.48 | 261483154 | 99849274 | 50030098 | 0.000000 | 10543021 | 19656598 | 0.000000
09-04-2025 20:26:15000 | -1066252 | 106.6252 | 58128311 | 233730.89 | 263789032 | 99851730 | 50003147 | 0.000000 | 10624056 | 19804012 | 0.000000
09-04-2025 20:26:20000 | -1083081 | 108.3081 | 61454326 | 233739.48 | 267975098 | 99839417 | 49958061 | 0.000000 | 10706992 | 19953564 | 0.000000
09-04-2025 20:26:25000 | -1077087 | 107.7087 | 59107148 | 233772.11 | 266427643 | 99849762 | 49975437 | 0.000000 | 10791209 | 20103631 | 0.000000
09-04-2025 20:26:30000 | -1068409 | 106.8409 | 55535708 | 233780.47 | 264231018 | 99865181 | 49984756 | 0.000000 | 10869161 | 20252479 | 0.000000
09-04-2025 20:26:35000 | -1053970 | 105.397 | 56304458 | 233910.30 | 260536621 | 99857613 | 50013199 | 0.000000 | 10946987 | 20399563 | 0.000000
09-04-2025 20:26:40000 | -1040270 | 104.027 | 54747354 | 233901.08 | 257150208 | 99861801 | 50032959 | 0.000000 | 11024758 | 20544771 | 0.000000
09-04-2025 20:26:45000 | -1033387 | 103.3387 | 56235635 | 233924.86 | 255445206 | 99852257 | 50057060 | 0.000000 | 11101620 | 20688395 | 0.000000
09-04-2025 20:26:50000 | -1033577 | 103.3577 | 58578843 | 233967.22 | 255478043 | 99839775 | 50058319 | 0.000000 | 11180677 | 20831914 | 0.000000
09-04-2025 20:26:55000 | -1046142 | 104.6142 | 59560630 | 233824.33 | 258745880 | 99838318 | 50044319 | 0.000000 | 11263055 | 20976498 | 0.000000
09-04-2025 20:27:00000 | -1067704 | 106.7704 | 62247700 | 233749.81 | 264194733 | 99830482 | 50000885 | 0.000000 | 11347780 | 21123596 | 0.000000
09-04-2025 20:27:05000 | -1080698 | 108.0698 | 61739741 | 233693.52 | 267446320 | 99837212 | 49969933 | 0.000000 | 11434338 | 21272779 | 0.000000
09-04-2025 20:27:10000 | -1078122 | 107.8122 | 60444712 | 233795.50 | 266676056 | 99843208 | 49976990 | 0.000000 | 11518381 | 21422893 | 0.000000
09-04-2025 20:27:15000 | -1062034 | 106.2034 | 56401909 | 233840.59 | 262602539 | 99859276 | 50008671 | 0.000000 | 11599451 | 21571270 | 0.000000
09-04-2025 20:27:20000 | -1050631 | 105.0631 | 55796035 | 233873.30 | 259749359 | 99859276 | 50024330 | 0.000000 | 11676909 | 21717660 | 0.000000
09-04-2025 20:27:25000 | -1038883 | 103.8883 | 55573296 | 233933.42 | 256782471 | 99857231 | 50034336 | 0.000000 | 11753713 | 21862693 | 0.000000
09-04-2025 20:27:30000 | -1018941 | 101.8941 | 55685352 | 234060.41 | 251734222 | 99850998 | 50091724 | 0.000000 | 11830433 | 22005064 | 0.000000
09-04-2025 20:27:35000 | -1026090 | 102.609 | 55923794 | 233846.30 | 253727875 | 99851807 | 50073662 | 0.000000 | 11908073 | 22146654 | 0.000000
09-04-2025 20:27:40000 | -1049299 | 104.9299 | 60595127 | 233798.52 | 259570251 | 99833672 | 50020855 | 0.000000 | 11990459 | 22291311 | 0.000000
09-04-2025 20:27:45000 | -1062291 | 106.2291 | 61913608 | 233797.02 | 262791107 | 99830582 | 50004547 | 0.000000 | 12076000 | 22438164 | 0.000000
09-04-2025 20:27:50000 | -1067687 | 106.7687 | 62999956 | 233839.98 | 264087219 | 99826370 | 49999561 | 0.000000 | 12162783 | 22586463 | 0.000000
09-04-2025 20:27:55000 | -1052585 | 105.2585 | 59381689 | 233936.88 | 260206451 | 99841248 | 50033009 | 0.000000 | 12247875 | 22733529 | 0.000000
09-04-2025 20:28:00000 | -1038665 | 103.8665 | 59354092 | 234029.08 | 256675751 | 99837120 | 50067852 | 0.000000 | 12329875 | 22878439 | 0.000000
09-04-2025 20:28:05000 | -1032442 | 103.2442 | 61104019 | 234036.78 | 255158936 | 99825325 | 50088158 | 0.000000 | 12413542 | 23021965 | 0.000000
09-04-2025 20:28:10000 | -1026862 | 102.6862 | 61257168 | 234044.30 | 253778397 | 99822540 | 50098827 | 0.000000 | 12497594 | 23164926 | 0.000000
09-04-2025 20:28:15000 | -1040739 | 104.0739 | 61655483 | 233920.30 | 257342743 | 99824982 | 50082928 | 0.000000 | 12582446 | 23308551 | 0.000000
09-04-2025 20:28:20000 | -1050448 | 105.0448 | 60271816 | 233776.56 | 259872375 | 99835800 | 50066303 | 0.000000 | 12668438 | 23454035 | 0.000000
09-04-2025 20:28:25000 | -1059466 | 105.9466 | 60931685 | 233811.45 | 262064514 | 99835030 | 50049526 | 0.000000 | 12751600 | 23600680 | 0.000000
09-04-2025 20:28:30000 | -1070488 | 107.0488 | 62172959 | 233825.61 | 264788391 | 99831764 | 50030575 | 0.000000 | 12836893 | 23748861 | 0.000000
09-04-2025 20:28:35000 | -1073778 | 107.3778 | 60447593 | 233766.25 | 265636566 | 99841927 | 50029224 | 0.000000 | 12922638 | 23897730 | 0.000000
09-04-2025 20:28:40000 | -1066595 | 106.6595 | 56061011 | 233738.03 | 263838196 | 99862152 | 50025845 | 0.000000 | 13003097 | 24046424 | 0.000000
09-04-2025 20:28:45000 | -1051417 | 105.1417 | 55596328 | 233916.25 | 259892456 | 99860489 | 50048752 | 0.000000 | 13080922 | 24193371 | 0.000000
09-04-2025 20:28:50000 | -1045323 | 104.5323 | 55071582 | 233839.97 | 258466217 | 99861511 | 50062721 | 0.000000 | 13157211 | 24338523 | 0.000000
09-04-2025 20:28:55000 | -1049656 | 104.9656 | 57381855 | 233841.64 | 259562897 | 99850906 | 50036205 | 0.000000 | 13234357 | 24484068 | 0.000000
09-04-2025 20:29:00000 | -1051820 | 105.182 | 57986523 | 233821.95 | 260127960 | 99848381 | 50043060 | 0.000000 | 13315499 | 24630154 | 0.000000
09-04-2025 20:29:05000 | -1033739 | 103.3739 | 53938823 | 233921.31 | 255506165 | 99864151 | 50081913 | 0.000000 | 13391630 | 24774902 | 0.000000
09-04-2025 20:29:10000 | -1028909 | 102.8909 | 56988145 | 233960.52 | 254314178 | 99846970 | 50103985 | 0.000000 | 13469403 | 24918121 | 0.000000
09-04-2025 20:29:15000 | -1026514 | 102.6514 | 61048267 | 234027.36 | 253708160 | 99823624 | 50114971 | 0.000000 | 13552166 | 25060807 | 0.000000
09-04-2025 20:29:20000 | -1033742 | 103.3742 | 63285884 | 234019.92 | 255529434 | 99813133 | 50113194 | 0.000000 | 13638291 | 25203707 | 0.000000
09-04-2025 20:29:25000 | -1040701 | 104.0701 | 66171577 | 234055.27 | 257248047 | 99798470 | 50109524 | 0.000000 | 13729014 | 25347674 | 0.000000
09-04-2025 20:29:30000 | -1047866 | 104.7866 | 69840005 | 234109.64 | 259011078 | 99778625 | 50111771 | 0.000000 | 13824578 | 25492883 | 0.000000
09-04-2025 20:29:35000 | -1049726 | 104.9726 | 69203228 | 234144.44 | 259419586 | 99783401 | 50104988 | 0.000000 | 13920437 | 25638545 | 0.000000
09-04-2025 20:29:40000 | -1045772 | 104.5772 | 70358794 | 234169.30 | 258437927 | 99774437 | 50120522 | 0.000000 | 14018297 | 25784096 | 0.000000
09-04-2025 20:29:45000 | -1049983 | 104.9983 | 68725859 | 234102.39 | 259522003 | 99786476 | 50107040 | 0.000000 | 14113936 | 25929363 | 0.000000
09-04-2025 20:29:50000 | -1068777 | 106.8777 | 68863066 | 233933.86 | 264344513 | 99793076 | 50056034 | 0.000000 | 14209807 | 26076701 | 0.000000
09-04-2025 20:29:55000 | -1075934 | 107.5934 | 71166396 | 234058.33 | 265998077 | 99781967 | 50033482 | 0.000000 | 14306777 | 26226008 | 0.000000
09-04-2025 20:30:00000 | -1069729 | 106.9729 | 70431001 | 234070.55 | 264445862 | 99783958 | 50053947 | 0.000000 | 14406866 | 26375004 | 0.000000
09-04-2025 20:30:05000 | -1066320 | 106.632 | 67725835 | 234067.42 | 263565765 | 99798912 | 50051094 | 0.000000 | 9471581 | 148239517 | 0.000000
09-04-2025 20:30:10000 | -1049928 | 104.9928 | 64036025 | 234058.83 | 259486450 | 99814522 | 50076622 | 0.000000 | 18616550 | 294642456 | 0.000000
09-04-2025 20:30:15000 | -1046835 | 104.6835 | 63786221 | 234037.23 | 258742188 | 99814880 | 50071148 | 0.000000 | 27352509 | 439875061 | 0.000000
09-04-2025 20:30:20000 | -1064837 | 106.4837 | 64893706 | 233906.28 | 263337799 | 99814819 | 50031097 | 0.000000 | 36241253 | 586423218 | 0.000000
09-04-2025 20:30:25000 | -1071907 | 107.1907 | 67463271 | 233953.25 | 265066254 | 99802528 | 50013863 | 0.000000 | 45480675 | 735196960 | 0.000000
09-04-2025 20:30:30000 | -1048038 | 104.8038 | 64237480 | 234110.38 | 258964325 | 99812683 | 50070675 | 0.000000 | 54635727 | 882082092 | 0.000000
09-04-2025 20:30:35000 | -1043468 | 104.3468 | 59960732 | 233960.30 | 257942719 | 99835312 | 50074909 | 0.000000 | 63192062 | 10271438 | 0.000000
09-04-2025 20:30:40000 | -1045782 | 104.5782 | 63391367 | 234039.23 | 258475586 | 99816788 | 50066650 | 0.000000 | 71726540 | 11721887 | 0.000000
09-04-2025 20:30:45000 | -1035743 | 103.5743 | 62618516 | 234048.50 | 255981415 | 99817741 | 50091320 | 0.000000 | 80527740 | 13164591 | 0.000000
09-04-2025 20:30:50000 | -1045166 | 104.5166 | 65032695 | 234005.55 | 258386078 | 99806976 | 50078068 | 0.000000 | 89348396 | 14612050 | 0.000000
09-04-2025 20:30:55000 | -1053638 | 105.3638 | 68075757 | 234056.19 | 260463379 | 99791924 | 50068806 | 0.000000 | 98703728 | 16074731 | 0.000000
09-04-2025 20:31:00000 | -1049030 | 104.903 | 67265293 | 234101.16 | 259265259 | 99795052 | 50083965 | 0.000000 | 108015259 | 17535378 | 0.000000
09-04-2025 20:31:05000 | -1039356 | 103.9356 | 66614517 | 234174.47 | 256794800 | 99795242 | 50122368 | 0.000000 | 117235825 | 18981948 | 0.000000
09-04-2025 20:31:10000 | -1043580 | 104.358 | 66514287 | 234071.92 | 257944763 | 99797501 | 50107578 | 0.000000 | 126327209 | 20424130 | 0.000000
09-04-2025 20:31:15000 | -1062675 | 106.2675 | 68791831 | 233961.27 | 262806061 | 99791130 | 50060795 | 0.000000 | 135879898 | 21890833 | 0.000000
09-04-2025 20:31:20000 | -1073923 | 107.3923 | 71712886 | 234036.91 | 265535126 | 99777786 | 50045052 | 0.000000 | 145755508 | 23378611 | 0.000000
09-04-2025 20:31:25000 | -1069501 | 106.9501 | 68132441 | 233983.83 | 264450684 | 99797699 | 50056503 | 0.000000 | 155455872 | 24867612 | 0.000000
09-04-2025 20:31:30000 | -1059269 | 105.9269 | 65259868 | 234074.36 | 261785065 | 99810760 | 50073055 | 0.000000 | 164660797 | 26343267 | 0.000000
09-04-2025 20:31:35000 | -1050148 | 105.0148 | 63276519 | 234018.80 | 259570038 | 99818962 | 50081631 | 0.000000 | 173654648 | 27805996 | 0.000000
09-04-2025 20:31:40000 | -1054941 | 105.4941 | 65222471 | 234023.53 | 260775726 | 99809425 | 50064030 | 0.000000 | 182551651 | 29267749 | 0.000000
09-04-2025 20:31:45000 | -1064102 | 106.4102 | 66082417 | 233942.95 | 263134918 | 99807724 | 50049335 | 0.000000 | 191627579 | 30739365 | 0.000000
09-04-2025 20:31:50000 | -1067050 | 106.705 | 62674966 | 233863.34 | 263899780 | 99827942 | 50037495 | 0.000000 | 200520721 | 32217712 | 0.000000
09-04-2025 20:31:55000 | -1069321 | 106.9321 | 64193281 | 233930.22 | 264408325 | 99820297 | 50038063 | 0.000000 | 209428101 | 33703103 | 0.000000
09-04-2025 20:32:00000 | -1057358 | 105.7358 | 61962920 | 233995.59 | 261353210 | 99828735 | 50059059 | 0.000000 | 218116013 | 35178215 | 0.000000
09-04-2025 20:32:05000 | -1052336 | 105.2336 | 60186318 | 233915.88 | 260178894 | 99836845 | 50073044 | 0.000000 | 226659973 | 36640417 | 0.000000
09-04-2025 20:32:10000 | -1050978 | 105.0978 | 60507480 | 233909.61 | 259858154 | 99834679 | 50056786 | 0.000000 | 235058395 | 38097488 | 0.000000
09-04-2025 20:32:15000 | -1055525 | 105.5525 | 64524790 | 233984.39 | 260952087 | 99813675 | 50052010 | 0.000000 | 243807175 | 39561987 | 0.000000
09-04-2025 20:32:20000 | -1050492 | 105.0492 | 64718770 | 234038.20 | 259657532 | 99810760 | 50076000 | 0.000000 | 252742676 | 41024102 | 0.000000
09-04-2025 20:32:25000 | -1041948 | 104.1948 | 63510645 | 234046.80 | 257525604 | 99814751 | 50084270 | 0.000000 | 261686462 | 42474746 | 0.000000
09-04-2025 20:32:30000 | -1048944 | 104.8944 | 65263813 | 234043.63 | 259276733 | 99806999 | 50071529 | 0.000000 | 270576843 | 43927964 | 0.000000
09-04-2025 20:32:35000 | -1058021 | 105.8021 | 65383057 | 233934.86 | 261634979 | 99809601 | 50051834 | 0.000000 | 279709869 | 45393647 | 0.000000
09-04-2025 20:32:40000 | -1058327 | 105.8327 | 65446255 | 233989.84 | 261650024 | 99809341 | 50052193 | 0.000000 | 288833954 | 46862798 | 0.000000
09-04-2025 20:32:45000 | -1062870 | 106.287 | 66967573 | 233990.66 | 262790863 | 99802101 | 50049107 | 0.000000 | 298062012 | 48336953 | 0.000000
09-04-2025 20:32:50000 | -1064781 | 106.4781 | 67460200 | 234054.36 | 263200043 | 99799904 | 50052883 | 0.000000 | 307250702 | 49814673 | 0.000000
09-04-2025 20:32:55000 | -1055819 | 105.5819 | 64758877 | 234035.66 | 260970825 | 99812431 | 50069790 | 0.000000 | 316393463 | 51287676 | 0.000000
09-04-2025 20:33:00000 | -1054066 | 105.4066 | 64386519 | 234017.63 | 260553253 | 99813957 | 50072338 | 0.000000 | 325390381 | 52751978 | 0.000000
09-04-2025 20:33:05000 | -1050377 | 105.0377 | 64449028 | 234043.33 | 259617004 | 99812286 | 50078270 | 0.000000 | 334369354 | 54212261 | 0.000000
09-04-2025 20:33:10000 | -1052973 | 105.2973 | 63787061 | 233956.89 | 260343170 | 99817017 | 50064796 | 0.000000 | 343227997 | 55672896 | 0.000000
09-04-2025 20:33:15000 | -1062454 | 106.2454 | 65455591 | 233940.59 | 262721680 | 99810760 | 50045513 | 0.000000 | 352207214 | 57142290 | 0.000000
09-04-2025 20:33:20000 | -1063480 | 106.348 | 65605234 | 233966.75 | 262946960 | 99810265 | 50047184 | 0.000000 | 361253448 | 58619058 | 0.000000
09-04-2025 20:33:25000 | -1051758 | 105.1758 | 66175698 | 234091.23 | 259931274 | 99802643 | 50084145 | 0.000000 | 370376770 | 60088647 | 0.000000
09-04-2025 20:33:30000 | -1043894 | 104.3894 | 61554556 | 234035.33 | 257987732 | 99826599 | 50092400 | 0.000000 | 378994324 | 61543052 | 0.000000
09-04-2025 20:33:35000 | -1049530 | 104.953 | 62548169 | 233948.50 | 259486176 | 99822884 | 50083828 | 0.000000 | 387545502 | 62993774 | 0.000000
09-04-2025 20:33:40000 | -1052576 | 105.2576 | 64925137 | 233970.83 | 260253204 | 99810310 | 50059711 | 0.000000 | 396541840 | 64456611 | 0.000000
09-04-2025 20:33:45000 | -1057926 | 105.7926 | 66080962 | 234021.58 | 261527130 | 99805489 | 50066177 | 0.000000 | 405681305 | 65926543 | 0.000000
09-04-2025 20:33:50000 | -1057341 | 105.7341 | 67340830 | 234076.34 | 261339569 | 99797798 | 50068226 | 0.000000 | 414926849 | 67396260 | 0.000000
09-04-2025 20:33:55000 | -1053078 | 105.3078 | 65675488 | 234075.59 | 260265839 | 99806091 | 50076748 | 0.000000 | 424134247 | 68862007 | 0.000000
09-04-2025 20:34:00000 | -1050549 | 105.0549 | 64927705 | 234013.73 | 259699982 | 99809563 | 50081696 | 0.000000 | 433254700 | 70323325 | 0.000000
09-04-2025 20:34:05000 | -1051548 | 105.1548 | 64919678 | 234023.00 | 259935822 | 99809967 | 50076221 | 0.000000 | 442325745 | 71784600 | 0.000000
09-04-2025 20:34:10000 | -1054794 | 105.4794 | 65166899 | 233995.44 | 260775269 | 99809692 | 50068512 | 0.000000 | 451268707 | 73246875 | 0.000000
09-04-2025 20:34:15000 | -1060829 | 106.0829 | 66678179 | 234001.89 | 262272156 | 99803047 | 50058105 | 0.000000 | 460400391 | 74717554 | 0.000000
09-04-2025 20:34:20000 | -1055643 | 105.5643 | 65887471 | 234064.97 | 260911469 | 99805786 | 50071053 | 0.000000 | 469683228 | 76190498 | 0.000000
09-04-2025 20:34:25000 | -1040569 | 104.0569 | 62945645 | 234089.20 | 257130493 | 99817543 | 50112782 | 0.000000 | 478578247 | 77645317 | 0.000000
09-04-2025 20:34:30000 | -1036204 | 103.6204 | 62357891 | 234058.48 | 256080780 | 99819412 | 50118649 | 0.000000 | 487298950 | 79085596 | 0.000000
09-04-2025 20:34:35000 | -1054348 | 105.4348 | 66642114 | 233998.94 | 260679352 | 99800842 | 50091003 | 0.000000 | 496240570 | 80538027 | 0.000000
09-04-2025 20:34:40000 | -1062829 | 106.2829 | 70227183 | 234062.59 | 262752991 | 99782410 | 50074295 | 0.000000 | 505913544 | 82010664 | 0.000000
09-04-2025 20:34:45000 | -1064437 | 106.4437 | 70407554 | 234066.95 | 263145874 | 99781952 | 50083839 | 0.000000 | 515711182 | 83487061 | 0.000000
09-04-2025 20:34:50000 | -1067264 | 106.7264 | 70427744 | 234056.97 | 263853821 | 99782982 | 50086113 | 0.000000 | 525444275 | 84966182 | 0.000000
09-04-2025 20:34:55000 | -1067682 | 106.7682 | 70260884 | 234087.48 | 263920837 | 99784172 | 50074379 | 0.000000 | 535081604 | 86447227 | 0.000000
09-04-2025 20:35:00000 | -1053009 | 105.3009 | 69258555 | 234172.16 | 260202271 | 99784401 | 50117752 | 0.000000 | 544896606 | 87918057 | 0.000000
09-04-2025 20:35:05000 | -1052509 | 105.2509 | 66165259 | 234046.00 | 260165924 | 99802986 | 50104855 | 0.000000 | 554212952 | 89378232 | 0.000000
09-04-2025 20:35:10000 | -1066630 | 106.663 | 68786748 | 233998.94 | 263740936 | 99792702 | 50072777 | 0.000000 | 563552185 | 90850059 | 0.000000
09-04-2025 20:35:15000 | -1070706 | 107.0706 | 71129756 | 234062.03 | 264705322 | 99780060 | 50059193 | 0.000000 | 573306519 | 92332861 | 0.000000
09-04-2025 20:35:20000 | -1068822 | 106.8822 | 70872285 | 234060.61 | 264239807 | 99780876 | 50064186 | 0.000000 | 583347107 | 93821240 | 0.000000
09-04-2025 20:35:25000 | -1069600 | 106.96 | 66989683 | 233987.42 | 264453125 | 99804443 | 50056503 | 0.000000 | 592816833 | 95306260 | 0.000000
09-04-2025 20:35:30000 | -1064697 | 106.4697 | 64052217 | 233945.17 | 263247711 | 99819527 | 50037823 | 0.000000 | 601897522 | 96788965 | 0.000000
09-04-2025 20:35:35000 | -1062663 | 106.2663 | 64838398 | 234046.77 | 262644958 | 99814377 | 50032127 | 0.000000 | 610810791 | 98267285 | 0.000000
09-04-2025 20:35:40000 | -1056229 | 105.6229 | 63881777 | 234013.13 | 261088318 | 99817604 | 50054008 | 0.000000 | 619837952 | 99738105 | 0.000000
09-04-2025 20:35:45000 | -1052611 | 105.2611 | 63353989 | 234027.78 | 260170502 | 99819366 | 50063942 | 0.000000 | 628671936 | 10120030 | 0.000000
09-04-2025 20:35:50000 | -1048409 | 104.8409 | 61474307 | 233962.67 | 259180573 | 99828537 | 50061520 | 0.000000 | 637275269 | 10265785 | 0.000000
09-04-2025 20:35:55000 | -1052773 | 105.2773 | 62971836 | 233960.67 | 260276947 | 99821587 | 50045891 | 0.000000 | 645768799 | 10411689 | 0.000000
09-04-2025 20:36:00000 | -1053004 | 105.3004 | 64583628 | 233997.09 | 260317444 | 99812447 | 50052094 | 0.000000 | 654652344 | 10558078 | 0.000000
09-04-2025 20:36:05000 | -1054667 | 105.4667 | 64992280 | 233989.05 | 260741882 | 99810669 | 50053200 | 0.000000 | 663591125 | 10704468 | 0.000000
09-04-2025 20:36:10000 | -1045976 | 104.5976 | 63041938 | 234003.83 | 258556458 | 99818863 | 50068035 | 0.000000 | 672539185 | 10850243 | 0.000000
09-04-2025 20:36:15000 | -1046056 | 104.6056 | 62875615 | 234008.02 | 258569427 | 99819847 | 50065556 | 0.000000 | 681266968 | 10995417 | 0.000000
09-04-2025 20:36:20000 | -1047652 | 104.7652 | 63581040 | 234007.75 | 258973694 | 99816345 | 50064949 | 0.000000 | 689981567 | 11140658 | 0.000000
09-04-2025 20:36:25000 | -1043560 | 104.356 | 63906387 | 234029.25 | 257946259 | 99813019 | 50064426 | 0.000000 | 698821289 | 11285829 | 0.000000
09-04-2025 20:36:30000 | -1038109 | 103.8109 | 65271201 | 234153.86 | 256489410 | 99802917 | 50084965 | 0.000000 | 707773071 | 11430497 | 0.000000
09-04-2025 20:36:35000 | -1031016 | 103.1016 | 66413076 | 234166.81 | 254747452 | 99793175 | 50107918 | 0.000000 | 716877808 | 11574096 | 0.000000
09-04-2025 20:36:40000 | -1039672 | 103.9672 | 65386919 | 234034.88 | 257007111 | 99802818 | 50094833 | 0.000000 | 725924500 | 11717688 | 0.000000
09-04-2025 20:36:45000 | -1057723 | 105.7723 | 68658525 | 233990.98 | 261550507 | 99789986 | 50058060 | 0.000000 | 735428955 | 11863864 | 0.000000
09-04-2025 20:36:50000 | -1067536 | 106.7536 | 71941758 | 234071.59 | 263928345 | 99773697 | 50042252 | 0.000000 | 745267334 | 12011871 | 0.000000
09-04-2025 20:36:55000 | -1060397 | 106.0397 | 69662236 | 234148.22 | 262052643 | 99784904 | 50077003 | 0.000000 | 755099487 | 12159744 | 0.000000
09-04-2025 20:37:00000 | -1054603 | 105.4603 | 68620469 | 234126.86 | 260629883 | 99788979 | 50090439 | 0.000000 | 764756409 | 12306697 | 0.000000
09-04-2025 20:37:05000 | -1052343 | 105.2343 | 66689399 | 234082.77 | 260092743 | 99799797 | 50086033 | 0.000000 | 774054260 | 12452820 | 0.000000
09-04-2025 20:37:10000 | -1051149 | 105.1149 | 65875220 | 234065.56 | 259804443 | 99804199 | 50095436 | 0.000000 | 783223999 | 12598810 | 0.000000
09-04-2025 20:37:15000 | -1049391 | 104.9391 | 64911152 | 233995.36 | 259434814 | 99809242 | 50091118 | 0.000000 | 792336914 | 12744331 | 0.000000
09-04-2025 20:37:20000 | -1056860 | 105.686 | 66985947 | 234048.89 | 261247650 | 99799736 | 50075436 | 0.000000 | 801445862 | 12890549 | 0.000000
09-04-2025 20:37:25000 | -1057572 | 105.7572 | 68474697 | 234071.03 | 261420715 | 99791046 | 50068726 | 0.000000 | 810879395 | 13037474 | 0.000000
09-04-2025 20:37:30000 | -1060074 | 106.0074 | 67395322 | 234001.00 | 262098114 | 99798515 | 50074223 | 0.000000 | 820282227 | 13184462 | 0.000000
09-04-2025 20:37:35000 | -1068002 | 106.8002 | 67777314 | 233994.97 | 264063232 | 99799232 | 50053974 | 0.000000 | 829675720 | 13332229 | 0.000000
09-04-2025 20:37:40000 | -1065271 | 106.5271 | 68497583 | 234064.92 | 263323395 | 99793907 | 50059090 | 0.000000 | 839245544 | 13480503 | 0.000000
09-04-2025 20:37:45000 | -1065403 | 106.5403 | 64222100 | 233928.19 | 263444397 | 99818810 | 50055058 | 0.000000 | 848321655 | 13628088 | 0.000000
09-04-2025 20:37:50000 | -1074711 | 107.4711 | 65411250 | 233913.47 | 265771027 | 99815292 | 50017006 | 0.000000 | 857439392 | 13776973 | 0.000000
09-04-2025 20:37:55000 | -1068303 | 106.8303 | 66279092 | 233987.77 | 264121643 | 99808098 | 50037666 | 0.000000 | 866685242 | 13925715 | 0.000000
09-04-2025 20:38:00000 | -1047912 | 104.7912 | 63399868 | 234108.97 | 258922333 | 99817482 | 50063942 | 0.000000 | 875615295 | 14072476 | 0.000000
09-04-2025 20:38:05000 | -1033820 | 103.382 | 58083350 | 233968.47 | 255530212 | 99842545 | 50072594 | 0.000000 | 883937500 | 14216603 | 0.000000
09-04-2025 20:38:10000 | -1023052 | 102.3052 | 58918315 | 234062.39 | 252787369 | 99834579 | 50075615 | 0.000000 | 892069336 | 14359188 | 0.000000
09-04-2025 20:38:15000 | -1011480 | 101.148 | 59890991 | 234105.45 | 249909271 | 99825157 | 50075150 | 0.000000 | 900397766 | 14500489 | 0.000000
09-04-2025 20:38:20000 | -9969832 | 99.6983 | 58434790 | 234110.92 | 246311279 | 99828674 | 50093994 | 0.000000 | 908591492 | 14639592 | 0.000000
09-04-2025 20:38:25000 | -9993970 | 99.9397 | 57691489 | 234019.00 | 246991028 | 99833801 | 50058418 | 0.000000 | 916590271 | 14778187 | 0.000000
09-04-2025 20:38:30000 | -1003137 | 100.3137 | 59999751 | 234034.56 | 247930267 | 99821602 | 50030140 | 0.000000 | 924799133 | 14917402 | 0.000000
09-04-2025 20:38:35000 | -9956118 | 99.5612 | 59223569 | 234085.73 | 246010803 | 99823547 | 50052921 | 0.000000 | 933094666 | 15056150 | 0.000000
09-04-2025 20:38:40000 | -9861737 | 98.6174 | 56580210 | 234089.52 | 243644653 | 99835823 | 50051254 | 0.000000 | 941070374 | 15193580 | 0.000000
09-04-2025 20:38:45000 | -9816077 | 98.1608 | 55282158 | 234052.28 | 242541107 | 99841789 | 50045235 | 0.000000 | 948739258 | 15330313 | 0.000000
09-04-2025 20:38:50000 | -9678037 | 96.7804 | 51510801 | 234006.03 | 239137970 | 99858658 | 50057068 | 0.000000 | 956104004 | 15465442 | 0.000000
09-04-2025 20:38:55000 | -9586615 | 95.8662 | 51823169 | 234065.44 | 236829910 | 99854210 | 50060478 | 0.000000 | 963235596 | 15599063 | 0.000000
09-04-2025 20:39:00000 | -9496406 | 94.9641 | 51853672 | 234080.50 | 234595886 | 99851257 | 50065285 | 0.000000 | 970380188 | 15731308 | 0.000000
09-04-2025 20:39:05000 | -9353772 | 93.5377 | 49747666 | 234061.59 | 231070847 | 99858871 | 50069427 | 0.000000 | 977382568 | 15862014 | 0.000000
09-04-2025 20:39:10000 | -9218257 | 92.1826 | 49586987 | 234143.00 | 227653015 | 99855637 | 50084713 | 0.000000 | 984258728 | 15990997 | 0.000000
09-04-2025 20:39:15000 | -9046401 | 90.464 | 48562173 | 234158.47 | 223396484 | 99856224 | 50102337 | 0.000000 | 991081055 | 16117580 | 0.000000
09-04-2025 20:39:20000 | -9003634 | 90.0363 | 46948672 | 234085.77 | 222387207 | 99864326 | 50087662 | 0.000000 | 997663635 | 16242788 | 0.000000
09-04-2025 20:39:25000 | -8997756 | 89.9776 | 48615483 | 234095.80 | 222254608 | 99854355 | 50074741 | 0.000000 | 10042851 | 16367867 | 0.000000
09-04-2025 20:39:30000 | -8815588 | 88.1559 | 46848960 | 234199.61 | 217648773 | 99859085 | 50097355 | 0.000000 | 10109215 | 16491549 | 0.000000
09-04-2025 20:39:35000 | -8775073 | 87.7507 | 43937886 | 234092.39 | 216713669 | 99874878 | 50094906 | 0.000000 | 10171490 | 16613676 | 0.000000
09-04-2025 20:39:40000 | -8732941 | 87.3294 | 42798853 | 234058.50 | 215693375 | 99880127 | 50079067 | 0.000000 | 10231635 | 16735037 | 0.000000
09-04-2025 20:39:45000 | -8833276 | 88.3328 | 46274863 | 234065.70 | 218201859 | 99863060 | 50063877 | 0.000000 | 10294048 | 16857219 | 0.000000
09-04-2025 20:39:50000 | -8873218 | 88.7322 | 46034946 | 234042.77 | 219207245 | 99865692 | 50051929 | 0.000000 | 10357817 | 16980232 | 0.000000
09-04-2025 20:39:55000 | -8854575 | 88.5457 | 43700669 | 233986.56 | 218767639 | 99878433 | 50032837 | 0.000000 | 10419587 | 17103275 | 0.000000
09-04-2025 20:40:00000 | -8823768 | 88.2377 | 43395767 | 233988.06 | 218002777 | 99879280 | 50028606 | 0.000000 | 10480833 | 17226092 | 0.000000
09-04-2025 20:40:05000 | -8656283 | 86.5628 | 39248044 | 234019.05 | 213800018 | 99897369 | 50067741 | 0.000000 | 10537915 | 17346977 | 0.000000
09-04-2025 20:40:10000 | -8554542 | 85.5454 | 37692856 | 233981.48 | 211306885 | 99903069 | 50080414 | 0.000000 | 10591060 | 17466238 | 0.000000
09-04-2025 20:40:15000 | -8496973 | 84.9697 | 38354194 | 234022.86 | 209859024 | 99898277 | 50083233 | 0.000000 | 10643361 | 17584219 | 0.000000
09-04-2025 20:40:20000 | -8589412 | 85.8941 | 41736143 | 234024.44 | 212174713 | 99882156 | 50082874 | 0.000000 | 10699312 | 17702973 | 0.000000
09-04-2025 20:40:25000 | -8713224 | 87.1322 | 40389043 | 233878.56 | 215343491 | 99892738 | 50050301 | 0.000000 | 10755978 | 17823201 | 0.000000
09-04-2025 20:40:30000 | -8793123 | 87.9312 | 45262896 | 234036.95 | 217223999 | 99867775 | 50040112 | 0.000000 | 10815541 | 17945268 | 0.000000
09-04-2025 20:40:35000 | -8692541 | 86.9254 | 43831616 | 234086.83 | 214683212 | 99873108 | 50078876 | 0.000000 | 10877687 | 18066727 | 0.000000
09-04-2025 20:40:40000 | -8641110 | 86.4111 | 40876890 | 234019.47 | 213442261 | 99888298 | 50081650 | 0.000000 | 10935490 | 18187121 | 0.000000
09-04-2025 20:40:45000 | -8689447 | 86.8945 | 39733970 | 233960.27 | 214675949 | 99895615 | 50063431 | 0.000000 | 10990699 | 18307533 | 0.000000
09-04-2025 20:40:50000 | -8590593 | 85.9059 | 40857542 | 234052.34 | 212168137 | 99887093 | 50095703 | 0.000000 | 11048114 | 18427564 | 0.000000
09-04-2025 20:40:55000 | -8562220 | 85.6222 | 38338418 | 233992.13 | 211495010 | 99899902 | 50090855 | 0.000000 | 11102303 | 18546529 | 0.000000
09-04-2025 20:41:00000 | -8675424 | 86.7542 | 40853347 | 233958.30 | 214344223 | 99889305 | 50064106 | 0.000000 | 11158215 | 18666467 | 0.000000
09-04-2025 20:41:05000 | -8749306 | 87.4931 | 43141558 | 233968.53 | 216181717 | 99878654 | 50048897 | 0.000000 | 11217710 | 18787801 | 0.000000
09-04-2025 20:41:10000 | -8712323 | 87.1232 | 42982686 | 234043.11 | 215199158 | 99878525 | 50061691 | 0.000000 | 11277554 | 18909143 | 0.000000
09-04-2025 20:41:15000 | -8627779 | 86.2778 | 41072417 | 234046.83 | 213091125 | 99886879 | 50085781 | 0.000000 | 11335552 | 19029430 | 0.000000
09-04-2025 20:41:20000 | -8568258 | 85.6826 | 41531924 | 234058.63 | 211619507 | 99882729 | 50092907 | 0.000000 | 11393817 | 19149002 | 0.000000
09-04-2025 20:41:25000 | -8550159 | 85.5016 | 42702207 | 234107.63 | 211142609 | 99875519 | 50098930 | 0.000000 | 11451687 | 19267764 | 0.000000
09-04-2025 20:41:30000 | -8530808 | 85.3081 | 44041484 | 234160.67 | 210636612 | 99867004 | 50096210 | 0.000000 | 11511209 | 19386482 | 0.000000
09-04-2025 20:41:35000 | -8583921 | 85.8392 | 44891353 | 234090.02 | 212025482 | 99863533 | 50097282 | 0.000000 | 11573029 | 19505129 | 0.000000
09-04-2025 20:41:40000 | -8644889 | 86.4489 | 47992900 | 234123.19 | 213530487 | 99846252 | 50082497 | 0.000000 | 11637705 | 19624910 | 0.000000
09-04-2025 20:41:45000 | -8625221 | 86.2522 | 47542437 | 234158.63 | 213007813 | 99848434 | 50094429 | 0.000000 | 11703629 | 19744729 | 0.000000
09-04-2025 20:41:50000 | -8636782 | 86.3678 | 45092949 | 234091.02 | 213326309 | 99863983 | 50091801 | 0.000000 | 11767595 | 19864533 | 0.000000
09-04-2025 20:41:55000 | -8591885 | 85.9189 | 44536880 | 234125.45 | 212177612 | 99865921 | 50099861 | 0.000000 | 11829337 | 19984121 | 0.000000
09-04-2025 20:42:00000 | -8584534 | 85.8453 | 43759663 | 234086.80 | 212021698 | 99870331 | 50104462 | 0.000000 | 11890673 | 20103336 | 0.000000
09-04-2025 20:42:05000 | -8680355 | 86.8036 | 41591919 | 233940.88 | 214491028 | 99885406 | 50074291 | 0.000000 | 11949176 | 20223006 | 0.000000
09-04-2025 20:42:10000 | -8774514 | 87.7451 | 44031104 | 234005.03 | 216783981 | 99874329 | 50061283 | 0.000000 | 12010350 | 20344414 | 0.000000
09-04-2025 20:42:15000 | -8752814 | 87.5281 | 43823179 | 234040.59 | 216211853 | 99874901 | 50069721 | 0.000000 | 12072229 | 20466275 | 0.000000
09-04-2025 20:42:20000 | -8752485 | 87.5249 | 39854668 | 233905.78 | 216279968 | 99896484 | 50066093 | 0.000000 | 12130176 | 20587721 | 0.000000
09-04-2025 20:42:25000 | -8814682 | 88.1468 | 42840488 | 234001.72 | 217759659 | 99882103 | 50064072 | 0.000000 | 12188698 | 20709668 | 0.000000
09-04-2025 20:42:30000 | -8696595 | 86.966 | 41495605 | 234024.41 | 214812973 | 99886360 | 50083862 | 0.000000 | 12247531 | 20831107 | 0.000000
09-04-2025 20:42:35000 | -8678018 | 86.7802 | 42519048 | 234074.42 | 214323792 | 99880180 | 50086781 | 0.000000 | 12304208 | 20951633 | 0.000000
09-04-2025 20:42:40000 | -8664905 | 86.6491 | 42417764 | 234010.34 | 214055695 | 99880394 | 50086658 | 0.000000 | 12363566 | 21072098 | 0.000000
09-04-2025 20:42:45000 | -8601202 | 86.012 | 41720059 | 234046.48 | 212444046 | 99882568 | 50101139 | 0.000000 | 12421844 | 21191793 | 0.000000
09-04-2025 20:42:50000 | -8561494 | 85.6149 | 42240571 | 234038.30 | 211479477 | 99878510 | 50104485 | 0.000000 | 12481138 | 21310953 | 0.000000
09-04-2025 20:42:55000 | -8638361 | 86.3836 | 42135508 | 233997.28 | 213414093 | 99881248 | 50081261 | 0.000000 | 12537975 | 21430438 | 0.000000
09-04-2025 20:43:00000 | -8701965 | 87.0196 | 43943042 | 234058.72 | 214942673 | 99872742 | 50075798 | 0.000000 | 12598107 | 21551010 | 0.000000
09-04-2025 20:43:05000 | -8625084 | 86.2508 | 42258149 | 234029.31 | 213054581 | 99880196 | 50092072 | 0.000000 | 12658619 | 21671227 | 0.000000
09-04-2025 20:43:10000 | -8632728 | 86.3273 | 42595161 | 234076.69 | 213204102 | 99878494 | 50091091 | 0.000000 | 12716318 | 21791178 | 0.000000
09-04-2025 20:43:15000 | -8563706 | 85.6371 | 41974009 | 234078.50 | 211495270 | 99880096 | 50106865 | 0.000000 | 12775778 | 21910596 | 0.000000
09-04-2025 20:43:20000 | -8611978 | 86.1198 | 43337661 | 234050.75 | 212725937 | 99873619 | 50102974 | 0.000000 | 12835964 | 22029492 | 0.000000
09-04-2025 20:43:25000 | -8692038 | 86.9204 | 44690474 | 234036.52 | 214729446 | 99868088 | 50082588 | 0.000000 | 12897806 | 22149797 | 0.000000
09-04-2025 20:43:30000 | -8739120 | 87.3912 | 46778862 | 234095.91 | 215861877 | 99857040 | 50078587 | 0.000000 | 12961703 | 22271031 | 0.000000
09-04-2025 20:43:35000 | -8862571 | 88.6257 | 43090542 | 233877.53 | 219058578 | 99882011 | 50048763 | 0.000000 | 13023851 | 22393598 | 0.000000
09-04-2025 20:43:40000 | -8937352 | 89.3735 | 42215298 | 233896.66 | 220873260 | 99888634 | 50014278 | 0.000000 | 13082227 | 22517529 | 0.000000
09-04-2025 20:43:45000 | -8896949 | 88.9695 | 40508589 | 233908.48 | 219846527 | 99896507 | 50025917 | 0.000000 | 13140280 | 22641645 | 0.000000
09-04-2025 20:43:50000 | -8761821 | 87.6182 | 36888853 | 233915.70 | 216469070 | 99911491 | 50046326 | 0.000000 | 13194031 | 22764094 | 0.000000
09-04-2025 20:43:55000 | -8677004 | 86.77 | 34831321 | 233897.75 | 214373230 | 99919525 | 50052704 | 0.000000 | 13243126 | 22884854 | 0.000000
09-04-2025 20:44:00000 | -8574359 | 85.7436 | 35942371 | 233972.94 | 211785202 | 99912254 | 50069382 | 0.000000 | 13294111 | 23004635 | 0.000000
09-04-2025 20:44:05000 | -8494746 | 84.9475 | 36547251 | 234024.36 | 209782852 | 99907578 | 50082451 | 0.000000 | 13344556 | 23123047 | 0.000000
09-04-2025 20:44:10000 | -8453905 | 84.5391 | 37911345 | 234024.63 | 208790909 | 99899597 | 50104389 | 0.000000 | 13395951 | 23240529 | 0.000000
09-04-2025 20:44:15000 | -8411395 | 84.114 | 39620269 | 234098.92 | 207697662 | 99889252 | 50119141 | 0.000000 | 13449797 | 23357477 | 0.000000
09-04-2025 20:44:20000 | -8405098 | 84.051 | 42550068 | 234137.31 | 207542282 | 99872108 | 50137688 | 0.000000 | 13506628 | 23474252 | 0.000000
09-04-2025 20:44:25000 | -8479788 | 84.7979 | 43151826 | 234094.08 | 209428833 | 99870773 | 50129105 | 0.000000 | 13565438 | 23591572 | 0.000000
09-04-2025 20:44:30000 | -8649257 | 86.4926 | 46274873 | 234061.95 | 213670944 | 99857185 | 50105080 | 0.000000 | 13628297 | 23710629 | 0.000000
09-04-2025 20:44:35000 | -8728963 | 87.2896 | 47520737 | 234080.75 | 215632980 | 99852142 | 50098228 | 0.000000 | 13693994 | 23831322 | 0.000000
09-04-2025 20:44:40000 | -8807175 | 88.0717 | 46933940 | 234038.81 | 217591110 | 99858307 | 50079086 | 0.000000 | 13759664 | 23953053 | 0.000000
09-04-2025 20:44:45000 | -8837531 | 88.3753 | 46269824 | 234012.09 | 218359436 | 99863220 | 50079578 | 0.000000 | 13825562 | 24075691 | 0.000000
09-04-2025 20:44:50000 | -8814517 | 88.1452 | 45496138 | 234056.00 | 217737152 | 99867058 | 50067429 | 0.000000 | 13888898 | 24198551 | 0.000000
09-04-2025 20:44:55000 | -8722731 | 87.2273 | 41525957 | 234045.36 | 215436661 | 99886871 | 50078331 | 0.000000 | 13948035 | 24320271 | 0.000000
09-04-2025 20:45:00000 | -8700095 | 87.001 | 42053623 | 234050.94 | 214880280 | 99883385 | 50079338 | 0.000000 | 14005568 | 24441201 | 0.000000
09-04-2025 20:45:05000 | -8664807 | 86.6481 | 40602749 | 233987.19 | 214054703 | 99890388 | 50075954 | 0.000000 | 5734618 | 120565552 | 0.000000
09-04-2025 20:45:10000 | -8644485 | 86.4449 | 42802334 | 234058.20 | 213512512 | 99877640 | 50085651 | 0.000000 | 11594104 | 240939011 | 0.000000
09-04-2025 20:45:15000 | -8612156 | 86.1216 | 40239739 | 233999.13 | 212740463 | 99891022 | 50089077 | 0.000000 | 17329906 | 360926086 | 0.000000
09-04-2025 20:45:20000 | -8548520 | 85.4852 | 40811855 | 234058.89 | 211125046 | 99886230 | 50103699 | 0.000000 | 22988693 | 480042999 | 0.000000
09-04-2025 20:45:25000 | -8515869 | 85.1587 | 41251118 | 234074.56 | 210310501 | 99882881 | 50109829 | 0.000000 | 28678343 | 598595337 | 0.000000
09-04-2025 20:45:30000 | -8575487 | 85.7549 | 41795889 | 234022.03 | 211838409 | 99881439 | 50089043 | 0.000000 | 34341805 | 717323669 | 0.000000
09-04-2025 20:45:35000 | -8740855 | 87.4086 | 43067842 | 233931.72 | 216006836 | 99878838 | 50053146 | 0.000000 | 40209301 | 837998901 | 0.000000
09-04-2025 20:45:40000 | -8800232 | 88.0023 | 43677144 | 233992.56 | 217421661 | 99877060 | 50041954 | 0.000000 | 46099083 | 960113586 | 0.000000
09-04-2025 20:45:45000 | -8803430 | 88.0343 | 42754546 | 233966.58 | 217517593 | 99882278 | 50054272 | 0.000000 | 52190090 | 10826056 | 0.000000
09-04-2025 20:45:50000 | -8780095 | 87.801 | 39844011 | 233923.91 | 216944809 | 99897194 | 50053974 | 0.000000 | 57850273 | 12042872 | 0.000000
09-04-2025 20:45:55000 | -8760161 | 87.6016 | 40914033 | 233985.14 | 216408218 | 99891113 | 50049461 | 0.000000 | 63440353 | 13262081 | 0.000000
09-04-2025 20:46:00000 | -8665121 | 86.6512 | 41613018 | 234080.94 | 213985474 | 99884888 | 50074188 | 0.000000 | 69152557 | 14470293 | 0.000000
09-04-2025 20:46:05000 | -8680021 | 86.8002 | 38681196 | 233921.05 | 214465607 | 99900856 | 50065182 | 0.000000 | 74712479 | 15672988 | 0.000000
09-04-2025 20:46:10000 | -8830679 | 88.3068 | 40432124 | 233874.31 | 218246078 | 99895348 | 50027126 | 0.000000 | 80261765 | 16892350 | 0.000000
09-04-2025 20:46:15000 | -8809692 | 88.0969 | 40857954 | 233923.30 | 217685654 | 99892624 | 50027645 | 0.000000 | 86034988 | 18115066 | 0.000000
09-04-2025 20:46:20000 | -8763188 | 87.6319 | 38198923 | 233875.73 | 216553909 | 99905128 | 50023186 | 0.000000 | 91460533 | 19334296 | 0.000000
09-04-2025 20:46:25000 | -8719020 | 87.1902 | 38439312 | 233957.06 | 215392670 | 99902962 | 50032307 | 0.000000 | 96680321 | 20546514 | 0.000000
09-04-2025 20:46:30000 | -8592170 | 85.9217 | 37162256 | 233994.52 | 212217987 | 99906601 | 50057240 | 0.000000 | 101937675 | 21747546 | 0.000000
09-04-2025 20:46:35000 | -8459621 | 84.5962 | 37198223 | 234074.97 | 208880127 | 99903465 | 50086922 | 0.000000 | 107022797 | 22931501 | 0.000000
09-04-2025 20:46:40000 | -8423767 | 84.2377 | 35790215 | 233952.03 | 208090607 | 99909866 | 50102440 | 0.000000 | 112167702 | 24099695 | 0.000000
09-04-2025 20:46:45000 | -8635072 | 86.3507 | 39803059 | 233892.09 | 213398605 | 99893936 | 50055702 | 0.000000 | 117427956 | 25287693 | 0.000000
09-04-2025 20:46:50000 | -8646873 | 86.4687 | 42743804 | 234020.27 | 213608017 | 99878044 | 50065468 | 0.000000 | 123289078 | 26489478 | 0.000000
09-04-2025 20:46:55000 | -8558379 | 85.5838 | 41312363 | 234040.25 | 211390793 | 99883698 | 50090305 | 0.000000 | 129144516 | 27684338 | 0.000000
09-04-2025 20:47:00000 | -8579455 | 85.7946 | 37420400 | 233900.77 | 211991699 | 99905014 | 50083439 | 0.000000 | 134599838 | 28874705 | 0.000000
09-04-2025 20:47:05000 | -8679365 | 86.7936 | 40074358 | 233932.50 | 214455078 | 99893578 | 50055946 | 0.000000 | 139943893 | 30072874 | 0.000000
09-04-2025 20:47:10000 | -8732778 | 87.3278 | 42657212 | 233987.00 | 215753342 | 99880913 | 50058197 | 0.000000 | 145759064 | 31281733 | 0.000000
09-04-2025 20:47:15000 | -8778283 | 87.7828 | 41832451 | 233942.83 | 216906494 | 99886642 | 50042145 | 0.000000 | 151602966 | 32496765 | 0.000000
09-04-2025 20:47:20000 | -8852233 | 88.5223 | 42761240 | 233915.58 | 218766434 | 99883530 | 50020935 | 0.000000 | 157491837 | 33722559 | 0.000000
09-04-2025 20:47:25000 | -8851182 | 88.5118 | 39609988 | 233891.42 | 218724350 | 99900017 | 50016460 | 0.000000 | 163218491 | 34952571 | 0.000000
09-04-2025 20:47:30000 | -8729174 | 87.2917 | 38137380 | 233922.38 | 215673294 | 99904701 | 50035763 | 0.000000 | 168684113 | 36170242 | 0.000000
09-04-2025 20:47:35000 | -8702663 | 87.0266 | 36428413 | 233891.05 | 215030014 | 99912506 | 50033623 | 0.000000 | 173819702 | 37378909 | 0.000000
09-04-2025 20:47:40000 | -8722930 | 87.2293 | 39153975 | 233956.45 | 215496399 | 99899414 | 50028034 | 0.000000 | 179057541 | 38587920 | 0.000000
09-04-2025 20:47:45000 | -8747880 | 87.4788 | 38796519 | 233881.19 | 216178482 | 99901802 | 50028969 | 0.000000 | 184636734 | 39801143 | 0.000000
09-04-2025 20:47:50000 | -8718827 | 87.1883 | 38432190 | 233907.67 | 215432159 | 99902992 | 50028080 | 0.000000 | 189996918 | 41012285 | 0.000000
09-04-2025 20:47:55000 | -8754180 | 87.5418 | 38146990 | 233915.86 | 216293839 | 99905190 | 50011097 | 0.000000 | 195208786 | 42227905 | 0.000000
09-04-2025 20:48:00000 | -8669062 | 86.6906 | 40839272 | 234055.34 | 214099457 | 99889221 | 50039036 | 0.000000 | 200708038 | 43442036 | 0.000000
09-04-2025 20:48:05000 | -8490750 | 84.9075 | 38009221 | 234084.73 | 209645676 | 99899956 | 50086140 | 0.000000 | 206102509 | 44632554 | 0.000000
09-04-2025 20:48:10000 | -8329238 | 83.2924 | 38186553 | 234142.16 | 205617767 | 99895073 | 50122433 | 0.000000 | 211330154 | 45798521 | 0.000000
09-04-2025 20:48:15000 | -8345254 | 83.4525 | 36419648 | 234028.66 | 206097473 | 99904907 | 50125816 | 0.000000 | 216297668 | 46954990 | 0.000000
09-04-2025 20:48:20000 | -8543257 | 85.4326 | 40407693 | 233948.89 | 211090759 | 99888336 | 50085983 | 0.000000 | 221720047 | 48127681 | 0.000000
09-04-2025 20:48:25000 | -8722905 | 87.2291 | 43797817 | 233940.33 | 215566299 | 99874184 | 50056049 | 0.000000 | 227630478 | 49330518 | 0.000000
09-04-2025 20:48:30000 | -8820358 | 88.2036 | 45335908 | 233974.88 | 217956116 | 99868164 | 50050636 | 0.000000 | 233820480 | 50553613 | 0.000000
09-04-2025 20:48:35000 | -8740123 | 87.4012 | 41556929 | 233971.89 | 215937302 | 99887154 | 50055138 | 0.000000 | 239847580 | 51772368 | 0.000000
09-04-2025 20:48:40000 | -8700662 | 87.0066 | 40329995 | 233972.80 | 214947021 | 99892746 | 50071587 | 0.000000 | 245539856 | 52982769 | 0.000000
09-04-2025 20:48:45000 | -8716915 | 87.1692 | 39152439 | 233924.98 | 215378113 | 99899284 | 50060314 | 0.000000 | 251039581 | 54191611 | 0.000000
09-04-2025 20:48:50000 | -8726899 | 87.269 | 39288589 | 233930.78 | 215621262 | 99898811 | 50052700 | 0.000000 | 256492462 | 55403481 | 0.000000
09-04-2025 20:48:55000 | -8841377 | 88.4138 | 40303835 | 233889.81 | 218491501 | 99896263 | 50025322 | 0.000000 | 261854401 | 56625063 | 0.000000
09-04-2025 20:49:00000 | -8856189 | 88.5619 | 38625820 | 233826.38 | 218899368 | 99905022 | 50018234 | 0.000000 | 267386810 | 57856851 | 0.000000
09-04-2025 20:49:05000 | -8844620 | 88.4462 | 35913015 | 233812.94 | 218596939 | 99917664 | 50010555 | 0.000000 | 272509918 | 59087056 | 0.000000
09-04-2025 20:49:10000 | -8878256 | 88.7826 | 34014497 | 233704.14 | 219511047 | 99926689 | 49981430 | 0.000000 | 277388672 | 60318286 | 0.000000
09-04-2025 20:49:15000 | -8783006 | 87.8301 | 36482192 | 233922.97 | 216982117 | 99913841 | 49997150 | 0.000000 | 282293823 | 61546685 | 0.000000
09-04-2025 20:49:20000 | -8512967 | 85.1297 | 34325859 | 234019.97 | 210212463 | 99918808 | 50054447 | 0.000000 | 287204651 | 62744165 | 0.000000
09-04-2025 20:49:25000 | -8389498 | 83.895 | 33328616 | 233974.95 | 207202118 | 99921181 | 50084820 | 0.000000 | 291820862 | 63915083 | 0.000000
09-04-2025 20:49:30000 | -8317363 | 83.1736 | 34843594 | 234038.92 | 205379150 | 99912369 | 50101936 | 0.000000 | 296504089 | 65069800 | 0.000000
09-04-2025 20:49:35000 | -8388559 | 83.8856 | 36837446 | 233936.84 | 207246979 | 99903717 | 50090488 | 0.000000 | 301506256 | 66227427 | 0.000000
09-04-2025 20:49:40000 | -8559708 | 85.5971 | 40615557 | 233947.47 | 211499252 | 99887619 | 50060150 | 0.000000 | 306868042 | 67406060 | 0.000000
09-04-2025 20:49:45000 | -8666923 | 86.6692 | 42535898 | 233967.89 | 214145081 | 99879784 | 50052067 | 0.000000 | 312721527 | 68606646 | 0.000000
09-04-2025 20:49:50000 | -8672688 | 86.7269 | 42839746 | 234017.59 | 214245651 | 99878227 | 50068092 | 0.000000 | 318699341 | 69811904 | 0.000000
09-04-2025 20:49:55000 | -8697302 | 86.973 | 41054473 | 233973.03 | 214872620 | 99888779 | 50049000 | 0.000000 | 324426086 | 71017114 | 0.000000
09-04-2025 20:50:00000 | -8746493 | 87.4649 | 42999971 | 234000.11 | 216082443 | 99879372 | 50047077 | 0.000000 | 330329834 | 72228950 | 0.000000
09-04-2025 20:50:05000 | -8771966 | 87.7197 | 44402095 | 234026.25 | 216702057 | 99872139 | 50038315 | 0.000000 | 336342957 | 73447261 | 0.000000
09-04-2025 20:50:10000 | -8769152 | 87.6915 | 41785625 | 233982.45 | 216643951 | 99886665 | 50051392 | 0.000000 | 342308777 | 74667021 | 0.000000
09-04-2025 20:50:15000 | -8635477 | 86.3548 | 40267141 | 234061.56 | 213257751 | 99891457 | 50073093 | 0.000000 | 347963318 | 75873535 | 0.000000
09-04-2025 20:50:20000 | -8596680 | 85.9668 | 38738159 | 233992.81 | 212347595 | 99898628 | 50084309 | 0.000000 | 353508026 | 77069111 | 0.000000
09-04-2025 20:50:25000 | -8613673 | 86.1367 | 39111235 | 233970.38 | 212789627 | 99897072 | 50068909 | 0.000000 | 358916748 | 78264692 | 0.000000
09-04-2025 20:50:30000 | -8745472 | 87.4547 | 38733362 | 233845.53 | 216153351 | 99902069 | 50035946 | 0.000000 | 364359406 | 79470454 | 0.000000
09-04-2025 20:50:35000 | -8799110 | 87.9911 | 41608115 | 233934.31 | 217424500 | 99888382 | 50026875 | 0.000000 | 370108826 | 80692075 | 0.000000
09-04-2025 20:50:40000 | -8661253 | 86.6125 | 40770576 | 234046.19 | 213915726 | 99889397 | 50055866 | 0.000000 | 375803131 | 81905122 | 0.000000
09-04-2025 20:50:45000 | -8483214 | 84.8321 | 37258979 | 234047.86 | 209484375 | 99903687 | 50094505 | 0.000000 | 381226105 | 83092354 | 0.000000
09-04-2025 20:50:50000 | -8526590 | 85.2659 | 39510374 | 234018.66 | 210606155 | 99892815 | 50087303 | 0.000000 | 386622681 | 84270781 | 0.000000
09-04-2025 20:50:55000 | -8604077 | 86.0408 | 42540596 | 233999.14 | 212571823 | 99877998 | 50075470 | 0.000000 | 392381256 | 85462148 | 0.000000
09-04-2025 20:51:00000 | -8623946 | 86.2395 | 42073638 | 234025.53 | 213027344 | 99881203 | 50074459 | 0.000000 | 398295105 | 86659893 | 0.000000
09-04-2025 20:51:05000 | -8700435 | 87.0044 | 42862188 | 233993.13 | 214952209 | 99878868 | 50065376 | 0.000000 | 404196198 | 87863350 | 0.000000
09-04-2025 20:51:10000 | -8748038 | 87.4804 | 43642734 | 233993.83 | 216133301 | 99875786 | 50050987 | 0.000000 | 410203430 | 89077598 | 0.000000
09-04-2025 20:51:15000 | -8837100 | 88.371 | 44064707 | 233971.09 | 218357254 | 99875916 | 50033825 | 0.000000 | 416263031 | 90299014 | 0.000000
09-04-2025 20:51:20000 | -8725989 | 87.2599 | 41774961 | 234026.72 | 215537140 | 99885597 | 50055172 | 0.000000 | 422273865 | 91518691 | 0.000000
09-04-2025 20:51:25000 | -8733634 | 87.3363 | 38038625 | 233905.17 | 215797577 | 99905289 | 50050869 | 0.000000 | 427698578 | 92727773 | 0.000000
09-04-2025 20:51:30000 | -8664993 | 86.6499 | 41098345 | 234023.45 | 214031540 | 99887711 | 50060116 | 0.000000 | 433294128 | 93935996 | 0.000000
09-04-2025 20:51:35000 | -8677701 | 86.777 | 39264075 | 233973.44 | 214368195 | 99897789 | 50051662 | 0.000000 | 438840149 | 95139482 | 0.000000
09-04-2025 20:51:40000 | -8719405 | 87.1941 | 41376133 | 233968.84 | 215424469 | 99887604 | 50045452 | 0.000000 | 444516754 | 96349805 | 0.000000
09-04-2025 20:51:45000 | -8821316 | 88.2132 | 40729495 | 233892.39 | 217999619 | 99893578 | 50030396 | 0.000000 | 450181946 | 97565723 | 0.000000
09-04-2025 20:51:50000 | -8942286 | 89.4229 | 41254985 | 233845.59 | 221031952 | 99893745 | 49991016 | 0.000000 | 455915070 | 98803604 | 0.000000
09-04-2025 20:51:55000 | -8862248 | 88.6225 | 40211599 | 233950.09 | 218949493 | 99897217 | 50009422 | 0.000000 | 461609253 | 10004163 | 0.000000
09-04-2025 20:52:00000 | -8677443 | 86.7744 | 38440964 | 234011.09 | 214317047 | 99902023 | 50037331 | 0.000000 | 467166931 | 10125536 | 0.000000
09-04-2025 20:52:05000 | -8547498 | 85.475 | 35916946 | 233982.00 | 211116913 | 99911835 | 50054131 | 0.000000 | 472277893 | 10244688 | 0.000000
09-04-2025 20:52:10000 | -8528728 | 85.2873 | 36094346 | 233929.75 | 210699799 | 99910568 | 50066341 | 0.000000 | 477270477 | 10363065 | 0.000000
09-04-2025 20:52:15000 | -8611373 | 86.1137 | 36833635 | 233884.89 | 212788483 | 99908646 | 50065163 | 0.000000 | 482305969 | 10481949 | 0.000000
09-04-2025 20:52:20000 | -8599634 | 85.9963 | 38303323 | 233942.89 | 212460190 | 99900955 | 50058239 | 0.000000 | 487593994 | 10601416 | 0.000000
09-04-2025 20:52:25000 | -8694884 | 86.9488 | 40282554 | 233915.77 | 214855179 | 99892853 | 50045174 | 0.000000 | 493099701 | 10721759 | 0.000000
09-04-2025 20:52:30000 | -8792764 | 87.9276 | 40772356 | 233903.39 | 217286087 | 99892662 | 50022308 | 0.000000 | 498786285 | 10843556 | 0.000000
09-04-2025 20:52:35000 | -8828472 | 88.2847 | 42045166 | 233915.53 | 218169373 | 99886787 | 50027946 | 0.000000 | 504628784 | 10966027 | 0.000000
09-04-2025 20:52:40000 | -8776952 | 87.7695 | 39115854 | 233903.95 | 216878403 | 99900841 | 50029278 | 0.000000 | 510242035 | 11088602 | 0.000000
09-04-2025 20:52:45000 | -8671302 | 86.713 | 36989861 | 233953.50 | 214203522 | 99909142 | 50045193 | 0.000000 | 515432373 | 11209440 | 0.000000
09-04-2025 20:52:50000 | -8754363 | 87.5436 | 37340623 | 233863.98 | 216344421 | 99909157 | 50014626 | 0.000000 | 520592163 | 11330365 | 0.000000
09-04-2025 20:52:55000 | -8805678 | 88.0568 | 39683899 | 233934.78 | 217563339 | 99898605 | 50007847 | 0.000000 | 526010742 | 11452592 | 0.000000
09-04-2025 20:53:00000 | -8743459 | 87.4346 | 39763953 | 233972.48 | 215995987 | 99896744 | 50031498 | 0.000000 | 531596008 | 11574539 | 0.000000
09-04-2025 20:53:05000 | -8676270 | 86.7627 | 38986404 | 233960.83 | 214341690 | 99899200 | 50041779 | 0.000000 | 537034424 | 11695301 | 0.000000
09-04-2025 20:53:10000 | -8697953 | 86.9795 | 38480942 | 233911.38 | 214915298 | 99902275 | 50036259 | 0.000000 | 542411438 | 11816031 | 0.000000
09-04-2025 20:53:15000 | -8594178 | 85.9418 | 37034631 | 233954.36 | 212302261 | 99907280 | 50057159 | 0.000000 | 547627380 | 11936141 | 0.000000
09-04-2025 20:53:20000 | -8618841 | 86.1884 | 34215688 | 233807.11 | 213015320 | 99921295 | 50047417 | 0.000000 | 552554688 | 12055474 | 0.000000
09-04-2025 20:53:25000 | -8681016 | 86.8102 | 37215073 | 233876.39 | 214517441 | 99908234 | 50030949 | 0.000000 | 557526001 | 12175673 | 0.000000
09-04-2025 20:53:30000 | -8677458 | 86.7746 | 36808647 | 233882.34 | 214418182 | 99910156 | 50035324 | 0.000000 | 562629639 | 12296295 | 0.000000
09-04-2025 20:53:35000 | -8640141 | 86.4014 | 36872954 | 233905.05 | 213477798 | 99909058 | 50051735 | 0.000000 | 567698059 | 12416769 | 0.000000
09-04-2025 20:53:40000 | -8574882 | 85.7488 | 36294973 | 233943.58 | 211829773 | 99910538 | 50056980 | 0.000000 | 572737183 | 12536238 | 0.000000
09-04-2025 20:53:45000 | -8599454 | 85.9945 | 36027119 | 233882.55 | 212486710 | 99912354 | 50048256 | 0.000000 | 577830078 | 12655502 | 0.000000
09-04-2025 20:53:50000 | -8756141 | 87.5614 | 36803657 | 233777.06 | 216461807 | 99911781 | 50011734 | 0.000000 | 582886230 | 12776258 | 0.000000
09-04-2025 20:53:55000 | -8836581 | 88.3658 | 39240051 | 233843.09 | 218404449 | 99901550 | 49992825 | 0.000000 | 588121399 | 12898814 | 0.000000
09-04-2025 20:54:00000 | -8719514 | 87.1951 | 35398879 | 233851.50 | 215472900 | 99917694 | 50016350 | 0.000000 | 593223877 | 13020821 | 0.000000
09-04-2025 20:54:05000 | -8579509 | 85.7951 | 32793677 | 233890.63 | 211955704 | 99927032 | 50053047 | 0.000000 | 597892517 | 13140682 | 0.000000
09-04-2025 20:54:10000 | -8509254 | 85.0925 | 32801069 | 233891.22 | 210222321 | 99925789 | 50060398 | 0.000000 | 602470337 | 13258840 | 0.000000
09-04-2025 20:54:15000 | -8653117 | 86.5312 | 37228271 | 233861.28 | 213842758 | 99907578 | 50035007 | 0.000000 | 607338806 | 13377821 | 0.000000
09-04-2025 20:54:20000 | -8678352 | 86.7835 | 39146108 | 233918.27 | 214433319 | 99898422 | 50031521 | 0.000000 | 612607605 | 13498169 | 0.000000
09-04-2025 20:54:25000 | -8857605 | 88.576 | 37281707 | 233742.86 | 218997208 | 99911537 | 49993259 | 0.000000 | 617816406 | 13620117 | 0.000000
09-04-2025 20:54:30000 | -8858295 | 88.5829 | 39159934 | 233869.91 | 218914963 | 99902428 | 49990215 | 0.000000 | 623159790 | 13743250 | 0.000000
09-04-2025 20:54:35000 | -8666936 | 86.6694 | 35510281 | 233939.88 | 214093918 | 99916168 | 50028561 | 0.000000 | 628366333 | 13864765 | 0.000000
09-04-2025 20:54:40000 | -8525231 | 85.2523 | 37191094 | 234054.67 | 210513641 | 99904984 | 50064495 | 0.000000 | 633309265 | 13983912 | 0.000000
09-04-2025 20:54:45000 | -8488905 | 84.889 | 34718967 | 233914.27 | 209718933 | 99916466 | 50058514 | 0.000000 | 638259644 | 14101642 | 0.000000
09-04-2025 20:54:50000 | -8537203 | 85.372 | 39291902 | 233979.56 | 210900543 | 99894257 | 50063324 | 0.000000 | 643433350 | 14220140 | 0.000000
09-04-2025 20:54:55000 | -8644631 | 86.4463 | 40511902 | 233937.44 | 213601715 | 99890373 | 50061703 | 0.000000 | 648953918 | 14339380 | 0.000000
09-04-2025 20:55:00000 | -8708206 | 87.0821 | 39155530 | 233898.50 | 215187408 | 99899063 | 50037262 | 0.000000 | 654424561 | 14459874 | 0.000000
09-04-2025 20:55:05000 | -8843413 | 88.4341 | 40376853 | 233851.36 | 218582108 | 99895935 | 50011307 | 0.000000 | 660010803 | 14582043 | 0.000000
09-04-2025 20:55:10000 | -8838842 | 88.3884 | 39201929 | 233887.78 | 218418854 | 99901787 | 50009239 | 0.000000 | 665510559 | 14704799 | 0.000000
09-04-2025 20:55:15000 | -8823427 | 88.2343 | 39443608 | 233915.45 | 218019562 | 99900230 | 49996239 | 0.000000 | 670910583 | 14827651 | 0.000000
09-04-2025 20:55:20000 | -8730645 | 87.3064 | 37890361 | 233944.31 | 215684219 | 99905960 | 50010597 | 0.000000 | 676195557 | 14949482 | 0.000000
09-04-2025 20:55:25000 | -8668781 | 86.6878 | 34983721 | 233890.88 | 214179871 | 99918671 | 50017902 | 0.000000 | 681179810 | 15070091 | 0.000000
09-04-2025 20:55:30000 | -8651759 | 86.5176 | 33605269 | 233814.28 | 213815079 | 99924652 | 50018787 | 0.000000 | 685930664 | 15190089 | 0.000000
09-04-2025 20:55:35000 | -8751368 | 87.5137 | 32418333 | 233721.61 | 216349472 | 99931458 | 49986423 | 0.000000 | 690409851 | 15311157 | 0.000000
09-04-2025 20:55:40000 | -8832136 | 88.3214 | 33401528 | 233691.13 | 218379059 | 99928566 | 49980530 | 0.000000 | 695178162 | 15433492 | 0.000000
09-04-2025 20:55:45000 | -8659104 | 86.591 | 31305876 | 233802.05 | 213986206 | 99934708 | 50014408 | 0.000000 | 699710876 | 15554732 | 0.000000
09-04-2025 20:55:50000 | -8604172 | 86.0417 | 29878096 | 233764.08 | 212652328 | 99939766 | 50024055 | 0.000000 | 703940857 | 15674381 | 0.000000
09-04-2025 20:55:55000 | -8594566 | 85.9457 | 32087788 | 233833.75 | 212373871 | 99930374 | 50021473 | 0.000000 | 708286621 | 15793769 | 0.000000
09-04-2025 20:56:00000 | -8605810 | 86.0581 | 32223909 | 233799.44 | 212681915 | 99929970 | 50017262 | 0.000000 | 712808899 | 15913199 | 0.000000
09-04-2025 20:56:05000 | -8599145 | 85.9915 | 32991743 | 233826.75 | 212500046 | 99926483 | 50022903 | 0.000000 | 717352905 | 16032824 | 0.000000
09-04-2025 20:56:10000 | -8522231 | 85.2223 | 32082136 | 233851.13 | 210572159 | 99929214 | 50032112 | 0.000000 | 721848816 | 16151642 | 0.000000
09-04-2025 20:56:15000 | -8548955 | 85.4895 | 35066958 | 233906.31 | 211210297 | 99915977 | 50027546 | 0.000000 | 726471191 | 16270247 | 0.000000
09-04-2025 20:56:20000 | -8610777 | 86.1078 | 37115991 | 233874.11 | 212784668 | 99907234 | 50035061 | 0.000000 | 731688965 | 16389324 | 0.000000
09-04-2025 20:56:25000 | -8688116 | 86.8812 | 37541160 | 233855.97 | 214714676 | 99906776 | 50024319 | 0.000000 | 736918396 | 16509498 | 0.000000
09-04-2025 20:56:30000 | -8741142 | 87.4114 | 39513689 | 233909.22 | 215993286 | 99897987 | 50015045 | 0.000000 | 742194092 | 16630607 | 0.000000
09-04-2025 20:56:35000 | -8759770 | 87.5977 | 39444790 | 233910.89 | 216450058 | 99898773 | 50021301 | 0.000000 | 747787659 | 16752068 | 0.000000
09-04-2025 20:56:40000 | -8867172 | 88.6717 | 39910532 | 233855.94 | 219155426 | 99898865 | 49989349 | 0.000000 | 753285339 | 16874697 | 0.000000
09-04-2025 20:56:45000 | -8856085 | 88.5609 | 39675879 | 233887.25 | 218850159 | 99899796 | 49984257 | 0.000000 | 758867737 | 16998004 | 0.000000
09-04-2025 20:56:50000 | -8821717 | 88.2172 | 37368418 | 233855.81 | 218006668 | 99910400 | 49978607 | 0.000000 | 764159058 | 17120826 | 0.000000
09-04-2025 20:56:55000 | -8798749 | 87.9875 | 36612888 | 233878.36 | 217411301 | 99913536 | 49963871 | 0.000000 | 769182434 | 17243189 | 0.000000
09-04-2025 20:57:00000 | -8726862 | 87.2686 | 38182969 | 233956.77 | 215583405 | 99904419 | 49965084 | 0.000000 | 774492065 | 17365158 | 0.000000
09-04-2025 20:57:05000 | -8702863 | 87.0286 | 33625554 | 233801.84 | 215088013 | 99925438 | 49965240 | 0.000000 | 779351990 | 17486162 | 0.000000
09-04-2025 20:57:10000 | -8795045 | 87.9505 | 36145635 | 233825.92 | 217366547 | 99915657 | 49944191 | 0.000000 | 784099792 | 17607820 | 0.000000
09-04-2025 20:57:15000 | -8763744 | 87.6374 | 35618110 | 233871.44 | 216544159 | 99917511 | 49963821 | 0.000000 | 789110962 | 17729885 | 0.000000
09-04-2025 20:57:20000 | -8634926 | 86.3493 | 35278210 | 233950.81 | 213291855 | 99916649 | 49992844 | 0.000000 | 793951050 | 17850557 | 0.000000
09-04-2025 20:57:25000 | -8581591 | 85.8159 | 33140759 | 233852.89 | 212043976 | 99925514 | 49998688 | 0.000000 | 798660278 | 17969891 | 0.000000
09-04-2025 20:57:30000 | -8586910 | 85.8691 | 32908560 | 233830.59 | 212194183 | 99926643 | 49991970 | 0.000000 | 803216064 | 18088867 | 0.000000
09-04-2025 20:57:35000 | -8580295 | 85.8029 | 32140847 | 233759.41 | 212088837 | 99929916 | 49989536 | 0.000000 | 807837219 | 18207820 | 0.000000
09-04-2025 20:57:40000 | -8609437 | 86.0944 | 34448052 | 233843.34 | 212752136 | 99920052 | 49979851 | 0.000000 | 812434998 | 18327275 | 0.000000
09-04-2025 20:57:45000 | -8602705 | 86.0271 | 36757900 | 233920.39 | 212542130 | 99908836 | 49989258 | 0.000000 | 817475159 | 18446873 | 0.000000
09-04-2025 20:57:50000 | -8604634 | 86.0463 | 35144714 | 233888.80 | 212598679 | 99916695 | 49980785 | 0.000000 | 822356812 | 18566416 | 0.000000
09-04-2025 20:57:55000 | -8629775 | 86.2977 | 38448020 | 233958.53 | 213194672 | 99900902 | 49980602 | 0.000000 | 827509705 | 18686232 | 0.000000
09-04-2025 20:58:00000 | -8587665 | 85.8766 | 36206621 | 233894.03 | 212187744 | 99911240 | 49987732 | 0.000000 | 832602051 | 18805586 | 0.000000
09-04-2025 20:58:05000 | -8582316 | 85.8232 | 36010200 | 233908.47 | 212039551 | 99912086 | 49984818 | 0.000000 | 837587524 | 18924803 | 0.000000
09-04-2025 20:58:10000 | -8594622 | 85.9462 | 34642913 | 233859.09 | 212375153 | 99918861 | 49985172 | 0.000000 | 842438232 | 19044068 | 0.000000
09-04-2025 20:58:15000 | -8570909 | 85.7091 | 35176699 | 233874.80 | 211780334 | 99915886 | 49992817 | 0.000000 | 847251221 | 19163281 | 0.000000
09-04-2025 20:58:20000 | -8632051 | 86.3205 | 33998223 | 233780.22 | 213365906 | 99922523 | 49973480 | 0.000000 | 852047668 | 19282529 | 0.000000
09-04-2025 20:58:25000 | -8814932 | 88.1493 | 37771628 | 233793.67 | 217902405 | 99908325 | 49934235 | 0.000000 | 857051086 | 19404205 | 0.000000
09-04-2025 20:58:30000 | -8856269 | 88.5627 | 36582881 | 233791.83 | 218910721 | 99914795 | 49932281 | 0.000000 | 862166687 | 19527309 | 0.000000
09-04-2025 20:58:35000 | -8712209 | 87.1221 | 31369749 | 233786.28 | 215312805 | 99935242 | 49948658 | 0.000000 | 866809814 | 19649244 | 0.000000
09-04-2025 20:58:40000 | -8592465 | 85.9246 | 32165923 | 233874.42 | 212285263 | 99930008 | 49977341 | 0.000000 | 871317444 | 19769359 | 0.000000
09-04-2025 20:58:45000 | -8593299 | 85.933 | 30887788 | 233799.06 | 212362350 | 99935463 | 49978809 | 0.000000 | 875600525 | 19888604 | 0.000000
09-04-2025 20:58:50000 | -8549730 | 85.4973 | 31564959 | 233830.42 | 211265961 | 99931915 | 49991020 | 0.000000 | 879958496 | 20007221 | 0.000000
09-04-2025 20:58:55000 | -8652509 | 86.5251 | 32158745 | 233726.28 | 213900528 | 99931000 | 49966202 | 0.000000 | 884353882 | 20126773 | 0.000000
09-04-2025 20:59:00000 | -8719179 | 87.1918 | 33879653 | 233799.89 | 215493988 | 99924591 | 49955849 | 0.000000 | 889002869 | 20247783 | 0.000000
09-04-2025 20:59:05000 | -8673480 | 86.7348 | 33793826 | 233787.61 | 214378601 | 99924187 | 49971836 | 0.000000 | 893764893 | 20368719 | 0.000000
09-04-2025 20:59:10000 | -8698438 | 86.9844 | 31498469 | 233756.95 | 215002090 | 99934502 | 49963604 | 0.000000 | 898197754 | 20489287 | 0.000000
09-04-2025 20:59:15000 | -8724111 | 87.2411 | 31426436 | 233693.64 | 215691422 | 99935181 | 49960171 | 0.000000 | 902711914 | 20610178 | 0.000000
09-04-2025 20:59:20000 | -8805497 | 88.055 | 35367998 | 233789.86 | 217647659 | 99919434 | 49941795 | 0.000000 | 907417603 | 20732389 | 0.000000
09-04-2025 20:59:25000 | -8714678 | 87.1468 | 33706721 | 233824.22 | 215360825 | 99925285 | 49949604 | 0.000000 | 912277710 | 20854080 | 0.000000
09-04-2025 20:59:30000 | -8570902 | 85.709 | 32609346 | 233898.09 | 211734695 | 99927704 | 49979591 | 0.000000 | 916932129 | 20974018 | 0.000000
09-04-2025 20:59:35000 | -8465841 | 84.6584 | 33007412 | 233935.59 | 209116150 | 99924080 | 49999668 | 0.000000 | 921476318 | 21092098 | 0.000000
09-04-2025 20:59:40000 | -8600009 | 86.0001 | 33858931 | 233795.20 | 212558960 | 99922585 | 49976204 | 0.000000 | 926096130 | 21210717 | 0.000000
09-04-2025 20:59:45000 | -8660563 | 86.6056 | 34536128 | 233791.23 | 214063187 | 99920586 | 49972572 | 0.000000 | 930925537 | 21330803 | 0.000000
09-04-2025 20:59:50000 | -8685273 | 86.8527 | 35191433 | 233812.89 | 214658539 | 99918015 | 49976227 | 0.000000 | 935807312 | 21451314 | 0.000000
09-04-2025 20:59:55000 | -8819092 | 88.1909 | 36501084 | 233764.63 | 218019302 | 99914459 | 49949509 | 0.000000 | 940862549 | 21573012 | 0.000000
09-04-2025 21:00:00000 | -8835064 | 88.3506 | 38354453 | 233854.98 | 218348190 | 99905907 | 49944660 | 0.000000 | 946021912 | 21695914 | 0.000000
09-04-2025 21:00:05000 | -8714150 | 87.1415 | 32998977 | 233790.69 | 215372635 | 99928375 | 49953976 | 0.000000 | 4870393 | 121747810 | 0.000000
09-04-2025 21:00:10000 | -8719054 | 87.1905 | 33825459 | 233831.30 | 215462189 | 99924835 | 49954632 | 0.000000 | 9516960 | 242976959 | 0.000000
09-04-2025 21:00:15000 | -8646740 | 86.4674 | 34365818 | 233865.88 | 213651016 | 99921112 | 49977741 | 0.000000 | 14362836 | 363516327 | 0.000000
09-04-2025 21:00:20000 | -8636932 | 86.3693 | 33209702 | 233819.67 | 213440674 | 99926155 | 49972450 | 0.000000 | 18966343 | 483400299 | 0.000000
09-04-2025 21:00:25000 | -8646223 | 86.4622 | 33984334 | 233870.28 | 213630661 | 99922844 | 49968586 | 0.000000 | 23519596 | 603504211 | 0.000000
09-04-2025 21:00:30000 | -8696510 | 86.9651 | 32106362 | 233739.50 | 214974579 | 99931923 | 49957958 | 0.000000 | 28057121 | 723916077 | 0.000000
09-04-2025 21:00:35000 | -8708834 | 87.0883 | 32912820 | 233769.20 | 215258438 | 99928665 | 49948933 | 0.000000 | 32510422 | 844930176 | 0.000000
09-04-2025 21:00:40000 | -8733547 | 87.3355 | 34588604 | 233819.58 | 215841400 | 99921669 | 49945255 | 0.000000 | 37110764 | 966209717 | 0.000000
09-04-2025 21:00:45000 | -8706580 | 87.0658 | 34341060 | 233822.08 | 215167480 | 99922302 | 49966801 | 0.000000 | 42008949 | 10875945 | 0.000000
09-04-2025 21:00:50000 | -8676371 | 86.7637 | 34233745 | 233857.75 | 214390945 | 99922249 | 49966461 | 0.000000 | 46619022 | 12080857 | 0.000000
09-04-2025 21:00:55000 | -8601321 | 86.0132 | 33107732 | 233852.16 | 212530960 | 99926003 | 49984905 | 0.000000 | 51316708 | 13278236 | 0.000000
09-04-2025 21:01:00000 | -8569655 | 85.6966 | 33815740 | 233880.31 | 211733948 | 99922234 | 49984039 | 0.000000 | 55929874 | 14468420 | 0.000000
09-04-2025 21:01:05000 | -8621146 | 86.2115 | 36064746 | 233903.39 | 213002731 | 99912613 | 49980583 | 0.000000 | 60763775 | 15662765 | 0.000000
09-04-2025 21:01:10000 | -8677142 | 86.7714 | 36244878 | 233842.92 | 214441162 | 99912872 | 49980042 | 0.000000 | 65779022 | 16864664 | 0.000000
09-04-2025 21:01:15000 | -8783741 | 87.8374 | 36535161 | 233787.00 | 217131042 | 99913612 | 49956581 | 0.000000 | 70834663 | 18078976 | 0.000000
09-04-2025 21:01:20000 | -8886992 | 88.8699 | 36645718 | 233748.92 | 219709885 | 99915092 | 49931725 | 0.000000 | 75964088 | 19307313 | 0.000000
09-04-2025 21:01:25000 | -8860866 | 88.6087 | 36982544 | 233842.88 | 218979904 | 99913017 | 49925224 | 0.000000 | 81017532 | 20542871 | 0.000000
09-04-2025 21:01:30000 | -8713568 | 87.1357 | 30901021 | 233777.38 | 215349747 | 99937180 | 49958130 | 0.000000 | 85679916 | 21756917 | 0.000000
09-04-2025 21:01:35000 | -8668798 | 86.688 | 32006084 | 233858.70 | 214179718 | 99931915 | 49958351 | 0.000000 | 89947876 | 22962947 | 0.000000
09-04-2025 21:01:40000 | -8685373 | 86.8537 | 33468132 | 233813.47 | 214643356 | 99925842 | 49950375 | 0.000000 | 94681290 | 24168735 | 0.000000
09-04-2025 21:01:45000 | -8679571 | 86.7957 | 30730186 | 233739.47 | 214543701 | 99937386 | 49952133 | 0.000000 | 99081451 | 25374629 | 0.000000
09-04-2025 21:01:50000 | -8503698 | 85.037 | 30444387 | 233860.30 | 210091507 | 99935974 | 49988358 | 0.000000 | 103332649 | 26566841 | 0.000000
09-04-2025 21:01:55000 | -8496270 | 84.9627 | 28978911 | 233778.03 | 209969757 | 99941887 | 49993031 | 0.000000 | 107380455 | 27747227 | 0.000000
09-04-2025 21:02:00000 | -8511598 | 85.116 | 32052017 | 233843.84 | 210315689 | 99929176 | 50001190 | 0.000000 | 111656815 | 28928545 | 0.000000
09-04-2025 21:02:05000 | -8560672 | 85.6067 | 31368582 | 233765.50 | 211590546 | 99932930 | 50004803 | 0.000000 | 116108879 | 30115317 | 0.000000
09-04-2025 21:02:10000 | -8747663 | 87.4766 | 32782034 | 233680.56 | 216298569 | 99929855 | 49972458 | 0.000000 | 120561584 | 31321304 | 0.000000
09-04-2025 21:02:15000 | -8886281 | 88.8628 | 34673140 | 233698.22 | 219722443 | 99923965 | 49944454 | 0.000000 | 125273552 | 32547944 | 0.000000
09-04-2025 21:02:20000 | -8801655 | 88.0165 | 36039351 | 233867.39 | 217487885 | 99916275 | 49970993 | 0.000000 | 130234955 | 33776279 | 0.000000
09-04-2025 21:02:25000 | -8758269 | 87.5827 | 32945840 | 233784.84 | 216465439 | 99929321 | 49968189 | 0.000000 | 134949570 | 34992004 | 0.000000
09-04-2025 21:02:30000 | -8786805 | 87.868 | 35109487 | 233846.11 | 217131622 | 99920265 | 49947178 | 0.000000 | 139620422 | 36211248 | 0.000000
09-04-2025 21:02:35000 | -8732620 | 87.3262 | 35800820 | 233857.22 | 215791672 | 99916069 | 49967411 | 0.000000 | 144685150 | 37429038 | 0.000000
09-04-2025 21:02:40000 | -8600495 | 86.0049 | 32503015 | 233856.69 | 212500900 | 99928665 | 49994335 | 0.000000 | 149429565 | 38629031 | 0.000000
09-04-2025 21:02:45000 | -8531577 | 85.3158 | 30725183 | 233839.53 | 210804047 | 99935211 | 50001320 | 0.000000 | 153776688 | 39818230 | 0.000000
09-04-2025 21:02:50000 | -8586780 | 85.8678 | 30759453 | 233739.59 | 212254013 | 99935898 | 49994621 | 0.000000 | 158019638 | 41005430 | 0.000000
09-04-2025 21:02:55000 | -8676934 | 86.7693 | 32386482 | 233737.14 | 214495865 | 99930412 | 49979839 | 0.000000 | 162456512 | 42206987 | 0.000000
09-04-2025 21:03:00000 | -8634432 | 86.3443 | 32886228 | 233822.92 | 213373138 | 99927544 | 49997761 | 0.000000 | 167064316 | 43408223 | 0.000000
09-04-2025 21:03:05000 | -8648952 | 86.4895 | 35304788 | 233856.88 | 213723633 | 99916794 | 49990898 | 0.000000 | 171841949 | 44608750 | 0.000000
09-04-2025 21:03:10000 | -8690899 | 86.909 | 35500579 | 233849.00 | 214770203 | 99916679 | 49984394 | 0.000000 | 176747253 | 45813726 | 0.000000
09-04-2025 21:03:15000 | -8682190 | 86.8219 | 34153340 | 233818.31 | 214567749 | 99922722 | 49982544 | 0.000000 | 181538223 | 47020869 | 0.000000
09-04-2025 21:03:20000 | -8638020 | 86.3802 | 36174624 | 233912.16 | 213412323 | 99912422 | 50003464 | 0.000000 | 186536621 | 48224639 | 0.000000
09-04-2025 21:03:25000 | -8675263 | 86.7526 | 33824839 | 233784.86 | 214424118 | 99924072 | 49987007 | 0.000000 | 191311325 | 49425425 | 0.000000
09-04-2025 21:03:30000 | -8792154 | 87.9215 | 36635759 | 233805.91 | 217318604 | 99913300 | 49964581 | 0.000000 | 196228531 | 50638564 | 0.000000
09-04-2025 21:03:35000 | -8915216 | 89.1522 | 37497305 | 233736.06 | 220427231 | 99911667 | 49931061 | 0.000000 | 201402695 | 51869907 | 0.000000
09-04-2025 21:03:40000 | -8892366 | 88.9237 | 37317534 | 233818.50 | 219784012 | 99912056 | 49927368 | 0.000000 | 206559219 | 53108252 | 0.000000
09-04-2025 21:03:45000 | -8784823 | 87.8482 | 34834385 | 233852.78 | 217074234 | 99921478 | 49937878 | 0.000000 | 211564102 | 54335542 | 0.000000
09-04-2025 21:03:50000 | -8679930 | 86.7993 | 33308748 | 233877.06 | 214450302 | 99926453 | 49958099 | 0.000000 | 216329376 | 55547246 | 0.000000
09-04-2025 21:03:55000 | -8557904 | 85.579 | 30733145 | 233829.34 | 211459930 | 99935577 | 49985119 | 0.000000 | 220733185 | 56739492 | 0.000000
09-04-2025 21:04:00000 | -8613434 | 86.1343 | 28796365 | 233709.91 | 212928497 | 99944160 | 49968052 | 0.000000 | 224787247 | 57928691 | 0.000000
09-04-2025 21:04:05000 | -8615147 | 86.1515 | 30528904 | 233737.17 | 212954361 | 99937271 | 49959488 | 0.000000 | 229043533 | 59126177 | 0.000000
09-04-2025 21:04:10000 | -8523884 | 85.2388 | 30862449 | 233834.25 | 210616287 | 99934517 | 49991390 | 0.000000 | 233306885 | 60316455 | 0.000000
09-04-2025 21:04:15000 | -8415729 | 84.1573 | 29665984 | 233850.53 | 207923767 | 99937927 | 50020058 | 0.000000 | 237525406 | 61489438 | 0.000000
09-04-2025 21:04:20000 | -8435634 | 84.3563 | 29516580 | 233784.70 | 208471252 | 99938843 | 50020584 | 0.000000 | 241585266 | 62658076 | 0.000000
09-04-2025 21:04:25000 | -8528523 | 85.2852 | 33269585 | 233804.91 | 210779572 | 99923996 | 50013271 | 0.000000 | 246036545 | 63838604 | 0.000000
09-04-2025 21:04:30000 | -8650384 | 86.5038 | 35684714 | 233810.27 | 213805328 | 99915024 | 50001827 | 0.000000 | 250842987 | 65034155 | 0.000000
09-04-2025 21:04:35000 | -8673735 | 86.7374 | 32775239 | 233738.39 | 214420837 | 99928688 | 50003174 | 0.000000 | 255603943 | 66237231 | 0.000000
09-04-2025 21:04:40000 | -8745520 | 87.4552 | 34189316 | 233771.09 | 216174393 | 99923676 | 49983009 | 0.000000 | 260218414 | 67448940 | 0.000000
09-04-2025 21:04:45000 | -8800698 | 88.007 | 35036948 | 233768.52 | 217548981 | 99920845 | 49978039 | 0.000000 | 265071808 | 68668472 | 0.000000
09-04-2025 21:04:50000 | -8770827 | 87.7083 | 35796396 | 233843.94 | 216746399 | 99916817 | 49983162 | 0.000000 | 270010956 | 69889194 | 0.000000
09-04-2025 21:04:55000 | -8737120 | 87.3712 | 34355110 | 233839.08 | 215905609 | 99922783 | 49994297 | 0.000000 | 274850342 | 71104985 | 0.000000
09-04-2025 21:05:00000 | -8675616 | 86.7562 | 33461802 | 233850.69 | 214371552 | 99925697 | 50005093 | 0.000000 | 279618073 | 72314473 | 0.000000
09-04-2025 21:05:05000 | -8704262 | 87.0426 | 32502747 | 233772.47 | 215139801 | 99930351 | 49992710 | 0.000000 | 284230865 | 73521572 | 0.000000
09-04-2025 21:05:10000 | -8737330 | 87.3733 | 35426626 | 233852.88 | 215908463 | 99917900 | 49987873 | 0.000000 | 288886261 | 74735767 | 0.000000
09-04-2025 21:05:15000 | -8631402 | 86.314 | 34386282 | 233898.31 | 213246414 | 99920738 | 50021038 | 0.000000 | 293789978 | 75940947 | 0.000000
09-04-2025 21:05:20000 | -8575195 | 85.7519 | 33025471 | 233861.89 | 211878281 | 99925919 | 50026245 | 0.000000 | 298350861 | 77133701 | 0.000000
09-04-2025 21:05:25000 | -8546631 | 85.4663 | 35572683 | 233937.27 | 211130737 | 99913490 | 50028347 | 0.000000 | 303121857 | 78322974 | 0.000000
09-04-2025 21:05:30000 | -8556017 | 85.5602 | 36596787 | 233945.63 | 211367386 | 99908646 | 50034336 | 0.000000 | 308156342 | 79509448 | 0.000000
09-04-2025 21:05:35000 | -8643291 | 86.4329 | 37913992 | 233890.39 | 213580017 | 99903931 | 50028381 | 0.000000 | 313371735 | 80703364 | 0.000000
09-04-2025 21:05:40000 | -8673151 | 86.7315 | 37482075 | 233883.88 | 214318909 | 99906746 | 50025810 | 0.000000 | 318540771 | 81908071 | 0.000000
09-04-2025 21:05:45000 | -8688184 | 86.8818 | 35544773 | 233828.86 | 214719635 | 99916420 | 50018101 | 0.000000 | 323618927 | 83113066 | 0.000000
09-04-2025 21:05:50000 | -8771191 | 87.7119 | 35642449 | 233778.80 | 216814453 | 99917542 | 50000732 | 0.000000 | 328630981 | 84324424 | 0.000000
09-04-2025 21:05:55000 | -8802792 | 88.0279 | 38312903 | 233909.08 | 217501877 | 99905418 | 49983414 | 0.000000 | 333733246 | 85548135 | 0.000000
09-04-2025 21:06:00000 | -8691492 | 86.9149 | 35064600 | 233868.16 | 214759872 | 99918716 | 50005192 | 0.000000 | 338926880 | 86762529 | 0.000000
09-04-2025 21:06:05000 | -8645355 | 86.4536 | 33500190 | 233871.19 | 213606232 | 99925011 | 50010750 | 0.000000 | 343560730 | 87966748 | 0.000000
09-04-2025 21:06:10000 | -8551202 | 85.512 | 30422234 | 233789.00 | 211329163 | 99936775 | 50030258 | 0.000000 | 348023865 | 89158320 | 0.000000
09-04-2025 21:06:15000 | -8586419 | 85.8642 | 32050811 | 233820.83 | 212185089 | 99930405 | 50029346 | 0.000000 | 352277893 | 90346729 | 0.000000
09-04-2025 21:06:20000 | -8522634 | 85.2263 | 36480095 | 233967.47 | 210519852 | 99908516 | 50051304 | 0.000000 | 357160706 | 91536143 | 0.000000
09-04-2025 21:06:25000 | -8545962 | 85.4596 | 34688169 | 233871.23 | 211163284 | 99917725 | 50051136 | 0.000000 | 361892670 | 92719307 | 0.000000
09-04-2025 21:06:30000 | -8606827 | 86.0683 | 38519814 | 233926.38 | 212654556 | 99900002 | 50044556 | 0.000000 | 367053894 | 93912158 | 0.000000
09-04-2025 21:06:35000 | -8675518 | 86.7552 | 39323694 | 233936.73 | 214349091 | 99897430 | 50040546 | 0.000000 | 372473328 | 95113877 | 0.000000
09-04-2025 21:06:40000 | -8595805 | 85.9581 | 40514424 | 234023.77 | 212317841 | 99889107 | 50069862 | 0.000000 | 378185150 | 96312744 | 0.000000
09-04-2025 21:06:45000 | -8726238 | 87.2624 | 38323516 | 233853.80 | 215665054 | 99903702 | 50038960 | 0.000000 | 383531372 | 97512441 | 0.000000
09-04-2025 21:06:50000 | -8835914 | 88.3591 | 42004448 | 233919.61 | 218351563 | 99887199 | 50003155 | 0.000000 | 389147858 | 98734043 | 0.000000
09-04-2025 21:06:55000 | -8713848 | 87.1385 | 40055984 | 233967.78 | 215272736 | 99894516 | 50037292 | 0.000000 | 394817719 | 99952939 | 0.000000
09-04-2025 21:07:00000 | -8585533 | 85.8553 | 39369004 | 234057.16 | 212020935 | 99895035 | 50059895 | 0.000000 | 400141510 | 10115271 | 0.000000
09-04-2025 21:07:05000 | -8590449 | 85.9045 | 39456936 | 234030.09 | 212171890 | 99894684 | 50053951 | 0.000000 | 405460022 | 10234570 | 0.000000
09-04-2025 21:07:10000 | -8621997 | 86.22 | 39683767 | 233960.73 | 213011017 | 99894249 | 50048801 | 0.000000 | 410962280 | 10354195 | 0.000000
09-04-2025 21:07:15000 | -8603089 | 86.0309 | 37922158 | 233914.89 | 212566452 | 99902992 | 50051247 | 0.000000 | 416419617 | 10473754 | 0.000000
09-04-2025 21:07:20000 | -8642571 | 86.4257 | 37607024 | 233907.45 | 213543716 | 99905464 | 50041695 | 0.000000 | 421566406 | 10593303 | 0.000000
09-04-2025 21:07:25000 | -8672402 | 86.724 | 39395618 | 233958.80 | 214251968 | 99896980 | 50037968 | 0.000000 | 426857727 | 10713709 | 0.000000
09-04-2025 21:07:30000 | -8695882 | 86.9588 | 38283220 | 233897.09 | 214874664 | 99903236 | 50035233 | 0.000000 | 432300171 | 10834338 | 0.000000
09-04-2025 21:07:35000 | -8707221 | 87.0722 | 38961658 | 233928.03 | 215133636 | 99900040 | 50038891 | 0.000000 | 437698090 | 10955288 | 0.000000
09-04-2025 21:07:40000 | -8717901 | 87.179 | 37249771 | 233862.52 | 215439499 | 99908844 | 50023808 | 0.000000 | 442881409 | 11076215 | 0.000000
09-04-2025 21:07:45000 | -8746831 | 87.4683 | 39164968 | 233936.08 | 216106018 | 99899902 | 50027672 | 0.000000 | 448198669 | 11197523 | 0.000000
09-04-2025 21:07:50000 | -8687421 | 86.8742 | 39482493 | 233964.97 | 214618210 | 99896881 | 50041355 | 0.000000 | 453735046 | 11318514 | 0.000000
09-04-2025 21:07:55000 | -8692884 | 86.9288 | 39348459 | 233949.23 | 214765518 | 99897713 | 50035320 | 0.000000 | 459115662 | 11439272 | 0.000000
09-04-2025 21:08:00000 | -8770677 | 87.7068 | 38568228 | 233842.75 | 216776825 | 99903458 | 50026485 | 0.000000 | 464525604 | 11560437 | 0.000000
09-04-2025 21:08:05000 | -8848878 | 88.4888 | 39593701 | 233850.22 | 218706665 | 99900047 | 50006523 | 0.000000 | 469864441 | 11682784 | 0.000000
09-04-2025 21:08:10000 | -8734536 | 87.3454 | 36005581 | 233863.95 | 215835098 | 99915146 | 50017307 | 0.000000 | 475086395 | 11804959 | 0.000000
09-04-2025 21:08:15000 | -8518064 | 85.1806 | 33694714 | 233954.08 | 210390900 | 99921852 | 50067413 | 0.000000 | 479950867 | 11924395 | 0.000000
09-04-2025 21:08:20000 | -8442302 | 84.423 | 33645964 | 233946.16 | 208531311 | 99920677 | 50085110 | 0.000000 | 484622437 | 12041766 | 0.000000
09-04-2025 21:08:25000 | -8452131 | 84.5213 | 35827275 | 233936.36 | 208803177 | 99910278 | 50084862 | 0.000000 | 489526947 | 12158920 | 0.000000
09-04-2025 21:08:30000 | -8530905 | 85.309 | 37461235 | 233924.70 | 210772903 | 99903725 | 50081577 | 0.000000 | 494655151 | 12276779 | 0.000000
09-04-2025 21:08:35000 | -8766589 | 87.6659 | 41289580 | 233868.05 | 216679367 | 99889267 | 50035877 | 0.000000 | 500136505 | 12397241 | 0.000000
09-04-2025 21:08:40000 | -8905991 | 89.0599 | 43614668 | 233889.42 | 220124924 | 99880302 | 50009575 | 0.000000 | 506059845 | 12520536 | 0.000000
09-04-2025 21:08:45000 | -8796728 | 87.9673 | 40684048 | 233964.22 | 217325821 | 99893219 | 50031914 | 0.000000 | 511956116 | 12643561 | 0.000000
09-04-2025 21:08:50000 | -8752288 | 87.5229 | 35988123 | 233855.20 | 216282654 | 99915573 | 50027176 | 0.000000 | 517211548 | 12765035 | 0.000000
09-04-2025 21:08:55000 | -8728123 | 87.2812 | 39363643 | 234012.73 | 215575470 | 99898453 | 50029209 | 0.000000 | 522348694 | 12886344 | 0.000000
09-04-2025 21:09:00000 | -8690166 | 86.9017 | 40109377 | 233981.59 | 214677429 | 99893654 | 50042229 | 0.000000 | 527882751 | 13007376 | 0.000000
09-04-2025 21:09:05000 | -8723137 | 87.2314 | 38114187 | 233912.86 | 215530853 | 99904678 | 50029228 | 0.000000 | 533138550 | 13128197 | 0.000000
09-04-2025 21:09:10000 | -8768610 | 87.6861 | 38118899 | 233861.97 | 216700180 | 99905640 | 50027027 | 0.000000 | 538440918 | 13249853 | 0.000000
09-04-2025 21:09:15000 | -8671980 | 86.7198 | 35830903 | 233881.25 | 214274582 | 99914749 | 50050087 | 0.000000 | 543536743 | 13370820 | 0.000000
09-04-2025 21:09:20000 | -8578304 | 85.783 | 33824246 | 233884.95 | 211940582 | 99922356 | 50057980 | 0.000000 | 548261292 | 13490662 | 0.000000
09-04-2025 21:09:25000 | -8559796 | 85.598 | 33687314 | 233867.89 | 211498428 | 99922646 | 50066811 | 0.000000 | 553038025 | 13609523 | 0.000000
09-04-2025 21:09:30000 | -8638087 | 86.3809 | 36387859 | 233884.98 | 213442474 | 99911392 | 50042526 | 0.000000 | 557867981 | 13729259 | 0.000000
09-04-2025 21:09:35000 | -8585089 | 85.8509 | 35930164 | 233927.83 | 212092270 | 99912537 | 50057171 | 0.000000 | 562920776 | 13848933 | 0.000000
09-04-2025 21:09:40000 | -8535690 | 85.3569 | 33444934 | 233887.83 | 210884064 | 99923325 | 50077927 | 0.000000 | 567561523 | 13967474 | 0.000000
09-04-2025 21:09:45000 | -8632157 | 86.3216 | 35490781 | 233824.11 | 213343018 | 99915588 | 50066906 | 0.000000 | 572415222 | 14086596 | 0.000000
09-04-2025 21:09:50000 | -8705617 | 87.0562 | 39379233 | 233905.92 | 215120651 | 99897850 | 50045128 | 0.000000 | 577673157 | 14207236 | 0.000000
09-04-2025 21:09:55000 | -8721214 | 87.2121 | 39301182 | 233916.20 | 215493515 | 99898613 | 50057655 | 0.000000 | 583208191 | 14328236 | 0.000000
09-04-2025 21:10:00000 | -8767340 | 87.6734 | 37757576 | 233841.80 | 216683182 | 99907394 | 50039429 | 0.000000 | 588484985 | 14449691 | 0.000000
09-04-2025 21:10:05000 | -8853051 | 88.5305 | 39815964 | 233881.58 | 218781921 | 99899017 | 50031384 | 0.000000 | 593945923 | 14572357 | 0.000000
09-04-2025 21:10:10000 | -8805576 | 88.0558 | 37874492 | 233868.50 | 217603149 | 99907623 | 50035244 | 0.000000 | 599308716 | 14695051 | 0.000000
09-04-2025 21:10:15000 | -8698050 | 86.9805 | 34974507 | 233871.00 | 214917877 | 99919258 | 50049496 | 0.000000 | 604369873 | 14816325 | 0.000000
09-04-2025 21:10:20000 | -8655769 | 86.5577 | 33484382 | 233869.31 | 213862686 | 99925262 | 50059799 | 0.000000 | 609089111 | 14936666 | 0.000000
09-04-2025 21:10:25000 | -8673491 | 86.7349 | 34452161 | 233851.25 | 214325653 | 99921204 | 50049988 | 0.000000 | 613764404 | 15056882 | 0.000000
09-04-2025 21:10:30000 | -8702472 | 87.0247 | 36641445 | 233893.00 | 215025192 | 99911476 | 50036938 | 0.000000 | 618762085 | 15177883 | 0.000000
09-04-2025 21:10:35000 | -8650739 | 86.5074 | 34626365 | 233849.25 | 213767960 | 99919991 | 50055614 | 0.000000 | 623785034 | 15298264 | 0.000000
09-04-2025 21:10:40000 | -8620345 | 86.2035 | 34482329 | 233864.23 | 213003647 | 99920090 | 50058640 | 0.000000 | 628579895 | 15418208 | 0.000000
09-04-2025 21:10:45000 | -8580570 | 85.8057 | 35649334 | 233924.05 | 211979340 | 99913803 | 50067410 | 0.000000 | 633517395 | 15537603 | 0.000000
09-04-2025 21:10:50000 | -8575044 | 85.7504 | 32452388 | 233803.11 | 211922211 | 99928467 | 50057262 | 0.000000 | 638288940 | 15656760 | 0.000000
09-04-2025 21:10:55000 | -8607984 | 86.0798 | 37304043 | 233946.28 | 212653641 | 99906227 | 50055233 | 0.000000 | 643231995 | 15776257 | 0.000000
09-04-2025 21:11:00000 | -8628384 | 86.2838 | 35758059 | 233881.69 | 213200317 | 99914238 | 50066875 | 0.000000 | 648383179 | 15895958 | 0.000000
09-04-2025 21:11:05000 | -8578534 | 85.7853 | 35713069 | 233908.89 | 211943359 | 99913460 | 50065651 | 0.000000 | 653477844 | 16015259 | 0.000000
09-04-2025 21:11:10000 | -8565522 | 85.6552 | 35376746 | 233898.44 | 211628860 | 99914818 | 50064545 | 0.000000 | 658457520 | 16134290 | 0.000000
09-04-2025 21:11:15000 | -8642821 | 86.4282 | 36653337 | 233882.48 | 213564117 | 99910194 | 50048405 | 0.000000 | 663346985 | 16253897 | 0.000000
09-04-2025 21:11:20000 | -8723871 | 87.2387 | 37351479 | 233848.66 | 215604202 | 99908470 | 50030766 | 0.000000 | 668483521 | 16374985 | 0.000000
09-04-2025 21:11:25000 | -8713866 | 87.1387 | 35840359 | 233851.14 | 215335526 | 99915520 | 50035637 | 0.000000 | 673518677 | 16496316 | 0.000000
09-04-2025 21:11:30000 | -8723204 | 87.232 | 34177957 | 233796.16 | 215602768 | 99923332 | 50036636 | 0.000000 | 678420837 | 16617434 | 0.000000
09-04-2025 21:11:35000 | -8792233 | 87.9223 | 36421340 | 233826.48 | 217301178 | 99914314 | 50024132 | 0.000000 | 683254333 | 16739197 | 0.000000
09-04-2025 21:11:40000 | -8784923 | 87.8492 | 34528101 | 233806.33 | 217117538 | 99922852 | 50027733 | 0.000000 | 688137024 | 16861273 | 0.000000
09-04-2025 21:11:45000 | -8646569 | 86.4657 | 35098528 | 233926.27 | 213599655 | 99917717 | 50069855 | 0.000000 | 693041138 | 16982223 | 0.000000
09-04-2025 21:11:50000 | -8509980 | 85.0998 | 34919761 | 233981.52 | 210181000 | 99915916 | 50084995 | 0.000000 | 697838928 | 17100914 | 0.000000
09-04-2025 21:11:55000 | -8674571 | 86.7457 | 35394341 | 233799.16 | 214409805 | 99916862 | 50049316 | 0.000000 | 702693481 | 17220271 | 0.000000
09-04-2025 21:12:00000 | -8749889 | 87.4989 | 40578416 | 233903.14 | 216227295 | 99892639 | 50042885 | 0.000000 | 708093689 | 17341455 | 0.000000
09-04-2025 21:12:05000 | -8690883 | 86.9088 | 38572888 | 233919.53 | 214734528 | 99901649 | 50062492 | 0.000000 | 713670715 | 17462553 | 0.000000
09-04-2025 21:12:10000 | -8606687 | 86.0669 | 36819475 | 233966.80 | 212596207 | 99908615 | 50079559 | 0.000000 | 718773682 | 17582439 | 0.000000
09-04-2025 21:12:15000 | -8544990 | 85.4499 | 37274375 | 234006.27 | 211044754 | 99904991 | 50090145 | 0.000000 | 723902588 | 17701443 | 0.000000
09-04-2025 21:12:20000 | -8603877 | 86.0388 | 36559353 | 233875.64 | 212612488 | 99909843 | 50069881 | 0.000000 | 728973389 | 17820336 | 0.000000
09-04-2025 21:12:25000 | -8697013 | 86.9701 | 39422937 | 233914.84 | 214899979 | 99897423 | 50045341 | 0.000000 | 734204285 | 17940811 | 0.000000
09-04-2025 21:12:30000 | -8782458 | 87.8246 | 40673799 | 233911.33 | 217023865 | 99892929 | 50046314 | 0.000000 | 739814392 | 18062422 | 0.000000
09-04-2025 21:12:35000 | -8773932 | 87.7393 | 39550588 | 233897.23 | 216813828 | 99898560 | 50043892 | 0.000000 | 745424744 | 18184430 | 0.000000
09-04-2025 21:12:40000 | -8855317 | 88.5532 | 36717283 | 233776.73 | 218903625 | 99914146 | 50020142 | 0.000000 | 750577087 | 18306914 | 0.000000
09-04-2025 21:12:45000 | -8873527 | 88.7353 | 36782009 | 233799.89 | 219332306 | 99914200 | 50009689 | 0.000000 | 755699280 | 18430041 | 0.000000
09-04-2025 21:12:50000 | -8835633 | 88.3563 | 37440869 | 233888.41 | 218320251 | 99910339 | 50011456 | 0.000000 | 760883545 | 18553127 | 0.000000
09-04-2025 21:12:55000 | -8667707 | 86.6771 | 34601882 | 233936.08 | 214110641 | 99920410 | 50040714 | 0.000000 | 765805237 | 18674281 | 0.000000
09-04-2025 21:13:00000 | -8628595 | 86.2859 | 34467512 | 233881.19 | 213189835 | 99920311 | 50040508 | 0.000000 | 770586670 | 18794188 | 0.000000
09-04-2025 21:13:05000 | -8669880 | 86.6988 | 35282170 | 233841.41 | 214253052 | 99917297 | 50031193 | 0.000000 | 775442078 | 18914414 | 0.000000
09-04-2025 21:13:10000 | -8707702 | 87.077 | 34950811 | 233776.88 | 215242554 | 99919548 | 50011505 | 0.000000 | 780285278 | 19035146 | 0.000000
09-04-2025 21:13:15000 | -8686041 | 86.8604 | 37070083 | 233942.77 | 214578049 | 99909058 | 50023617 | 0.000000 | 785314331 | 19156104 | 0.000000
09-04-2025 21:13:20000 | -8519301 | 85.193 | 35192698 | 233965.27 | 210427475 | 99914787 | 50065945 | 0.000000 | 790307251 | 19275252 | 0.000000
09-04-2025 21:13:25000 | -8461030 | 84.6103 | 35943896 | 234011.47 | 208956329 | 99909889 | 50079788 | 0.000000 | 795158691 | 19393121 | 0.000000
09-04-2025 21:13:30000 | -8475018 | 84.7502 | 37677878 | 233983.84 | 209346497 | 99901321 | 50089111 | 0.000000 | 800350342 | 19510844 | 0.000000
09-04-2025 21:13:35000 | -8508505 | 85.085 | 40394951 | 233979.75 | 210207840 | 99887489 | 50094429 | 0.000000 | 805878540 | 19628723 | 0.000000
09-04-2025 21:13:40000 | -8535672 | 85.3567 | 41357896 | 234041.66 | 210829254 | 99882820 | 50100845 | 0.000000 | 811603882 | 19747285 | 0.000000
09-04-2025 21:13:45000 | -8580695 | 85.807 | 42122305 | 234030.67 | 211961349 | 99879730 | 50108131 | 0.000000 | 817400879 | 19866076 | 0.000000
09-04-2025 21:13:50000 | -8609723 | 86.0972 | 43903105 | 234067.92 | 212661636 | 99870239 | 50107780 | 0.000000 | 823440613 | 19985607 | 0.000000
09-04-2025 21:13:55000 | -8699772 | 86.9977 | 43690249 | 234013.08 | 214931686 | 99874138 | 50090794 | 0.000000 | 829465881 | 20105703 | 0.000000
09-04-2025 21:14:00000 | -8869591 | 88.6959 | 40846860 | 233791.81 | 219285767 | 99894127 | 50050068 | 0.000000 | 835329163 | 20227914 | 0.000000
09-04-2025 21:14:05000 | -8915803 | 89.158 | 41447598 | 233896.94 | 220343307 | 99892120 | 50035336 | 0.000000 | 841073425 | 20351527 | 0.000000
09-04-2025 21:14:10000 | -8829341 | 88.2934 | 41489717 | 233956.92 | 218147552 | 99889778 | 50048481 | 0.000000 | 846925049 | 20474738 | 0.000000
09-04-2025 21:14:15000 | -8765513 | 87.6551 | 40627341 | 234025.44 | 216499573 | 99892761 | 50044285 | 0.000000 | 852491333 | 20597113 | 0.000000
09-04-2025 21:14:20000 | -8557405 | 85.574 | 37515554 | 234025.73 | 211339813 | 99904045 | 50086777 | 0.000000 | 857984558 | 20717244 | 0.000000
09-04-2025 21:14:25000 | -8558468 | 85.5847 | 37745911 | 234004.88 | 211383194 | 99902885 | 50089058 | 0.000000 | 863076294 | 20835873 | 0.000000
09-04-2025 21:14:30000 | -8720796 | 87.208 | 41072280 | 233940.09 | 215481216 | 99889275 | 50060814 | 0.000000 | 868558594 | 20955961 | 0.000000
09-04-2025 21:14:35000 | -8877350 | 88.7735 | 43518848 | 233953.58 | 219356064 | 99880058 | 50015583 | 0.000000 | 874352356 | 21078395 | 0.000000
09-04-2025 21:14:40000 | -8885259 | 88.8526 | 43357227 | 233958.30 | 219546631 | 99881157 | 50015480 | 0.000000 | 880491394 | 21201855 | 0.000000
09-04-2025 21:14:45000 | -8732148 | 87.3215 | 39052542 | 233985.69 | 215697556 | 99900146 | 50042923 | 0.000000 | 886194397 | 21324148 | 0.000000
09-04-2025 21:14:50000 | -8716286 | 87.1629 | 37692173 | 233918.47 | 215351715 | 99906631 | 50046783 | 0.000000 | 891478394 | 21444955 | 0.000000
09-04-2025 21:14:55000 | -8743389 | 87.4339 | 39717168 | 233957.17 | 216006729 | 99896988 | 50030582 | 0.000000 | 896836182 | 21566021 | 0.000000
09-04-2025 21:15:00000 | -8732960 | 87.3296 | 42415186 | 234015.94 | 215726990 | 99882263 | 50037529 | 0.000000 | 902598572 | 21687496 | 0.000000
09-04-2025 21:15:05000 | -8659195 | 86.5919 | 39977542 | 234009.45 | 213887115 | 99893600 | 50049351 | 0.000000 | 5684767 | 120618416 | 0.000000
09-04-2025 21:15:10000 | -8598182 | 85.9818 | 38989124 | 234004.66 | 212382675 | 99897346 | 50068092 | 0.000000 | 11246108 | 239983582 | 0.000000
09-04-2025 21:15:15000 | -8659684 | 86.5968 | 40311140 | 233979.44 | 213930130 | 99891830 | 50045204 | 0.000000 | 16781116 | 359742645 | 0.000000
09-04-2025 21:15:20000 | -8785234 | 87.8523 | 40575869 | 233867.78 | 217130493 | 99893509 | 50016838 | 0.000000 | 22452803 | 481087952 | 0.000000
09-04-2025 21:15:25000 | -8799966 | 87.9997 | 43175923 | 233971.09 | 217428589 | 99879852 | 50020229 | 0.000000 | 28348307 | 603261780 | 0.000000
09-04-2025 21:15:30000 | -8643689 | 86.4369 | 39976653 | 234015.30 | 213498657 | 99893219 | 50057594 | 0.000000 | 34107914 | 724317383 | 0.000000
09-04-2025 21:15:35000 | -8523937 | 85.2394 | 41115005 | 234114.95 | 210470795 | 99883873 | 50081757 | 0.000000 | 39715115 | 843308228 | 0.000000
09-04-2025 21:15:40000 | -8537366 | 85.3737 | 40161489 | 234061.42 | 210841125 | 99889534 | 50084366 | 0.000000 | 45196667 | 961770325 | 0.000000
09-04-2025 21:15:45000 | -8537634 | 85.3763 | 38242627 | 233936.84 | 210936752 | 99899834 | 50089424 | 0.000000 | 50636478 | 10800194 | 0.000000
09-04-2025 21:15:50000 | -8778033 | 87.7803 | 39008569 | 233796.28 | 217002838 | 99901405 | 50048195 | 0.000000 | 55868706 | 12004039 | 0.000000
09-04-2025 21:15:55000 | -8846308 | 88.4631 | 41721035 | 233868.44 | 218649567 | 99888969 | 50038280 | 0.000000 | 61641640 | 13228959 | 0.000000
09-04-2025 21:16:00000 | -8978720 | 89.7872 | 38613521 | 233725.73 | 222016449 | 99907654 | 50000217 | 0.000000 | 67253029 | 14466534 | 0.000000
09-04-2025 21:16:05000 | -9142633 | 91.4263 | 38407937 | 233678.34 | 226104752 | 99911873 | 49950050 | 0.000000 | 72565933 | 15728707 | 0.000000
09-04-2025 21:16:10000 | -9018205 | 90.1821 | 38258606 | 233842.11 | 222874847 | 99910133 | 49992847 | 0.000000 | 78052208 | 16989331 | 0.000000
09-04-2025 21:16:15000 | -8726789 | 87.2679 | 34722019 | 233960.11 | 215543610 | 99920937 | 50037045 | 0.000000 | 83070999 | 18217393 | 0.000000
09-04-2025 21:16:20000 | -8587910 | 85.8791 | 33487847 | 233932.78 | 212132919 | 99924057 | 50045700 | 0.000000 | 87723236 | 19415173 | 0.000000
09-04-2025 21:16:25000 | -8592155 | 85.9215 | 33707668 | 233845.67 | 212316589 | 99923134 | 50034889 | 0.000000 | 92407036 | 20608779 | 0.000000
09-04-2025 21:16:30000 | -8605236 | 86.0524 | 35384517 | 233882.63 | 212624023 | 99915565 | 50039242 | 0.000000 | 97218086 | 21805154 | 0.000000
09-04-2025 21:16:35000 | -8591184 | 85.9118 | 35014888 | 233862.98 | 212293396 | 99917046 | 50039677 | 0.000000 | 102124603 | 22997991 | 0.000000
09-04-2025 21:16:40000 | -8644280 | 86.4428 | 35558323 | 233822.14 | 213642883 | 99915504 | 50022427 | 0.000000 | 107053871 | 24196948 | 0.000000
09-04-2025 21:16:45000 | -8600337 | 86.0034 | 36471580 | 233943.67 | 212457764 | 99910202 | 50038437 | 0.000000 | 112060318 | 25394624 | 0.000000
09-04-2025 21:16:50000 | -8534983 | 85.3498 | 36584639 | 233961.58 | 210831055 | 99908257 | 50065979 | 0.000000 | 117202934 | 26580657 | 0.000000
09-04-2025 21:16:55000 | -8581748 | 85.8175 | 38917915 | 233986.86 | 211987427 | 99897331 | 50059177 | 0.000000 | 122411713 | 27769307 | 0.000000
09-04-2025 21:17:00000 | -8631818 | 86.3182 | 39951924 | 233952.92 | 213267365 | 99893059 | 50051811 | 0.000000 | 127883614 | 28968774 | 0.000000
09-04-2025 21:17:05000 | -8587609 | 85.8761 | 37969429 | 233947.20 | 212156769 | 99902397 | 50068176 | 0.000000 | 133375626 | 30163574 | 0.000000
09-04-2025 21:17:10000 | -8608584 | 86.0858 | 37070376 | 233908.23 | 212699463 | 99907410 | 50061535 | 0.000000 | 138543259 | 31356863 | 0.000000
09-04-2025 21:17:15000 | -8552566 | 85.5257 | 39925022 | 234015.39 | 211252029 | 99891220 | 50077511 | 0.000000 | 143966522 | 32547668 | 0.000000
09-04-2025 21:17:20000 | -8615713 | 86.1571 | 37671360 | 233893.30 | 212894684 | 99904549 | 50046925 | 0.000000 | 149159180 | 33738623 | 0.000000
09-04-2025 21:17:25000 | -8687451 | 86.8745 | 39840427 | 233943.25 | 214643845 | 99895012 | 50036457 | 0.000000 | 154702942 | 34943579 | 0.000000
09-04-2025 21:17:30000 | -8720269 | 87.2027 | 39535793 | 233931.80 | 215459259 | 99897385 | 50041115 | 0.000000 | 160212173 | 36153501 | 0.000000
09-04-2025 21:17:35000 | -8657328 | 86.5733 | 40264055 | 233989.20 | 213863647 | 99892021 | 50059433 | 0.000000 | 165829544 | 37360012 | 0.000000
09-04-2025 21:17:40000 | -8609870 | 86.0987 | 38828447 | 234004.09 | 212663162 | 99898468 | 50057831 | 0.000000 | 171196426 | 38557693 | 0.000000
09-04-2025 21:17:45000 | -8545034 | 85.4503 | 39437136 | 234057.95 | 211025558 | 99893669 | 50078220 | 0.000000 | 176685959 | 39749497 | 0.000000
09-04-2025 21:17:50000 | -8501594 | 85.0159 | 39382397 | 234062.03 | 209950897 | 99892876 | 50096821 | 0.000000 | 182053268 | 40933450 | 0.000000
09-04-2025 21:17:55000 | -8547889 | 85.4789 | 38628286 | 233958.86 | 211182449 | 99898048 | 50089283 | 0.000000 | 187494247 | 42115537 | 0.000000
09-04-2025 21:18:00000 | -8621210 | 86.2121 | 42990557 | 234050.06 | 212949005 | 99875900 | 50082264 | 0.000000 | 193323090 | 43311177 | 0.000000
09-04-2025 21:18:05000 | -8568760 | 85.6876 | 41692910 | 234077.45 | 211617523 | 99881836 | 50092552 | 0.000000 | 199178589 | 44504834 | 0.000000
09-04-2025 21:18:10000 | -8558689 | 85.5869 | 39605557 | 234008.75 | 211407501 | 99893105 | 50097878 | 0.000000 | 204853394 | 45692871 | 0.000000
09-04-2025 21:18:15000 | -8623658 | 86.2366 | 39886858 | 233954.55 | 213059708 | 99893204 | 50078106 | 0.000000 | 210372559 | 46885703 | 0.000000
09-04-2025 21:18:20000 | -8708280 | 87.0828 | 43352964 | 234014.98 | 215132324 | 99876312 | 50064392 | 0.000000 | 216221878 | 48091177 | 0.000000
09-04-2025 21:18:25000 | -8722733 | 87.2273 | 44001748 | 234024.55 | 215487793 | 99873009 | 50065990 | 0.000000 | 222350708 | 49304292 | 0.000000
09-04-2025 21:18:30000 | -8751112 | 87.5111 | 42613833 | 233989.20 | 216201614 | 99881645 | 50056248 | 0.000000 | 228231750 | 50517275 | 0.000000
09-04-2025 21:18:35000 | -8812001 | 88.12 | 41103320 | 233900.25 | 217768265 | 99891388 | 50048069 | 0.000000 | 234049362 | 51737119 | 0.000000
09-04-2025 21:18:40000 | -8834134 | 88.3413 | 41791240 | 233934.75 | 218288269 | 99888290 | 50042934 | 0.000000 | 239838226 | 52964390 | 0.000000
09-04-2025 21:18:45000 | -8715978 | 87.1598 | 37327341 | 233924.16 | 215334854 | 99908424 | 50046299 | 0.000000 | 245271652 | 54182749 | 0.000000
09-04-2025 21:18:50000 | -8565382 | 85.6538 | 39133530 | 234099.38 | 211484467 | 99895790 | 50083115 | 0.000000 | 250637344 | 55380439 | 0.000000
09-04-2025 21:18:55000 | -8527111 | 85.2711 | 37540173 | 234015.52 | 210599457 | 99903236 | 50088009 | 0.000000 | 255904816 | 56564917 | 0.000000
09-04-2025 21:19:00000 | -8576227 | 85.7623 | 42579170 | 234057.16 | 211832642 | 99876984 | 50067215 | 0.000000 | 261496582 | 57754355 | 0.000000
09-04-2025 21:19:05000 | -8541773 | 85.4177 | 44211636 | 234106.17 | 210957718 | 99866318 | 50101456 | 0.000000 | 267682739 | 58944390 | 0.000000
09-04-2025 21:19:10000 | -8607638 | 86.0764 | 42770747 | 234041.80 | 212621277 | 99876778 | 50088123 | 0.000000 | 273769318 | 60136445 | 0.000000
09-04-2025 21:19:15000 | -8678837 | 86.7884 | 44916714 | 234067.05 | 214377655 | 99866341 | 50080082 | 0.000000 | 279986420 | 61339526 | 0.000000
09-04-2025 21:19:20000 | -8690027 | 86.9003 | 46415186 | 234105.33 | 214636795 | 99857666 | 50088215 | 0.000000 | 286381653 | 62546831 | 0.000000
09-04-2025 21:19:25000 | -8711273 | 87.1127 | 43939336 | 234026.77 | 215205093 | 99873032 | 50074238 | 0.000000 | 292570679 | 63754395 | 0.000000
09-04-2025 21:19:30000 | -8770277 | 87.7028 | 46277974 | 234097.94 | 216620682 | 99861076 | 50069633 | 0.000000 | 298811523 | 64970571 | 0.000000
09-04-2025 21:19:35000 | -8734179 | 87.3418 | 44277998 | 234058.77 | 215739578 | 99871750 | 50077450 | 0.000000 | 305139709 | 66185645 | 0.000000
09-04-2025 21:19:40000 | -8706170 | 87.0617 | 44299712 | 234110.19 | 215003494 | 99870796 | 50087524 | 0.000000 | 311316650 | 67395215 | 0.000000
09-04-2025 21:19:45000 | -8713988 | 87.1399 | 42873457 | 234031.20 | 215253891 | 99879181 | 50074883 | 0.000000 | 317343567 | 68605200 | 0.000000
09-04-2025 21:19:50000 | -8844028 | 88.4403 | 45731704 | 234002.16 | 218517502 | 99866577 | 50049175 | 0.000000 | 323584137 | 69824800 | 0.000000
09-04-2025 21:19:55000 | -8910558 | 89.1056 | 44920732 | 233957.05 | 220189072 | 99873169 | 50022560 | 0.000000 | 329917786 | 71059795 | 0.000000
09-04-2025 21:20:00000 | -8865784 | 88.6578 | 42930278 | 233978.80 | 219040771 | 99882973 | 50031647 | 0.000000 | 336069763 | 72295854 | 0.000000
09-04-2025 21:20:05000 | -8731109 | 87.3111 | 38281201 | 233969.28 | 215679703 | 99904022 | 50056141 | 0.000000 | 341598267 | 73514814 | 0.000000
09-04-2025 21:20:10000 | -8636175 | 86.3618 | 36616465 | 233983.86 | 213306503 | 99910240 | 50057709 | 0.000000 | 346788025 | 74719590 | 0.000000
09-04-2025 21:20:15000 | -8636086 | 86.3609 | 37478069 | 233960.75 | 213334488 | 99905968 | 50060593 | 0.000000 | 352048889 | 75919053 | 0.000000
09-04-2025 21:20:20000 | -8635618 | 86.3562 | 39246108 | 233979.98 | 213325089 | 99896889 | 50062309 | 0.000000 | 357442657 | 77116851 | 0.000000
09-04-2025 21:20:25000 | -8514935 | 85.1493 | 39903730 | 234101.28 | 210247818 | 99890373 | 50082081 | 0.000000 | 363001312 | 78308584 | 0.000000
09-04-2025 21:20:30000 | -8500756 | 85.0076 | 40254346 | 234074.59 | 209926636 | 99888069 | 50106014 | 0.000000 | 368539795 | 79486963 | 0.000000
09-04-2025 21:20:35000 | -8552234 | 85.5223 | 42896948 | 234074.86 | 211226868 | 99874443 | 50090031 | 0.000000 | 374366028 | 80671318 | 0.000000
09-04-2025 21:20:40000 | -8743455 | 87.4346 | 45758857 | 234016.75 | 216026001 | 99863335 | 50061714 | 0.000000 | 380535004 | 81874883 | 0.000000
09-04-2025 21:20:45000 | -8803973 | 88.0397 | 47121543 | 234049.69 | 217504913 | 99857071 | 50061478 | 0.000000 | 387020050 | 83093135 | 0.000000
09-04-2025 21:20:50000 | -8778298 | 87.783 | 44760884 | 234048.88 | 216842880 | 99870255 | 50059631 | 0.000000 | 393424133 | 84314619 | 0.000000
09-04-2025 21:20:55000 | -8747199 | 87.472 | 43798550 | 234060.39 | 216053223 | 99874878 | 50077782 | 0.000000 | 399545380 | 85532363 | 0.000000
09-04-2025 21:21:00000 | -8667109 | 86.6711 | 43075317 | 234112.31 | 214025620 | 99876724 | 50093849 | 0.000000 | 405432495 | 86743398 | 0.000000
09-04-2025 21:21:05000 | -8565123 | 85.6512 | 42058252 | 234127.42 | 211485855 | 99879654 | 50111656 | 0.000000 | 411339233 | 87937910 | 0.000000
09-04-2025 21:21:10000 | -8513575 | 85.1358 | 42570532 | 234110.84 | 210237717 | 99875221 | 50127277 | 0.000000 | 417316681 | 89120254 | 0.000000
09-04-2025 21:21:15000 | -8629730 | 86.2973 | 45985396 | 234123.86 | 213131088 | 99858322 | 50100307 | 0.000000 | 423388245 | 90311631 | 0.000000
09-04-2025 21:21:20000 | -8764498 | 87.645 | 47306699 | 234033.53 | 216551880 | 99854652 | 50072769 | 0.000000 | 430018921 | 91523652 | 0.000000
09-04-2025 21:21:25000 | -8859985 | 88.5999 | 46043350 | 234013.44 | 218903778 | 99865242 | 50061985 | 0.000000 | 436485626 | 92750664 | 0.000000
09-04-2025 21:21:30000 | -8846143 | 88.4614 | 44625469 | 233999.66 | 218558411 | 99873001 | 50062717 | 0.000000 | 442800873 | 93980566 | 0.000000
09-04-2025 21:21:35000 | -8749364 | 87.4936 | 42470977 | 234030.59 | 216118256 | 99882393 | 50069744 | 0.000000 | 448846436 | 95200596 | 0.000000
09-04-2025 21:21:40000 | -8746985 | 87.4698 | 40992114 | 234004.56 | 216071808 | 99890366 | 50069458 | 0.000000 | 454593933 | 96412920 | 0.000000
09-04-2025 21:21:45000 | -8706248 | 87.0625 | 43777798 | 234089.80 | 215020309 | 99873817 | 50080299 | 0.000000 | 460566711 | 97622412 | 0.000000
09-04-2025 21:21:50000 | -8696034 | 86.9603 | 42178267 | 234032.30 | 214801468 | 99882584 | 50064114 | 0.000000 | 466503296 | 98830078 | 0.000000
09-04-2025 21:21:55000 | -8716805 | 87.168 | 44474751 | 234078.53 | 215296661 | 99870094 | 50067963 | 0.000000 | 472635590 | 10004123 | 0.000000
09-04-2025 21:22:00000 | -8588007 | 85.8801 | 43151553 | 234116.95 | 212079147 | 99874001 | 50101738 | 0.000000 | 478801849 | 10124473 | 0.000000
09-04-2025 21:22:05000 | -8466957 | 84.6696 | 43365020 | 234194.39 | 209024353 | 99869102 | 50134766 | 0.000000 | 484843140 | 10242651 | 0.000000
09-04-2025 21:22:10000 | -8476241 | 84.7624 | 44772407 | 234145.38 | 209314682 | 99860786 | 50127773 | 0.000000 | 490986877 | 10360362 | 0.000000
09-04-2025 21:22:15000 | -8636814 | 86.3681 | 48843921 | 234187.88 | 213284332 | 99840469 | 50110325 | 0.000000 | 497512207 | 10479581 | 0.000000
09-04-2025 21:22:20000 | -8637580 | 86.3758 | 47250693 | 234138.83 | 213328278 | 99850708 | 50109131 | 0.000000 | 504273468 | 10599658 | 0.000000
09-04-2025 21:22:25000 | -8607245 | 86.0725 | 47262993 | 234167.59 | 212553558 | 99849579 | 50129395 | 0.000000 | 510961426 | 10719552 | 0.000000
09-04-2025 21:22:30000 | -8635601 | 86.356 | 44703589 | 234100.36 | 213279251 | 99866280 | 50115654 | 0.000000 | 517223145 | 10839126 | 0.000000
09-04-2025 21:22:35000 | -8626259 | 86.2626 | 47869761 | 234179.56 | 213019516 | 99846382 | 50119293 | 0.000000 | 523827759 | 10959283 | 0.000000
09-04-2025 21:22:40000 | -8601340 | 86.0134 | 46493877 | 234163.73 | 212401688 | 99854225 | 50129036 | 0.000000 | 530276978 | 11078815 | 0.000000
09-04-2025 21:22:45000 | -8632327 | 86.3233 | 45337856 | 234108.38 | 213201263 | 99862358 | 50117851 | 0.000000 | 536585815 | 11198242 | 0.000000
09-04-2025 21:22:50000 | -8767633 | 87.6763 | 48409458 | 234117.83 | 216583252 | 99847916 | 50086479 | 0.000000 | 543138855 | 11319574 | 0.000000
09-04-2025 21:22:55000 | -8844236 | 88.4424 | 48653643 | 234081.61 | 218488937 | 99849030 | 50069771 | 0.000000 | 549861084 | 11441998 | 0.000000
09-04-2025 21:23:00000 | -8758239 | 87.5824 | 46203960 | 234112.89 | 216307404 | 99861137 | 50089703 | 0.000000 | 556432434 | 11564154 | 0.000000
09-04-2025 21:23:05000 | -8635184 | 86.3518 | 42638003 | 234082.64 | 213259613 | 99878319 | 50105717 | 0.000000 | 562606445 | 11684532 | 0.000000
09-04-2025 21:23:10000 | -8683838 | 86.8384 | 42990737 | 234046.28 | 214499405 | 99877678 | 50088352 | 0.000000 | 568440430 | 11804856 | 0.000000
09-04-2025 21:23:15000 | -8734463 | 87.3446 | 44862607 | 234042.95 | 215768860 | 99868355 | 50070271 | 0.000000 | 574495178 | 11926072 | 0.000000
09-04-2025 21:23:20000 | -8813045 | 88.1304 | 43283301 | 233936.69 | 217788452 | 99879616 | 50065594 | 0.000000 | 580598206 | 12047910 | 0.000000
09-04-2025 21:23:25000 | -8816832 | 88.1683 | 44024438 | 234035.08 | 217796432 | 99875572 | 50058064 | 0.000000 | 586711853 | 12170325 | 0.000000
09-04-2025 21:23:30000 | -8646716 | 86.4672 | 41914272 | 234094.27 | 213523727 | 99882721 | 50082600 | 0.000000 | 592618469 | 12291207 | 0.000000
09-04-2025 21:23:35000 | -8529655 | 85.2965 | 41007183 | 234113.61 | 210612778 | 99884636 | 50105888 | 0.000000 | 598383484 | 12410377 | 0.000000
09-04-2025 21:23:40000 | -8410722 | 84.1072 | 41216221 | 234150.02 | 207652496 | 99880142 | 50135994 | 0.000000 | 604108521 | 12527708 | 0.000000
09-04-2025 21:23:45000 | -8485010 | 84.8501 | 42981553 | 234100.45 | 209549622 | 99871948 | 50132130 | 0.000000 | 609931763 | 12644862 | 0.000000
09-04-2025 21:23:50000 | -8653184 | 86.5318 | 46040356 | 234044.50 | 213780396 | 99858757 | 50096287 | 0.000000 | 616077820 | 12763794 | 0.000000
09-04-2025 21:23:55000 | -8702577 | 87.0258 | 47393994 | 234108.31 | 214959534 | 99852036 | 50093864 | 0.000000 | 622593750 | 12884646 | 0.000000
09-04-2025 21:24:00000 | -8570373 | 85.7037 | 46658691 | 234205.66 | 211603027 | 99852135 | 50133602 | 0.000000 | 629149841 | 13004545 | 0.000000
09-04-2025 21:24:05000 | -8451846 | 84.5185 | 45911772 | 234266.28 | 208621384 | 99852783 | 50161114 | 0.000000 | 635459961 | 13122620 | 0.000000
09-04-2025 21:24:10000 | -8509845 | 85.0984 | 46221367 | 234183.45 | 210127396 | 99852821 | 50147991 | 0.000000 | 641692139 | 13240739 | 0.000000
09-04-2025 21:24:15000 | -8553996 | 85.54 | 47894072 | 234198.25 | 211229706 | 99843620 | 50160938 | 0.000000 | 648260132 | 13359427 | 0.000000
09-04-2025 21:24:20000 | -8629106 | 86.2911 | 49456997 | 234174.05 | 213116074 | 99836159 | 50157578 | 0.000000 | 655026978 | 13478785 | 0.000000
09-04-2025 21:24:25000 | -8748525 | 87.4852 | 51462271 | 234196.36 | 216063461 | 99827438 | 50131500 | 0.000000 | 662047729 | 13599762 | 0.000000
09-04-2025 21:24:30000 | -8699014 | 86.9901 | 52692637 | 234301.81 | 214773712 | 99817047 | 50153404 | 0.000000 | 669369751 | 13721000 | 0.000000
09-04-2025 21:24:35000 | -8571543 | 85.7154 | 50185186 | 234336.61 | 211562103 | 99829041 | 50186874 | 0.000000 | 676415833 | 13840703 | 0.000000
09-04-2025 21:24:40000 | -8586888 | 85.8689 | 49983389 | 234280.86 | 211986954 | 99831017 | 50170963 | 0.000000 | 683210205 | 13959686 | 0.000000
09-04-2025 21:24:45000 | -8660479 | 86.6048 | 55623008 | 234358.17 | 213810867 | 99794388 | 50148758 | 0.000000 | 690674255 | 14079591 | 0.000000
09-04-2025 21:24:50000 | -8768575 | 87.6857 | 56057529 | 234281.59 | 216546600 | 99796272 | 50130428 | 0.000000 | 698477051 | 14200644 | 0.000000
09-04-2025 21:24:55000 | -8819080 | 88.1908 | 56326226 | 234279.50 | 217794708 | 99796661 | 50124760 | 0.000000 | 706308716 | 14322820 | 0.000000
09-04-2025 21:25:00000 | -8823040 | 88.2304 | 54463564 | 234252.34 | 217889175 | 99810020 | 50123856 | 0.000000 | 714015259 | 14445248 | 0.000000
09-04-2025 21:25:05000 | -8750607 | 87.5061 | 52396587 | 234256.05 | 216074875 | 99821213 | 50134243 | 0.000000 | 721538452 | 14567420 | 0.000000
09-04-2025 21:25:10000 | -8775023 | 87.7502 | 52961250 | 234290.95 | 216649475 | 99818359 | 50133057 | 0.000000 | 728752625 | 14689043 | 0.000000
09-04-2025 21:25:15000 | -8741692 | 87.4169 | 53448242 | 234296.14 | 215831451 | 99813606 | 50136135 | 0.000000 | 736088684 | 14810390 | 0.000000
09-04-2025 21:25:20000 | -8655392 | 86.5539 | 53766465 | 234371.30 | 213645508 | 99807617 | 50149384 | 0.000000 | 743496704 | 14931262 | 0.000000
09-04-2025 21:25:25000 | -8611692 | 86.1169 | 51526035 | 234282.66 | 212620392 | 99821480 | 50155453 | 0.000000 | 750790344 | 15051139 | 0.000000
09-04-2025 21:25:30000 | -8587504 | 85.875 | 52154731 | 234330.41 | 211989120 | 99816086 | 50164307 | 0.000000 | 758019287 | 15170577 | 0.000000
09-04-2025 21:25:35000 | -8646189 | 86.4619 | 52688140 | 234280.86 | 213486374 | 99814842 | 50140400 | 0.000000 | 765219910 | 15290368 | 0.000000
09-04-2025 21:25:40000 | -8732562 | 87.3256 | 53335508 | 234238.59 | 215659103 | 99814003 | 50124538 | 0.000000 | 772596863 | 15411408 | 0.000000
09-04-2025 21:25:45000 | -8796883 | 87.9688 | 54267520 | 234257.19 | 217241440 | 99810265 | 50117989 | 0.000000 | 780076660 | 15533283 | 0.000000
09-04-2025 21:25:50000 | -8771432 | 87.7143 | 51884302 | 234226.80 | 216606552 | 99825516 | 50129715 | 0.000000 | 787432190 | 15655180 | 0.000000
09-04-2025 21:25:55000 | -8768726 | 87.6873 | 51073999 | 234199.50 | 216552917 | 99830803 | 50121445 | 0.000000 | 794556641 | 15777035 | 0.000000
09-04-2025 21:26:00000 | -8813234 | 88.1323 | 56138022 | 234352.58 | 217579666 | 99797745 | 50123997 | 0.000000 | 801863037 | 15899342 | 0.000000
09-04-2025 21:26:05000 | -8754865 | 87.5486 | 52144736 | 234246.84 | 216182571 | 99823097 | 50133118 | 0.000000 | 809388611 | 16021101 | 0.000000
09-04-2025 21:26:10000 | -8674216 | 86.7422 | 52210610 | 234319.06 | 214132309 | 99819344 | 50146049 | 0.000000 | 816697998 | 16142315 | 0.000000
09-04-2025 21:26:15000 | -8598341 | 85.9834 | 51459258 | 234314.48 | 212262344 | 99821388 | 50165646 | 0.000000 | 823890930 | 16262154 | 0.000000
09-04-2025 21:26:20000 | -8534058 | 85.3406 | 53025459 | 234380.58 | 210644760 | 99807526 | 50176292 | 0.000000 | 831119446 | 16380802 | 0.000000
09-04-2025 21:26:25000 | -8654198 | 86.542 | 54109194 | 234292.06 | 213695831 | 99805115 | 50155712 | 0.000000 | 838494446 | 16500133 | 0.000000
09-04-2025 21:26:30000 | -8699401 | 86.994 | 54272485 | 234301.66 | 214802017 | 99805962 | 50143879 | 0.000000 | 845966248 | 16620561 | 0.000000
09-04-2025 21:26:35000 | -8692006 | 86.9201 | 54038076 | 234293.13 | 214621857 | 99807304 | 50152325 | 0.000000 | 853525146 | 16741516 | 0.000000
09-04-2025 21:26:40000 | -8598316 | 85.9832 | 52310908 | 234330.20 | 212258942 | 99815445 | 50174744 | 0.000000 | 860909790 | 16861570 | 0.000000
09-04-2025 21:26:45000 | -8618848 | 86.1885 | 53320649 | 234341.56 | 212767899 | 99809181 | 50166874 | 0.000000 | 868205994 | 16981168 | 0.000000
09-04-2025 21:26:50000 | -8598147 | 85.9815 | 53668379 | 234318.69 | 212289749 | 99805763 | 50169170 | 0.000000 | 875632874 | 17100625 | 0.000000
09-04-2025 21:26:55000 | -8651744 | 86.5174 | 54778179 | 234355.84 | 213585281 | 99800163 | 50153072 | 0.000000 | 883189209 | 17220639 | 0.000000
09-04-2025 21:27:00000 | -8680991 | 86.8099 | 53925063 | 234262.17 | 214377029 | 99807617 | 50147724 | 0.000000 | 890769409 | 17341141 | 0.000000
09-04-2025 21:27:05000 | -8673857 | 86.7386 | 53902363 | 234295.00 | 214171814 | 99807465 | 50159916 | 0.000000 | 898279175 | 17461861 | 0.000000
09-04-2025 21:27:10000 | -8772271 | 87.7227 | 52588853 | 234214.72 | 216648849 | 99820786 | 50134575 | 0.000000 | 905430237 | 17582932 | 0.000000
09-04-2025 21:27:15000 | -8763567 | 87.6357 | 53784531 | 234316.00 | 216356628 | 99812202 | 50140144 | 0.000000 | 912817505 | 17704611 | 0.000000
09-04-2025 21:27:20000 | -8644720 | 86.4472 | 51861982 | 234307.03 | 213416489 | 99820526 | 50168228 | 0.000000 | 920239258 | 17825260 | 0.000000
09-04-2025 21:27:25000 | -8663963 | 86.6396 | 51551348 | 234246.67 | 213939957 | 99823448 | 50154640 | 0.000000 | 927485291 | 17945555 | 0.000000
09-04-2025 21:27:30000 | -8717476 | 87.1748 | 54825630 | 234320.11 | 215236282 | 99802818 | 50146988 | 0.000000 | 934924133 | 18066291 | 0.000000
09-04-2025 21:27:35000 | -8718017 | 87.1802 | 53445112 | 234291.78 | 215254333 | 99812614 | 50145847 | 0.000000 | 942394775 | 18187354 | 0.000000
09-04-2025 21:27:40000 | -8706733 | 87.0673 | 52639424 | 234275.52 | 214978745 | 99817741 | 50150494 | 0.000000 | 949874939 | 18308377 | 0.000000
09-04-2025 21:27:45000 | -8683852 | 86.8385 | 53022334 | 234273.19 | 214423431 | 99814110 | 50154034 | 0.000000 | 957287170 | 18429227 | 0.000000
09-04-2025 21:27:50000 | -8632718 | 86.3272 | 52525361 | 234313.27 | 213122299 | 99815407 | 50172874 | 0.000000 | 964602966 | 18549479 | 0.000000
09-04-2025 21:27:55000 | -8648536 | 86.4854 | 51993823 | 234287.05 | 213526779 | 99819778 | 50162426 | 0.000000 | 971805725 | 18669295 | 0.000000
09-04-2025 21:28:00000 | -8649477 | 86.4948 | 55976367 | 234408.28 | 213503693 | 99791245 | 50162041 | 0.000000 | 979346436 | 18789332 | 0.000000
09-04-2025 21:28:05000 | -8527488 | 85.2749 | 55106196 | 234455.03 | 210447418 | 99791855 | 50193806 | 0.000000 | 987116333 | 18908297 | 0.000000
09-04-2025 21:28:10000 | -8522430 | 85.2243 | 55172495 | 234407.13 | 210369080 | 99791107 | 50199894 | 0.000000 | 994794922 | 19026508 | 0.000000
09-04-2025 21:28:15000 | -8602483 | 86.0248 | 57025918 | 234368.56 | 212398773 | 99781006 | 50188084 | 0.000000 | 10026142 | 19145479 | 0.000000
09-04-2025 21:28:20000 | -8739721 | 87.3972 | 59407075 | 234396.63 | 215784897 | 99769775 | 50161633 | 0.000000 | 10107034 | 19266461 | 0.000000
09-04-2025 21:28:25000 | -8802279 | 88.0228 | 58389536 | 234311.73 | 217385452 | 99780708 | 50158176 | 0.000000 | 10189415 | 19388480 | 0.000000
09-04-2025 21:28:30000 | -8842753 | 88.4275 | 56536851 | 234308.78 | 218352921 | 99796234 | 50148800 | 0.000000 | 10268256 | 19511250 | 0.000000
09-04-2025 21:28:35000 | -8750355 | 87.5036 | 56342988 | 234384.36 | 216011551 | 99793343 | 50163509 | 0.000000 | 10346710 | 19633162 | 0.000000
09-04-2025 21:28:40000 | -8619784 | 86.1978 | 54867998 | 234435.53 | 212731735 | 99798027 | 50186626 | 0.000000 | 10424336 | 19753408 | 0.000000
09-04-2025 21:28:45000 | -8651387 | 86.5139 | 55415654 | 234365.00 | 213578720 | 99795486 | 50164997 | 0.000000 | 10500626 | 19873344 | 0.000000
09-04-2025 21:28:50000 | -8667684 | 86.6768 | 57016807 | 234399.30 | 213972961 | 99784340 | 50164055 | 0.000000 | 10579886 | 19993969 | 0.000000
09-04-2025 21:28:55000 | -8687028 | 86.8703 | 60271602 | 234477.23 | 214431885 | 99760178 | 50164677 | 0.000000 | 10661013 | 20114594 | 0.000000
09-04-2025 21:29:00000 | -8750334 | 87.5033 | 61887808 | 234482.05 | 216009491 | 99750824 | 50151226 | 0.000000 | 10745017 | 20235783 | 0.000000
09-04-2025 21:29:05000 | -8803559 | 88.0356 | 63827334 | 234508.45 | 217326050 | 99738205 | 50141747 | 0.000000 | 10831945 | 20357652 | 0.000000
09-04-2025 21:29:10000 | -8814101 | 88.141 | 62647744 | 234458.08 | 217612869 | 99748360 | 50134708 | 0.000000 | 10919790 | 20480135 | 0.000000
09-04-2025 21:29:15000 | -8758517 | 87.5852 | 61243677 | 234453.11 | 216226669 | 99756416 | 50133636 | 0.000000 | 11006687 | 20602201 | 0.000000
09-04-2025 21:29:20000 | -8816475 | 88.1647 | 61574375 | 234427.70 | 217678650 | 99757004 | 50112545 | 0.000000 | 11092244 | 20723998 | 0.000000
09-04-2025 21:29:25000 | -8786555 | 87.8655 | 63216899 | 234540.53 | 216867538 | 99742180 | 50109119 | 0.000000 | 11179980 | 20846527 | 0.000000
09-04-2025 21:29:30000 | -8660065 | 86.6007 | 60492637 | 234529.94 | 213724213 | 99756920 | 50139214 | 0.000000 | 11266614 | 20967477 | 0.000000
09-04-2025 21:29:35000 | -8507563 | 85.0756 | 58767144 | 234572.41 | 209911758 | 99762276 | 50166153 | 0.000000 | 11348104 | 21086299 | 0.000000
09-04-2025 21:29:40000 | -8546712 | 85.4671 | 60549189 | 234525.81 | 210945419 | 99749992 | 50157730 | 0.000000 | 11432002 | 21204471 | 0.000000
09-04-2025 21:29:45000 | -8634222 | 86.3422 | 64972266 | 234556.02 | 213146332 | 99718071 | 50136929 | 0.000000 | 11520189 | 21324113 | 0.000000
09-04-2025 21:29:50000 | -8696442 | 86.9644 | 66211558 | 234580.41 | 214675674 | 99711418 | 50140324 | 0.000000 | 11611295 | 21444656 | 0.000000
09-04-2025 21:29:55000 | -8675849 | 86.7585 | 62219863 | 234509.11 | 214165527 | 99743828 | 50137012 | 0.000000 | 11699912 | 21565279 | 0.000000
09-04-2025 21:30:00000 | -8669748 | 86.6975 | 62045220 | 234556.91 | 213965515 | 99744904 | 50146736 | 0.000000 | 11786770 | 21685973 | 0.000000
09-04-2025 21:30:05000 | -8565580 | 85.6558 | 61666748 | 234588.08 | 211373413 | 99741852 | 50167854 | 0.000000 | 8601927 | 119813965 | 0.000000
09-04-2025 21:30:10000 | -8535728 | 85.3573 | 59262417 | 234500.95 | 210675735 | 99759850 | 50174488 | 0.000000 | 16915394 | 238581497 | 0.000000
09-04-2025 21:30:15000 | -8581006 | 85.8101 | 59429219 | 234454.86 | 211832306 | 99761032 | 50164665 | 0.000000 | 25145792 | 357148865 | 0.000000
09-04-2025 21:30:20000 | -8591814 | 85.9181 | 64138589 | 234615.56 | 212036926 | 99722519 | 50171368 | 0.000000 | 33841087 | 476518890 | 0.000000
09-04-2025 21:30:25000 | -8586569 | 85.8657 | 64392007 | 234592.27 | 211933258 | 99719994 | 50174133 | 0.000000 | 42865746 | 595840820 | 0.000000
09-04-2025 21:30:30000 | -8725588 | 87.2559 | 68139072 | 234615.56 | 215392258 | 99696480 | 50141457 | 0.000000 | 52062782 | 716329041 | 0.000000
09-04-2025 21:30:35000 | -8767619 | 87.6762 | 69740879 | 234617.34 | 216453400 | 99685135 | 50137394 | 0.000000 | 61732723 | 838027466 | 0.000000
09-04-2025 21:30:40000 | -8737532 | 87.3753 | 69133091 | 234673.97 | 215651505 | 99688446 | 50156956 | 0.000000 | 71406326 | 959556030 | 0.000000
09-04-2025 21:30:45000 | -8734931 | 87.3493 | 66961626 | 234637.64 | 215579010 | 99707451 | 50147976 | 0.000000 | 80822884 | 10807030 | 0.000000
09-04-2025 21:30:50000 | -8746588 | 87.4659 | 68086772 | 234638.45 | 215885635 | 99698387 | 50154465 | 0.000000 | 90319077 | 12020918 | 0.000000
09-04-2025 21:30:55000 | -8778007 | 87.7801 | 67734429 | 234620.08 | 216666580 | 99703613 | 50133465 | 0.000000 | 99721733 | 13238340 | 0.000000
09-04-2025 21:31:00000 | -8853394 | 88.5339 | 68709448 | 234595.39 | 218557251 | 99700203 | 50127071 | 0.000000 | 109263489 | 14464697 | 0.000000
09-04-2025 21:31:05000 | -8756656 | 87.5666 | 66824238 | 234625.77 | 216120575 | 99710083 | 50134075 | 0.000000 | 118680168 | 15686289 | 0.000000
09-04-2025 21:31:10000 | -8680026 | 86.8003 | 64680508 | 234607.88 | 214217484 | 99723518 | 50138634 | 0.000000 | 127783241 | 16895894 | 0.000000
09-04-2025 21:31:15000 | -8617951 | 86.1795 | 64864053 | 234638.02 | 212670761 | 99717949 | 50154991 | 0.000000 | 136837372 | 18095544 | 0.000000
09-04-2025 21:31:20000 | -8538621 | 85.3862 | 64437808 | 234685.45 | 210672623 | 99716454 | 50166985 | 0.000000 | 145793243 | 19283939 | 0.000000
09-04-2025 21:31:25000 | -8550504 | 85.505 | 62763628 | 234546.34 | 211059052 | 99731682 | 50160580 | 0.000000 | 154601044 | 20467452 | 0.000000
09-04-2025 21:31:30000 | -8577820 | 85.7782 | 66398921 | 234643.25 | 211711182 | 99701744 | 50162434 | 0.000000 | 163741882 | 21660977 | 0.000000
09-04-2025 21:31:35000 | -8558369 | 85.5837 | 66278740 | 234647.69 | 211226791 | 99701469 | 50169178 | 0.000000 | 172922836 | 22851902 | 0.000000
09-04-2025 21:31:40000 | -8582995 | 85.8299 | 65750718 | 234641.80 | 211826355 | 99707863 | 50168098 | 0.000000 | 182063782 | 24042451 | 0.000000
09-04-2025 21:31:45000 | -8579318 | 85.7932 | 66252959 | 234673.11 | 211716827 | 99703148 | 50166794 | 0.000000 | 191219620 | 25233423 | 0.000000
09-04-2025 21:31:50000 | -8545541 | 85.4554 | 66529414 | 234669.61 | 210899689 | 99698318 | 50180744 | 0.000000 | 200479004 | 26419167 | 0.000000
09-04-2025 21:31:55000 | -8560770 | 85.6077 | 68420811 | 234732.64 | 211249405 | 99682129 | 50174084 | 0.000000 | 209799942 | 27610020 | 0.000000
09-04-2025 21:32:00000 | -8539305 | 85.3931 | 66872090 | 234680.78 | 210739746 | 99694771 | 50184654 | 0.000000 | 219200531 | 28795659 | 0.000000
09-04-2025 21:32:05000 | -8603616 | 86.0362 | 67577998 | 234667.48 | 212342606 | 99692947 | 50162914 | 0.000000 | 228553558 | 29987358 | 0.000000
09-04-2025 21:32:10000 | -8621623 | 86.2162 | 69257676 | 234686.41 | 212799911 | 99678909 | 50157688 | 0.000000 | 238179626 | 31184795 | 0.000000
09-04-2025 21:32:15000 | -8666971 | 86.6697 | 70759331 | 234702.25 | 213926926 | 99668381 | 50158745 | 0.000000 | 247956497 | 32387437 | 0.000000
09-04-2025 21:32:20000 | -8681593 | 86.8159 | 70507593 | 234696.78 | 214285599 | 99671829 | 50153820 | 0.000000 | 257871979 | 33591116 | 0.000000
09-04-2025 21:32:25000 | -8616902 | 86.169 | 71679907 | 234793.38 | 212636017 | 99655800 | 50173691 | 0.000000 | 267820251 | 34792698 | 0.000000
09-04-2025 21:32:30000 | -8614071 | 86.1407 | 70109785 | 234711.03 | 212608887 | 99670418 | 50173901 | 0.000000 | 277672363 | 35985186 | 0.000000
09-04-2025 21:32:35000 | -8647738 | 86.4774 | 71644233 | 234743.52 | 213436127 | 99658569 | 50172031 | 0.000000 | 287546509 | 37185254 | 0.000000
09-04-2025 21:32:40000 | -8648411 | 86.4841 | 73036606 | 234812.25 | 213418350 | 99645302 | 50168674 | 0.000000 | 297560516 | 38386467 | 0.000000
09-04-2025 21:32:45000 | -8618237 | 86.1824 | 70991494 | 234777.20 | 212670013 | 99662445 | 50179535 | 0.000000 | 307520355 | 39586516 | 0.000000
09-04-2025 21:32:50000 | -8598763 | 85.9876 | 69564883 | 234731.11 | 212204498 | 99674347 | 50183430 | 0.000000 | 317211609 | 40780825 | 0.000000
09-04-2025 21:32:55000 | -8639565 | 86.3957 | 72334204 | 234777.84 | 213219254 | 99651344 | 50172520 | 0.000000 | 327045959 | 41978286 | 0.000000
09-04-2025 21:33:00000 | -8631975 | 86.3197 | 71268364 | 234782.02 | 213008530 | 99660896 | 50177013 | 0.000000 | 336955841 | 43177139 | 0.000000
09-04-2025 21:33:05000 | -8661300 | 86.613 | 71510767 | 234750.80 | 213759201 | 99660896 | 50167404 | 0.000000 | 346895142 | 44377080 | 0.000000
09-04-2025 21:33:10000 | -8728493 | 87.2849 | 74325054 | 234788.97 | 215430466 | 99639412 | 50152161 | 0.000000 | 356952972 | 45585229 | 0.000000
09-04-2025 21:33:15000 | -8682027 | 86.8203 | 74117129 | 234828.50 | 214251205 | 99637589 | 50168438 | 0.000000 | 367278076 | 46796870 | 0.000000
09-04-2025 21:33:20000 | -8663062 | 86.6306 | 71167202 | 234762.22 | 213785675 | 99664268 | 50170361 | 0.000000 | 377257874 | 48002451 | 0.000000
09-04-2025 21:33:25000 | -8541845 | 85.4185 | 72599004 | 234871.59 | 210747101 | 99640762 | 50204098 | 0.000000 | 387340851 | 49196870 | 0.000000
09-04-2025 21:33:30000 | -8602430 | 86.0243 | 70716631 | 234745.53 | 212306061 | 99663818 | 50189117 | 0.000000 | 397103394 | 50386177 | 0.000000
09-04-2025 21:33:35000 | -8640603 | 86.406 | 72174648 | 234823.34 | 213199310 | 99652954 | 50169044 | 0.000000 | 406986938 | 51583657 | 0.000000
09-04-2025 21:33:40000 | -8711673 | 87.1167 | 75575493 | 234824.84 | 215010864 | 99625816 | 50184399 | 0.000000 | 417337463 | 52790850 | 0.000000
09-04-2025 21:33:45000 | -8690377 | 86.9038 | 75819160 | 234860.48 | 214460068 | 99621574 | 50193836 | 0.000000 | 427808655 | 53998696 | 0.000000
09-04-2025 21:33:50000 | -8808327 | 88.0833 | 74574526 | 234715.20 | 217461502 | 99643517 | 50166782 | 0.000000 | 438133301 | 55212568 | 0.000000
09-04-2025 21:33:55000 | -8832961 | 88.3296 | 76646504 | 234787.38 | 218044189 | 99625633 | 50144714 | 0.000000 | 448625244 | 56437437 | 0.000000
09-04-2025 21:34:00000 | -8695142 | 86.9514 | 74630068 | 234865.58 | 214547562 | 99633690 | 50168755 | 0.000000 | 459146729 | 57653872 | 0.000000
09-04-2025 21:34:05000 | -8678748 | 86.7875 | 72811055 | 234794.20 | 214173401 | 99649925 | 50167458 | 0.000000 | 469383301 | 58859961 | 0.000000
09-04-2025 21:34:10000 | -8565543 | 85.6554 | 74568916 | 234945.63 | 211300415 | 99623199 | 50192009 | 0.000000 | 479648468 | 60058931 | 0.000000
09-04-2025 21:34:15000 | -8485762 | 84.8576 | 74159106 | 234961.19 | 209329910 | 99620300 | 50219810 | 0.000000 | 489876038 | 61241118 | 0.000000
09-04-2025 21:34:20000 | -8576013 | 85.7601 | 75557476 | 234878.77 | 211639496 | 99614136 | 50200130 | 0.000000 | 500081085 | 62428306 | 0.000000
09-04-2025 21:34:25000 | -8630755 | 86.3076 | 77637095 | 234901.83 | 213003250 | 99597855 | 50193108 | 0.000000 | 510761993 | 63628369 | 0.000000
09-04-2025 21:34:30000 | -8628627 | 86.2863 | 77193843 | 234863.08 | 212981750 | 99602211 | 50195332 | 0.000000 | 521488892 | 64828325 | 0.000000
09-04-2025 21:34:35000 | -8780143 | 87.8014 | 77525820 | 234776.02 | 216773514 | 99612450 | 50160057 | 0.000000 | 532135254 | 66040181 | 0.000000
09-04-2025 21:34:40000 | -8860034 | 88.6003 | 78324419 | 234815.75 | 218712982 | 99611526 | 50148293 | 0.000000 | 542969666 | 67267739 | 0.000000
09-04-2025 21:34:45000 | -8749230 | 87.4923 | 75007817 | 234842.77 | 215902512 | 99634521 | 50158810 | 0.000000 | 553525269 | 68488350 | 0.000000
09-04-2025 21:34:50000 | -8750570 | 87.5057 | 75386060 | 234810.45 | 215972214 | 99630966 | 50161930 | 0.000000 | 563902832 | 69701636 | 0.000000
09-04-2025 21:34:55000 | -8807731 | 88.0773 | 73167427 | 234707.20 | 217422806 | 99656731 | 50140938 | 0.000000 | 574157349 | 70920068 | 0.000000
09-04-2025 21:35:00000 | -8891317 | 88.9132 | 75401792 | 234748.36 | 219478149 | 99642342 | 50117390 | 0.000000 | 584455627 | 72152432 | 0.000000
09-04-2025 21:35:05000 | -8755730 | 87.5573 | 72684282 | 234797.23 | 216058441 | 99657211 | 50137455 | 0.000000 | 594701050 | 73377036 | 0.000000
09-04-2025 21:35:10000 | -8636631 | 86.3663 | 70801670 | 234805.27 | 213090424 | 99665665 | 50164749 | 0.000000 | 604557983 | 74581104 | 0.000000
09-04-2025 21:35:15000 | -8663063 | 86.6306 | 68811138 | 234684.92 | 213808136 | 99686028 | 50145786 | 0.000000 | 614221191 | 75783188 | 0.000000
09-04-2025 21:35:20000 | -8654609 | 86.5461 | 70616787 | 234767.14 | 213561905 | 99668770 | 50151451 | 0.000000 | 623963257 | 76986743 | 0.000000
09-04-2025 21:35:25000 | -8599495 | 85.995 | 71490806 | 234820.59 | 212180603 | 99656219 | 50163910 | 0.000000 | 633860840 | 78183472 | 0.000000
09-04-2025 21:35:30000 | -8535416 | 85.3542 | 71286665 | 234821.14 | 210605408 | 99653046 | 50171871 | 0.000000 | 643697388 | 79373066 | 0.000000
09-04-2025 21:35:35000 | -8520953 | 85.2095 | 72206909 | 234836.11 | 210257385 | 99642876 | 50174988 | 0.000000 | 653645691 | 80558604 | 0.000000
09-04-2025 21:35:40000 | -8483159 | 84.8316 | 73459448 | 234878.77 | 209321243 | 99627167 | 50184502 | 0.000000 | 663756348 | 81739761 | 0.000000
09-04-2025 21:35:45000 | -8710780 | 87.1078 | 76392031 | 234810.38 | 215019958 | 99617653 | 50143883 | 0.000000 | 674130188 | 82938975 | 0.000000
09-04-2025 21:35:50000 | -8778614 | 87.7861 | 78679175 | 234829.22 | 216717392 | 99600761 | 50127930 | 0.000000 | 685036499 | 84156318 | 0.000000
09-04-2025 21:35:55000 | -8808357 | 88.0836 | 77314619 | 234820.78 | 217418945 | 99616997 | 50131554 | 0.000000 | 695894348 | 85379082 | 0.000000
09-04-2025 21:36:00000 | -8704246 | 87.0425 | 75850122 | 234869.45 | 214796219 | 99622467 | 50142403 | 0.000000 | 706585571 | 86593994 | 0.000000
09-04-2025 21:36:05000 | -8643872 | 86.4387 | 74079072 | 234866.86 | 213280273 | 99634773 | 50158306 | 0.000000 | 716919128 | 87798906 | 0.000000
09-04-2025 21:36:10000 | -8649535 | 86.4954 | 71688159 | 234761.25 | 213469696 | 99658295 | 50150654 | 0.000000 | 727019409 | 88998730 | 0.000000
09-04-2025 21:36:15000 | -8703322 | 87.0332 | 73423945 | 234775.16 | 214807663 | 99646034 | 50137478 | 0.000000 | 737185791 | 90204443 | 0.000000
09-04-2025 21:36:20000 | -8755500 | 87.555 | 74305645 | 234773.11 | 216106476 | 99641808 | 50126255 | 0.000000 | 747489807 | 91418047 | 0.000000
09-04-2025 21:36:25000 | -8732752 | 87.3275 | 75458608 | 234866.13 | 215487457 | 99628754 | 50139866 | 0.000000 | 757883728 | 92631426 | 0.000000
09-04-2025 21:36:30000 | -8826624 | 88.2662 | 76078438 | 234802.00 | 217858185 | 99630608 | 50116261 | 0.000000 | 768381409 | 93851182 | 0.000000
09-04-2025 21:36:35000 | -8946277 | 89.4628 | 78218657 | 234749.53 | 220882935 | 99619965 | 50076458 | 0.000000 | 779216797 | 95087129 | 0.000000
09-04-2025 21:36:40000 | -8884827 | 88.8483 | 75580996 | 234771.08 | 219306290 | 99640129 | 50080296 | 0.000000 | 789946838 | 96323750 | 0.000000
09-04-2025 21:36:45000 | -8874377 | 88.7438 | 72162881 | 234694.42 | 219047241 | 99671013 | 50075481 | 0.000000 | 800179932 | 97557754 | 0.000000
09-04-2025 21:36:50000 | -8773316 | 87.7332 | 69712896 | 234734.03 | 216485580 | 99685791 | 50073273 | 0.000000 | 810021362 | 98784170 | 0.000000
09-04-2025 21:36:55000 | -8699237 | 86.9924 | 67754224 | 234734.33 | 214634064 | 99698067 | 50086224 | 0.000000 | 819545227 | 99998301 | 0.000000
09-04-2025 21:37:00000 | -8617591 | 86.1759 | 67900264 | 234729.50 | 212639893 | 99691025 | 50102859 | 0.000000 | 829018677 | 10120106 | 0.000000
09-04-2025 21:37:05000 | -8571575 | 85.7157 | 68769541 | 234752.03 | 211510956 | 99679703 | 50104935 | 0.000000 | 838522095 | 10239586 | 0.000000
09-04-2025 21:37:10000 | -8489755 | 84.8975 | 71321567 | 234884.27 | 209444672 | 99648979 | 50139931 | 0.000000 | 848236938 | 10357912 | 0.000000
09-04-2025 21:37:15000 | -8448736 | 84.4874 | 72440308 | 234897.45 | 208450272 | 99634438 | 50154873 | 0.000000 | 858102722 | 10475341 | 0.000000
09-04-2025 21:37:20000 | -8429748 | 84.2975 | 73344614 | 234887.45 | 208005524 | 99623627 | 50173180 | 0.000000 | 868164124 | 10592355 | 0.000000
09-04-2025 21:37:25000 | -8513817 | 85.1382 | 72376484 | 234776.23 | 210147293 | 99640610 | 50158325 | 0.000000 | 878253723 | 10709828 | 0.000000
09-04-2025 21:37:30000 | -8620686 | 86.2069 | 77529912 | 234864.58 | 212798935 | 99598022 | 50132656 | 0.000000 | 888793701 | 10829510 | 0.000000
09-04-2025 21:37:35000 | -8786412 | 87.8641 | 79400137 | 234829.39 | 216929230 | 99594177 | 50117428 | 0.000000 | 899694214 | 10950615 | 0.000000
09-04-2025 21:37:40000 | -8808805 | 88.088 | 78114771 | 234886.17 | 217395676 | 99609116 | 50103218 | 0.000000 | 910599548 | 11072734 | 0.000000
09-04-2025 21:37:45000 | -8719715 | 87.1971 | 77067783 | 234914.17 | 215159332 | 99611694 | 50128948 | 0.000000 | 921374634 | 11194238 | 0.000000
09-04-2025 21:37:50000 | -8664691 | 86.6469 | 73449380 | 234849.31 | 213797562 | 99642639 | 50135708 | 0.000000 | 931739929 | 11314835 | 0.000000
09-04-2025 21:37:55000 | -8610566 | 86.1057 | 73656855 | 234864.81 | 212462021 | 99636124 | 50147480 | 0.000000 | 942003113 | 11434548 | 0.000000
09-04-2025 21:38:00000 | -8487139 | 84.8714 | 74735376 | 234953.91 | 209387177 | 99614540 | 50160976 | 0.000000 | 952314331 | 11553624 | 0.000000
09-04-2025 21:38:05000 | -8559359 | 85.5936 | 75777510 | 234900.89 | 211220123 | 99610397 | 50157761 | 0.000000 | 962692200 | 11672382 | 0.000000
09-04-2025 21:38:10000 | -8696616 | 86.9662 | 76397666 | 234806.75 | 214679993 | 99616356 | 50130844 | 0.000000 | 973190552 | 11792361 | 0.000000
09-04-2025 21:38:15000 | -8777439 | 87.7744 | 78803613 | 234869.13 | 216660370 | 99599403 | 50113716 | 0.000000 | 984088379 | 11914164 | 0.000000
09-04-2025 21:38:20000 | -8813523 | 88.1352 | 77688271 | 234839.34 | 217538849 | 99613754 | 50110081 | 0.000000 | 994939514 | 12036323 | 0.000000
09-04-2025 21:38:25000 | -8815542 | 88.1554 | 76745654 | 234849.78 | 217559189 | 99623192 | 50105732 | 0.000000 | 10056314 | 12158373 | 0.000000
09-04-2025 21:38:30000 | -8866063 | 88.6606 | 78247368 | 234860.72 | 218816544 | 99612816 | 50078472 | 0.000000 | 10162899 | 12281314 | 0.000000
09-04-2025 21:38:35000 | -8699034 | 86.9903 | 77551934 | 234978.86 | 214608124 | 99604965 | 50103249 | 0.000000 | 10270413 | 12403011 | 0.000000
09-04-2025 21:38:40000 | -8613585 | 86.1359 | 76147612 | 234945.34 | 212510880 | 99611511 | 50129581 | 0.000000 | 10376266 | 12523462 | 0.000000
09-04-2025 21:38:45000 | -8534735 | 85.3474 | 74212188 | 234951.73 | 210537445 | 99624084 | 50147141 | 0.000000 | 10479003 | 12642016 | 0.000000
09-04-2025 21:38:50000 | -8621698 | 86.217 | 76329683 | 234857.66 | 212795364 | 99610390 | 50116776 | 0.000000 | 10584042 | 12761404 | 0.000000
09-04-2025 21:38:55000 | -8703950 | 87.0395 | 80051367 | 234931.36 | 214822662 | 99579727 | 50112782 | 0.000000 | 10693298 | 12881947 | 0.000000
09-04-2025 21:39:00000 | -8733651 | 87.3365 | 77714556 | 234855.44 | 215568222 | 99606438 | 50100708 | 0.000000 | 10801627 | 13002752 | 0.000000
09-04-2025 21:39:05000 | -8713216 | 87.1322 | 78222949 | 234865.05 | 215069611 | 99599442 | 50108688 | 0.000000 | 10910743 | 13124000 | 0.000000
09-04-2025 21:39:10000 | -8737020 | 87.3702 | 77440322 | 234888.53 | 215612930 | 99609497 | 50102707 | 0.000000 | 11018298 | 13245287 | 0.000000
09-04-2025 21:39:15000 | -8789797 | 87.898 | 78641938 | 234904.19 | 216930954 | 99602150 | 50100204 | 0.000000 | 11126649 | 13367142 | 0.000000
09-04-2025 21:39:20000 | -8741709 | 87.4171 | 79502104 | 234938.39 | 215729599 | 99588989 | 50104816 | 0.000000 | 11236195 | 13488496 | 0.000000
09-04-2025 21:39:25000 | -8709908 | 87.0991 | 78957861 | 234922.92 | 214954315 | 99591621 | 50114441 | 0.000000 | 11346277 | 13609556 | 0.000000
09-04-2025 21:39:30000 | -8643663 | 86.4366 | 78021641 | 234969.92 | 213268127 | 99595085 | 50123917 | 0.000000 | 11454178 | 13729932 | 0.000000
09-04-2025 21:39:35000 | -8537816 | 85.3782 | 77458228 | 235012.83 | 210627457 | 99590981 | 50139950 | 0.000000 | 11561382 | 13849344 | 0.000000
09-04-2025 21:39:40000 | -8597191 | 85.9719 | 78925708 | 234948.77 | 212167831 | 99581245 | 50133015 | 0.000000 | 11669412 | 13968608 | 0.000000
09-04-2025 21:39:45000 | -8642360 | 86.4236 | 79358633 | 234950.95 | 213281113 | 99581055 | 50124855 | 0.000000 | 11778140 | 14088494 | 0.000000
09-04-2025 21:39:50000 | -8625709 | 86.2571 | 77945645 | 234933.27 | 212857925 | 99594200 | 50124332 | 0.000000 | 11887175 | 14208620 | 0.000000
09-04-2025 21:39:55000 | -8617876 | 86.1788 | 79549409 | 234964.25 | 212677292 | 99576668 | 50132523 | 0.000000 | 11997223 | 14328460 | 0.000000
09-04-2025 21:40:00000 | -8683954 | 86.8395 | 78188203 | 234884.78 | 214332962 | 99597107 | 50117893 | 0.000000 | 12106288 | 14448451 | 0.000000
09-04-2025 21:40:05000 | -8700929 | 87.0093 | 81830693 | 234975.39 | 214748718 | 99560661 | 50114868 | 0.000000 | 12218553 | 14569141 | 0.000000
09-04-2025 21:40:10000 | -8762815 | 87.6282 | 82494395 | 234996.55 | 216262024 | 99559792 | 50103905 | 0.000000 | 12332229 | 14690362 | 0.000000
09-04-2025 21:40:15000 | -8750927 | 87.5093 | 81120703 | 234947.00 | 215985413 | 99573090 | 50098076 | 0.000000 | 12446503 | 14812005 | 0.000000
09-04-2025 21:40:20000 | -8795201 | 87.952 | 80994966 | 234955.41 | 217054199 | 99578651 | 50091007 | 0.000000 | 12558896 | 14934211 | 0.000000
09-04-2025 21:40:25000 | -8867975 | 88.6797 | 79803442 | 234871.88 | 218889572 | 99597527 | 50062531 | 0.000000 | 12670778 | 15057074 | 0.000000
09-04-2025 21:40:30000 | -8701738 | 87.0174 | 79965767 | 235066.73 | 214641876 | 99580406 | 50094753 | 0.000000 | 12780420 | 15178843 | 0.000000
09-04-2025 21:40:35000 | -8615155 | 86.1516 | 76956729 | 234953.20 | 212561096 | 99603401 | 50115372 | 0.000000 | 12888562 | 15298945 | 0.000000
09-04-2025 21:40:40000 | -8633354 | 86.3335 | 78961484 | 234993.70 | 213012085 | 99584351 | 50100227 | 0.000000 | 12995972 | 15418658 | 0.000000
09-04-2025 21:40:45000 | -8617305 | 86.1731 | 79156421 | 234949.47 | 212666916 | 99580765 | 50104313 | 0.000000 | 13107081 | 15538382 | 0.000000
09-04-2025 21:40:50000 | -8661135 | 86.6114 | 82285713 | 235040.88 | 213726913 | 99551727 | 50092941 | 0.000000 | 13219037 | 15658525 | 0.000000
09-04-2025 21:40:55000 | -8663786 | 86.6379 | 80201606 | 234913.16 | 213867233 | 99574265 | 50092190 | 0.000000 | 13332274 | 15778975 | 0.000000
09-04-2025 21:41:00000 | -8721586 | 87.2159 | 81437212 | 234947.61 | 215269073 | 99566895 | 50078484 | 0.000000 | 13444196 | 15899818 | 0.000000
09-04-2025 21:41:05000 | -8740262 | 87.4026 | 81267280 | 234962.42 | 215714005 | 99570518 | 50083027 | 0.000000 | 13557723 | 16021392 | 0.000000
09-04-2025 21:41:10000 | -8687352 | 86.8735 | 78556348 | 234947.27 | 214368881 | 99593643 | 50090641 | 0.000000 | 13668439 | 16142254 | 0.000000
09-04-2025 21:41:15000 | -8641205 | 86.412 | 79451367 | 235001.53 | 213212860 | 99579971 | 50108894 | 0.000000 | 13778174 | 16262571 | 0.000000
09-04-2025 21:41:20000 | -8540926 | 85.4093 | 78469346 | 235023.02 | 210718140 | 99580605 | 50122044 | 0.000000 | 13887239 | 16381622 | 0.000000
09-04-2025 21:41:25000 | -8562189 | 85.6219 | 78682285 | 234972.05 | 211287567 | 99580421 | 50120129 | 0.000000 | 13996533 | 16500539 | 0.000000
09-04-2025 21:41:30000 | -8556288 | 85.5629 | 82573779 | 235088.84 | 211125320 | 99537552 | 50125614 | 0.000000 | 14108800 | 16619443 | 0.000000
09-04-2025 21:41:35000 | -8607951 | 86.0795 | 82527529 | 235023.06 | 212447021 | 99543556 | 50123451 | 0.000000 | 14224230 | 16738701 | 0.000000
09-04-2025 21:41:40000 | -8612444 | 86.1244 | 82310361 | 235027.16 | 212552460 | 99546410 | 50131390 | 0.000000 | 14338909 | 16858369 | 0.000000
09-04-2025 21:41:45000 | -8658529 | 86.5853 | 82783545 | 235015.13 | 213696198 | 99546051 | 50116955 | 0.000000 | 14453507 | 16977992 | 0.000000
09-04-2025 21:41:50000 | -8728765 | 87.2876 | 85967656 | 235024.20 | 215484116 | 99518509 | 50094036 | 0.000000 | 14572662 | 17099082 | 0.000000
09-04-2025 21:41:55000 | -8837755 | 88.3775 | 84230625 | 234943.27 | 218184341 | 99548889 | 50077763 | 0.000000 | 14691161 | 17221359 | 0.000000
09-04-2025 21:42:00000 | -8792698 | 87.927 | 81746851 | 234943.95 | 217021332 | 99570602 | 50071526 | 0.000000 | 14806890 | 17343906 | 0.000000
09-04-2025 21:42:05000 | -8792359 | 87.9236 | 80525117 | 234967.11 | 216964630 | 99583229 | 50065617 | 0.000000 | 14918969 | 17465975 | 0.000000
09-04-2025 21:42:10000 | -8701185 | 87.0118 | 80660063 | 235017.16 | 214689957 | 99573082 | 50076859 | 0.000000 | 15030742 | 17587326 | 0.000000
09-04-2025 21:42:15000 | -8608506 | 86.0851 | 78324063 | 234966.22 | 212416382 | 99588646 | 50086491 | 0.000000 | 15140159 | 17707629 | 0.000000
09-04-2025 21:42:20000 | -8595096 | 85.951 | 78683936 | 235031.28 | 212036926 | 99583588 | 50094437 | 0.000000 | 15247837 | 17827268 | 0.000000
09-04-2025 21:42:25000 | -8567100 | 85.671 | 79334072 | 235000.44 | 211395828 | 99573967 | 50091934 | 0.000000 | 15357552 | 17946496 | 0.000000
09-04-2025 21:42:30000 | -8565612 | 85.6561 | 80016021 | 235029.88 | 211348251 | 99566513 | 50096592 | 0.000000 | 15467622 | 18065396 | 0.000000
09-04-2025 21:42:35000 | -8584898 | 85.849 | 81901309 | 235032.36 | 211860474 | 99548012 | 50107761 | 0.000000 | 15579802 | 18184611 | 0.000000
09-04-2025 21:42:40000 | -8644352 | 86.4435 | 80336968 | 234959.34 | 213343887 | 99570923 | 50097172 | 0.000000 | 15691942 | 18304248 | 0.000000
09-04-2025 21:42:45000 | -8612870 | 86.1287 | 81671152 | 235023.72 | 212546738 | 99553421 | 50103615 | 0.000000 | 15805992 | 18424211 | 0.000000
09-04-2025 21:42:50000 | -8660253 | 86.6025 | 81358027 | 234988.77 | 213731720 | 99561623 | 50095276 | 0.000000 | 15917875 | 18544111 | 0.000000
09-04-2025 21:42:55000 | -8747723 | 87.4772 | 81526099 | 234896.98 | 215961426 | 99568527 | 50073105 | 0.000000 | 16032030 | 18665412 | 0.000000
09-04-2025 21:43:00000 | -8768880 | 87.6888 | 81540068 | 234982.03 | 216403076 | 99570442 | 50078602 | 0.000000 | 16145195 | 18786904 | 0.000000
09-04-2025 21:43:05000 | -8635467 | 86.3547 | 81693564 | 235080.47 | 213051910 | 99555504 | 50110741 | 0.000000 | 16259008 | 18907355 | 0.000000
09-04-2025 21:43:10000 | -8543339 | 85.4334 | 80312788 | 235078.73 | 210771011 | 99561050 | 50124851 | 0.000000 | 16371373 | 19026496 | 0.000000
09-04-2025 21:43:15000 | -8540689 | 85.4069 | 82389111 | 235069.58 | 210757751 | 99537933 | 50128796 | 0.000000 | 16484542 | 19145117 | 0.000000
09-04-2025 21:43:20000 | -8649634 | 86.4963 | 85072119 | 235059.48 | 213494171 | 99519814 | 50112610 | 0.000000 | 16601414 | 19264510 | 0.000000
09-04-2025 21:43:25000 | -8613980 | 86.1398 | 85448643 | 235106.47 | 212588516 | 99511597 | 50121677 | 0.000000 | 16720845 | 19384467 | 0.000000
09-04-2025 21:43:30000 | -8685640 | 86.8564 | 84178291 | 235030.02 | 214380188 | 99533638 | 50110573 | 0.000000 | 16837874 | 19504639 | 0.000000
09-04-2025 21:43:35000 | -8783782 | 87.8378 | 83606758 | 234949.67 | 216839920 | 99550064 | 50086353 | 0.000000 | 16953716 | 19625604 | 0.000000
09-04-2025 21:43:40000 | -8807573 | 88.0757 | 85484629 | 235046.31 | 217375824 | 99532288 | 50083111 | 0.000000 | 17071801 | 19747838 | 0.000000
09-04-2025 21:43:45000 | -8709303 | 87.093 | 83221914 | 235079.27 | 214889877 | 99546562 | 50093159 | 0.000000 | 17188262 | 19869264 | 0.000000
09-04-2025 21:43:50000 | -8707941 | 87.0794 | 82595498 | 235025.33 | 214891510 | 99553177 | 50099895 | 0.000000 | 17303351 | 19990164 | 0.000000
09-04-2025 21:43:55000 | -8677705 | 86.7771 | 83151250 | 235075.06 | 214121429 | 99544044 | 50097237 | 0.000000 | 17418356 | 20110813 | 0.000000
09-04-2025 21:44:00000 | -8683297 | 86.833 | 84422930 | 235082.00 | 214279846 | 99530693 | 50097893 | 0.000000 | 17534946 | 20231570 | 0.000000
09-04-2025 21:44:05000 | -8570232 | 85.7023 | 84254297 | 235149.59 | 211452454 | 99520226 | 50125278 | 0.000000 | 17653429 | 20351195 | 0.000000
09-04-2025 21:44:10000 | -8637855 | 86.3786 | 83607627 | 235052.75 | 213176331 | 99534828 | 50109940 | 0.000000 | 17768992 | 20470725 | 0.000000
09-04-2025 21:44:15000 | -8606320 | 86.0632 | 85708262 | 235146.53 | 212371490 | 99507774 | 50109650 | 0.000000 | 17887067 | 20590295 | 0.000000
09-04-2025 21:44:20000 | -8642399 | 86.424 | 84837891 | 235045.72 | 213322571 | 99521637 | 50098175 | 0.000000 | 18005974 | 20710051 | 0.000000
09-04-2025 21:44:25000 | -8730913 | 87.3091 | 86532344 | 235089.50 | 215492371 | 99512444 | 50085804 | 0.000000 | 18124532 | 20830666 | 0.000000
09-04-2025 21:44:30000 | -8650764 | 86.5076 | 87247949 | 235164.63 | 213477432 | 99495255 | 50103115 | 0.000000 | 18246090 | 20951381 | 0.000000
09-04-2025 21:44:35000 | -8705209 | 87.0521 | 84185820 | 235022.86 | 214865509 | 99535637 | 50097206 | 0.000000 | 18363999 | 21071623 | 0.000000
09-04-2025 21:44:40000 | -8684131 | 86.8413 | 86923320 | 235127.56 | 214318909 | 99502785 | 50096375 | 0.000000 | 18482955 | 21192361 | 0.000000
09-04-2025 21:44:45000 | -8695062 | 86.9506 | 85144668 | 235063.55 | 214608063 | 99523972 | 50097603 | 0.000000 | 18602327 | 21312840 | 0.000000
09-04-2025 21:44:50000 | -8731451 | 87.3145 | 84072207 | 235034.39 | 215497742 | 99539642 | 50089699 | 0.000000 | 18720214 | 21433814 | 0.000000
09-04-2025 21:44:55000 | -8696537 | 86.9654 | 84948672 | 235106.02 | 214599319 | 99526306 | 50092892 | 0.000000 | 18836859 | 21554754 | 0.000000
09-04-2025 21:45:00000 | -8780323 | 87.8032 | 85094609 | 235059.31 | 216691467 | 99533653 | 50087582 | 0.000000 | 18954453 | 21676002 | 0.000000
09-04-2025 21:45:05000 | -8706805 | 87.068 | 85640771 | 235112.47 | 214856766 | 99519737 | 50087421 | 0.000000 | 11888699 | 121229347 | 0.000000
09-04-2025 21:45:10000 | -8695911 | 86.9591 | 85834609 | 235130.19 | 214583389 | 99516380 | 50096878 | 0.000000 | 23843287 | 242310623 | 0.000000
09-04-2025 21:45:15000 | -8661165 | 86.6116 | 86645576 | 235139.81 | 213740341 | 99503334 | 50097443 | 0.000000 | 35899574 | 363014252 | 0.000000
09-04-2025 21:45:20000 | -8668887 | 86.6889 | 88176318 | 235215.69 | 213897018 | 99486671 | 50103222 | 0.000000 | 48040195 | 483541931 | 0.000000
09-04-2025 21:45:25000 | -8583382 | 85.8338 | 87100225 | 235204.34 | 211793320 | 99489082 | 50118523 | 0.000000 | 60236916 | 603315613 | 0.000000
09-04-2025 21:45:30000 | -8647370 | 86.4737 | 86292881 | 235127.53 | 213405914 | 99505775 | 50107002 | 0.000000 | 72232445 | 723064697 | 0.000000
09-04-2025 21:45:35000 | -8583125 | 85.8312 | 88187480 | 235223.67 | 211799820 | 99476311 | 50113781 | 0.000000 | 84384056 | 842548828 | 0.000000
09-04-2025 21:45:40000 | -8598343 | 85.9834 | 86680498 | 235152.22 | 212195816 | 99495697 | 50114029 | 0.000000 | 96530106 | 961932800 | 0.000000
09-04-2025 21:45:45000 | -8689152 | 86.8915 | 88200146 | 235133.16 | 214476990 | 99488770 | 50090984 | 0.000000 | 108592468 | 10818369 | 0.000000
09-04-2025 21:45:50000 | -8777532 | 87.7753 | 91815479 | 235188.83 | 216665497 | 99457359 | 50072395 | 0.000000 | 121096123 | 12035038 | 0.000000
09-04-2025 21:45:55000 | -8647322 | 86.4732 | 90299873 | 235308.05 | 213341797 | 99459190 | 50108597 | 0.000000 | 133752884 | 13243988 | 0.000000
09-04-2025 21:46:00000 | -8521984 | 85.2198 | 88784102 | 235318.22 | 210237686 | 99461678 | 50139702 | 0.000000 | 146124954 | 14436564 | 0.000000
09-04-2025 21:46:05000 | -8499008 | 84.9901 | 89170693 | 235284.58 | 209716171 | 99454102 | 50147987 | 0.000000 | 158402710 | 15615883 | 0.000000
09-04-2025 21:46:10000 | -8586638 | 85.8664 | 89209678 | 235207.81 | 211932770 | 99464638 | 50132393 | 0.000000 | 170746429 | 16802605 | 0.000000
09-04-2025 21:46:15000 | -8697391 | 86.9739 | 91196406 | 235178.97 | 214703888 | 99454765 | 50111774 | 0.000000 | 183381897 | 18004938 | 0.000000
09-04-2025 21:46:20000 | -8889434 | 88.8943 | 92807441 | 235128.23 | 219480560 | 99459427 | 50076698 | 0.000000 | 196215179 | 19227383 | 0.000000
09-04-2025 21:46:25000 | -8883584 | 88.8358 | 91331650 | 235112.41 | 219314972 | 99475662 | 50072617 | 0.000000 | 209052704 | 20461777 | 0.000000
09-04-2025 21:46:30000 | -8825789 | 88.2579 | 87561982 | 235104.80 | 217819305 | 99511459 | 50064697 | 0.000000 | 221412506 | 21693669 | 0.000000
09-04-2025 21:46:35000 | -8705534 | 87.0553 | 87102666 | 235251.94 | 214735062 | 99503181 | 50095898 | 0.000000 | 233471420 | 22910559 | 0.000000
09-04-2025 21:46:40000 | -8521416 | 85.2142 | 85097373 | 235228.19 | 210209396 | 99505066 | 50124737 | 0.000000 | 245446960 | 24105632 | 0.000000
09-04-2025 21:46:45000 | -8608816 | 86.0882 | 85313877 | 235100.89 | 212463364 | 99512543 | 50117622 | 0.000000 | 257298157 | 25293618 | 0.000000
09-04-2025 21:46:50000 | -8699288 | 86.9929 | 88005117 | 235113.59 | 214728317 | 99492188 | 50089226 | 0.000000 | 269396301 | 26495063 | 0.000000
09-04-2025 21:46:55000 | -8784077 | 87.8408 | 90565752 | 235128.88 | 216850189 | 99472694 | 50079117 | 0.000000 | 281919922 | 27711919 | 0.000000
09-04-2025 21:47:00000 | -8667283 | 86.6728 | 89276602 | 235254.45 | 213850143 | 99473694 | 50112991 | 0.000000 | 294465759 | 28923418 | 0.000000
09-04-2025 21:47:05000 | -8633730 | 86.3373 | 87049248 | 235190.61 | 213034332 | 99495560 | 50121578 | 0.000000 | 306540497 | 30123306 | 0.000000
09-04-2025 21:47:10000 | -8620006 | 86.2001 | 87122969 | 235186.44 | 212705780 | 99493118 | 50112682 | 0.000000 | 318618286 | 31320310 | 0.000000
09-04-2025 21:47:15000 | -8622364 | 86.2236 | 88632383 | 235183.17 | 212803009 | 99475822 | 50116417 | 0.000000 | 330944702 | 32518904 | 0.000000
09-04-2025 21:47:20000 | -8599002 | 85.99 | 89152314 | 235215.38 | 212215546 | 99466843 | 50122753 | 0.000000 | 343217834 | 33711616 | 0.000000
09-04-2025 21:47:25000 | -8595140 | 85.9514 | 87773291 | 235169.16 | 212129242 | 99482620 | 50112011 | 0.000000 | 355440247 | 34906997 | 0.000000
09-04-2025 21:47:30000 | -8625045 | 86.2505 | 89129160 | 235237.44 | 212831741 | 99470306 | 50114109 | 0.000000 | 367704956 | 36105439 | 0.000000
09-04-2025 21:47:35000 | -8555261 | 85.5526 | 88905615 | 235262.95 | 211101288 | 99464371 | 50131435 | 0.000000 | 380121460 | 37297920 | 0.000000
09-04-2025 21:47:40000 | -8551565 | 85.5156 | 87588760 | 235195.78 | 211036484 | 99479553 | 50134651 | 0.000000 | 392432831 | 38487739 | 0.000000
09-04-2025 21:47:45000 | -8610777 | 86.1078 | 88316152 | 235176.56 | 212522888 | 99478142 | 50128223 | 0.000000 | 404641663 | 39681975 | 0.000000
09-04-2025 21:47:50000 | -8684518 | 86.8452 | 88921309 | 235148.55 | 214359634 | 99479897 | 50114513 | 0.000000 | 417013519 | 40881619 | 0.000000
09-04-2025 21:47:55000 | -8725502 | 87.255 | 91419424 | 235214.95 | 215364182 | 99455612 | 50105724 | 0.000000 | 429558136 | 42092827 | 0.000000
09-04-2025 21:48:00000 | -8701034 | 87.0103 | 89507998 | 235176.30 | 214760178 | 99475044 | 50111309 | 0.000000 | 442061859 | 43302056 | 0.000000
09-04-2025 21:48:05000 | -8670234 | 86.7023 | 87851582 | 235172.42 | 213964340 | 99490578 | 50118896 | 0.000000 | 454340607 | 44511333 | 0.000000
09-04-2025 21:48:10000 | -8660449 | 86.6045 | 87732539 | 235182.66 | 213710098 | 99490807 | 50129852 | 0.000000 | 466563690 | 45716201 | 0.000000
09-04-2025 21:48:15000 | -8560907 | 85.6091 | 87429072 | 235229.81 | 211229248 | 99482559 | 50156216 | 0.000000 | 478741394 | 46906880 | 0.000000
09-04-2025 21:48:20000 | -8592348 | 85.9235 | 88712822 | 235197.06 | 212062836 | 99471237 | 50144039 | 0.000000 | 490974670 | 48099063 | 0.000000
09-04-2025 21:48:25000 | -8668470 | 86.6847 | 91678965 | 235215.02 | 213980255 | 99445374 | 50127754 | 0.000000 | 503386932 | 49300435 | 0.000000
09-04-2025 21:48:30000 | -8726888 | 87.2689 | 91416299 | 235202.73 | 215407669 | 99455818 | 50121017 | 0.000000 | 516068298 | 50507871 | 0.000000
09-04-2025 21:48:35000 | -8745334 | 87.4533 | 91191504 | 235172.52 | 215879135 | 99460739 | 50113537 | 0.000000 | 528717346 | 51720889 | 0.000000
09-04-2025 21:48:40000 | -8841422 | 88.4142 | 91650234 | 235128.81 | 218288651 | 99467018 | 50083527 | 0.000000 | 541416382 | 52948110 | 0.000000
09-04-2025 21:48:45000 | -8784593 | 87.8459 | 89809238 | 235202.80 | 216780838 | 99481461 | 50094456 | 0.000000 | 553984497 | 54175288 | 0.000000
09-04-2025 21:48:50000 | -8691370 | 86.9137 | 87624248 | 235205.16 | 214447647 | 99495636 | 50121662 | 0.000000 | 566234558 | 55386890 | 0.000000
09-04-2025 21:48:55000 | -8539948 | 85.3995 | 85991475 | 235238.72 | 210673599 | 99496864 | 50149876 | 0.000000 | 578231628 | 56579463 | 0.000000
09-04-2025 21:49:00000 | -8504446 | 85.0445 | 86986104 | 235237.44 | 209834686 | 99480980 | 50150452 | 0.000000 | 590260315 | 57762607 | 0.000000
09-04-2025 21:49:05000 | -8522168 | 85.2217 | 88948428 | 235253.94 | 210301712 | 99459724 | 50154465 | 0.000000 | 602457397 | 58943267 | 0.000000
09-04-2025 21:49:10000 | -8640011 | 86.4001 | 91692314 | 235224.80 | 213273666 | 99441582 | 50143650 | 0.000000 | 615032349 | 60135659 | 0.000000
09-04-2025 21:49:15000 | -8693605 | 86.936 | 90765479 | 235161.61 | 214622162 | 99459396 | 50135754 | 0.000000 | 627813599 | 61338940 | 0.000000
09-04-2025 21:49:20000 | -8786908 | 87.8691 | 93001172 | 235185.89 | 216927582 | 99444550 | 50120098 | 0.000000 | 640530701 | 62554639 | 0.000000
09-04-2025 21:49:25000 | -8838194 | 88.3819 | 93098516 | 235187.61 | 218183121 | 99449783 | 50106918 | 0.000000 | 653422791 | 63778149 | 0.000000
09-04-2025 21:49:30000 | -8685170 | 86.8517 | 92371162 | 235352.64 | 214276581 | 99439186 | 50128212 | 0.000000 | 666268982 | 64997568 | 0.000000
09-04-2025 21:49:35000 | -8539606 | 85.3961 | 88048496 | 235296.47 | 210666199 | 99472656 | 50169243 | 0.000000 | 678736023 | 66190371 | 0.000000
09-04-2025 21:49:40000 | -8541047 | 85.4105 | 88509834 | 235237.64 | 210764359 | 99467339 | 50163769 | 0.000000 | 690865662 | 67374863 | 0.000000
09-04-2025 21:49:45000 | -8623755 | 86.2375 | 91219287 | 235255.09 | 212838257 | 99445213 | 50152760 | 0.000000 | 703442627 | 68568398 | 0.000000
09-04-2025 21:49:50000 | -8566992 | 85.6699 | 93690322 | 235357.98 | 211426788 | 99407310 | 50172657 | 0.000000 | 716426086 | 69764224 | 0.000000
09-04-2025 21:49:55000 | -8609895 | 86.099 | 92503398 | 235273.75 | 212516098 | 99427795 | 50177258 | 0.000000 | 729369446 | 70955347 | 0.000000
09-04-2025 21:50:00000 | -8630930 | 86.3093 | 95377998 | 235360.66 | 213026001 | 99394943 | 50168442 | 0.000000 | 742425598 | 72152979 | 0.000000
09-04-2025 21:50:05000 | -8669955 | 86.6996 | 95467930 | 235314.25 | 214024994 | 99399208 | 50165314 | 0.000000 | 755625671 | 73354136 | 0.000000
09-04-2025 21:50:10000 | -8792198 | 87.922 | 94695117 | 235227.77 | 217065582 | 99424995 | 50143684 | 0.000000 | 768799072 | 74564243 | 0.000000
09-04-2025 21:50:15000 | -8841702 | 88.417 | 94946270 | 235234.39 | 218271667 | 99428368 | 50118053 | 0.000000 | 782060730 | 75788828 | 0.000000
09-04-2025 21:50:20000 | -8794358 | 87.9436 | 93155137 | 235236.72 | 217068726 | 99443665 | 50122677 | 0.000000 | 795044800 | 77013979 | 0.000000
09-04-2025 21:50:25000 | -8662413 | 86.6241 | 88600908 | 235203.34 | 213762985 | 99480988 | 50140430 | 0.000000 | 807556763 | 78222881 | 0.000000
09-04-2025 21:50:30000 | -8626377 | 86.2638 | 88272080 | 235247.66 | 212835144 | 99480522 | 50126362 | 0.000000 | 819810608 | 79421982 | 0.000000
09-04-2025 21:50:35000 | -8615248 | 86.1525 | 89569199 | 235238.23 | 212603302 | 99463898 | 50110184 | 0.000000 | 832202576 | 80619976 | 0.000000
09-04-2025 21:50:40000 | -8588659 | 85.8866 | 88065781 | 235191.39 | 211957214 | 99478416 | 50099384 | 0.000000 | 844413940 | 81813569 | 0.000000
09-04-2025 21:50:45000 | -8493175 | 84.9317 | 87733975 | 235216.38 | 209602310 | 99470695 | 50112911 | 0.000000 | 856644165 | 82997969 | 0.000000
09-04-2025 21:50:50000 | -8472400 | 84.724 | 85076865 | 235194.16 | 209041946 | 99499611 | 50095688 | 0.000000 | 868508301 | 84175576 | 0.000000
09-04-2025 21:50:55000 | -8371053 | 83.7105 | 87218809 | 235255.52 | 206567917 | 99461594 | 50101711 | 0.000000 | 880635315 | 85345439 | 0.000000
09-04-2025 21:51:00000 | -8239371 | 82.3937 | 84718271 | 235254.94 | 203289124 | 99475548 | 50115185 | 0.000000 | 892468994 | 86499053 | 0.000000
09-04-2025 21:51:05000 | -7989861 | 79.8986 | 81202588 | 235292.13 | 197077118 | 99487511 | 50150730 | 0.000000 | 903991760 | 87623906 | 0.000000
09-04-2025 21:51:10000 | -7802779 | 78.0278 | 80982881 | 235324.36 | 192481308 | 99465721 | 50174686 | 0.000000 | 915350708 | 88718623 | 0.000000
09-04-2025 21:51:15000 | -7741274 | 77.4127 | 81189917 | 235297.27 | 191023010 | 99454514 | 50159557 | 0.000000 | 926489990 | 89796777 | 0.000000
09-04-2025 21:51:20000 | -7693916 | 76.9392 | 81673188 | 235299.67 | 189874313 | 99441292 | 50147770 | 0.000000 | 937828003 | 90866279 | 0.000000
09-04-2025 21:51:25000 | -7595227 | 75.9523 | 83057256 | 235395.23 | 187415375 | 99407387 | 50153526 | 0.000000 | 949307312 | 91927822 | 0.000000
09-04-2025 21:51:30000 | -7480450 | 74.8045 | 81964082 | 235376.80 | 184606033 | 99405060 | 50162586 | 0.000000 | 960787659 | 92975371 | 0.000000
09-04-2025 21:51:35000 | -7348410 | 73.4841 | 79844277 | 235364.72 | 181257904 | 99414879 | 50170914 | 0.000000 | 972041260 | 94007539 | 0.000000
09-04-2025 21:51:40000 | -7432948 | 74.3295 | 80051914 | 235269.84 | 183476730 | 99425049 | 50148403 | 0.000000 | 982945129 | 95029473 | 0.000000
09-04-2025 21:51:45000 | -7393608 | 73.9361 | 80143984 | 235310.95 | 182487503 | 99417641 | 50124317 | 0.000000 | 994012634 | 96058965 | 0.000000
09-04-2025 21:51:50000 | -7345698 | 73.457 | 79311621 | 235330.98 | 181207275 | 99422173 | 50123158 | 0.000000 | 10050858 | 97085215 | 0.000000
09-04-2025 21:51:55000 | -7248848 | 72.4885 | 78117720 | 235331.17 | 178887207 | 99424339 | 50141296 | 0.000000 | 10159216 | 98093701 | 0.000000
09-04-2025 21:52:00000 | -7098035 | 70.9804 | 75500283 | 235325.23 | 175147583 | 99439049 | 50142464 | 0.000000 | 10265763 | 99090127 | 0.000000
09-04-2025 21:52:05000 | -6993866 | 69.9387 | 76387612 | 235367.45 | 172603561 | 99408821 | 50145924 | 0.000000 | 10372438 | 10006947 | 0.000000
09-04-2025 21:52:10000 | -7063342 | 70.6334 | 75861201 | 235263.36 | 174353378 | 99428192 | 50122032 | 0.000000 | 10478042 | 10104634 | 0.000000
09-04-2025 21:52:15000 | -7148868 | 71.4887 | 75574722 | 235210.55 | 176473633 | 99445854 | 50079163 | 0.000000 | 10582762 | 10203744 | 0.000000
09-04-2025 21:52:20000 | -6994361 | 69.9436 | 74742231 | 235318.78 | 172600723 | 99433884 | 50107960 | 0.000000 | 10689425 | 10302165 | 0.000000
09-04-2025 21:52:25000 | -6812307 | 68.1231 | 73552534 | 235373.78 | 168091141 | 99422173 | 50132576 | 0.000000 | 10791904 | 10397768 | 0.000000
09-04-2025 21:52:30000 | -6694709 | 66.9471 | 71451572 | 235323.77 | 165200836 | 99435272 | 50148033 | 0.000000 | 10892502 | 10491107 | 0.000000
09-04-2025 21:52:35000 | -6635694 | 66.3569 | 73242139 | 235359.25 | 163791916 | 99396370 | 50158379 | 0.000000 | 10992963 | 10583150 | 0.000000
09-04-2025 21:52:40000 | -6685369 | 66.8537 | 72581772 | 235277.97 | 165037491 | 99415810 | 50140720 | 0.000000 | 11093683 | 10675463 | 0.000000
09-04-2025 21:52:45000 | -6700795 | 67.0079 | 76275151 | 235357.23 | 165455826 | 99358368 | 50133026 | 0.000000 | 11198060 | 10768384 | 0.000000
09-04-2025 21:52:50000 | -6606795 | 66.0679 | 74986973 | 235379.27 | 163114700 | 99362045 | 50156670 | 0.000000 | 11304015 | 10860616 | 0.000000
09-04-2025 21:52:55000 | -6547116 | 65.4712 | 74890977 | 235379.25 | 161657288 | 99352127 | 50161629 | 0.000000 | 11408057 | 10952017 | 0.000000
09-04-2025 21:53:00000 | -6636544 | 66.3654 | 77505103 | 235390.11 | 163900940 | 99324959 | 50153648 | 0.000000 | 11514390 | 11043905 | 0.000000
09-04-2025 21:53:05000 | -6652909 | 66.5291 | 76519502 | 235352.84 | 164298920 | 99345047 | 50138348 | 0.000000 | 11621613 | 11135810 | 0.000000
09-04-2025 21:53:10000 | -6639134 | 66.3913 | 77121929 | 235372.56 | 163970169 | 99332062 | 50139977 | 0.000000 | 11729193 | 11228362 | 0.000000
09-04-2025 21:53:15000 | -6688202 | 66.882 | 75815605 | 235334.97 | 165152939 | 99363632 | 50134159 | 0.000000 | 11835157 | 11321290 | 0.000000
09-04-2025 21:53:20000 | -6771412 | 67.7141 | 76739902 | 235321.95 | 167214584 | 99363945 | 50126675 | 0.000000 | 11941719 | 11414632 | 0.000000
09-04-2025 21:53:25000 | -6788115 | 67.8812 | 77775156 | 235384.53 | 167612473 | 99350014 | 50119423 | 0.000000 | 12048538 | 11508755 | 0.000000
09-04-2025 21:53:30000 | -6739136 | 67.3914 | 77702969 | 235395.72 | 166411224 | 99341835 | 50125340 | 0.000000 | 12156580 | 11602942 | 0.000000
09-04-2025 21:53:35000 | -6714784 | 67.1478 | 75734819 | 235375.00 | 165769699 | 99369949 | 50136402 | 0.000000 | 12262997 | 11696470 | 0.000000
09-04-2025 21:53:40000 | -6745102 | 67.451 | 76022344 | 235325.45 | 166553604 | 99370842 | 50119900 | 0.000000 | 12368490 | 11790251 | 0.000000
09-04-2025 21:53:45000 | -6789761 | 67.8976 | 76356113 | 235333.48 | 167645401 | 99373596 | 50115524 | 0.000000 | 12474646 | 11884533 | 0.000000
09-04-2025 21:53:50000 | -6704595 | 67.046 | 74313311 | 235313.86 | 165524139 | 99391335 | 50122189 | 0.000000 | 12579436 | 11977661 | 0.000000
09-04-2025 21:53:55000 | -6704729 | 67.0473 | 75451372 | 235370.78 | 165519760 | 99372749 | 50120956 | 0.000000 | 12683275 | 12070962 | 0.000000
09-04-2025 21:54:00000 | -6608277 | 66.0828 | 75675430 | 235437.19 | 163129166 | 99350685 | 50142742 | 0.000000 | 12787886 | 12163603 | 0.000000
09-04-2025 21:54:05000 | -6499770 | 64.9977 | 74056733 | 235461.66 | 160426346 | 99357162 | 50177776 | 0.000000 | 12891418 | 12254218 | 0.000000
09-04-2025 21:54:10000 | -6609940 | 66.0994 | 75214639 | 235379.36 | 163200714 | 99358810 | 50159409 | 0.000000 | 12995706 | 12345058 | 0.000000
09-04-2025 21:54:15000 | -6638250 | 66.3825 | 77754629 | 235395.28 | 163948105 | 99320992 | 50147812 | 0.000000 | 13102756 | 12437100 | 0.000000
09-04-2025 21:54:20000 | -6740945 | 67.4095 | 79427007 | 235392.84 | 166498489 | 99312981 | 50132309 | 0.000000 | 13211903 | 12530350 | 0.000000
09-04-2025 21:54:25000 | -6767095 | 67.671 | 79914907 | 235420.83 | 167130585 | 99309906 | 50126621 | 0.000000 | 13322089 | 12624298 | 0.000000
09-04-2025 21:54:30000 | -6756088 | 67.5609 | 77834087 | 235386.11 | 166830414 | 99342911 | 50134014 | 0.000000 | 13431465 | 12718313 | 0.000000
09-04-2025 21:54:35000 | -6690403 | 66.904 | 77966426 | 235454.19 | 165186050 | 99327820 | 50153839 | 0.000000 | 13539680 | 12811642 | 0.000000
09-04-2025 21:54:40000 | -6588352 | 65.8835 | 77045991 | 235476.23 | 162654678 | 99323151 | 50171509 | 0.000000 | 13646820 | 12903521 | 0.000000
09-04-2025 21:54:45000 | -6586932 | 65.8693 | 77641362 | 235466.69 | 162644760 | 99312469 | 50165977 | 0.000000 | 13752832 | 12994831 | 0.000000
09-04-2025 21:54:50000 | -6592634 | 65.9263 | 76723340 | 235389.53 | 162808624 | 99329620 | 50163506 | 0.000000 | 13861516 | 13086255 | 0.000000
09-04-2025 21:54:55000 | -6665040 | 66.6504 | 79950996 | 235429.95 | 164641632 | 99288200 | 50141228 | 0.000000 | 13971327 | 13178566 | 0.000000
09-04-2025 21:55:00000 | -6733748 | 67.3375 | 80263350 | 235425.34 | 166323914 | 99297104 | 50134628 | 0.000000 | 14082847 | 13271997 | 0.000000
09-04-2025 21:55:05000 | -6758555 | 67.5855 | 82063887 | 235475.66 | 166948761 | 99270882 | 50128128 | 0.000000 | 14196582 | 13366031 | 0.000000
09-04-2025 21:55:10000 | -6692533 | 66.9253 | 79782969 | 235442.73 | 165294601 | 99296913 | 50149704 | 0.000000 | 14309733 | 13459498 | 0.000000
09-04-2025 21:55:15000 | -6695564 | 66.9556 | 78173750 | 235402.06 | 165349228 | 99325310 | 50147255 | 0.000000 | 14418591 | 13552553 | 0.000000
09-04-2025 21:55:20000 | -6707454 | 67.0745 | 79940313 | 235468.28 | 165646164 | 99297272 | 50150215 | 0.000000 | 14528658 | 13645697 | 0.000000
09-04-2025 21:55:25000 | -6630630 | 66.3063 | 79395088 | 235485.48 | 163745453 | 99290733 | 50164734 | 0.000000 | 14638804 | 13737919 | 0.000000
09-04-2025 21:55:30000 | -6562470 | 65.6247 | 79149717 | 235485.30 | 162080383 | 99280502 | 50173496 | 0.000000 | 14749308 | 13829417 | 0.000000
09-04-2025 21:55:35000 | -6581243 | 65.8124 | 78657686 | 235429.83 | 162560410 | 99293335 | 50173985 | 0.000000 | 14858472 | 13920517 | 0.000000
09-04-2025 21:55:40000 | -6607597 | 66.076 | 81103301 | 235481.30 | 163240570 | 99255119 | 50177055 | 0.000000 | 14970593 | 14012366 | 0.000000
09-04-2025 21:55:45000 | -6611278 | 66.1128 | 81563013 | 235481.25 | 163341263 | 99247574 | 50182194 | 0.000000 | 15084384 | 14104622 | 0.000000
09-04-2025 21:55:50000 | -6600633 | 66.0063 | 82538213 | 235536.45 | 163073090 | 99227226 | 50177692 | 0.000000 | 15197313 | 14196300 | 0.000000
09-04-2025 21:55:55000 | -6559555 | 65.5956 | 84700703 | 235633.02 | 162075409 | 99176613 | 50187790 | 0.000000 | 15312878 | 14287680 | 0.000000
09-04-2025 21:56:00000 | -6592445 | 65.9244 | 85261895 | 235603.33 | 162920547 | 99174004 | 50183960 | 0.000000 | 15430942 | 14378787 | 0.000000
09-04-2025 21:56:05000 | -6623435 | 66.2344 | 85590020 | 235580.84 | 163690674 | 99175385 | 50184689 | 0.000000 | 15550007 | 14470322 | 0.000000
09-04-2025 21:56:10000 | -6540879 | 65.4088 | 86552451 | 235673.02 | 161653839 | 99135834 | 50199142 | 0.000000 | 15669961 | 14561396 | 0.000000
09-04-2025 21:56:15000 | -6619584 | 66.1958 | 84858604 | 235575.23 | 163585770 | 99188316 | 50196445 | 0.000000 | 15787540 | 14652383 | 0.000000
09-04-2025 21:56:20000 | -6716309 | 67.1631 | 87394824 | 235574.08 | 166010513 | 99164001 | 50170528 | 0.000000 | 15907467 | 14744941 | 0.000000
09-04-2025 21:56:25000 | -6797295 | 67.9729 | 88721689 | 235562.25 | 168028870 | 99158897 | 50153473 | 0.000000 | 16029779 | 14839004 | 0.000000
09-04-2025 21:56:30000 | -6876651 | 68.7665 | 85412041 | 235452.56 | 169936752 | 99237457 | 50128407 | 0.000000 | 16150006 | 14934350 | 0.000000
09-04-2025 21:56:35000 | -6883955 | 68.8396 | 85626641 | 235529.69 | 170065918 | 99235268 | 50121876 | 0.000000 | 16269235 | 15030294 | 0.000000
09-04-2025 21:56:40000 | -6709416 | 67.0942 | 84037002 | 235588.27 | 165727890 | 99224701 | 50155701 | 0.000000 | 16387346 | 15124285 | 0.000000
09-04-2025 21:56:45000 | -6666852 | 66.6685 | 80527168 | 235515.78 | 164639038 | 99278404 | 50157066 | 0.000000 | 16500758 | 15217209 | 0.000000
09-04-2025 21:56:50000 | -6572484 | 65.7248 | 80932827 | 235532.86 | 162342331 | 99250359 | 50175175 | 0.000000 | 16613121 | 15309145 | 0.000000
09-04-2025 21:56:55000 | -6514037 | 65.1404 | 80847627 | 235551.89 | 160906860 | 99238586 | 50187607 | 0.000000 | 16725979 | 15400199 | 0.000000
09-04-2025 21:57:00000 | -6556061 | 65.5606 | 83127520 | 235585.95 | 161975311 | 99205719 | 50190308 | 0.000000 | 16840385 | 15491229 | 0.000000
09-04-2025 21:57:05000 | -6654304 | 66.543 | 84229004 | 235514.30 | 164445648 | 99208397 | 50185444 | 0.000000 | 16957515 | 15583000 | 0.000000
09-04-2025 21:57:10000 | -6675687 | 66.7569 | 87476260 | 235648.70 | 164973236 | 99152367 | 50178963 | 0.000000 | 17076178 | 15675731 | 0.000000
09-04-2025 21:57:15000 | -6643792 | 66.4379 | 85566895 | 235577.47 | 164192352 | 99180801 | 50187038 | 0.000000 | 17195920 | 15768147 | 0.000000
09-04-2025 21:57:20000 | -6643051 | 66.4305 | 85303682 | 235600.64 | 164146011 | 99185593 | 50189537 | 0.000000 | 17313586 | 15860386 | 0.000000
09-04-2025 21:57:25000 | -6608855 | 66.0885 | 84916055 | 235620.33 | 163293304 | 99184624 | 50202690 | 0.000000 | 17431881 | 15952218 | 0.000000
09-04-2025 21:57:30000 | -6587991 | 65.8799 | 85856084 | 235651.73 | 162806961 | 99161476 | 50208893 | 0.000000 | 17549534 | 16043579 | 0.000000
09-04-2025 21:57:35000 | -6664528 | 66.6453 | 85903672 | 235574.39 | 164711502 | 99179489 | 50199532 | 0.000000 | 17669298 | 16135282 | 0.000000
09-04-2025 21:57:40000 | -6816123 | 68.1612 | 85919668 | 235467.14 | 168470596 | 99214867 | 50167782 | 0.000000 | 17789312 | 16228630 | 0.000000
09-04-2025 21:57:45000 | -6878560 | 68.7856 | 86038525 | 235491.22 | 169980072 | 99226784 | 50136921 | 0.000000 | 17908014 | 16323788 | 0.000000
09-04-2025 21:57:50000 | -6815941 | 68.1594 | 86302773 | 235610.17 | 168371582 | 99207893 | 50141819 | 0.000000 | 18027343 | 16418967 | 0.000000
09-04-2025 21:57:55000 | -6716791 | 67.1679 | 86398789 | 235627.78 | 165953552 | 99182831 | 50152363 | 0.000000 | 18147919 | 16513004 | 0.000000
09-04-2025 21:58:00000 | -6598380 | 65.9838 | 83740225 | 235613.45 | 163002899 | 99204285 | 50179127 | 0.000000 | 18264885 | 16605162 | 0.000000
09-04-2025 21:58:05000 | -6570897 | 65.709 | 82490293 | 235550.52 | 162340561 | 99221191 | 50183949 | 0.000000 | 18379819 | 16696354 | 0.000000
09-04-2025 21:58:10000 | -6665508 | 66.6551 | 84849580 | 235541.38 | 164722580 | 99199493 | 50162815 | 0.000000 | 18495481 | 16788254 | 0.000000
09-04-2025 21:58:15000 | -6806166 | 68.0617 | 86888262 | 235527.58 | 168211609 | 99194962 | 50131279 | 0.000000 | 18615056 | 16882178 | 0.000000
09-04-2025 21:58:20000 | -6864999 | 68.65 | 87574551 | 235532.58 | 169659760 | 99196136 | 50124897 | 0.000000 | 18736661 | 16977225 | 0.000000
09-04-2025 21:58:25000 | -6758552 | 67.5855 | 84167705 | 235560.13 | 166947800 | 99233452 | 50140965 | 0.000000 | 18854907 | 17071459 | 0.000000
09-04-2025 21:58:30000 | -6568073 | 65.6807 | 83576670 | 235642.25 | 162240250 | 99200111 | 50178387 | 0.000000 | 18971857 | 17163758 | 0.000000
09-04-2025 21:58:35000 | -6561288 | 65.6129 | 81464336 | 235569.77 | 162060959 | 99238022 | 50180088 | 0.000000 | 19086410 | 17254732 | 0.000000
09-04-2025 21:58:40000 | -6633144 | 66.3314 | 86410850 | 235604.31 | 163936707 | 99162117 | 50166378 | 0.000000 | 19203508 | 17346584 | 0.000000
09-04-2025 21:58:45000 | -6613766 | 66.1377 | 85959961 | 235583.69 | 163467346 | 99165924 | 50171906 | 0.000000 | 19323440 | 17438662 | 0.000000
09-04-2025 21:58:50000 | -6603391 | 66.0339 | 85554854 | 235585.41 | 163201920 | 99171104 | 50178585 | 0.000000 | 19442856 | 17530551 | 0.000000
09-04-2025 21:58:55000 | -6557064 | 65.5706 | 85678223 | 235640.48 | 162040863 | 99157104 | 50194130 | 0.000000 | 19561582 | 17621863 | 0.000000
09-04-2025 21:59:00000 | -6616563 | 66.1656 | 86547871 | 235591.06 | 163550278 | 99155327 | 50190434 | 0.000000 | 19680854 | 17713262 | 0.000000
09-04-2025 21:59:05000 | -6785955 | 67.8595 | 88303730 | 235539.58 | 167755554 | 99163948 | 50162071 | 0.000000 | 19801705 | 17806719 | 0.000000
09-04-2025 21:59:10000 | -6750155 | 67.5015 | 88713848 | 235606.05 | 166853607 | 99147408 | 50170757 | 0.000000 | 19924358 | 17900459 | 0.000000
09-04-2025 21:59:15000 | -6721693 | 67.2169 | 87442256 | 235609.98 | 166123062 | 99164429 | 50172943 | 0.000000 | 20045920 | 17993959 | 0.000000
09-04-2025 21:59:20000 | -6689054 | 66.8905 | 86515664 | 235621.38 | 165289551 | 99173920 | 50183601 | 0.000000 | 20166622 | 18087273 | 0.000000
09-04-2025 21:59:25000 | -6686652 | 66.8665 | 84550068 | 235530.48 | 165237366 | 99210030 | 50180466 | 0.000000 | 20285200 | 18179979 | 0.000000
09-04-2025 21:59:30000 | -6761757 | 67.6176 | 86627139 | 235536.31 | 167119690 | 99189316 | 50161591 | 0.000000 | 20405237 | 18273705 | 0.000000
09-04-2025 21:59:35000 | -6780529 | 67.8053 | 87208545 | 235515.88 | 167608200 | 99183014 | 50162750 | 0.000000 | 20527268 | 18367861 | 0.000000
09-04-2025 21:59:40000 | -6814877 | 68.1488 | 86535459 | 235533.03 | 168409363 | 99203423 | 50159092 | 0.000000 | 20646970 | 18462242 | 0.000000
09-04-2025 21:59:45000 | -6828250 | 68.2825 | 87389648 | 235565.75 | 168738403 | 99190948 | 50153687 | 0.000000 | 20768254 | 18556922 | 0.000000
09-04-2025 21:59:50000 | -6745480 | 67.4548 | 87797480 | 235633.86 | 166689941 | 99163567 | 50173920 | 0.000000 | 20890667 | 18651170 | 0.000000
09-04-2025 21:59:55000 | -6638310 | 66.3831 | 87225547 | 235672.59 | 164042450 | 99147758 | 50189850 | 0.000000 | 21013066 | 18744045 | 0.000000
09-04-2025 22:00:00000 | -6676263 | 66.7626 | 88693379 | 235626.89 | 165042557 | 99129074 | 50189533 | 0.000000 | 21136226 | 18836283 | 0.000000
09-04-2025 22:00:05000 | -6795263 | 67.9526 | 90985527 | 235611.89 | 168016312 | 99115479 | 50155083 | 0.000000 | 12480232 | 93467056 | 0.000000
09-04-2025 22:00:10000 | -6849139 | 68.4914 | 94870527 | 235684.72 | 169400162 | 99054276 | 50142216 | 0.000000 | 25490870 | 188638626 | 0.000000
09-04-2025 22:00:15000 | -6899741 | 68.9974 | 92456592 | 235648.81 | 170582001 | 99114113 | 50126568 | 0.000000 | 38442448 | 283873322 | 0.000000
09-04-2025 22:00:20000 | -6964349 | 69.6435 | 92490254 | 235610.30 | 172173950 | 99129631 | 50091015 | 0.000000 | 51233887 | 380382324 | 0.000000
09-04-2025 22:00:25000 | -6918210 | 69.1821 | 90859854 | 235600.03 | 171009628 | 99148567 | 50098179 | 0.000000 | 64003807 | 476507477 | 0.000000
09-04-2025 22:00:30000 | -6775834 | 67.7583 | 88505537 | 235638.34 | 167448303 | 99157692 | 50110878 | 0.000000 | 76416908 | 571386230 | 0.000000
09-04-2025 22:00:35000 | -6743291 | 67.4329 | 87991328 | 235630.83 | 166644379 | 99159370 | 50116013 | 0.000000 | 88556389 | 664929626 | 0.000000
09-04-2025 22:00:40000 | -6616837 | 66.1684 | 88257969 | 235681.97 | 163547592 | 99122131 | 50132912 | 0.000000 | 100837395 | 757609131 | 0.000000
09-04-2025 22:00:45000 | -6619113 | 66.1911 | 85482354 | 235543.13 | 163615036 | 99176369 | 50133789 | 0.000000 | 112876427 | 849587036 | 0.000000
09-04-2025 22:00:50000 | -6552035 | 65.5203 | 89224834 | 235671.89 | 162013199 | 99085464 | 50146648 | 0.000000 | 125055222 | 940782959 | 0.000000
09-04-2025 22:00:55000 | -6573974 | 65.7397 | 86739473 | 235568.33 | 162536209 | 99140747 | 50145714 | 0.000000 | 137136093 | 10315944 | 0.000000
09-04-2025 22:01:00000 | -6657416 | 66.5742 | 88580801 | 235581.69 | 164615982 | 99126389 | 50123165 | 0.000000 | 149301529 | 11240177 | 0.000000
09-04-2025 22:01:05000 | -6654028 | 66.5403 | 91747227 | 235677.03 | 164570709 | 99062767 | 50133419 | 0.000000 | 161844971 | 12168711 | 0.000000
09-04-2025 22:01:10000 | -6499596 | 64.996 | 91158594 | 235780.33 | 160731705 | 99030739 | 50176197 | 0.000000 | 174589081 | 13078633 | 0.000000
09-04-2025 22:01:15000 | -6554291 | 65.5429 | 91328086 | 235789.75 | 162060089 | 99043114 | 50169445 | 0.000000 | 187274246 | 13984712 | 0.000000
09-04-2025 22:01:20000 | -6639517 | 66.3952 | 94492197 | 235802.92 | 164220169 | 99002411 | 50150471 | 0.000000 | 200299515 | 14906316 | 0.000000
09-04-2025 22:01:25000 | -6650899 | 66.509 | 95612949 | 235835.25 | 164512390 | 98982407 | 50155308 | 0.000000 | 213584137 | 15833416 | 0.000000
09-04-2025 22:01:30000 | -6649589 | 66.4959 | 95708701 | 235864.38 | 164464539 | 98980003 | 50165546 | 0.000000 | 226853394 | 16757397 | 0.000000
09-04-2025 22:01:35000 | -6646686 | 66.4669 | 95488281 | 235861.59 | 164389099 | 98983749 | 50165668 | 0.000000 | 240033371 | 17676151 | 0.000000
09-04-2025 22:01:40000 | -6666913 | 66.6691 | 95786357 | 235860.77 | 164890762 | 98983597 | 50156502 | 0.000000 | 253271988 | 18599308 | 0.000000
09-04-2025 22:01:45000 | -6680380 | 66.8038 | 96058857 | 235827.16 | 165249802 | 98981949 | 50151062 | 0.000000 | 266643463 | 19524915 | 0.000000
09-04-2025 22:01:50000 | -6672592 | 66.7259 | 10135968 | 236019.06 | 165113785 | 98865845 | 50152233 | 0.000000 | 280308868 | 20457074 | 0.000000
09-04-2025 22:01:55000 | -6555951 | 65.5595 | 96730918 | 235902.67 | 162205429 | 98928955 | 50182842 | 0.000000 | 294083618 | 21373042 | 0.000000
09-04-2025 22:02:00000 | -6616612 | 66.1661 | 94605254 | 235832.45 | 163652298 | 98993225 | 50174088 | 0.000000 | 307241577 | 22286277 | 0.000000
09-04-2025 22:02:05000 | -6698984 | 66.9898 | 95476172 | 235793.34 | 165702362 | 98999573 | 50152271 | 0.000000 | 320357239 | 23210442 | 0.000000
09-04-2025 22:02:10000 | -6797655 | 67.9766 | 96571504 | 235780.25 | 168143417 | 99005890 | 50139839 | 0.000000 | 333788391 | 24146934 | 0.000000
09-04-2025 22:02:15000 | -6814975 | 68.1497 | 96216309 | 235780.25 | 168548309 | 99018013 | 50127689 | 0.000000 | 347206787 | 25094045 | 0.000000
09-04-2025 22:02:20000 | -6830907 | 68.3091 | 95399932 | 235825.06 | 168879120 | 99038803 | 50116886 | 0.000000 | 360417023 | 26042119 | 0.000000
09-04-2025 22:02:25000 | -6785889 | 67.8589 | 95347686 | 235828.08 | 167783478 | 99027245 | 50118332 | 0.000000 | 373713867 | 26983203 | 0.000000
09-04-2025 22:02:30000 | -6785795 | 67.858 | 95848438 | 235830.14 | 167796082 | 99017120 | 50116333 | 0.000000 | 387022919 | 27925183 | 0.000000
09-04-2025 22:02:35000 | -6672994 | 66.7299 | 94789893 | 235857.47 | 165003143 | 99006104 | 50145851 | 0.000000 | 400366211 | 28856479 | 0.000000
09-04-2025 22:02:40000 | -6686743 | 66.8674 | 92679648 | 235780.17 | 165320908 | 99053093 | 50135735 | 0.000000 | 413385254 | 29782385 | 0.000000
09-04-2025 22:02:45000 | -6619502 | 66.195 | 96330566 | 235921.55 | 163715988 | 98957642 | 50143448 | 0.000000 | 426535431 | 30706978 | 0.000000
09-04-2025 22:02:50000 | -6615005 | 66.15 | 95682178 | 235861.00 | 163631180 | 98970039 | 50151638 | 0.000000 | 439863708 | 31624492 | 0.000000
09-04-2025 22:02:55000 | -6667234 | 66.6723 | 95159102 | 235808.31 | 164912781 | 98996758 | 50139572 | 0.000000 | 453079346 | 32543394 | 0.000000
09-04-2025 22:03:00000 | -6654661 | 66.5466 | 96754473 | 235806.23 | 164664581 | 98959503 | 50131886 | 0.000000 | 466501495 | 33470437 | 0.000000
09-04-2025 22:03:05000 | -6756652 | 67.5665 | 97555195 | 235796.34 | 167173813 | 98973686 | 50127743 | 0.000000 | 479966034 | 34402522 | 0.000000
09-04-2025 22:03:10000 | -6776682 | 67.7668 | 96258652 | 235725.48 | 167667801 | 99006187 | 50111965 | 0.000000 | 493335083 | 35338728 | 0.000000
09-04-2025 22:03:15000 | -6809741 | 68.0974 | 98013320 | 235781.28 | 168485535 | 98980011 | 50110439 | 0.000000 | 506933228 | 36285322 | 0.000000
09-04-2025 22:03:20000 | -6773994 | 67.7399 | 95393770 | 235752.14 | 167548843 | 99022942 | 50122715 | 0.000000 | 520373901 | 37224685 | 0.000000
09-04-2025 22:03:25000 | -6786790 | 67.8679 | 96924346 | 235779.31 | 167898285 | 98995560 | 50108410 | 0.000000 | 533740479 | 38166260 | 0.000000
09-04-2025 22:03:30000 | -6840863 | 68.4086 | 97677842 | 235777.34 | 169232162 | 98995941 | 50111904 | 0.000000 | 547356384 | 39112271 | 0.000000
09-04-2025 22:03:35000 | -6709609 | 67.0961 | 97311406 | 235857.34 | 165979050 | 98964577 | 50118755 | 0.000000 | 560899841 | 40050337 | 0.000000
09-04-2025 22:03:40000 | -6718135 | 67.1813 | 96585557 | 235818.25 | 166190109 | 98982285 | 50116199 | 0.000000 | 574223755 | 40983652 | 0.000000
09-04-2025 22:03:45000 | -6707652 | 67.0765 | 97878525 | 235855.63 | 165959763 | 98952065 | 50119476 | 0.000000 | 587723755 | 41915273 | 0.000000
09-04-2025 22:03:50000 | -6679234 | 66.7923 | 94702354 | 235767.17 | 165217453 | 99009735 | 50117813 | 0.000000 | 601088135 | 42844165 | 0.000000
09-04-2025 22:03:55000 | -6740805 | 67.4081 | 97049922 | 235806.52 | 166763214 | 98979416 | 50112339 | 0.000000 | 614385376 | 43778687 | 0.000000
09-04-2025 22:04:00000 | -6693098 | 66.931 | 97229521 | 235849.52 | 165582947 | 98961266 | 50121395 | 0.000000 | 627874146 | 44712427 | 0.000000
09-04-2025 22:04:05000 | -6565597 | 65.656 | 96165225 | 235895.88 | 162424591 | 98944305 | 50149967 | 0.000000 | 641317932 | 45631489 | 0.000000
09-04-2025 22:04:10000 | -6504085 | 65.0409 | 98495967 | 235947.23 | 160983994 | 98872696 | 50169285 | 0.000000 | 654955261 | 46534512 | 0.000000
09-04-2025 22:04:15000 | -6543861 | 65.4386 | 98649209 | 235862.23 | 162010895 | 98882721 | 50169205 | 0.000000 | 668734375 | 47439263 | 0.000000
09-04-2025 22:04:20000 | -6595373 | 65.9537 | 96080010 | 235791.31 | 163215698 | 98955490 | 50165390 | 0.000000 | 682229553 | 48351758 | 0.000000
09-04-2025 22:04:25000 | -6616120 | 66.1612 | 99204453 | 235893.13 | 163763412 | 98894455 | 50174606 | 0.000000 | 695892822 | 49270991 | 0.000000
09-04-2025 22:04:30000 | -6604252 | 66.0425 | 98725791 | 235884.16 | 163476425 | 98901047 | 50179424 | 0.000000 | 709676758 | 50186899 | 0.000000
09-04-2025 22:04:35000 | -6632625 | 66.3263 | 99974834 | 235886.17 | 164192413 | 98882996 | 50170582 | 0.000000 | 723554749 | 51107285 | 0.000000
09-04-2025 22:04:40000 | -6780966 | 67.8097 | 10170702 | 235849.98 | 167869217 | 98893791 | 50144821 | 0.000000 | 737562012 | 52039678 | 0.000000
09-04-2025 22:04:45000 | -6806213 | 68.0621 | 10352885 | 235921.33 | 168501312 | 98862831 | 50140194 | 0.000000 | 751837891 | 52983281 | 0.000000
09-04-2025 22:04:50000 | -6746970 | 67.4697 | 10154316 | 235936.36 | 166981796 | 98886345 | 50155376 | 0.000000 | 766101440 | 53922720 | 0.000000
09-04-2025 22:04:55000 | -6676713 | 66.7671 | 98969619 | 235875.61 | 165229721 | 98919159 | 50160881 | 0.000000 | 780013977 | 54853867 | 0.000000
09-04-2025 22:05:00000 | -6785091 | 67.8509 | 98901963 | 235792.31 | 167910065 | 98954285 | 50141972 | 0.000000 | 793773682 | 55790317 | 0.000000
09-04-2025 22:05:05000 | -6803374 | 68.0337 | 10117065 | 235866.33 | 168384293 | 98912323 | 50139675 | 0.000000 | 807650635 | 56733330 | 0.000000
09-04-2025 22:05:10000 | -6708732 | 67.0873 | 10035108 | 235881.59 | 166048798 | 98899681 | 50160721 | 0.000000 | 821743652 | 57669468 | 0.000000
09-04-2025 22:05:15000 | -6647824 | 66.4782 | 98571260 | 235856.66 | 164529953 | 98918510 | 50170010 | 0.000000 | 835554810 | 58596094 | 0.000000
09-04-2025 22:05:20000 | -6634775 | 66.3478 | 99458096 | 235906.52 | 164209106 | 98895027 | 50173920 | 0.000000 | 849325562 | 59519976 | 0.000000
09-04-2025 22:05:25000 | -6610002 | 66.1 | 98521182 | 235868.50 | 163604462 | 98907394 | 50171707 | 0.000000 | 863045349 | 60439976 | 0.000000
09-04-2025 22:05:30000 | -6615780 | 66.1578 | 97568477 | 235844.59 | 163728180 | 98929932 | 50177578 | 0.000000 | 876645081 | 61358628 | 0.000000
09-04-2025 22:05:35000 | -6638759 | 66.3876 | 97673252 | 235865.28 | 164269745 | 98934959 | 50171303 | 0.000000 | 890193726 | 62278701 | 0.000000
09-04-2025 22:05:40000 | -6652370 | 66.5237 | 99471963 | 235901.20 | 164640625 | 98900467 | 50171314 | 0.000000 | 903873596 | 63199702 | 0.000000
09-04-2025 22:05:45000 | -6531634 | 65.3163 | 10023986 | 235969.91 | 161707809 | 98842773 | 50194218 | 0.000000 | 917840637 | 64112212 | 0.000000
09-04-2025 22:05:50000 | -6593476 | 65.9348 | 99982617 | 235877.80 | 163253967 | 98869743 | 50190109 | 0.000000 | 931757813 | 65020420 | 0.000000
09-04-2025 22:05:55000 | -6728537 | 67.2854 | 10332678 | 235906.27 | 166624924 | 98841339 | 50158859 | 0.000000 | 945833496 | 65948682 | 0.000000
09-04-2025 22:06:00000 | -6799630 | 67.9963 | 10432908 | 235875.92 | 168400528 | 98843292 | 50147316 | 0.000000 | 960421936 | 66892119 | 0.000000
09-04-2025 22:06:05000 | -6752650 | 67.5265 | 10408398 | 235945.45 | 167210678 | 98832832 | 50161903 | 0.000000 | 974909302 | 67834570 | 0.000000
09-04-2025 22:06:10000 | -6683421 | 66.8342 | 10103582 | 235930.38 | 165427109 | 98876541 | 50183300 | 0.000000 | 989100098 | 68766411 | 0.000000
09-04-2025 22:06:15000 | -6735616 | 67.3562 | 99501084 | 235827.80 | 166711609 | 98926422 | 50167694 | 0.000000 | 10029516 | 69696509 | 0.000000
09-04-2025 22:06:20000 | -6729480 | 67.2948 | 10248509 | 235920.50 | 166610703 | 98860138 | 50164211 | 0.000000 | 10170620 | 70632690 | 0.000000
09-04-2025 22:06:25000 | -6699274 | 66.9927 | 10152122 | 235934.58 | 165825943 | 98871178 | 50178123 | 0.000000 | 10312639 | 71564648 | 0.000000
09-04-2025 22:06:30000 | -6719382 | 67.1938 | 10394846 | 235959.52 | 166385071 | 98824463 | 50165859 | 0.000000 | 10455123 | 72498013 | 0.000000
09-04-2025 22:06:35000 | -6798716 | 67.9872 | 10304465 | 235868.70 | 168336060 | 98870819 | 50151741 | 0.000000 | 10599170 | 73437314 | 0.000000
09-04-2025 22:06:40000 | -6840350 | 68.4035 | 10561398 | 235936.88 | 169388199 | 98828949 | 50147263 | 0.000000 | 10744835 | 74384985 | 0.000000
09-04-2025 22:06:45000 | -6800843 | 68.0084 | 10315051 | 235891.89 | 168378693 | 98869240 | 50156895 | 0.000000 | 10890386 | 75327334 | 0.000000
09-04-2025 22:06:50000 | -6840266 | 68.4027 | 10369373 | 235902.45 | 169345627 | 98870407 | 50129063 | 0.000000 | 11033999 | 76276548 | 0.000000
09-04-2025 22:06:55000 | -6770595 | 67.706 | 10206312 | 235913.41 | 167597412 | 98882805 | 50135437 | 0.000000 | 11177247 | 77221519 | 0.000000
09-04-2025 22:07:00000 | -6768241 | 67.6824 | 10211023 | 235900.67 | 167540054 | 98881027 | 50138134 | 0.000000 | 11318947 | 78159805 | 0.000000
09-04-2025 22:07:05000 | -6701310 | 67.0131 | 10236222 | 235934.28 | 165908218 | 98853401 | 50147499 | 0.000000 | 11461038 | 79091641 | 0.000000
09-04-2025 22:07:10000 | -6804959 | 68.0496 | 10290610 | 235872.14 | 168479889 | 98875839 | 50119663 | 0.000000 | 11602970 | 80032456 | 0.000000
09-04-2025 22:07:15000 | -6780908 | 67.8091 | 10514528 | 235960.94 | 167917633 | 98819061 | 50135788 | 0.000000 | 11747721 | 80973838 | 0.000000
09-04-2025 22:07:20000 | -6753310 | 67.5331 | 10220096 | 235891.31 | 167197937 | 98874191 | 50141075 | 0.000000 | 11891580 | 81908687 | 0.000000
09-04-2025 22:07:25000 | -6728398 | 67.284 | 10308063 | 235923.69 | 166597809 | 98846718 | 50138458 | 0.000000 | 12034587 | 82845254 | 0.000000
09-04-2025 22:07:30000 | -6684491 | 66.8449 | 10282080 | 235922.00 | 165526382 | 98837563 | 50149387 | 0.000000 | 12178372 | 83776357 | 0.000000
09-04-2025 22:07:35000 | -6747933 | 67.4793 | 10030597 | 235804.63 | 167051422 | 98913185 | 50138226 | 0.000000 | 12320028 | 84705811 | 0.000000
09-04-2025 22:07:40000 | -6843221 | 68.4322 | 10363154 | 235860.48 | 169441986 | 98872696 | 50109093 | 0.000000 | 12463003 | 85651025 | 0.000000
09-04-2025 22:07:45000 | -6852334 | 68.5233 | 10442476 | 235895.64 | 169666321 | 98858658 | 50098446 | 0.000000 | 12607716 | 86602939 | 0.000000
09-04-2025 22:07:50000 | -6741595 | 67.4159 | 10229229 | 235931.92 | 166883072 | 98868355 | 50114353 | 0.000000 | 12751439 | 87544492 | 0.000000
09-04-2025 22:07:55000 | -6729548 | 67.2955 | 10116041 | 235894.70 | 166574738 | 98888947 | 50115997 | 0.000000 | 12891575 | 88478848 | 0.000000
09-04-2025 22:08:00000 | -6596947 | 65.9695 | 99939424 | 235912.13 | 163309341 | 98871872 | 50139648 | 0.000000 | 13031580 | 89401279 | 0.000000
09-04-2025 22:08:05000 | -6529488 | 65.2949 | 10047850 | 235940.86 | 161677872 | 98836601 | 50149803 | 0.000000 | 13171321 | 90313857 | 0.000000
09-04-2025 22:08:10000 | -6646436 | 66.4644 | 10173936 | 235884.53 | 164591553 | 98848618 | 50134121 | 0.000000 | 13311079 | 91231475 | 0.000000
09-04-2025 22:08:15000 | -6768742 | 67.6874 | 10232306 | 235840.72 | 167607300 | 98876602 | 50111023 | 0.000000 | 13452163 | 92164648 | 0.000000
09-04-2025 22:08:20000 | -6795295 | 67.953 | 10389309 | 235886.47 | 168272583 | 98851334 | 50105312 | 0.000000 | 13595848 | 93108467 | 0.000000
09-04-2025 22:08:25000 | -6859943 | 68.5994 | 10276507 | 235841.27 | 169825516 | 98896469 | 50083477 | 0.000000 | 13738411 | 94059932 | 0.000000
09-04-2025 22:08:30000 | -6811333 | 68.1133 | 10262247 | 235907.13 | 168597443 | 98883980 | 50083721 | 0.000000 | 13881243 | 95009697 | 0.000000
09-04-2025 22:08:35000 | -6709330 | 67.0933 | 99463643 | 235874.30 | 166038086 | 98918930 | 50096375 | 0.000000 | 14021072 | 95946162 | 0.000000
09-04-2025 22:08:40000 | -6768761 | 67.6876 | 10092026 | 235836.92 | 167563110 | 98906700 | 50079559 | 0.000000 | 14159666 | 96886826 | 0.000000
09-04-2025 22:08:45000 | -6791376 | 67.9138 | 10076012 | 235847.13 | 168090240 | 98917236 | 50080112 | 0.000000 | 14300541 | 97828955 | 0.000000
09-04-2025 22:08:50000 | -6787236 | 67.8724 | 10093397 | 235835.44 | 168006027 | 98912254 | 50082870 | 0.000000 | 14440747 | 98771191 | 0.000000
09-04-2025 22:08:55000 | -6734722 | 67.3472 | 10080480 | 235888.69 | 166692444 | 98898285 | 50091671 | 0.000000 | 14580663 | 99708242 | 0.000000
09-04-2025 22:09:00000 | -6796491 | 67.9649 | 10060287 | 235836.11 | 168216431 | 98922157 | 50080318 | 0.000000 | 14720464 | 10064765 | 0.000000
09-04-2025 22:09:05000 | -6754900 | 67.549 | 10402460 | 235937.98 | 167262177 | 98834900 | 50081017 | 0.000000 | 14862867 | 10159112 | 0.000000
09-04-2025 22:09:10000 | -6762730 | 67.6273 | 10270795 | 235905.98 | 167427902 | 98866295 | 50085678 | 0.000000 | 15006067 | 10253142 | 0.000000
09-04-2025 22:09:15000 | -6760816 | 67.6082 | 10319028 | 235870.38 | 167422241 | 98855171 | 50085369 | 0.000000 | 15148661 | 10347130 | 0.000000
09-04-2025 22:09:20000 | -6817738 | 68.1774 | 10314848 | 235805.13 | 168847702 | 98874786 | 50070408 | 0.000000 | 15291676 | 10441594 | 0.000000
09-04-2025 22:09:25000 | -6750530 | 67.5053 | 10273110 | 235824.78 | 167191254 | 98861763 | 50080395 | 0.000000 | 15434534 | 10535546 | 0.000000
09-04-2025 22:09:30000 | -6634016 | 66.3402 | 10179193 | 235897.89 | 164286346 | 98843208 | 50091095 | 0.000000 | 15576545 | 10628322 | 0.000000
09-04-2025 22:09:35000 | -6671904 | 66.719 | 10105788 | 235835.14 | 165226807 | 98872246 | 50095245 | 0.000000 | 15718011 | 10720540 | 0.000000
09-04-2025 22:09:40000 | -6616153 | 66.1615 | 10155382 | 235859.89 | 163871277 | 98842400 | 50094341 | 0.000000 | 15859246 | 10812410 | 0.000000
09-04-2025 22:09:45000 | -6569457 | 65.6946 | 10282983 | 235910.86 | 162752487 | 98797020 | 50112194 | 0.000000 | 16001497 | 10903524 | 0.000000
09-04-2025 22:09:50000 | -6653164 | 66.5316 | 10276095 | 235860.88 | 164809540 | 98828117 | 50078041 | 0.000000 | 16143052 | 10995612 | 0.000000
09-04-2025 22:09:55000 | -6677305 | 66.773 | 10735282 | 235950.03 | 165505692 | 98732132 | 50082981 | 0.000000 | 16289907 | 11088396 | 0.000000
09-04-2025 22:10:00000 | -6675627 | 66.7563 | 10695890 | 235951.23 | 165456268 | 98740623 | 50084667 | 0.000000 | 16438369 | 11181038 | 0.000000
09-04-2025 22:10:05000 | -6682220 | 66.8222 | 10807838 | 235956.09 | 165650024 | 98717117 | 50082176 | 0.000000 | 16588084 | 11273473 | 0.000000
09-04-2025 22:10:10000 | -6830331 | 68.3033 | 10858326 | 235896.83 | 169291550 | 98759850 | 50053677 | 0.000000 | 16738152 | 11367576 | 0.000000
09-04-2025 22:10:15000 | -6866652 | 68.6665 | 10805137 | 235900.69 | 170145676 | 98784470 | 50028320 | 0.000000 | 16888582 | 11462757 | 0.000000
09-04-2025 22:10:20000 | -6804054 | 68.0405 | 10639474 | 235897.02 | 168570038 | 98799400 | 50027988 | 0.000000 | 17037075 | 11557881 | 0.000000
09-04-2025 22:10:25000 | -6783827 | 67.8383 | 10442395 | 235884.00 | 168016312 | 98835915 | 50035698 | 0.000000 | 17182161 | 11651900 | 0.000000
09-04-2025 22:10:30000 | -6795631 | 67.9563 | 10476568 | 235860.67 | 168330078 | 98832413 | 50030975 | 0.000000 | 17327408 | 11746097 | 0.000000
09-04-2025 22:10:35000 | -6717633 | 67.1763 | 10509950 | 235880.64 | 166449417 | 98798141 | 50046402 | 0.000000 | 17474008 | 11839919 | 0.000000
09-04-2025 22:10:40000 | -6717075 | 67.1707 | 10313170 | 236035.42 | 166244156 | 98841766 | 50042294 | 0.000000 | 17617813 | 11933486 | 0.000000
09-04-2025 22:10:45000 | -6737364 | 67.3736 | 10488204 | 236082.30 | 166767700 | 98809898 | 50038109 | 0.000000 | 17762017 | 12027074 | 0.000000
09-04-2025 22:10:50000 | -6845559 | 68.4556 | 10454930 | 235962.95 | 169462067 | 98853760 | 50014572 | 0.000000 | 17906747 | 12121367 | 0.000000
09-04-2025 22:10:55000 | -6937524 | 69.3752 | 10596613 | 235979.03 | 171721832 | 98853493 | 49982441 | 0.000000 | 18052723 | 12217357 | 0.000000
09-04-2025 22:11:00000 | -6966151 | 69.6615 | 10308017 | 235923.38 | 172357224 | 98922859 | 49968952 | 0.000000 | 18198356 | 12313788 | 0.000000
09-04-2025 22:11:05000 | -6966980 | 69.6698 | 10234852 | 235901.81 | 172358810 | 98938103 | 49947960 | 0.000000 | 18341042 | 12410725 | 0.000000
09-04-2025 22:11:10000 | -6938420 | 69.3842 | 10201046 | 235940.66 | 171627731 | 98936432 | 49955494 | 0.000000 | 18483507 | 12507226 | 0.000000
09-04-2025 22:11:15000 | -6760837 | 67.6084 | 10087318 | 236033.14 | 167223358 | 98905182 | 49976650 | 0.000000 | 18624314 | 12602325 | 0.000000
09-04-2025 22:11:20000 | -6624815 | 66.2481 | 98504658 | 235990.56 | 163875183 | 98912560 | 50008522 | 0.000000 | 18762896 | 12694807 | 0.000000
09-04-2025 22:11:25000 | -6688577 | 66.8858 | 97956250 | 235911.30 | 165455566 | 98944527 | 49978004 | 0.000000 | 18898369 | 12787259 | 0.000000
09-04-2025 22:11:30000 | -6747659 | 67.4766 | 10031785 | 235907.59 | 166977798 | 98912842 | 49960751 | 0.000000 | 19036605 | 12880765 | 0.000000
09-04-2025 22:11:35000 | -6755491 | 67.5549 | 10167789 | 235971.72 | 167166077 | 98886200 | 49958961 | 0.000000 | 19177357 | 12974654 | 0.000000
09-04-2025 22:11:40000 | -6784219 | 67.8422 | 10220486 | 235943.28 | 167900116 | 98884171 | 49952805 | 0.000000 | 19318390 | 13068877 | 0.000000
09-04-2025 22:11:45000 | -6753605 | 67.5361 | 10018144 | 235917.69 | 167103943 | 98917625 | 49961815 | 0.000000 | 19458311 | 13162757 | 0.000000
09-04-2025 22:11:50000 | -6686547 | 66.8655 | 96549863 | 235835.00 | 165413315 | 98973541 | 49970051 | 0.000000 | 19595277 | 13256200 | 0.000000
09-04-2025 22:11:55000 | -6729777 | 67.2978 | 97409639 | 235853.48 | 166476044 | 98968636 | 49963749 | 0.000000 | 19729457 | 13349527 | 0.000000
09-04-2025 22:12:00000 | -6744545 | 67.4454 | 97856621 | 235853.66 | 166848816 | 98963776 | 49954174 | 0.000000 | 19865065 | 13443229 | 0.000000
09-04-2025 22:12:05000 | -6814116 | 68.1412 | 97480869 | 235814.72 | 168549423 | 98992172 | 49945171 | 0.000000 | 20000928 | 13537351 | 0.000000
09-04-2025 22:12:10000 | -6815203 | 68.152 | 99297324 | 235866.33 | 168601593 | 98955185 | 49948929 | 0.000000 | 20138063 | 13632024 | 0.000000
09-04-2025 22:12:15000 | -6801722 | 68.0172 | 97520967 | 235824.97 | 168241013 | 98987732 | 49942837 | 0.000000 | 20275146 | 13726746 | 0.000000
09-04-2025 22:12:20000 | -6718019 | 67.1802 | 10505184 | 236149.13 | 166260101 | 98799347 | 49958344 | 0.000000 | 20414989 | 13820415 | 0.000000
09-04-2025 22:12:25000 | -6515452 | 65.1545 | 99225234 | 236024.55 | 161234268 | 98860146 | 49998241 | 0.000000 | 20556423 | 13911854 | 0.000000
09-04-2025 22:12:30000 | -6450079 | 64.5008 | 93800908 | 235887.80 | 159548630 | 98959045 | 50017185 | 0.000000 | 20689377 | 14001671 | 0.000000
09-04-2025 22:12:35000 | -6523598 | 65.236 | 94316709 | 235839.81 | 161382248 | 98970970 | 50009560 | 0.000000 | 20819031 | 14091661 | 0.000000
09-04-2025 22:12:40000 | -6691491 | 66.9149 | 97183525 | 235791.91 | 165582794 | 98961746 | 49985004 | 0.000000 | 20952759 | 14183640 | 0.000000
09-04-2025 22:12:45000 | -6912350 | 69.1235 | 98976055 | 235737.75 | 171037460 | 98990372 | 49940376 | 0.000000 | 21089785 | 14278508 | 0.000000
09-04-2025 22:12:50000 | -6923835 | 69.2383 | 99256221 | 235804.72 | 171275360 | 98988045 | 49937801 | 0.000000 | 21228218 | 14374646 | 0.000000
09-04-2025 22:12:55000 | -6761595 | 67.6159 | 98021563 | 235914.25 | 167223282 | 98965492 | 49962883 | 0.000000 | 21365125 | 14469410 | 0.000000
09-04-2025 22:13:00000 | -6759966 | 67.5997 | 96079775 | 235868.38 | 167149948 | 99004997 | 49950352 | 0.000000 | 21497693 | 14563305 | 0.000000
09-04-2025 22:13:05000 | -6715423 | 67.1542 | 97259053 | 235891.53 | 166095551 | 98967438 | 49955879 | 0.000000 | 21633037 | 14657016 | 0.000000
09-04-2025 22:13:10000 | -6646823 | 66.4682 | 96980068 | 235920.75 | 164405182 | 98952293 | 49971745 | 0.000000 | 21767686 | 14749830 | 0.000000
09-04-2025 22:13:15000 | -6677140 | 66.7714 | 94378037 | 235800.31 | 165138565 | 99015800 | 49975662 | 0.000000 | 21900332 | 14842086 | 0.000000
09-04-2025 22:13:20000 | -6738377 | 67.3838 | 97001367 | 235820.59 | 166693207 | 98979698 | 49950970 | 0.000000 | 22033162 | 14935421 | 0.000000
09-04-2025 22:13:25000 | -6766905 | 67.669 | 99573105 | 235889.92 | 167424240 | 98934654 | 49943775 | 0.000000 | 22169353 | 15029442 | 0.000000
09-04-2025 22:13:30000 | -6734505 | 67.3451 | 96502813 | 235820.83 | 166583511 | 98988861 | 49952721 | 0.000000 | 22305149 | 15123134 | 0.000000
09-04-2025 22:13:35000 | -6725193 | 67.2519 | 95512646 | 235828.27 | 166314255 | 99006493 | 49960541 | 0.000000 | 22438914 | 15216383 | 0.000000
09-04-2025 22:13:40000 | -6700751 | 67.0075 | 97206826 | 235904.22 | 165729248 | 98964081 | 49968727 | 0.000000 | 22572500 | 15309620 | 0.000000
09-04-2025 22:13:45000 | -6737222 | 67.3722 | 98206514 | 235857.98 | 166687134 | 98954231 | 49955482 | 0.000000 | 22708706 | 15402786 | 0.000000
09-04-2025 22:13:50000 | -6898714 | 68.9871 | 98142373 | 235724.33 | 170693634 | 99003181 | 49905952 | 0.000000 | 22845493 | 15497804 | 0.000000
09-04-2025 22:13:55000 | -6923234 | 69.2323 | 99267520 | 235833.08 | 171243149 | 98987648 | 49894764 | 0.000000 | 22982935 | 15594138 | 0.000000
09-04-2025 22:14:00000 | -6801221 | 68.0122 | 97106416 | 235860.47 | 168192352 | 98996048 | 49913052 | 0.000000 | 23119575 | 15689405 | 0.000000
09-04-2025 22:14:05000 | -6693620 | 66.9362 | 94814893 | 235865.50 | 165504684 | 99011620 | 49931995 | 0.000000 | 23252229 | 15782973 | 0.000000
09-04-2025 22:14:10000 | -6681349 | 66.8135 | 93534922 | 235807.66 | 165208298 | 99034256 | 49930435 | 0.000000 | 23382642 | 15875777 | 0.000000
09-04-2025 22:14:15000 | -6663524 | 66.6352 | 94725938 | 235814.00 | 164804306 | 99004646 | 49927048 | 0.000000 | 23515068 | 15968337 | 0.000000
09-04-2025 22:14:20000 | -6723248 | 67.2325 | 95810410 | 235792.00 | 166307953 | 98999809 | 49914791 | 0.000000 | 23647102 | 16061348 | 0.000000
09-04-2025 22:14:25000 | -6722056 | 67.2206 | 96065020 | 235825.00 | 166262222 | 98994217 | 49917038 | 0.000000 | 23780972 | 16155073 | 0.000000
09-04-2025 22:14:30000 | -6608512 | 66.0851 | 94456533 | 235846.53 | 163449631 | 98993919 | 49945980 | 0.000000 | 23913564 | 16247135 | 0.000000
09-04-2025 22:14:35000 | -6592104 | 65.921 | 94526328 | 235854.41 | 163040619 | 98987503 | 49955273 | 0.000000 | 24044182 | 16338433 | 0.000000
09-04-2025 22:14:40000 | -6576913 | 65.7691 | 96730996 | 235894.72 | 162720062 | 98935661 | 49970699 | 0.000000 | 24177783 | 16429867 | 0.000000
09-04-2025 22:14:45000 | -6566177 | 65.6618 | 97566904 | 235912.00 | 162478027 | 98914001 | 49981098 | 0.000000 | 24312021 | 16520957 | 0.000000
09-04-2025 22:14:50000 | -6657805 | 66.5781 | 98638506 | 235881.67 | 164759064 | 98920250 | 49963230 | 0.000000 | 24448206 | 16613039 | 0.000000
09-04-2025 22:14:55000 | -6766680 | 67.6668 | 98553750 | 235811.30 | 167438858 | 98955948 | 49944569 | 0.000000 | 24586313 | 16706629 | 0.000000
09-04-2025 22:15:00000 | -6823147 | 68.2315 | 99713584 | 235855.17 | 168816345 | 98948959 | 49928120 | 0.000000 | 24724368 | 16801387 | 0.000000
09-04-2025 22:15:05000 | -6788702 | 67.887 | 98282148 | 235823.53 | 167960236 | 98968231 | 49927986 | 0.000000 | 13815473 | 94636848 | 0.000000
09-04-2025 22:15:10000 | -6837409 | 68.3741 | 96821982 | 235776.34 | 169117462 | 99012215 | 49905479 | 0.000000 | 27297203 | 189505020 | 0.000000
09-04-2025 22:15:15000 | -6791215 | 67.9121 | 96903115 | 235840.14 | 167955139 | 98997276 | 49907108 | 0.000000 | 40671093 | 284132172 | 0.000000
09-04-2025 22:15:20000 | -6653631 | 66.5363 | 94929414 | 235872.92 | 164531403 | 98997498 | 49931877 | 0.000000 | 53986938 | 377177338 | 0.000000
09-04-2025 22:15:25000 | -6626498 | 66.265 | 94046279 | 235804.59 | 163890732 | 99007835 | 49931946 | 0.000000 | 67078003 | 469251343 | 0.000000
09-04-2025 22:15:30000 | -6633651 | 66.3365 | 95093711 | 235791.64 | 164109421 | 98988098 | 49932430 | 0.000000 | 80267204 | 561619202 | 0.000000
09-04-2025 22:15:35000 | -6559963 | 65.5996 | 94019521 | 235802.16 | 162281204 | 98988480 | 49948254 | 0.000000 | 93485100 | 653087341 | 0.000000
09-04-2025 22:15:40000 | -6595165 | 65.9517 | 94858486 | 235854.80 | 163124359 | 98981415 | 49944431 | 0.000000 | 106521896 | 744220154 | 0.000000
09-04-2025 22:15:45000 | -6689591 | 66.8959 | 96617090 | 235847.02 | 165479828 | 98973053 | 49927498 | 0.000000 | 119785378 | 836462280 | 0.000000
09-04-2025 22:15:50000 | -6738409 | 67.3841 | 98002383 | 235881.44 | 166684814 | 98958870 | 49923786 | 0.000000 | 133346893 | 929903687 | 0.000000
09-04-2025 22:15:55000 | -6767848 | 67.6785 | 97912373 | 235846.86 | 167423325 | 98969635 | 49917793 | 0.000000 | 146980621 | 10234077 | 0.000000
09-04-2025 22:16:00000 | -6787166 | 67.8717 | 99359316 | 235881.16 | 167916183 | 98945374 | 49908924 | 0.000000 | 160661972 | 11178282 | 0.000000
09-04-2025 22:16:05000 | -6767638 | 67.6764 | 96540654 | 235861.88 | 167355988 | 98997810 | 49911575 | 0.000000 | 174227921 | 12119961 | 0.000000
09-04-2025 22:16:10000 | -6737561 | 67.3756 | 96088691 | 235886.19 | 166595779 | 98998283 | 49922432 | 0.000000 | 187556717 | 13058545 | 0.000000
09-04-2025 22:16:15000 | -6637670 | 66.3767 | 94407617 | 235855.55 | 164137009 | 99003624 | 49943260 | 0.000000 | 200764999 | 13984908 | 0.000000
09-04-2025 22:16:20000 | -6636530 | 66.3653 | 92423809 | 235777.28 | 164099884 | 99044144 | 49931484 | 0.000000 | 213658066 | 14905906 | 0.000000
09-04-2025 22:16:25000 | -6809411 | 68.0941 | 95576621 | 235753.67 | 168415100 | 99029282 | 49897129 | 0.000000 | 226733963 | 15842745 | 0.000000
09-04-2025 22:16:30000 | -6891935 | 68.9193 | 96553730 | 235784.17 | 170423950 | 99032860 | 49865726 | 0.000000 | 239997528 | 16799481 | 0.000000
09-04-2025 22:16:35000 | -6786266 | 67.8627 | 94367432 | 235818.36 | 167763397 | 99046967 | 49886936 | 0.000000 | 253212128 | 17750719 | 0.000000
09-04-2025 22:16:40000 | -6633998 | 66.34 | 91146641 | 235819.86 | 163965179 | 99069313 | 49918308 | 0.000000 | 266092529 | 18677416 | 0.000000
09-04-2025 22:16:45000 | -6662178 | 66.6218 | 91852549 | 235816.67 | 164677658 | 99062912 | 49910965 | 0.000000 | 278715057 | 19601984 | 0.000000
09-04-2025 22:16:50000 | -6626396 | 66.264 | 91112490 | 235774.52 | 163814148 | 99067894 | 49912010 | 0.000000 | 291473389 | 20521821 | 0.000000
09-04-2025 22:16:55000 | -6677089 | 66.7709 | 91481279 | 235723.33 | 165088470 | 99074455 | 49899006 | 0.000000 | 304129456 | 21444170 | 0.000000
09-04-2025 22:17:00000 | -6722162 | 67.2216 | 92747754 | 235723.86 | 166223053 | 99061546 | 49883556 | 0.000000 | 317003387 | 22376479 | 0.000000
09-04-2025 22:17:05000 | -6638915 | 66.3892 | 94015684 | 235827.89 | 164176712 | 99012123 | 49909554 | 0.000000 | 330035706 | 23306030 | 0.000000
09-04-2025 22:17:10000 | -6600716 | 66.0072 | 89759521 | 235735.88 | 163166748 | 99088036 | 49913719 | 0.000000 | 342682800 | 24223977 | 0.000000
09-04-2025 22:17:15000 | -6658686 | 66.5869 | 91425889 | 235768.27 | 164605545 | 99070511 | 49908047 | 0.000000 | 355301941 | 25144106 | 0.000000
09-04-2025 22:17:20000 | -6553580 | 65.5358 | 91942578 | 235813.13 | 162046173 | 99030174 | 49926083 | 0.000000 | 368073151 | 26060032 | 0.000000
09-04-2025 22:17:25000 | -6619213 | 66.1921 | 91527783 | 235778.25 | 163648361 | 99057480 | 49926628 | 0.000000 | 380748138 | 26975105 | 0.000000
09-04-2025 22:17:30000 | -6730999 | 67.31 | 93126094 | 235727.72 | 166447647 | 99056435 | 49909248 | 0.000000 | 393555054 | 27901741 | 0.000000
09-04-2025 22:17:35000 | -6786041 | 67.8604 | 92050459 | 235695.30 | 167768280 | 99092499 | 49890839 | 0.000000 | 406422913 | 28841487 | 0.000000
09-04-2025 22:17:40000 | -6778563 | 67.7856 | 93090615 | 235743.39 | 167588928 | 99070145 | 49897816 | 0.000000 | 419415771 | 29784319 | 0.000000
09-04-2025 22:17:45000 | -6812247 | 68.1225 | 91413721 | 235677.03 | 168397644 | 99111626 | 49891541 | 0.000000 | 432220184 | 30728179 | 0.000000
09-04-2025 22:17:50000 | -6856769 | 68.5677 | 91563359 | 235666.95 | 169492889 | 99120140 | 49876312 | 0.000000 | 445000061 | 31681150 | 0.000000
09-04-2025 22:17:55000 | -6796841 | 67.9684 | 90137031 | 235718.72 | 167952133 | 99132080 | 49874447 | 0.000000 | 457581329 | 32630261 | 0.000000
09-04-2025 22:18:00000 | -6781615 | 67.8161 | 88083066 | 235653.00 | 167565140 | 99167015 | 49868927 | 0.000000 | 469986694 | 33572571 | 0.000000
09-04-2025 22:18:05000 | -6804370 | 68.0437 | 89714551 | 235673.11 | 168154968 | 99141968 | 49861450 | 0.000000 | 482326538 | 34517622 | 0.000000
09-04-2025 22:18:10000 | -6772177 | 67.7218 | 88946006 | 235657.63 | 167359451 | 99148483 | 49872265 | 0.000000 | 494749451 | 35458059 | 0.000000
09-04-2025 22:18:15000 | -6753469 | 67.5347 | 88674629 | 235653.73 | 166901291 | 99148972 | 49864449 | 0.000000 | 507015381 | 36400315 | 0.000000
09-04-2025 22:18:20000 | -6711003 | 67.11 | 90905801 | 235776.08 | 165857361 | 99094994 | 49888142 | 0.000000 | 519439819 | 37335457 | 0.000000
09-04-2025 22:18:25000 | -6647876 | 66.4788 | 88948594 | 235730.52 | 164289490 | 99116722 | 49887356 | 0.000000 | 531847046 | 38261328 | 0.000000
09-04-2025 22:18:30000 | -6806588 | 68.0659 | 92131875 | 235703.98 | 168264359 | 99096321 | 49860119 | 0.000000 | 544496826 | 39197942 | 0.000000
09-04-2025 22:18:35000 | -6865605 | 68.656 | 92031650 | 235720.55 | 169685074 | 99113495 | 49848087 | 0.000000 | 557205322 | 40146614 | 0.000000
09-04-2025 22:18:40000 | -6783242 | 67.8324 | 92778730 | 235778.89 | 167667969 | 99077538 | 49858536 | 0.000000 | 570275696 | 41092915 | 0.000000
09-04-2025 22:18:45000 | -6739046 | 67.3905 | 92172988 | 235779.47 | 166577484 | 99077560 | 49872200 | 0.000000 | 583062134 | 42032808 | 0.000000
09-04-2025 22:18:50000 | -6652846 | 66.5285 | 90063828 | 235753.56 | 164432724 | 99096069 | 49884621 | 0.000000 | 595632141 | 42960229 | 0.000000
09-04-2025 22:18:55000 | -6544742 | 65.4474 | 90406387 | 235806.97 | 161783005 | 99059364 | 49903591 | 0.000000 | 608207703 | 43877114 | 0.000000
09-04-2025 22:19:00000 | -6584723 | 65.8472 | 89721836 | 235756.63 | 162764893 | 99084427 | 49906796 | 0.000000 | 620651306 | 44787266 | 0.000000
09-04-2025 22:19:05000 | -6611009 | 66.1101 | 90482480 | 235741.44 | 163442108 | 99076340 | 49906345 | 0.000000 | 633230591 | 45703213 | 0.000000
09-04-2025 22:19:10000 | -6710089 | 67.1009 | 92033262 | 235724.06 | 165907944 | 99072472 | 49890450 | 0.000000 | 645963989 | 46627573 | 0.000000
09-04-2025 22:19:15000 | -6746507 | 67.4651 | 93171494 | 235759.38 | 166808243 | 99059799 | 49875458 | 0.000000 | 658886353 | 47564092 | 0.000000
09-04-2025 22:19:20000 | -6803430 | 68.0343 | 94380635 | 235756.45 | 168224350 | 99051437 | 49861229 | 0.000000 | 671916687 | 48509072 | 0.000000
09-04-2025 22:19:25000 | -6748014 | 67.4801 | 91330674 | 235742.58 | 166796204 | 99096489 | 49867054 | 0.000000 | 684770813 | 49450249 | 0.000000
09-04-2025 22:19:30000 | -6762986 | 67.6299 | 90424775 | 235700.42 | 167157791 | 99117950 | 49860565 | 0.000000 | 697378479 | 50391772 | 0.000000
09-04-2025 22:19:35000 | -6766102 | 67.661 | 92546084 | 235750.56 | 167264374 | 99077499 | 49861855 | 0.000000 | 710079163 | 51331836 | 0.000000
09-04-2025 22:19:40000 | -6774110 | 67.7411 | 90960039 | 235719.80 | 167426880 | 99110512 | 49866383 | 0.000000 | 722798462 | 52269009 | 0.000000
09-04-2025 22:19:45000 | -6901585 | 69.0159 | 91195420 | 235607.33 | 170611115 | 99138260 | 49822845 | 0.000000 | 735361511 | 53219956 | 0.000000
09-04-2025 22:19:50000 | -6898685 | 68.9869 | 91027363 | 235661.83 | 170497589 | 99140678 | 49815353 | 0.000000 | 748021667 | 54180586 | 0.000000
09-04-2025 22:19:55000 | -6697716 | 66.9772 | 90873359 | 235760.91 | 165541016 | 99092087 | 49860554 | 0.000000 | 760692932 | 55123374 | 0.000000
09-04-2025 22:20:00000 | -6635933 | 66.3593 | 86909580 | 235682.08 | 163966965 | 99153244 | 49871555 | 0.000000 | 772929077 | 56044951 | 0.000000
09-04-2025 22:20:05000 | -6640859 | 66.4086 | 88135625 | 235717.73 | 164106537 | 99130775 | 49855434 | 0.000000 | 785053589 | 56968188 | 0.000000
09-04-2025 22:20:10000 | -6613324 | 66.1332 | 90273525 | 235760.05 | 163472855 | 99081177 | 49868160 | 0.000000 | 797554810 | 57889624 | 0.000000
09-04-2025 22:20:15000 | -6577411 | 65.7741 | 90217510 | 235770.56 | 162593857 | 99072388 | 49881142 | 0.000000 | 810097717 | 58803677 | 0.000000
09-04-2025 22:20:20000 | -6552100 | 65.521 | 90693242 | 235787.78 | 161983826 | 99055565 | 49891087 | 0.000000 | 822741821 | 59714951 | 0.000000
09-04-2025 22:20:25000 | -6600780 | 66.0078 | 93338506 | 235781.72 | 163258499 | 99014977 | 49891796 | 0.000000 | 835484558 | 60630742 | 0.000000
09-04-2025 22:20:30000 | -6603475 | 66.0348 | 92306436 | 235755.41 | 163305588 | 99037102 | 49889847 | 0.000000 | 848302673 | 61548232 | 0.000000
09-04-2025 22:20:35000 | -6722297 | 67.223 | 91573184 | 235686.91 | 166211472 | 99084877 | 49869160 | 0.000000 | 861015747 | 62475283 | 0.000000
09-04-2025 22:20:40000 | -6768293 | 67.6829 | 92174805 | 235715.20 | 167330566 | 99085365 | 49858803 | 0.000000 | 873768188 | 63411167 | 0.000000
09-04-2025 22:20:45000 | -6730288 | 67.3029 | 91207510 | 235711.30 | 166377090 | 99094200 | 49870026 | 0.000000 | 886552795 | 64349561 | 0.000000
09-04-2025 22:20:50000 | -6664027 | 66.6403 | 90033203 | 235747.97 | 164705780 | 99099663 | 49895882 | 0.000000 | 899114563 | 65277441 | 0.000000
09-04-2025 22:20:55000 | -6635409 | 66.3541 | 88447744 | 235696.45 | 163994171 | 99123268 | 49884342 | 0.000000 | 911434448 | 66200044 | 0.000000
09-04-2025 22:21:00000 | -6624311 | 66.2431 | 89458594 | 235693.17 | 163761276 | 99100418 | 49888309 | 0.000000 | 923881592 | 67123032 | 0.000000
09-04-2025 22:21:05000 | -6623192 | 66.2319 | 88910996 | 235715.06 | 163699921 | 99110954 | 49888721 | 0.000000 | 936170044 | 68043511 | 0.000000
09-04-2025 22:21:10000 | -6638988 | 66.3899 | 88757109 | 235688.89 | 164095062 | 99118141 | 49887424 | 0.000000 | 948520264 | 68964775 | 0.000000
09-04-2025 22:21:15000 | -6663555 | 66.6355 | 88287803 | 235655.56 | 164707031 | 99133659 | 49875553 | 0.000000 | 960834900 | 69890137 | 0.000000
09-04-2025 22:21:20000 | -6564157 | 65.6416 | 89871162 | 235762.05 | 162266602 | 99075729 | 49903725 | 0.000000 | 973356628 | 70810586 | 0.000000
09-04-2025 22:21:25000 | -6505079 | 65.0508 | 87193838 | 235747.42 | 160755981 | 99113594 | 49915321 | 0.000000 | 985546814 | 71718296 | 0.000000
09-04-2025 22:21:30000 | -6570168 | 65.7017 | 87902861 | 235696.30 | 162394852 | 99116837 | 49918411 | 0.000000 | 997806091 | 72625054 | 0.000000
09-04-2025 22:21:35000 | -6679020 | 66.7902 | 93029688 | 235759.78 | 165159622 | 99043854 | 49901134 | 0.000000 | 10104494 | 73545093 | 0.000000
09-04-2025 22:21:40000 | -6632570 | 66.3257 | 94010459 | 235812.03 | 164031494 | 99010368 | 49911026 | 0.000000 | 10234526 | 74471196 | 0.000000
09-04-2025 22:21:45000 | -6526745 | 65.2674 | 91197764 | 235813.30 | 161368378 | 99037849 | 49935562 | 0.000000 | 10363055 | 75383735 | 0.000000
09-04-2025 22:21:50000 | -6508171 | 65.0817 | 90107637 | 235788.42 | 160902832 | 99055099 | 49951180 | 0.000000 | 10489464 | 76285117 | 0.000000
09-04-2025 22:21:55000 | -6698095 | 66.981 | 93740566 | 235777.72 | 165633667 | 99034843 | 49923561 | 0.000000 | 10616464 | 77205991 | 0.000000
09-04-2025 22:22:00000 | -6726250 | 67.2625 | 93566660 | 235761.20 | 166324524 | 99046288 | 49913162 | 0.000000 | 10746613 | 78139390 | 0.000000
09-04-2025 22:22:05000 | -6640025 | 66.4002 | 92161895 | 235774.77 | 164177155 | 99050461 | 49937767 | 0.000000 | 10876121 | 79064561 | 0.000000
09-04-2025 22:22:10000 | -6626327 | 66.2633 | 90156689 | 235750.61 | 163795837 | 99087059 | 49945198 | 0.000000 | 11002699 | 79986572 | 0.000000
09-04-2025 22:22:15000 | -6639835 | 66.3983 | 90578613 | 235734.05 | 164148468 | 99082306 | 49934978 | 0.000000 | 11128196 | 80906606 | 0.000000
09-04-2025 22:22:20000 | -6702803 | 67.028 | 90608535 | 235705.91 | 165694550 | 99098656 | 49916843 | 0.000000 | 11253198 | 81834287 | 0.000000
09-04-2025 22:22:25000 | -6711979 | 67.1198 | 90984434 | 235717.28 | 165921570 | 99093712 | 49925385 | 0.000000 | 11380178 | 82769248 | 0.000000
09-04-2025 22:22:30000 | -6747905 | 67.4791 | 89475449 | 235671.27 | 166779510 | 99132324 | 49915607 | 0.000000 | 11505303 | 83702080 | 0.000000
09-04-2025 22:22:35000 | -6765514 | 67.6551 | 92927334 | 235783.84 | 167237381 | 99069832 | 49915386 | 0.000000 | 11631721 | 84642119 | 0.000000
09-04-2025 22:22:40000 | -6666797 | 66.668 | 90119912 | 235727.81 | 164788437 | 99098686 | 49932919 | 0.000000 | 11758829 | 85572666 | 0.000000
09-04-2025 22:22:45000 | -6625870 | 66.2587 | 89770762 | 235753.39 | 163765427 | 99094635 | 49941006 | 0.000000 | 11883308 | 86495186 | 0.000000
09-04-2025 22:22:50000 | -6533949 | 65.3395 | 89220625 | 235778.16 | 161500031 | 99080551 | 49962101 | 0.000000 | 12008018 | 87406943 | 0.000000
09-04-2025 22:22:55000 | -6545525 | 65.4553 | 88493770 | 235709.73 | 161807922 | 99098427 | 49949364 | 0.000000 | 12131877 | 88316963 | 0.000000
09-04-2025 22:23:00000 | -6680034 | 66.8003 | 91285781 | 235722.42 | 165154358 | 99079155 | 49931580 | 0.000000 | 12257103 | 89237773 | 0.000000
09-04-2025 22:23:05000 | -6653942 | 66.5394 | 94180859 | 235844.47 | 164531693 | 99013107 | 49942272 | 0.000000 | 12386683 | 90163770 | 0.000000
09-04-2025 22:23:10000 | -6605545 | 66.0554 | 92272412 | 235807.30 | 163319244 | 99038391 | 49961514 | 0.000000 | 12515342 | 91081650 | 0.000000
09-04-2025 22:23:15000 | -6574116 | 65.7412 | 90223350 | 235736.58 | 162537460 | 99071350 | 49958702 | 0.000000 | 12641816 | 91995137 | 0.000000
09-04-2025 22:23:20000 | -6601849 | 66.0185 | 91335557 | 235751.98 | 163237625 | 99056511 | 49947739 | 0.000000 | 12767610 | 92912988 | 0.000000
09-04-2025 22:23:25000 | -6544411 | 65.4441 | 91930977 | 235822.14 | 161815094 | 99027740 | 49959183 | 0.000000 | 12894653 | 93828848 | 0.000000
09-04-2025 22:23:30000 | -6600574 | 66.0057 | 90410088 | 235740.31 | 163183350 | 99074913 | 49960434 | 0.000000 | 13020240 | 94740020 | 0.000000
09-04-2025 22:23:35000 | -6630225 | 66.3023 | 91895273 | 235738.11 | 163951996 | 99053116 | 49970795 | 0.000000 | 13147720 | 95660205 | 0.000000
09-04-2025 22:23:40000 | -6652095 | 66.5209 | 89742402 | 235714.92 | 164429031 | 99102219 | 49962521 | 0.000000 | 13273602 | 96582559 | 0.000000
09-04-2025 22:23:45000 | -6656202 | 66.562 | 91533408 | 235732.77 | 164575577 | 99067673 | 49955730 | 0.000000 | 13400541 | 97506680 | 0.000000
09-04-2025 22:23:50000 | -6722030 | 67.2203 | 90929355 | 235699.42 | 166176773 | 99097458 | 49939907 | 0.000000 | 13526703 | 98437959 | 0.000000
09-04-2025 22:23:55000 | -6637911 | 66.3791 | 90095859 | 235754.00 | 164070358 | 99091415 | 49966160 | 0.000000 | 13653345 | 99365273 | 0.000000
09-04-2025 22:24:00000 | -6655998 | 66.56 | 88098086 | 235666.47 | 164504578 | 99135399 | 49967487 | 0.000000 | 13776669 | 10028721 | 0.000000
09-04-2025 22:24:05000 | -6681810 | 66.8181 | 88932939 | 235673.58 | 165153915 | 99125854 | 49954002 | 0.000000 | 13900081 | 10121352 | 0.000000
09-04-2025 22:24:10000 | -6707991 | 67.0799 | 90593184 | 235710.50 | 165820297 | 99100327 | 49947960 | 0.000000 | 14024695 | 10214571 | 0.000000
09-04-2025 22:24:15000 | -6658995 | 66.59 | 89824473 | 235729.55 | 164591797 | 99102440 | 49954784 | 0.000000 | 14150100 | 10307488 | 0.000000
09-04-2025 22:24:20000 | -6646499 | 66.465 | 89518057 | 235702.77 | 164293884 | 99105164 | 49964970 | 0.000000 | 14275403 | 10399828 | 0.000000
09-04-2025 22:24:25000 | -6679848 | 66.7985 | 89864453 | 235697.69 | 165118530 | 99107178 | 49963223 | 0.000000 | 14399508 | 10492230 | 0.000000
09-04-2025 22:24:30000 | -6653346 | 66.5335 | 90671475 | 235762.05 | 164457504 | 99084129 | 49964024 | 0.000000 | 14524866 | 10584981 | 0.000000
09-04-2025 22:24:35000 | -6596231 | 65.9623 | 89775371 | 235753.17 | 163046021 | 99086494 | 49976616 | 0.000000 | 14650668 | 10676849 | 0.000000
09-04-2025 22:24:40000 | -6659045 | 66.5905 | 88884648 | 235656.13 | 164609512 | 99120888 | 49961494 | 0.000000 | 14774520 | 10768543 | 0.000000
09-04-2025 22:24:45000 | -6663202 | 66.632 | 90499395 | 235716.25 | 164721176 | 99090218 | 49949177 | 0.000000 | 14899587 | 10861018 | 0.000000
09-04-2025 22:24:50000 | -6782955 | 67.8295 | 88644746 | 235599.33 | 167653107 | 99156822 | 49937336 | 0.000000 | 15024246 | 10954521 | 0.000000
09-04-2025 22:24:55000 | -6758501 | 67.585 | 89771641 | 235695.78 | 167027908 | 99129341 | 49937469 | 0.000000 | 15148740 | 11048742 | 0.000000
09-04-2025 22:25:00000 | -6621409 | 66.2141 | 89113926 | 235792.88 | 163616333 | 99106468 | 49974888 | 0.000000 | 15273245 | 11141676 | 0.000000
09-04-2025 22:25:05000 | -6474736 | 64.7474 | 87789512 | 235789.02 | 160008575 | 99093277 | 50015823 | 0.000000 | 15395621 | 11231874 | 0.000000
09-04-2025 22:25:10000 | -6610468 | 66.1047 | 89184814 | 235700.84 | 163408691 | 99102142 | 49991676 | 0.000000 | 15516971 | 11322664 | 0.000000
09-04-2025 22:25:15000 | -6675104 | 66.751 | 90924268 | 235718.45 | 165027298 | 99084999 | 49985325 | 0.000000 | 15642581 | 11415016 | 0.000000
09-04-2025 22:25:20000 | -6678527 | 66.7853 | 92296865 | 235755.95 | 165126282 | 99058510 | 49979401 | 0.000000 | 15770217 | 11507661 | 0.000000
09-04-2025 22:25:25000 | -6737265 | 67.3726 | 92680000 | 235717.78 | 166592911 | 99067039 | 49963539 | 0.000000 | 15897954 | 11601320 | 0.000000
09-04-2025 22:25:30000 | -6665555 | 66.6556 | 92424707 | 235813.16 | 164778320 | 99052315 | 50000061 | 0.000000 | 16027266 | 11694094 | 0.000000
09-04-2025 22:25:35000 | -6528783 | 65.2878 | 90824629 | 235828.08 | 161397034 | 99046181 | 50018509 | 0.000000 | 16153661 | 11785313 | 0.000000
09-04-2025 22:25:40000 | -6497948 | 64.9795 | 91489531 | 235821.55 | 160673218 | 99023300 | 50039570 | 0.000000 | 16280437 | 11875776 | 0.000000
09-04-2025 22:25:45000 | -6522823 | 65.2282 | 93144063 | 235880.53 | 161292572 | 98995781 | 50038807 | 0.000000 | 16407441 | 11966466 | 0.000000
09-04-2025 22:25:50000 | -6614697 | 66.147 | 94241680 | 235821.33 | 163600220 | 99000267 | 50044399 | 0.000000 | 16537755 | 12057767 | 0.000000
09-04-2025 22:25:55000 | -6728058 | 67.2806 | 93947588 | 235745.84 | 166394806 | 99039124 | 50019390 | 0.000000 | 16668110 | 12150220 | 0.000000
09-04-2025 22:26:00000 | -6833040 | 68.3304 | 96220342 | 235788.42 | 168982574 | 99023041 | 49997627 | 0.000000 | 16800350 | 12244835 | 0.000000
09-04-2025 22:26:05000 | -6689600 | 66.896 | 95082725 | 235862.28 | 165416458 | 99004929 | 50037277 | 0.000000 | 16934427 | 12338734 | 0.000000
09-04-2025 22:26:10000 | -6584077 | 65.8408 | 90168652 | 235791.02 | 162738571 | 99075226 | 50054951 | 0.000000 | 17061788 | 12430541 | 0.000000
09-04-2025 22:26:15000 | -6611698 | 66.117 | 91562051 | 235798.42 | 163450882 | 99054672 | 50039116 | 0.000000 | 17187120 | 12522172 | 0.000000
09-04-2025 22:26:20000 | -6657316 | 66.5732 | 93293994 | 235803.70 | 164613525 | 99032303 | 50036228 | 0.000000 | 17316986 | 12614210 | 0.000000
09-04-2025 22:26:25000 | -6725079 | 67.2508 | 91772900 | 235706.72 | 166271744 | 99081688 | 50022434 | 0.000000 | 17446743 | 12706943 | 0.000000
09-04-2025 22:26:30000 | -6637959 | 66.3796 | 92957725 | 235822.30 | 164123291 | 99033638 | 50041096 | 0.000000 | 17576061 | 12799661 | 0.000000
09-04-2025 22:26:35000 | -6598192 | 65.9819 | 91397715 | 235791.28 | 163125885 | 99054207 | 50045891 | 0.000000 | 17703633 | 12891404 | 0.000000
09-04-2025 22:26:40000 | -6598495 | 65.9849 | 93352852 | 235832.45 | 163170486 | 99014008 | 50046352 | 0.000000 | 17832548 | 12982906 | 0.000000
09-04-2025 22:26:45000 | -6547115 | 65.4711 | 95235625 | 235907.50 | 161936401 | 98958542 | 50055714 | 0.000000 | 17964237 | 13074111 | 0.000000
09-04-2025 22:26:50000 | -6421348 | 64.2135 | 95207744 | 235976.20 | 158845688 | 98918633 | 50091179 | 0.000000 | 18096659 | 13164028 | 0.000000
09-04-2025 22:26:55000 | -6478404 | 64.784 | 93764375 | 235866.33 | 160247559 | 98968781 | 50084629 | 0.000000 | 18226561 | 13253744 | 0.000000
09-04-2025 22:27:00000 | -6589364 | 65.8936 | 97241367 | 235892.16 | 163043976 | 98928574 | 50080067 | 0.000000 | 18360117 | 13344933 | 0.000000
09-04-2025 22:27:05000 | -6614020 | 66.1402 | 95961406 | 235846.88 | 163628265 | 98963806 | 50074852 | 0.000000 | 18494692 | 13436223 | 0.000000
09-04-2025 22:27:10000 | -6725234 | 67.2523 | 97883877 | 235851.31 | 166382034 | 98957336 | 50063015 | 0.000000 | 18630081 | 13529050 | 0.000000
09-04-2025 22:27:15000 | -6739023 | 67.3902 | 97087441 | 235842.98 | 166695969 | 98978104 | 50059860 | 0.000000 | 18766193 | 13622486 | 0.000000
09-04-2025 22:27:20000 | -6658438 | 66.5844 | 99563203 | 235986.02 | 164734116 | 98900452 | 50071579 | 0.000000 | 18903064 | 13715750 | 0.000000
09-04-2025 22:27:25000 | -6597127 | 65.9713 | 97719521 | 235949.45 | 163211838 | 98920685 | 50098618 | 0.000000 | 19040011 | 13807558 | 0.000000
09-04-2025 22:27:30000 | -6538840 | 65.3884 | 96535400 | 235958.19 | 161749390 | 98927711 | 50097240 | 0.000000 | 19174496 | 13898761 | 0.000000
09-04-2025 22:27:35000 | -6530242 | 65.3024 | 98532285 | 235977.25 | 161603867 | 98880745 | 50110210 | 0.000000 | 19309767 | 13989736 | 0.000000
09-04-2025 22:27:40000 | -6553282 | 65.5328 | 98761348 | 235994.59 | 162153961 | 98883385 | 50118515 | 0.000000 | 19446255 | 14080927 | 0.000000
09-04-2025 22:27:45000 | -6731545 | 67.3154 | 99587402 | 235885.92 | 166574203 | 98923309 | 50091869 | 0.000000 | 19583678 | 14173464 | 0.000000
09-04-2025 22:27:50000 | -6736549 | 67.3655 | 10279338 | 235992.97 | 166732895 | 98855751 | 50089386 | 0.000000 | 19725103 | 14267162 | 0.000000
09-04-2025 22:27:55000 | -6775166 | 67.7517 | 98802861 | 235872.66 | 167608948 | 98953331 | 50091343 | 0.000000 | 19865048 | 14361044 | 0.000000
09-04-2025 22:28:00000 | -6714839 | 67.1484 | 99883340 | 235994.72 | 166104370 | 98911697 | 50095390 | 0.000000 | 20002902 | 14454875 | 0.000000
09-04-2025 22:28:05000 | -6696928 | 66.9693 | 10225998 | 236061.66 | 165708450 | 98854179 | 50110168 | 0.000000 | 20144065 | 14548239 | 0.000000
09-04-2025 22:28:10000 | -6588452 | 65.8845 | 10069818 | 236070.14 | 163023941 | 98852066 | 50131546 | 0.000000 | 20284836 | 14640301 | 0.000000
09-04-2025 22:28:15000 | -6669041 | 66.6904 | 98474736 | 235918.97 | 165003250 | 98927345 | 50108707 | 0.000000 | 20421810 | 14732266 | 0.000000
09-04-2025 22:28:20000 | -6755359 | 67.5536 | 10136562 | 235937.02 | 167181396 | 98892876 | 50085487 | 0.000000 | 20561262 | 14825426 | 0.000000
09-04-2025 22:28:25000 | -6836668 | 68.3667 | 10193546 | 235929.03 | 169173157 | 98906639 | 50071751 | 0.000000 | 20701960 | 14919952 | 0.000000
09-04-2025 22:28:30000 | -6716446 | 67.1645 | 99498301 | 235972.14 | 166142258 | 98920448 | 50082695 | 0.000000 | 20840999 | 15013947 | 0.000000
09-04-2025 22:28:35000 | -6632648 | 66.3265 | 98409873 | 235961.22 | 164083603 | 98917137 | 50105003 | 0.000000 | 20978076 | 15106472 | 0.000000
09-04-2025 22:28:40000 | -6487046 | 64.8705 | 98278711 | 236053.75 | 160493164 | 98871773 | 50138821 | 0.000000 | 21115554 | 15197334 | 0.000000
09-04-2025 22:28:45000 | -6453477 | 64.5348 | 98082129 | 235999.64 | 159709412 | 98864685 | 50146404 | 0.000000 | 21251074 | 15287132 | 0.000000
09-04-2025 22:28:50000 | -6510667 | 65.1067 | 10088921 | 236033.36 | 161175827 | 98820572 | 50149815 | 0.000000 | 21389031 | 15377310 | 0.000000
09-04-2025 22:28:55000 | -6553492 | 65.5349 | 10156038 | 236039.95 | 162233810 | 98820396 | 50156647 | 0.000000 | 21529731 | 15467903 | 0.000000
09-04-2025 22:29:00000 | -6604148 | 66.0415 | 10316356 | 236057.14 | 163504013 | 98801804 | 50158913 | 0.000000 | 21672891 | 15559265 | 0.000000
09-04-2025 22:29:05000 | -6550424 | 65.5042 | 10339992 | 236083.19 | 162196075 | 98776939 | 50173115 | 0.000000 | 21817144 | 15650762 | 0.000000
09-04-2025 22:29:10000 | -6613477 | 66.1348 | 10131656 | 235983.88 | 163711548 | 98846794 | 50166706 | 0.000000 | 21958303 | 15742162 | 0.000000
09-04-2025 22:29:15000 | -6766920 | 67.6692 | 10079341 | 235943.09 | 167433945 | 98908813 | 50138966 | 0.000000 | 22097932 | 15834980 | 0.000000
09-04-2025 22:29:20000 | -6733538 | 67.3354 | 10273801 | 236013.28 | 166648224 | 98855957 | 50140148 | 0.000000 | 22240454 | 15928797 | 0.000000
09-04-2025 22:29:25000 | -6729000 | 67.29 | 10351537 | 236028.44 | 166553772 | 98837341 | 50141941 | 0.000000 | 22383545 | 16022546 | 0.000000
09-04-2025 22:29:30000 | -6761651 | 67.6165 | 10357431 | 236033.11 | 167340393 | 98847061 | 50141624 | 0.000000 | 22526997 | 16116393 | 0.000000
09-04-2025 22:29:35000 | -6750509 | 67.5051 | 10099575 | 235968.44 | 167022293 | 98899254 | 50145264 | 0.000000 | 22668867 | 16209946 | 0.000000
09-04-2025 22:29:40000 | -6803691 | 68.0369 | 99792988 | 235909.83 | 168308395 | 98941376 | 50132954 | 0.000000 | 22808291 | 16303782 | 0.000000
09-04-2025 22:29:45000 | -6765499 | 67.655 | 10243021 | 236008.31 | 167410461 | 98873222 | 50132168 | 0.000000 | 22948909 | 16398500 | 0.000000
09-04-2025 22:29:50000 | -6662101 | 66.621 | 99946377 | 236027.58 | 164812973 | 98893311 | 50156738 | 0.000000 | 23088535 | 16491662 | 0.000000
09-04-2025 22:29:55000 | -6585427 | 65.8543 | 99005537 | 236041.02 | 162913040 | 98888695 | 50174129 | 0.000000 | 23226589 | 16583420 | 0.000000
09-04-2025 22:30:00000 | -6633436 | 66.3344 | 98781250 | 235943.67 | 164130737 | 98909332 | 50168095 | 0.000000 | 23363916 | 16674906 | 0.000000
09-04-2025 22:30:05000 | -6596161 | 65.9616 | 10104094 | 236043.31 | 163239319 | 98847023 | 50176552 | 0.000000 | 13978926 | 91746689 | 0.000000
09-04-2025 22:30:10000 | -6512212 | 65.1221 | 10100813 | 236055.94 | 161200989 | 98818390 | 50186138 | 0.000000 | 28006609 | 182862488 | 0.000000
09-04-2025 22:30:15000 | -6588778 | 65.8878 | 10175150 | 236046.36 | 163088577 | 98828461 | 50191872 | 0.000000 | 42053379 | 274095154 | 0.000000
09-04-2025 22:30:20000 | -6509588 | 65.0959 | 10259601 | 236088.05 | 161180283 | 98780663 | 50215977 | 0.000000 | 56353016 | 365112366 | 0.000000
09-04-2025 22:30:25000 | -6630190 | 66.3019 | 10264413 | 236016.73 | 164143951 | 98822762 | 50195232 | 0.000000 | 70594299 | 456669159 | 0.000000
09-04-2025 22:30:30000 | -6711931 | 67.1193 | 10478979 | 236043.84 | 166179855 | 98803093 | 50178333 | 0.000000 | 85073112 | 549703125 | 0.000000
09-04-2025 22:30:35000 | -6720272 | 67.2027 | 10437108 | 236029.73 | 166372772 | 98815361 | 50182579 | 0.000000 | 99621140 | 643239868 | 0.000000
09-04-2025 22:30:40000 | -6710792 | 67.1079 | 10325156 | 236039.41 | 166095673 | 98836983 | 50184700 | 0.000000 | 113984940 | 736722412 | 0.000000
09-04-2025 22:30:45000 | -6697892 | 66.9789 | 10294349 | 236020.91 | 165785309 | 98839409 | 50192181 | 0.000000 | 128279663 | 829812256 | 0.000000
09-04-2025 22:30:50000 | -6795774 | 67.9577 | 10264328 | 235956.55 | 168189163 | 98878502 | 50168503 | 0.000000 | 142473846 | 923544495 | 0.000000
09-04-2025 22:30:55000 | -6853280 | 68.5328 | 10500429 | 236040.42 | 169609222 | 98846489 | 50159794 | 0.000000 | 156806793 | 10184930 | 0.000000
09-04-2025 22:31:00000 | -6750352 | 67.5035 | 10104073 | 235978.70 | 167015076 | 98898239 | 50171993 | 0.000000 | 171162415 | 11127135 | 0.000000
09-04-2025 22:31:05000 | -6680133 | 66.8013 | 10167171 | 236058.69 | 165286545 | 98861496 | 50178513 | 0.000000 | 185223099 | 12060006 | 0.000000
09-04-2025 22:31:10000 | -6549936 | 65.4994 | 10222702 | 236100.02 | 162127090 | 98803864 | 50207439 | 0.000000 | 199475937 | 12977271 | 0.000000
09-04-2025 22:31:15000 | -6514229 | 65.1423 | 10142272 | 236051.63 | 161268936 | 98809570 | 50210724 | 0.000000 | 213608719 | 13883235 | 0.000000
09-04-2025 22:31:20000 | -6734280 | 67.3428 | 10284063 | 235941.63 | 166732651 | 98853958 | 50170090 | 0.000000 | 227797272 | 14805884 | 0.000000
09-04-2025 22:31:25000 | -6823449 | 68.2345 | 10688990 | 235959.45 | 169012161 | 98795158 | 50146233 | 0.000000 | 242506149 | 15751053 | 0.000000
09-04-2025 22:31:30000 | -6792062 | 67.9206 | 10549913 | 235978.84 | 168189606 | 98815071 | 50146065 | 0.000000 | 257228119 | 16697683 | 0.000000
09-04-2025 22:31:35000 | -6698059 | 66.9806 | 10338986 | 236051.08 | 165786102 | 98829559 | 50168198 | 0.000000 | 271656036 | 17632256 | 0.000000
09-04-2025 22:31:40000 | -6619674 | 66.1967 | 10069154 | 235960.06 | 163854080 | 98862831 | 50181927 | 0.000000 | 285779968 | 18553839 | 0.000000
09-04-2025 22:31:45000 | -6579657 | 65.7966 | 10227001 | 236032.08 | 162903427 | 98813477 | 50200424 | 0.000000 | 299797852 | 19466636 | 0.000000
09-04-2025 22:31:50000 | -6548563 | 65.4856 | 10102002 | 235933.31 | 162171814 | 98830971 | 50210400 | 0.000000 | 314014465 | 20372733 | 0.000000
09-04-2025 22:31:55000 | -6742932 | 67.4293 | 10367818 | 235936.03 | 166965622 | 98838478 | 50171303 | 0.000000 | 328250977 | 21295676 | 0.000000
09-04-2025 22:32:00000 | -6851101 | 68.511 | 10690021 | 235984.97 | 169670654 | 98804459 | 50155159 | 0.000000 | 342889618 | 22239355 | 0.000000
09-04-2025 22:32:05000 | -6800120 | 68.0012 | 10540840 | 236010.47 | 168359009 | 98819824 | 50151520 | 0.000000 | 357606689 | 23188882 | 0.000000
09-04-2025 22:32:10000 | -6686827 | 66.8683 | 10126759 | 235960.89 | 165499451 | 98872604 | 50165985 | 0.000000 | 371913879 | 24125674 | 0.000000
09-04-2025 22:32:15000 | -6525009 | 65.2501 | 10093798 | 236032.78 | 161526474 | 98824547 | 50203205 | 0.000000 | 385992218 | 25041323 | 0.000000
09-04-2025 22:32:20000 | -6570132 | 65.7013 | 10212865 | 236019.95 | 162669022 | 98813324 | 50199657 | 0.000000 | 399901794 | 25950161 | 0.000000
09-04-2025 22:32:25000 | -6667589 | 66.6759 | 10438381 | 235983.14 | 165137466 | 98796616 | 50183826 | 0.000000 | 414260315 | 26870862 | 0.000000
09-04-2025 22:32:30000 | -6846411 | 68.4641 | 10488365 | 235903.17 | 169533493 | 98846825 | 50148685 | 0.000000 | 428789490 | 27811572 | 0.000000
09-04-2025 22:32:35000 | -6866397 | 68.664 | 10470904 | 235926.11 | 169996368 | 98857162 | 50135651 | 0.000000 | 443428650 | 28763679 | 0.000000
09-04-2025 22:32:40000 | -6789184 | 67.8918 | 10414148 | 236044.11 | 168020706 | 98843887 | 50142891 | 0.000000 | 457854187 | 29712417 | 0.000000
09-04-2025 22:32:45000 | -6713066 | 67.1307 | 10116742 | 235986.03 | 166111359 | 98883423 | 50156326 | 0.000000 | 472159454 | 30648152 | 0.000000
09-04-2025 22:32:50000 | -6673774 | 66.7377 | 10270419 | 236074.80 | 165157898 | 98836487 | 50162960 | 0.000000 | 486271576 | 31578486 | 0.000000
09-04-2025 22:32:55000 | -6567359 | 65.6736 | 10014852 | 236034.13 | 162519882 | 98857170 | 50182827 | 0.000000 | 500322662 | 32494155 | 0.000000
09-04-2025 22:33:00000 | -6575385 | 65.7538 | 10068288 | 236041.08 | 162727203 | 98847916 | 50186478 | 0.000000 | 514245117 | 33404016 | 0.000000
09-04-2025 22:33:05000 | -6582530 | 65.8253 | 10268320 | 236057.34 | 162961502 | 98805069 | 50187523 | 0.000000 | 528433044 | 34319009 | 0.000000
09-04-2025 22:33:10000 | -6621685 | 66.2168 | 10264859 | 236059.19 | 163907730 | 98819687 | 50183067 | 0.000000 | 542733398 | 35233777 | 0.000000
09-04-2025 22:33:15000 | -6713826 | 67.1383 | 10365320 | 235998.02 | 166215195 | 98829109 | 50163136 | 0.000000 | 557038147 | 36159763 | 0.000000
09-04-2025 22:33:20000 | -6746187 | 67.4619 | 10499493 | 236043.95 | 167021332 | 98810440 | 50164604 | 0.000000 | 571645325 | 37098523 | 0.000000
09-04-2025 22:33:25000 | -6698677 | 66.9868 | 10393833 | 236067.03 | 165808563 | 98817535 | 50171246 | 0.000000 | 586024475 | 38030872 | 0.000000
09-04-2025 22:33:30000 | -6613638 | 66.1364 | 10366575 | 236084.23 | 163734848 | 98793724 | 50186478 | 0.000000 | 600310608 | 38954717 | 0.000000
09-04-2025 22:33:35000 | -6614177 | 66.1418 | 10391759 | 236079.44 | 163757935 | 98788155 | 50189903 | 0.000000 | 614600830 | 39873748 | 0.000000
09-04-2025 22:33:40000 | -6630668 | 66.3067 | 10236396 | 236012.64 | 164144669 | 98829231 | 50182159 | 0.000000 | 628828186 | 40792820 | 0.000000
09-04-2025 22:33:45000 | -6640198 | 66.402 | 10317458 | 236042.91 | 164397919 | 98814301 | 50184292 | 0.000000 | 643139709 | 41715317 | 0.000000
09-04-2025 22:33:50000 | -6691260 | 66.9126 | 10295215 | 236004.19 | 165647385 | 98836952 | 50173492 | 0.000000 | 657452148 | 42638589 | 0.000000
09-04-2025 22:33:55000 | -6732325 | 67.3233 | 10415632 | 235918.08 | 166739731 | 98824295 | 50162296 | 0.000000 | 671829529 | 43569766 | 0.000000
09-04-2025 22:34:00000 | -6783987 | 67.8399 | 10213648 | 235860.36 | 167952499 | 98885567 | 50152836 | 0.000000 | 686147339 | 44508735 | 0.000000
09-04-2025 22:34:05000 | -6849886 | 68.4989 | 10159821 | 235838.39 | 169547485 | 98917870 | 50129597 | 0.000000 | 700295105 | 45458818 | 0.000000
09-04-2025 22:34:10000 | -6865161 | 68.6516 | 10263585 | 235926.47 | 169886826 | 98900841 | 50124973 | 0.000000 | 714569092 | 46411724 | 0.000000
09-04-2025 22:34:15000 | -6755016 | 67.5502 | 10344882 | 236024.42 | 167188538 | 98847580 | 50133816 | 0.000000 | 728983093 | 47355708 | 0.000000
09-04-2025 22:34:20000 | -6657673 | 66.5767 | 10109013 | 235992.31 | 164764175 | 98866791 | 50154980 | 0.000000 | 743168579 | 48287212 | 0.000000
09-04-2025 22:34:25000 | -6657284 | 66.5728 | 10154504 | 236031.36 | 164744705 | 98856613 | 50157616 | 0.000000 | 757204590 | 49208105 | 0.000000
09-04-2025 22:34:30000 | -6656338 | 66.5634 | 10167054 | 235997.91 | 164751221 | 98853508 | 50147842 | 0.000000 | 771290466 | 50131978 | 0.000000
09-04-2025 22:34:35000 | -6637184 | 66.3718 | 10137876 | 236018.56 | 164264313 | 98853493 | 50161434 | 0.000000 | 785360474 | 51052773 | 0.000000
09-04-2025 22:34:40000 | -6623445 | 66.2344 | 10027654 | 235948.39 | 163936829 | 98873291 | 50150860 | 0.000000 | 799368835 | 51973374 | 0.000000
09-04-2025 22:34:45000 | -6574508 | 65.7451 | 10264993 | 236049.08 | 162774017 | 98802963 | 50163971 | 0.000000 | 813538147 | 52892915 | 0.000000
09-04-2025 22:34:50000 | -6661806 | 66.6181 | 10190494 | 235962.19 | 164923767 | 98850166 | 50158737 | 0.000000 | 827638489 | 53808203 | 0.000000
09-04-2025 22:34:55000 | -6841989 | 68.4199 | 10638883 | 235953.95 | 169445663 | 98812569 | 50113880 | 0.000000 | 842052307 | 54746060 | 0.000000
09-04-2025 22:35:00000 | -6864183 | 68.6418 | 10844313 | 235912.47 | 170093338 | 98774940 | 50102245 | 0.000000 | 857053284 | 55703936 | 0.000000
09-04-2025 22:35:05000 | -6793106 | 67.9311 | 10529904 | 235985.05 | 168204010 | 98819839 | 50109966 | 0.000000 | 871755249 | 56653096 | 0.000000
09-04-2025 22:35:10000 | -6713505 | 67.1351 | 10202462 | 235948.23 | 166183517 | 98864891 | 50125050 | 0.000000 | 886114197 | 57589473 | 0.000000
09-04-2025 22:35:15000 | -6724618 | 67.2462 | 10317205 | 235940.97 | 166497543 | 98843430 | 50122540 | 0.000000 | 900326782 | 58523740 | 0.000000
09-04-2025 22:35:20000 | -6664684 | 66.6468 | 10342004 | 236066.98 | 164967606 | 98817337 | 50132751 | 0.000000 | 914630005 | 59453340 | 0.000000
09-04-2025 22:35:25000 | -6644691 | 66.4469 | 10251049 | 236008.66 | 164493301 | 98830803 | 50134560 | 0.000000 | 928878723 | 60378096 | 0.000000
09-04-2025 22:35:30000 | -6672291 | 66.7229 | 10179025 | 235924.52 | 165200424 | 98856247 | 50121948 | 0.000000 | 943027832 | 61304956 | 0.000000
09-04-2025 22:35:35000 | -6745157 | 67.4516 | 10313902 | 235984.41 | 166960632 | 98851059 | 50112717 | 0.000000 | 957311157 | 62240596 | 0.000000
09-04-2025 22:35:40000 | -6970801 | 69.708 | 10057976 | 235762.58 | 172496201 | 98975037 | 50064438 | 0.000000 | 971381042 | 63194941 | 0.000000
09-04-2025 22:35:45000 | -7013048 | 70.1305 | 10202913 | 235841.03 | 173510574 | 98958221 | 50034809 | 0.000000 | 985533936 | 64165488 | 0.000000
09-04-2025 22:35:50000 | -7024721 | 70.2472 | 97967578 | 235723.86 | 173741730 | 99041489 | 50023888 | 0.000000 | 999428284 | 65139600 | 0.000000
09-04-2025 22:35:55000 | -6973034 | 69.7303 | 95878379 | 235735.75 | 172404449 | 99067902 | 50021347 | 0.000000 | 10128401 | 66113047 | 0.000000
09-04-2025 22:36:00000 | -6832303 | 68.323 | 95010195 | 235793.20 | 168923279 | 99046913 | 50040573 | 0.000000 | 10260211 | 67071528 | 0.000000
09-04-2025 22:36:05000 | -6782467 | 67.8247 | 91152861 | 235683.53 | 167670563 | 99108955 | 50055847 | 0.000000 | 10389567 | 68013345 | 0.000000
09-04-2025 22:36:10000 | -6730152 | 67.3015 | 89822031 | 235665.63 | 166360855 | 99121117 | 50046402 | 0.000000 | 10514493 | 68949604 | 0.000000
09-04-2025 22:36:15000 | -6777141 | 67.7714 | 91676182 | 235606.63 | 167619049 | 99097435 | 50030666 | 0.000000 | 10640673 | 69888223 | 0.000000
09-04-2025 22:36:20000 | -6904273 | 69.0427 | 92449619 | 235587.28 | 170733551 | 99115387 | 49999004 | 0.000000 | 10767200 | 70841138 | 0.000000
09-04-2025 22:36:25000 | -6837291 | 68.3729 | 91966152 | 235628.94 | 169060242 | 99107491 | 50001965 | 0.000000 | 10895813 | 71793706 | 0.000000
09-04-2025 22:36:30000 | -6705648 | 67.0565 | 89933867 | 235653.06 | 165779037 | 99112587 | 50017597 | 0.000000 | 11022327 | 72731680 | 0.000000
09-04-2025 22:36:35000 | -6536282 | 65.3628 | 91737021 | 235785.13 | 161645126 | 99029404 | 50052464 | 0.000000 | 11149883 | 73651157 | 0.000000
09-04-2025 22:36:40000 | -6524998 | 65.25 | 91068008 | 235712.27 | 161392395 | 99040039 | 50068558 | 0.000000 | 11276296 | 74557705 | 0.000000
09-04-2025 22:36:45000 | -6516523 | 65.1652 | 90792080 | 235675.19 | 161204895 | 99043320 | 50074959 | 0.000000 | 11402708 | 75462456 | 0.000000
09-04-2025 22:36:50000 | -6586667 | 65.8667 | 91159463 | 235608.84 | 162965271 | 99055817 | 50069622 | 0.000000 | 11527980 | 76372847 | 0.000000
09-04-2025 22:36:55000 | -6688126 | 66.8813 | 91878604 | 235638.91 | 165427505 | 99069542 | 50055359 | 0.000000 | 11655444 | 77299468 | 0.000000
09-04-2025 22:37:00000 | -6668227 | 66.6823 | 91755322 | 235666.55 | 164923279 | 99066536 | 50058670 | 0.000000 | 11782728 | 78226558 | 0.000000
09-04-2025 22:37:05000 | -6657861 | 66.5786 | 91324219 | 235691.08 | 164639404 | 99072327 | 50071415 | 0.000000 | 11909492 | 79152012 | 0.000000
09-04-2025 22:37:10000 | -6672702 | 66.727 | 91255410 | 235639.25 | 165040329 | 99077759 | 50062775 | 0.000000 | 12036074 | 80078193 | 0.000000
09-04-2025 22:37:15000 | -6706406 | 67.0641 | 92250254 | 235647.63 | 165878433 | 99067146 | 50047062 | 0.000000 | 12163481 | 81011455 | 0.000000
09-04-2025 22:37:20000 | -6698976 | 66.9898 | 93828457 | 235719.67 | 165707169 | 99033302 | 50062065 | 0.000000 | 12293866 | 81944531 | 0.000000
09-04-2025 22:37:25000 | -6799605 | 67.996 | 90777002 | 235564.22 | 168151489 | 99120583 | 50046974 | 0.000000 | 12422190 | 82879961 | 0.000000
09-04-2025 22:37:30000 | -6860433 | 68.6043 | 91903525 | 235549.00 | 169676636 | 99114609 | 50023533 | 0.000000 | 12550299 | 83826777 | 0.000000
09-04-2025 22:37:35000 | -6819059 | 68.1906 | 92337451 | 235655.61 | 168617355 | 99095612 | 50021706 | 0.000000 | 12679021 | 84774756 | 0.000000
09-04-2025 22:37:40000 | -6620802 | 66.208 | 90073477 | 235708.28 | 163689529 | 99087227 | 50053291 | 0.000000 | 12805924 | 85705059 | 0.000000
09-04-2025 22:37:45000 | -6534581 | 65.3458 | 87916455 | 235675.47 | 161545517 | 99107048 | 50076328 | 0.000000 | 12929391 | 86618213 | 0.000000
09-04-2025 22:37:50000 | -6596613 | 65.9661 | 90221523 | 235691.59 | 163118378 | 99077629 | 50070580 | 0.000000 | 13052606 | 87533203 | 0.000000
09-04-2025 22:37:55000 | -6553133 | 65.5313 | 89862627 | 235636.55 | 162090622 | 99072838 | 50078552 | 0.000000 | 13176770 | 88443887 | 0.000000
09-04-2025 22:38:00000 | -6666521 | 66.6652 | 91222217 | 235689.13 | 164848495 | 99076736 | 50074932 | 0.000000 | 13303225 | 89363066 | 0.000000
09-04-2025 22:38:05000 | -6660766 | 66.6077 | 91491543 | 235719.88 | 164699753 | 99069771 | 50065449 | 0.000000 | 13430732 | 90288984 | 0.000000
09-04-2025 22:38:10000 | -6716752 | 67.1675 | 92180596 | 235661.27 | 166127945 | 99071358 | 50052578 | 0.000000 | 13557872 | 91218838 | 0.000000
09-04-2025 22:38:15000 | -6783189 | 67.8319 | 90134375 | 235584.64 | 167715591 | 99128677 | 50049427 | 0.000000 | 13684720 | 92152773 | 0.000000
09-04-2025 22:38:20000 | -6772608 | 67.7261 | 90347041 | 235642.25 | 167426041 | 99121918 | 50040668 | 0.000000 | 13810818 | 93095508 | 0.000000
09-04-2025 22:38:25000 | -6772132 | 67.7213 | 89512500 | 235656.86 | 167377762 | 99137733 | 50028564 | 0.000000 | 13934037 | 94036846 | 0.000000
09-04-2025 22:38:30000 | -6696505 | 66.9651 | 88481465 | 235644.83 | 165513672 | 99138336 | 50055717 | 0.000000 | 14057874 | 94971455 | 0.000000
09-04-2025 22:38:35000 | -6611606 | 66.1161 | 87818242 | 235656.05 | 163424866 | 99129387 | 50069180 | 0.000000 | 14180276 | 95894102 | 0.000000
09-04-2025 22:38:40000 | -6614698 | 66.147 | 87510107 | 235623.94 | 163512695 | 99136208 | 50069378 | 0.000000 | 14302216 | 96813613 | 0.000000
09-04-2025 22:38:45000 | -6691053 | 66.9105 | 86163096 | 235542.66 | 165385101 | 99181038 | 50040287 | 0.000000 | 14422372 | 97738184 | 0.000000
09-04-2025 22:38:50000 | -6790820 | 67.9082 | 90370234 | 235647.05 | 167866852 | 99126114 | 50027172 | 0.000000 | 14546254 | 98679814 | 0.000000
09-04-2025 22:38:55000 | -6641122 | 66.4112 | 88999453 | 235697.20 | 164152054 | 99113945 | 50061054 | 0.000000 | 14671602 | 99611230 | 0.000000
09-04-2025 22:39:00000 | -6532907 | 65.3291 | 87678281 | 235700.73 | 161482056 | 99111366 | 50091141 | 0.000000 | 14795038 | 10052359 | 0.000000
09-04-2025 22:39:05000 | -6465121 | 64.6512 | 89760479 | 235780.08 | 159848206 | 99049911 | 50108459 | 0.000000 | 14918334 | 10142458 | 0.000000
09-04-2025 22:39:10000 | -6525938 | 65.2594 | 91477041 | 235776.23 | 161386887 | 99031799 | 50107754 | 0.000000 | 15044000 | 10232712 | 0.000000
09-04-2025 22:39:15000 | -6607722 | 66.0772 | 93047686 | 235770.78 | 163424927 | 99023041 | 50102272 | 0.000000 | 15171804 | 10324085 | 0.000000
09-04-2025 22:39:20000 | -6606158 | 66.0616 | 94151406 | 235802.22 | 163406647 | 98999611 | 50097244 | 0.000000 | 15300967 | 10416445 | 0.000000
09-04-2025 22:39:25000 | -6703468 | 67.0347 | 92167051 | 235679.72 | 165783112 | 99067993 | 50087887 | 0.000000 | 15430023 | 10509109 | 0.000000
09-04-2025 22:39:30000 | -6709530 | 67.0953 | 92934170 | 235732.48 | 165921631 | 99054329 | 50090664 | 0.000000 | 15559320 | 10602503 | 0.000000
09-04-2025 22:39:35000 | -6633745 | 66.3375 | 92863486 | 235827.23 | 164019135 | 99034355 | 50102314 | 0.000000 | 15687988 | 10695210 | 0.000000
09-04-2025 22:39:40000 | -6585672 | 65.8567 | 90931914 | 235746.81 | 162835434 | 99060173 | 50118435 | 0.000000 | 15816713 | 10787045 | 0.000000
09-04-2025 22:39:45000 | -6603255 | 66.0326 | 92108389 | 235778.09 | 163282715 | 99041107 | 50103764 | 0.000000 | 15943135 | 10878665 | 0.000000
09-04-2025 22:39:50000 | -6779044 | 67.7904 | 94058984 | 235727.08 | 167659515 | 99051109 | 50072868 | 0.000000 | 16071967 | 10972054 | 0.000000
09-04-2025 22:39:55000 | -6824686 | 68.2469 | 94892764 | 235755.52 | 168759537 | 99047142 | 50050671 | 0.000000 | 16202684 | 11066930 | 0.000000
09-04-2025 22:40:00000 | -6761005 | 67.6101 | 91807158 | 235742.56 | 167123383 | 99090622 | 50056812 | 0.000000 | 16331143 | 11161533 | 0.000000
09-04-2025 22:40:05000 | -6511086 | 65.1109 | 91168271 | 235873.84 | 160952911 | 99033905 | 50108089 | 0.000000 | 16458411 | 11253785 | 0.000000
09-04-2025 22:40:10000 | -6562174 | 65.6217 | 87590527 | 235706.58 | 162184219 | 99120911 | 50101593 | 0.000000 | 16580358 | 11344413 | 0.000000
09-04-2025 22:40:15000 | -6592355 | 65.9236 | 91492441 | 235763.77 | 163004089 | 99050621 | 50109043 | 0.000000 | 16706715 | 11435692 | 0.000000
09-04-2025 22:40:20000 | -6646357 | 66.4636 | 92343906 | 235755.08 | 164349182 | 99048546 | 50103226 | 0.000000 | 16834148 | 11527771 | 0.000000
09-04-2025 22:40:25000 | -6634477 | 66.3448 | 94889922 | 235894.56 | 164060226 | 98992615 | 50110645 | 0.000000 | 16963781 | 11620078 | 0.000000
09-04-2025 22:40:30000 | -6670864 | 66.7086 | 93983770 | 235788.00 | 164977173 | 99022079 | 50107018 | 0.000000 | 17094615 | 11712211 | 0.000000
09-04-2025 22:40:35000 | -6713989 | 67.1399 | 94760059 | 235803.41 | 166035995 | 99018639 | 50085712 | 0.000000 | 17225114 | 11805211 | 0.000000
09-04-2025 22:40:40000 | -6744422 | 67.4442 | 97615117 | 235845.30 | 166849701 | 98968765 | 50087513 | 0.000000 | 17359125 | 11899009 | 0.000000
09-04-2025 22:40:45000 | -6686363 | 66.8636 | 94329189 | 235780.83 | 165367676 | 99019478 | 50097797 | 0.000000 | 17492806 | 11992514 | 0.000000
09-04-2025 22:40:50000 | -6622517 | 66.2252 | 93562168 | 235813.36 | 163780029 | 99016708 | 50119057 | 0.000000 | 17622930 | 12084842 | 0.000000
09-04-2025 22:40:55000 | -6553623 | 65.5362 | 90519102 | 235684.91 | 162089310 | 99059570 | 50128269 | 0.000000 | 17752078 | 12175978 | 0.000000
09-04-2025 22:41:00000 | -6724008 | 67.2401 | 94665195 | 235694.69 | 166357971 | 99023445 | 50101757 | 0.000000 | 17880601 | 12268524 | 0.000000
09-04-2025 22:41:05000 | -6698186 | 66.9819 | 95804375 | 235784.77 | 165706833 | 98992546 | 50099224 | 0.000000 | 18013350 | 12361578 | 0.000000
09-04-2025 22:41:10000 | -6760405 | 67.6041 | 94769814 | 235668.25 | 167259064 | 99031677 | 50095463 | 0.000000 | 18146876 | 12454717 | 0.000000
09-04-2025 22:41:15000 | -6833695 | 68.337 | 96894160 | 235776.31 | 169033401 | 99009705 | 50078201 | 0.000000 | 18280637 | 12548951 | 0.000000
09-04-2025 22:41:20000 | -6815131 | 68.1513 | 97071680 | 235803.66 | 168565720 | 99000786 | 50079437 | 0.000000 | 18415405 | 12643613 | 0.000000
09-04-2025 22:41:25000 | -6768673 | 67.6867 | 95017510 | 235777.69 | 167395874 | 99029022 | 50070911 | 0.000000 | 18548123 | 12737896 | 0.000000
09-04-2025 22:41:30000 | -6798540 | 67.9854 | 92127295 | 235650.33 | 168109009 | 99094299 | 50068184 | 0.000000 | 18678250 | 12832061 | 0.000000
09-04-2025 22:41:35000 | -6773789 | 67.7379 | 94476270 | 235811.59 | 167470352 | 99041321 | 50081760 | 0.000000 | 18807461 | 12926576 | 0.000000
09-04-2025 22:41:40000 | -6641942 | 66.4194 | 89100049 | 235680.44 | 164186432 | 99112183 | 50101162 | 0.000000 | 18934626 | 13019086 | 0.000000
09-04-2025 22:41:45000 | -6725120 | 67.2512 | 91617266 | 235690.67 | 166285233 | 99084770 | 50085701 | 0.000000 | 19060577 | 13112147 | 0.000000
09-04-2025 22:41:50000 | -6783111 | 67.8311 | 92238633 | 235669.59 | 167722733 | 99088058 | 50066048 | 0.000000 | 19187965 | 13206054 | 0.000000
09-04-2025 22:41:55000 | -6832892 | 68.3289 | 96995654 | 235764.91 | 169029144 | 99007431 | 50056229 | 0.000000 | 19320269 | 13300763 | 0.000000
09-04-2025 22:42:00000 | -6813957 | 68.1396 | 97120029 | 235720.73 | 168601151 | 98999466 | 50059406 | 0.000000 | 19454808 | 13395354 | 0.000000
09-04-2025 22:42:05000 | -6720238 | 67.2024 | 98396484 | 235854.83 | 166280655 | 98945023 | 50076740 | 0.000000 | 19590117 | 13489300 | 0.000000
09-04-2025 22:42:10000 | -6663769 | 66.6377 | 94128145 | 235711.13 | 164867188 | 99017059 | 50088951 | 0.000000 | 19722444 | 13581805 | 0.000000
09-04-2025 22:42:15000 | -6667785 | 66.6779 | 95412793 | 235697.59 | 165015182 | 98991646 | 50088764 | 0.000000 | 19854205 | 13674000 | 0.000000
09-04-2025 22:42:20000 | -6697807 | 66.9781 | 96651621 | 235811.41 | 165707474 | 98974808 | 50067616 | 0.000000 | 19987241 | 13766639 | 0.000000
09-04-2025 22:42:25000 | -6779716 | 67.7972 | 10121253 | 235865.02 | 167816803 | 98903954 | 50057102 | 0.000000 | 20126328 | 13860324 | 0.000000
09-04-2025 22:42:30000 | -6661062 | 66.6106 | 10221460 | 235959.41 | 164918182 | 98843033 | 50080711 | 0.000000 | 20268173 | 13953583 | 0.000000
09-04-2025 22:42:35000 | -6617402 | 66.174 | 99460127 | 235796.50 | 163868988 | 98889267 | 50091053 | 0.000000 | 20407740 | 14045646 | 0.000000
09-04-2025 22:42:40000 | -6639720 | 66.3972 | 99893047 | 235788.84 | 164432800 | 98887131 | 50081337 | 0.000000 | 20546938 | 14137981 | 0.000000
09-04-2025 22:42:45000 | -6619090 | 66.1909 | 10246072 | 235887.66 | 163956421 | 98823021 | 50087566 | 0.000000 | 20687188 | 14230091 | 0.000000
09-04-2025 22:42:50000 | -6661690 | 66.6169 | 10146659 | 235836.92 | 164983917 | 98859825 | 50081211 | 0.000000 | 20827744 | 14322379 | 0.000000
09-04-2025 22:42:55000 | -6696942 | 66.9694 | 10070048 | 235802.34 | 165832748 | 98888290 | 50070580 | 0.000000 | 20968091 | 14414966 | 0.000000
09-04-2025 22:43:00000 | -6828255 | 68.2826 | 10194324 | 235778.64 | 169077148 | 98903824 | 50041870 | 0.000000 | 21108789 | 14508959 | 0.000000
09-04-2025 22:43:05000 | -6883108 | 68.8311 | 10154412 | 235756.94 | 170408600 | 98929245 | 50022121 | 0.000000 | 21250293 | 14604331 | 0.000000
09-04-2025 22:43:10000 | -6804252 | 68.0425 | 10133497 | 235839.28 | 168429611 | 98909126 | 50026077 | 0.000000 | 21391543 | 14699615 | 0.000000
09-04-2025 22:43:15000 | -6773089 | 67.7309 | 98100918 | 235769.20 | 167615616 | 98967300 | 50016556 | 0.000000 | 21528569 | 14794193 | 0.000000
09-04-2025 22:43:20000 | -6770628 | 67.7063 | 97829795 | 235763.38 | 167548889 | 98972176 | 50014809 | 0.000000 | 21663879 | 14888324 | 0.000000
09-04-2025 22:43:25000 | -6643769 | 66.4377 | 97832803 | 235820.06 | 164434967 | 98933121 | 50039608 | 0.000000 | 21800381 | 14981413 | 0.000000
09-04-2025 22:43:30000 | -6570751 | 65.7075 | 95900811 | 235768.44 | 162633011 | 98951637 | 50058250 | 0.000000 | 21935408 | 15073041 | 0.000000
09-04-2025 22:43:35000 | -6517427 | 65.1743 | 99006367 | 235875.72 | 161382156 | 98865761 | 50074196 | 0.000000 | 22071877 | 15163585 | 0.000000
09-04-2025 22:43:40000 | -6538378 | 65.3838 | 98349229 | 235794.95 | 161914825 | 98887558 | 50078316 | 0.000000 | 22209185 | 15254197 | 0.000000
09-04-2025 22:43:45000 | -6644209 | 66.4421 | 97546123 | 235693.06 | 164522293 | 98939400 | 50070229 | 0.000000 | 22344253 | 15345958 | 0.000000
09-04-2025 22:43:50000 | -6502525 | 65.0252 | 99538281 | 235860.06 | 161051620 | 98848579 | 50110313 | 0.000000 | 22481938 | 15437167 | 0.000000
09-04-2025 22:43:55000 | -6479048 | 64.7905 | 97329922 | 235816.94 | 160428284 | 98890404 | 50124313 | 0.000000 | 22618225 | 15526978 | 0.000000
09-04-2025 22:44:00000 | -6587780 | 65.8778 | 10059843 | 235838.97 | 163166992 | 98854065 | 50105003 | 0.000000 | 22756226 | 15618090 | 0.000000
09-04-2025 22:44:05000 | -6724482 | 67.2448 | 10291032 | 235824.47 | 166566879 | 98849144 | 50082169 | 0.000000 | 22897957 | 15710879 | 0.000000
09-04-2025 22:44:10000 | -6823979 | 68.2398 | 10484508 | 235847.25 | 169031403 | 98840195 | 50065121 | 0.000000 | 23043250 | 15805221 | 0.000000
09-04-2025 22:44:15000 | -6823781 | 68.2378 | 10363126 | 235860.48 | 168970871 | 98866379 | 50054848 | 0.000000 | 23188201 | 15900132 | 0.000000
09-04-2025 22:44:20000 | -6925455 | 69.2545 | 97251143 | 235592.50 | 171409912 | 99028381 | 50023888 | 0.000000 | 23328833 | 15995773 | 0.000000
09-04-2025 22:44:25000 | -6844919 | 68.4492 | 95864102 | 235644.67 | 169368835 | 99033478 | 50022579 | 0.000000 | 23462095 | 16091476 | 0.000000
09-04-2025 22:44:30000 | -6739365 | 67.3936 | 94627559 | 235729.97 | 166698685 | 99028587 | 50043724 | 0.000000 | 23593833 | 16186032 | 0.000000
09-04-2025 22:44:35000 | -6713444 | 67.1344 | 95723662 | 235770.81 | 166085541 | 98998718 | 50034702 | 0.000000 | 23725713 | 16279420 | 0.000000
09-04-2025 22:44:40000 | -6617580 | 66.1758 | 98419199 | 235881.19 | 163774811 | 98912079 | 50051613 | 0.000000 | 23861067 | 16372117 | 0.000000
09-04-2025 22:44:45000 | -6665820 | 66.6582 | 97024170 | 235781.44 | 164966141 | 98957230 | 50043228 | 0.000000 | 23995740 | 16464320 | 0.000000
09-04-2025 22:44:50000 | -6744795 | 67.448 | 10034945 | 235810.06 | 166975113 | 98911263 | 50023548 | 0.000000 | 24132878 | 16557797 | 0.000000
09-04-2025 22:44:55000 | -6783321 | 67.8332 | 99004648 | 235758.73 | 167902924 | 98951607 | 50026367 | 0.000000 | 24271646 | 16651609 | 0.000000
09-04-2025 22:45:00000 | -6763602 | 67.636 | 84161025 | 235384.48 | 167198578 | 99234703 | 50030842 | 0.000000 | 24396067 | 16745439 | 0.000000
09-04-2025 22:45:05000 | -6608005 | 66.08 | 82899951 | 235460.22 | 163318375 | 99222237 | 50054897 | 0.000000 | 11551804 | 92592682 | 0.000000
09-04-2025 22:45:10000 | -6559491 | 65.5949 | 85525928 | 235574.17 | 162148575 | 99160675 | 50087849 | 0.000000 | 23154871 | 184516983 | 0.000000
09-04-2025 22:45:15000 | -6544604 | 65.446 | 85995547 | 235535.48 | 161826813 | 99147736 | 50074158 | 0.000000 | 35195072 | 274959961 | 0.000000
09-04-2025 22:45:20000 | -6653355 | 66.5336 | 89681182 | 235554.86 | 164572510 | 99103767 | 50050411 | 0.000000 | 47458778 | 366698395 | 0.000000
09-04-2025 22:45:25000 | -6697820 | 66.9782 | 91722783 | 235577.02 | 165709412 | 99075302 | 50047977 | 0.000000 | 60138668 | 459440735 | 0.000000
09-04-2025 22:45:30000 | -6779056 | 67.7906 | 90668066 | 235513.75 | 167689072 | 99117409 | 50035385 | 0.000000 | 72815941 | 553185852 | 0.000000
09-04-2025 22:45:35000 | -6860284 | 68.6028 | 91027314 | 235520.42 | 169667877 | 99131157 | 50012730 | 0.000000 | 85418678 | 648355103 | 0.000000
09-04-2025 22:45:40000 | -6894514 | 68.9451 | 89580410 | 235451.22 | 170504761 | 99166451 | 50002354 | 0.000000 | 97990944 | 743950073 | 0.000000
09-04-2025 22:45:45000 | -6851895 | 68.519 | 87422842 | 235490.11 | 169371704 | 99195854 | 49999859 | 0.000000 | 110212593 | 839499939 | 0.000000
09-04-2025 22:45:50000 | -6651394 | 66.5139 | 87144404 | 235569.33 | 164436920 | 99152626 | 50032742 | 0.000000 | 122512451 | 932803223 | 0.000000
09-04-2025 22:45:55000 | -6516703 | 65.167 | 83267881 | 235504.25 | 161088593 | 99193527 | 50050289 | 0.000000 | 134297379 | 10243523 | 0.000000
09-04-2025 22:46:00000 | -6445947 | 64.4595 | 82452461 | 235500.36 | 159339600 | 99191811 | 50078861 | 0.000000 | 145771332 | 11141560 | 0.000000
09-04-2025 22:46:05000 | -6521202 | 65.212 | 83980547 | 235498.69 | 161225067 | 99180946 | 50073017 | 0.000000 | 157319839 | 12040538 | 0.000000
09-04-2025 22:46:10000 | -6590056 | 65.9006 | 86610859 | 235512.48 | 162967316 | 99147385 | 50067650 | 0.000000 | 169269562 | 12950854 | 0.000000
09-04-2025 22:46:15000 | -6629012 | 66.2901 | 89389551 | 235553.78 | 163972794 | 99103043 | 50070751 | 0.000000 | 181470062 | 13871610 | 0.000000
09-04-2025 22:46:20000 | -6573514 | 65.7351 | 87767988 | 235557.42 | 162569687 | 99120392 | 50086151 | 0.000000 | 193818863 | 14787906 | 0.000000
09-04-2025 22:46:25000 | -6534856 | 65.3486 | 88645889 | 235600.17 | 161628952 | 99092445 | 50088852 | 0.000000 | 206085999 | 15697324 | 0.000000
09-04-2025 22:46:30000 | -6594080 | 65.9408 | 89195488 | 235585.16 | 163101135 | 99097519 | 50084084 | 0.000000 | 218438980 | 16607554 | 0.000000
09-04-2025 22:46:35000 | -6597572 | 65.9757 | 89945225 | 235577.42 | 163210953 | 99083450 | 50075714 | 0.000000 | 230809265 | 17524034 | 0.000000
09-04-2025 22:46:40000 | -6624617 | 66.2462 | 91683193 | 235605.27 | 163906311 | 99055847 | 50083763 | 0.000000 | 243550278 | 18443070 | 0.000000
09-04-2025 22:46:45000 | -6553975 | 65.5397 | 90072305 | 235608.78 | 162136429 | 99068802 | 50093872 | 0.000000 | 256109619 | 19357216 | 0.000000
09-04-2025 22:46:50000 | -6633810 | 66.3381 | 91073271 | 235570.73 | 164133957 | 99070732 | 50085308 | 0.000000 | 268722046 | 20269092 | 0.000000
09-04-2025 22:46:55000 | -6676557 | 66.7656 | 94746924 | 235634.44 | 165249924 | 99008034 | 50077236 | 0.000000 | 281645020 | 21197527 | 0.000000
09-04-2025 22:47:00000 | -6683446 | 66.8345 | 93718223 | 235627.38 | 165390076 | 99031120 | 50078373 | 0.000000 | 294698486 | 22124614 | 0.000000
09-04-2025 22:47:05000 | -6762616 | 67.6262 | 91961826 | 235537.88 | 167313019 | 99088028 | 50065933 | 0.000000 | 307585724 | 23057620 | 0.000000
09-04-2025 22:47:10000 | -6772043 | 67.7204 | 92953389 | 235609.05 | 167527924 | 99071083 | 50061993 | 0.000000 | 320468842 | 23998643 | 0.000000
09-04-2025 22:47:15000 | -6772584 | 67.7258 | 92525205 | 235571.67 | 167549896 | 99079651 | 50063545 | 0.000000 | 333393677 | 24937991 | 0.000000
09-04-2025 22:47:20000 | -6708914 | 67.0891 | 95362881 | 235736.75 | 165983658 | 99004814 | 50087772 | 0.000000 | 346400269 | 25874309 | 0.000000
09-04-2025 22:47:25000 | -6589881 | 65.8988 | 91444336 | 235646.06 | 163027145 | 99050903 | 50097130 | 0.000000 | 359241821 | 26795425 | 0.000000
09-04-2025 22:47:30000 | -6577696 | 65.777 | 91867441 | 235656.58 | 162739899 | 99038727 | 50104294 | 0.000000 | 371942261 | 27711064 | 0.000000
09-04-2025 22:47:35000 | -6508401 | 65.084 | 92824453 | 235709.06 | 161055023 | 98998199 | 50112816 | 0.000000 | 384803314 | 28619775 | 0.000000
09-04-2025 22:47:40000 | -6556248 | 65.5625 | 94649277 | 235676.58 | 162304047 | 98973946 | 50110600 | 0.000000 | 397798035 | 29528728 | 0.000000
09-04-2025 22:47:45000 | -6677673 | 66.7767 | 94817656 | 235589.44 | 165312698 | 99006905 | 50084831 | 0.000000 | 410925049 | 30450107 | 0.000000
09-04-2025 22:47:50000 | -6820280 | 68.2028 | 97899004 | 235612.92 | 168860626 | 98985451 | 50066616 | 0.000000 | 424307861 | 31391934 | 0.000000
09-04-2025 22:47:55000 | -6641995 | 66.42 | 95927939 | 235900.89 | 164266846 | 98973091 | 50102955 | 0.000000 | 437826660 | 32324292 | 0.000000
09-04-2025 22:48:00000 | -6548239 | 65.4824 | 94825723 | 235932.86 | 161934937 | 98967697 | 50123512 | 0.000000 | 450919220 | 33238235 | 0.000000
09-04-2025 22:48:05000 | -6459189 | 64.5919 | 92472158 | 235895.88 | 159726440 | 98990692 | 50138275 | 0.000000 | 463901276 | 34137444 | 0.000000
09-04-2025 22:48:10000 | -6545802 | 65.458 | 95023809 | 235838.25 | 161951843 | 98962685 | 50122665 | 0.000000 | 476888000 | 35042891 | 0.000000
09-04-2025 22:48:15000 | -6663442 | 66.6344 | 98913340 | 235893.36 | 164899338 | 98916130 | 50119713 | 0.000000 | 490475861 | 35961682 | 0.000000
09-04-2025 22:48:20000 | -6679241 | 66.7924 | 96883516 | 235799.81 | 165276047 | 98964317 | 50118568 | 0.000000 | 504188354 | 36887371 | 0.000000
09-04-2025 22:48:25000 | -6844645 | 68.4464 | 96555264 | 235698.03 | 169346802 | 99019615 | 50083790 | 0.000000 | 517534912 | 37827400 | 0.000000
09-04-2025 22:48:30000 | -6956173 | 69.5617 | 98025342 | 235701.50 | 172097046 | 99021645 | 50038139 | 0.000000 | 531124512 | 38788010 | 0.000000
09-04-2025 22:48:35000 | -6918668 | 69.1867 | 98592080 | 235784.44 | 171149216 | 98999870 | 50047241 | 0.000000 | 544959961 | 39749849 | 0.000000
09-04-2025 22:48:40000 | -6926183 | 69.2618 | 96607871 | 235733.53 | 171299210 | 99041206 | 50026512 | 0.000000 | 558429077 | 40711882 | 0.000000
09-04-2025 22:48:45000 | -6839955 | 68.3996 | 95394209 | 235749.00 | 169155090 | 99041420 | 50046318 | 0.000000 | 571751648 | 41667280 | 0.000000
09-04-2025 22:48:50000 | -6738665 | 67.3867 | 92163467 | 235726.48 | 166604340 | 99077644 | 50040501 | 0.000000 | 584666931 | 42609541 | 0.000000
09-04-2025 22:48:55000 | -6720067 | 67.2007 | 90649209 | 235641.98 | 166163116 | 99102425 | 50035675 | 0.000000 | 597334045 | 43542012 | 0.000000
09-04-2025 22:49:00000 | -6737663 | 67.3766 | 90186699 | 235683.69 | 166546158 | 99116013 | 50029709 | 0.000000 | 609852905 | 44474751 | 0.000000
09-04-2025 22:49:05000 | -6786245 | 67.8624 | 90520361 | 235626.19 | 167779587 | 99122078 | 50020901 | 0.000000 | 622526062 | 45415103 | 0.000000
09-04-2025 22:49:10000 | -6833316 | 68.3332 | 90554111 | 235583.19 | 168952240 | 99133339 | 50010761 | 0.000000 | 635090088 | 46361528 | 0.000000
09-04-2025 22:49:15000 | -6808497 | 68.085 | 90646836 | 235625.94 | 168322662 | 99125328 | 50002129 | 0.000000 | 647692322 | 47310381 | 0.000000
09-04-2025 22:49:20000 | -6703998 | 67.04 | 90082344 | 235737.03 | 165688828 | 99109268 | 50014072 | 0.000000 | 660166382 | 48248823 | 0.000000
09-04-2025 22:49:25000 | -6594979 | 65.9498 | 89714131 | 235753.31 | 163021942 | 99087387 | 50039875 | 0.000000 | 672661255 | 49173491 | 0.000000
09-04-2025 22:49:30000 | -6491335 | 64.9133 | 87998242 | 235734.70 | 160460693 | 99093613 | 50063770 | 0.000000 | 684976685 | 50078594 | 0.000000
09-04-2025 22:49:35000 | -6526917 | 65.2692 | 84157588 | 235562.56 | 161320969 | 99178955 | 50055328 | 0.000000 | 696781677 | 50979233 | 0.000000
09-04-2025 22:49:40000 | -6598406 | 65.9841 | 88655605 | 235641.98 | 163146545 | 99109421 | 50059006 | 0.000000 | 708890198 | 51892925 | 0.000000
09-04-2025 22:49:45000 | -6613011 | 66.1301 | 88607852 | 235589.00 | 163536041 | 99114243 | 50058262 | 0.000000 | 721176392 | 52811089 | 0.000000
09-04-2025 22:49:50000 | -6591044 | 65.9104 | 87201641 | 235578.52 | 162963776 | 99136116 | 50054150 | 0.000000 | 733371582 | 53727783 | 0.000000
09-04-2025 22:49:55000 | -6603575 | 66.0357 | 90533389 | 235672.72 | 163319977 | 99073257 | 50057388 | 0.000000 | 745733398 | 54649941 | 0.000000
09-04-2025 22:50:00000 | -6505068 | 65.0507 | 88509756 | 235674.23 | 160853424 | 99087006 | 50089905 | 0.000000 | 758182129 | 55558208 | 0.000000
09-04-2025 22:50:05000 | -6503297 | 65.033 | 88148672 | 235640.25 | 160820282 | 99093849 | 50098251 | 0.000000 | 770371582 | 56459453 | 0.000000
09-04-2025 22:50:10000 | -6553709 | 65.5371 | 90506914 | 235635.48 | 162126007 | 99059845 | 50105400 | 0.000000 | 782786133 | 57364507 | 0.000000
09-04-2025 22:50:15000 | -6631755 | 66.3175 | 91278203 | 235610.34 | 164063232 | 99066040 | 50095470 | 0.000000 | 795413452 | 58277085 | 0.000000
09-04-2025 22:50:20000 | -6721905 | 67.219 | 92566885 | 235584.33 | 166317871 | 99065086 | 50081078 | 0.000000 | 808245605 | 59204863 | 0.000000
09-04-2025 22:50:25000 | -6797348 | 67.9735 | 92929199 | 235529.16 | 168197418 | 99078362 | 50057156 | 0.000000 | 821201172 | 60144209 | 0.000000
09-04-2025 22:50:30000 | -6815284 | 68.1528 | 95467324 | 235629.13 | 168646820 | 99033112 | 50056915 | 0.000000 | 834309021 | 61093354 | 0.000000
09-04-2025 22:50:35000 | -6690324 | 66.9032 | 92668037 | 235621.55 | 165528534 | 99054329 | 50080406 | 0.000000 | 847405640 | 62027661 | 0.000000
09-04-2025 22:50:40000 | -6637982 | 66.3798 | 91448008 | 235609.64 | 164223511 | 99064339 | 50080250 | 0.000000 | 860099121 | 62950996 | 0.000000
09-04-2025 22:50:45000 | -6697992 | 66.9799 | 92650605 | 235621.22 | 165708054 | 99056808 | 50069767 | 0.000000 | 872813782 | 63878896 | 0.000000
09-04-2025 22:50:50000 | -6771891 | 67.7189 | 94662998 | 235652.53 | 167548813 | 99037056 | 50052628 | 0.000000 | 885818054 | 64819087 | 0.000000
09-04-2025 22:50:55000 | -6839352 | 68.3935 | 95017764 | 235655.14 | 169194824 | 99048698 | 50035603 | 0.000000 | 898848450 | 65766787 | 0.000000
09-04-2025 22:51:00000 | -6801236 | 68.0124 | 93566084 | 235562.64 | 168288147 | 99066917 | 50040203 | 0.000000 | 911931946 | 66713062 | 0.000000
09-04-2025 22:51:05000 | -6690030 | 66.9003 | 92960977 | 235688.36 | 165481613 | 99048340 | 50056122 | 0.000000 | 924842590 | 67649326 | 0.000000
09-04-2025 22:51:10000 | -6530851 | 65.3085 | 92484541 | 235712.09 | 161591827 | 99012138 | 50085289 | 0.000000 | 937682922 | 68568320 | 0.000000
09-04-2025 22:51:15000 | -6509029 | 65.0903 | 91880791 | 235582.67 | 161128967 | 99018356 | 50100224 | 0.000000 | 950377869 | 69471978 | 0.000000
09-04-2025 22:51:20000 | -6651434 | 66.5143 | 92205137 | 235580.00 | 164597198 | 99052795 | 50074924 | 0.000000 | 963073486 | 70386636 | 0.000000
09-04-2025 22:51:25000 | -6769575 | 67.6958 | 95961240 | 235645.80 | 167545074 | 99010185 | 50050278 | 0.000000 | 976147766 | 71320591 | 0.000000
09-04-2025 22:51:30000 | -6826403 | 68.264 | 95798252 | 235530.14 | 168997375 | 99029617 | 50040848 | 0.000000 | 989436157 | 72266753 | 0.000000
09-04-2025 22:51:35000 | -6775459 | 67.7546 | 96174277 | 235628.75 | 167704636 | 99007553 | 50048203 | 0.000000 | 10028594 | 73210088 | 0.000000
09-04-2025 22:51:40000 | -6880828 | 68.8083 | 97262275 | 235617.63 | 170312119 | 99015701 | 50015678 | 0.000000 | 10161107 | 74161597 | 0.000000
09-04-2025 22:51:45000 | -6938361 | 69.3836 | 97869658 | 235601.14 | 171734283 | 99019768 | 49990807 | 0.000000 | 10296622 | 75122378 | 0.000000
09-04-2025 22:51:50000 | -6930349 | 69.3035 | 97414209 | 235613.83 | 171519806 | 99026520 | 49984093 | 0.000000 | 10432322 | 76086431 | 0.000000
09-04-2025 22:51:55000 | -6859000 | 68.59 | 96675557 | 235627.23 | 169748962 | 99021255 | 49981625 | 0.000000 | 10565553 | 77043262 | 0.000000
09-04-2025 22:52:00000 | -6850513 | 68.5051 | 95014219 | 235570.44 | 169536865 | 99051819 | 49968224 | 0.000000 | 10697390 | 77997168 | 0.000000
09-04-2025 22:52:05000 | -6762213 | 67.6221 | 92614102 | 235554.56 | 167321640 | 99075111 | 49977467 | 0.000000 | 10828025 | 78941450 | 0.000000
09-04-2025 22:52:10000 | -6644466 | 66.4447 | 88835352 | 235476.98 | 164393478 | 99118042 | 49995388 | 0.000000 | 10954194 | 79868218 | 0.000000
09-04-2025 22:52:15000 | -6562197 | 65.622 | 91028779 | 235575.97 | 162393738 | 99051544 | 50008678 | 0.000000 | 11080441 | 80785132 | 0.000000
09-04-2025 22:52:20000 | -6625851 | 66.2585 | 93532510 | 235649.81 | 163978302 | 99018295 | 50002625 | 0.000000 | 11207529 | 81700679 | 0.000000
09-04-2025 22:52:25000 | -6664284 | 66.6428 | 92607861 | 235579.84 | 164919403 | 99048248 | 49990788 | 0.000000 | 11336008 | 82624209 | 0.000000
09-04-2025 22:52:30000 | -6677201 | 66.772 | 94791582 | 235641.28 | 165268814 | 99007301 | 49993271 | 0.000000 | 11466547 | 83553184 | 0.000000
09-04-2025 22:52:35000 | -6606390 | 66.0639 | 91847539 | 235591.14 | 163482147 | 99047348 | 50012203 | 0.000000 | 11595676 | 84475010 | 0.000000
09-04-2025 22:52:40000 | -6539597 | 65.396 | 92072305 | 235631.00 | 161843643 | 99023376 | 50016636 | 0.000000 | 11724525 | 85387227 | 0.000000
09-04-2025 22:52:45000 | -6594970 | 65.9497 | 92455410 | 235623.67 | 163202713 | 99031578 | 50014194 | 0.000000 | 11851927 | 86302100 | 0.000000
09-04-2025 22:52:50000 | -6557436 | 65.5744 | 94181201 | 235696.67 | 162306839 | 98984283 | 50032661 | 0.000000 | 11981726 | 87216523 | 0.000000
09-04-2025 22:52:55000 | -6629280 | 66.2928 | 92272803 | 235543.00 | 164090286 | 99045158 | 50021118 | 0.000000 | 12109949 | 88131230 | 0.000000
09-04-2025 22:53:00000 | -6671473 | 66.7147 | 92147646 | 235501.97 | 165132950 | 99059555 | 50009983 | 0.000000 | 12237224 | 89052471 | 0.000000
09-04-2025 22:53:05000 | -6732545 | 67.3255 | 93158848 | 235483.17 | 166670258 | 99056206 | 49993240 | 0.000000 | 12366587 | 89984873 | 0.000000
09-04-2025 22:53:10000 | -6765538 | 67.6554 | 94617734 | 235814.16 | 167278503 | 99036179 | 49994087 | 0.000000 | 12496841 | 90922314 | 0.000000
09-04-2025 22:53:15000 | -6904448 | 69.0445 | 94287832 | 235684.23 | 170733185 | 99080399 | 49961468 | 0.000000 | 12628158 | 91871338 | 0.000000
09-04-2025 22:53:20000 | -6952561 | 69.5256 | 97862383 | 235840.56 | 171905792 | 99023849 | 49938911 | 0.000000 | 12760897 | 92837432 | 0.000000
09-04-2025 22:53:25000 | -6837250 | 68.3725 | 95857461 | 235819.64 | 169058044 | 99031471 | 49958298 | 0.000000 | 12896113 | 93793359 | 0.000000
09-04-2025 22:53:30000 | -6630315 | 66.3032 | 93150947 | 235917.59 | 163881470 | 99027466 | 49986225 | 0.000000 | 13025417 | 94728896 | 0.000000
09-04-2025 22:53:35000 | -6612394 | 66.1239 | 86802598 | 235690.89 | 163391541 | 99149353 | 49980495 | 0.000000 | 13148475 | 95648174 | 0.000000
09-04-2025 22:53:40000 | -6646623 | 66.4662 | 91706943 | 235795.94 | 164310959 | 99061523 | 49971329 | 0.000000 | 13272601 | 96571699 | 0.000000
09-04-2025 22:53:45000 | -6645946 | 66.4595 | 90760166 | 235749.00 | 164293488 | 99080345 | 49971970 | 0.000000 | 13399340 | 97495703 | 0.000000
09-04-2025 22:53:50000 | -6651177 | 66.5118 | 93521836 | 235833.22 | 164451492 | 99025871 | 49982716 | 0.000000 | 13527986 | 98421748 | 0.000000
09-04-2025 22:53:55000 | -6604436 | 66.0444 | 91462607 | 235797.84 | 163277222 | 99054649 | 49996628 | 0.000000 | 13655281 | 99342227 | 0.000000
09-04-2025 22:54:00000 | -6567077 | 65.6708 | 90464727 | 235793.44 | 162340469 | 99064476 | 50013050 | 0.000000 | 13781565 | 10025323 | 0.000000
09-04-2025 22:54:05000 | -6536650 | 65.3665 | 91410625 | 235789.48 | 161636719 | 99036308 | 50021515 | 0.000000 | 13909071 | 10116127 | 0.000000
09-04-2025 22:54:10000 | -6623071 | 66.2307 | 93637637 | 235835.97 | 163775818 | 99015312 | 50006493 | 0.000000 | 14035747 | 10207789 | 0.000000
09-04-2025 22:54:15000 | -6745853 | 67.4585 | 92890684 | 235700.91 | 166827255 | 99065201 | 49979309 | 0.000000 | 14165021 | 10300762 | 0.000000
09-04-2025 22:54:20000 | -6892255 | 68.9226 | 94298086 | 235665.73 | 170446777 | 99076988 | 49953106 | 0.000000 | 14295535 | 10395842 | 0.000000
09-04-2025 22:54:25000 | -6856945 | 68.5695 | 93906455 | 235785.39 | 169487762 | 99075211 | 49944183 | 0.000000 | 14425103 | 10491682 | 0.000000
09-04-2025 22:54:30000 | -6700147 | 67.0015 | 90537490 | 235753.33 | 165595917 | 99099342 | 49977016 | 0.000000 | 14554270 | 10585450 | 0.000000
09-04-2025 22:54:35000 | -6705458 | 67.0546 | 87844863 | 235670.09 | 165696838 | 99152771 | 49962101 | 0.000000 | 14676672 | 10678588 | 0.000000
09-04-2025 22:54:40000 | -6872038 | 68.7204 | 89895742 | 235597.75 | 169860184 | 99155212 | 49923130 | 0.000000 | 14799939 | 10773170 | 0.000000
09-04-2025 22:54:45000 | -6835150 | 68.3515 | 90930791 | 235673.44 | 168943390 | 99126671 | 49930908 | 0.000000 | 14927634 | 10868367 | 0.000000
09-04-2025 22:54:50000 | -6702127 | 67.0213 | 91132451 | 235811.89 | 165623718 | 99088158 | 49942261 | 0.000000 | 15052682 | 10962418 | 0.000000
09-04-2025 22:54:55000 | -6763622 | 67.6362 | 87278799 | 235633.14 | 167119354 | 99177673 | 49924599 | 0.000000 | 15174019 | 11055849 | 0.000000
09-04-2025 22:55:00000 | -6818583 | 68.1858 | 89929063 | 235666.45 | 168517654 | 99141457 | 49914478 | 0.000000 | 15297021 | 11150383 | 0.000000
09-04-2025 22:55:05000 | -6706734 | 67.0673 | 90690742 | 235792.23 | 165736816 | 99098083 | 49919216 | 0.000000 | 15421515 | 11244491 | 0.000000
09-04-2025 22:55:10000 | -6807795 | 68.078 | 86713730 | 235546.44 | 168240738 | 99198532 | 49912586 | 0.000000 | 15543840 | 11338106 | 0.000000
09-04-2025 22:55:15000 | -6775130 | 67.7513 | 89865469 | 235699.75 | 167439117 | 99131767 | 49896175 | 0.000000 | 15666455 | 11432645 | 0.000000
09-04-2025 22:55:20000 | -6787100 | 67.871 | 88600693 | 235658.77 | 167713608 | 99158669 | 49906303 | 0.000000 | 15789778 | 11526614 | 0.000000
09-04-2025 22:55:25000 | -6772522 | 67.7252 | 88322178 | 235674.67 | 167337891 | 99160324 | 49896133 | 0.000000 | 15911647 | 11620872 | 0.000000
09-04-2025 22:55:30000 | -6682816 | 66.8282 | 87643955 | 235664.44 | 165150681 | 99150948 | 49932724 | 0.000000 | 16035496 | 11714059 | 0.000000
09-04-2025 22:55:35000 | -6506644 | 65.0664 | 87430156 | 235788.06 | 160775238 | 99109268 | 49965775 | 0.000000 | 16156727 | 11805046 | 0.000000
09-04-2025 22:55:40000 | -6515582 | 65.1558 | 88390400 | 235758.22 | 161045547 | 99092331 | 49969456 | 0.000000 | 16277961 | 11895502 | 0.000000
09-04-2025 22:55:45000 | -6623244 | 66.2324 | 89053535 | 235676.47 | 163737961 | 99108154 | 49953003 | 0.000000 | 16400405 | 11986814 | 0.000000
09-04-2025 22:55:50000 | -6768710 | 67.6871 | 89957061 | 235614.88 | 167343460 | 99128387 | 49925812 | 0.000000 | 16525640 | 12079853 | 0.000000
09-04-2025 22:55:55000 | -6830993 | 68.3099 | 91187490 | 235655.06 | 168863663 | 99120743 | 49924271 | 0.000000 | 16651621 | 12174321 | 0.000000
09-04-2025 22:56:00000 | -6806596 | 68.066 | 89987930 | 235672.70 | 168221161 | 99137360 | 49920467 | 0.000000 | 16776447 | 12268979 | 0.000000
09-04-2025 22:56:05000 | -6772259 | 67.7226 | 91217070 | 235729.50 | 167385040 | 99105057 | 49940804 | 0.000000 | 16903635 | 12363241 | 0.000000
09-04-2025 22:56:10000 | -6755631 | 67.5563 | 88396504 | 235664.27 | 166940613 | 99154770 | 49943840 | 0.000000 | 17027507 | 12457366 | 0.000000
09-04-2025 22:56:15000 | -6636809 | 66.3681 | 85784248 | 235625.94 | 163996292 | 99174980 | 49963760 | 0.000000 | 17150675 | 12549604 | 0.000000
09-04-2025 22:56:20000 | -6608014 | 66.0801 | 87830166 | 235703.39 | 163303482 | 99128220 | 49964947 | 0.000000 | 17270616 | 12641520 | 0.000000
09-04-2025 22:56:25000 | -6595905 | 65.9591 | 88448428 | 235716.66 | 163031204 | 99112862 | 49956268 | 0.000000 | 17392556 | 12733308 | 0.000000
09-04-2025 22:56:30000 | -6738633 | 67.3863 | 89512324 | 235647.02 | 166571869 | 99129257 | 49934509 | 0.000000 | 17515966 | 12826476 | 0.000000
09-04-2025 22:56:35000 | -6816649 | 68.1665 | 89589922 | 235593.84 | 168509659 | 99147362 | 49922043 | 0.000000 | 17641337 | 12920589 | 0.000000
09-04-2025 22:56:40000 | -6867164 | 68.6716 | 89018789 | 235583.83 | 169727005 | 99170250 | 49906139 | 0.000000 | 17767460 | 13015485 | 0.000000
09-04-2025 22:56:45000 | -6856928 | 68.5693 | 91877031 | 235706.48 | 169476440 | 99114220 | 49902092 | 0.000000 | 17892664 | 13111095 | 0.000000
09-04-2025 22:56:50000 | -6663985 | 66.6398 | 88575625 | 235736.70 | 164668915 | 99128189 | 49932381 | 0.000000 | 18017693 | 13204776 | 0.000000
09-04-2025 22:56:55000 | -6594940 | 65.9494 | 84497354 | 235640.66 | 162928986 | 99189171 | 49949368 | 0.000000 | 18137238 | 13296687 | 0.000000
09-04-2025 22:57:00000 | -6500941 | 65.0094 | 85380869 | 235683.17 | 160647186 | 99148537 | 49955868 | 0.000000 | 18255996 | 13387646 | 0.000000
09-04-2025 22:57:05000 | -6468984 | 64.6898 | 87031895 | 235734.19 | 159884460 | 99107094 | 49972363 | 0.000000 | 18376650 | 13477720 | 0.000000
09-04-2025 22:57:10000 | -6543416 | 65.4342 | 86039805 | 235598.66 | 161752914 | 99146561 | 49965748 | 0.000000 | 18497676 | 13567771 | 0.000000
09-04-2025 22:57:15000 | -6820820 | 68.2082 | 90036602 | 235533.00 | 168669998 | 99139992 | 49916771 | 0.000000 | 18620992 | 13660803 | 0.000000
09-04-2025 22:57:20000 | -7032986 | 70.3299 | 91401377 | 235538.72 | 173862823 | 99166054 | 49871407 | 0.000000 | 18748032 | 13757501 | 0.000000
09-04-2025 22:57:25000 | -7011459 | 70.1146 | 91847949 | 235646.16 | 173278732 | 99152878 | 49870106 | 0.000000 | 18876215 | 13854985 | 0.000000
09-04-2025 22:57:30000 | -6933298 | 69.333 | 88112188 | 235569.09 | 171314117 | 99202118 | 49875546 | 0.000000 | 19001323 | 13951814 | 0.000000
09-04-2025 22:57:35000 | -6887972 | 68.8797 | 84884131 | 235556.41 | 170122910 | 99249191 | 49872471 | 0.000000 | 19120271 | 14047737 | 0.000000
09-04-2025 22:57:40000 | -6808563 | 68.0856 | 84337070 | 235574.58 | 168166260 | 99241539 | 49871803 | 0.000000 | 19238010 | 14142707 | 0.000000
09-04-2025 22:57:45000 | -6769363 | 67.6936 | 82726553 | 235540.06 | 167186554 | 99261528 | 49871078 | 0.000000 | 19353848 | 14236765 | 0.000000
09-04-2025 22:57:50000 | -6777591 | 67.7759 | 84465723 | 235576.22 | 167411072 | 99232361 | 49864250 | 0.000000 | 19469447 | 14330653 | 0.000000
09-04-2025 22:57:55000 | -6723462 | 67.2346 | 85117754 | 235595.86 | 166101410 | 99208153 | 49873756 | 0.000000 | 19587632 | 14424399 | 0.000000
09-04-2025 22:58:00000 | -6664973 | 66.6497 | 84279658 | 235615.06 | 164643280 | 99209961 | 49889904 | 0.000000 | 19704436 | 14517342 | 0.000000
09-04-2025 22:58:05000 | -6539796 | 65.398 | 81629775 | 235552.70 | 161562668 | 99229980 | 49916862 | 0.000000 | 19820166 | 14608368 | 0.000000
09-04-2025 22:58:10000 | -6601227 | 66.0123 | 84159824 | 235618.63 | 163083405 | 99197075 | 49909313 | 0.000000 | 19934642 | 14699938 | 0.000000
09-04-2025 22:58:15000 | -6532879 | 65.3288 | 83866992 | 235610.02 | 161418839 | 99186020 | 49923420 | 0.000000 | 20052303 | 14790952 | 0.000000
09-04-2025 22:58:20000 | -6650449 | 66.5045 | 86120693 | 235606.59 | 164348648 | 99171936 | 49912781 | 0.000000 | 20169335 | 14882691 | 0.000000
09-04-2025 22:58:25000 | -6757891 | 67.5789 | 86303574 | 235537.11 | 167017487 | 99194374 | 49888714 | 0.000000 | 20289041 | 14975864 | 0.000000
09-04-2025 22:58:30000 | -6804724 | 68.0472 | 89277910 | 235681.89 | 168142456 | 99150284 | 49884666 | 0.000000 | 20409719 | 15070375 | 0.000000
09-04-2025 22:58:35000 | -6695313 | 66.9531 | 86492734 | 235635.03 | 165433807 | 99175873 | 49909332 | 0.000000 | 20531523 | 15163919 | 0.000000
09-04-2025 22:58:40000 | -6703488 | 67.0349 | 84959365 | 235597.47 | 165612228 | 99206406 | 49907570 | 0.000000 | 20649395 | 15257020 | 0.000000
09-04-2025 22:58:45000 | -6718802 | 67.188 | 84344902 | 235560.03 | 165991699 | 99221230 | 49899502 | 0.000000 | 20766990 | 15350338 | 0.000000
09-04-2025 22:58:50000 | -6753025 | 67.5302 | 85355605 | 235583.75 | 166842300 | 99210648 | 49898331 | 0.000000 | 20885557 | 15443807 | 0.000000
09-04-2025 22:58:55000 | -6715545 | 67.1555 | 84711396 | 235599.11 | 165894302 | 99213776 | 49901730 | 0.000000 | 21003904 | 15537397 | 0.000000
09-04-2025 22:59:00000 | -6795996 | 67.96 | 84017949 | 235527.88 | 167883560 | 99244446 | 49888996 | 0.000000 | 21121157 | 15631070 | 0.000000
09-04-2025 22:59:05000 | -6851823 | 68.5182 | 85256152 | 235498.06 | 169298340 | 99234756 | 49872849 | 0.000000 | 21239902 | 15725732 | 0.000000
09-04-2025 22:59:10000 | -6907137 | 69.0714 | 83884609 | 235465.17 | 170625351 | 99270599 | 49848324 | 0.000000 | 21356765 | 15821541 | 0.000000
09-04-2025 22:59:15000 | -6572827 | 65.7283 | 85675420 | 235743.30 | 162360291 | 99161148 | 49926727 | 0.000000 | 21478088 | 15914468 | 0.000000
09-04-2025 22:59:20000 | -6424529 | 64.2453 | 81818315 | 235686.53 | 158672272 | 99198792 | 49960392 | 0.000000 | 21593247 | 16004304 | 0.000000
09-04-2025 22:59:25000 | -6393125 | 63.9312 | 82588643 | 235638.88 | 157964050 | 99175880 | 49964161 | 0.000000 | 21708022 | 16093155 | 0.000000
09-04-2025 22:59:30000 | -6462986 | 64.6299 | 84871211 | 235647.36 | 159729233 | 99148758 | 49958115 | 0.000000 | 21824624 | 16182654 | 0.000000
09-04-2025 22:59:35000 | -6432801 | 64.328 | 86695439 | 235689.92 | 159026184 | 99104027 | 49982433 | 0.000000 | 21945305 | 16272086 | 0.000000
09-04-2025 22:59:40000 | -6579333 | 65.7933 | 88318047 | 235647.98 | 162665466 | 99111038 | 49963924 | 0.000000 | 22066624 | 16362243 | 0.000000
09-04-2025 22:59:45000 | -6642550 | 66.4255 | 91689092 | 235739.55 | 164246964 | 99060745 | 49958889 | 0.000000 | 22191641 | 16454221 | 0.000000
09-04-2025 22:59:50000 | -6675973 | 66.7597 | 91797734 | 235740.08 | 165060486 | 99067825 | 49962383 | 0.000000 | 22319070 | 16546793 | 0.000000
09-04-2025 22:59:55000 | -6749843 | 67.4984 | 89488311 | 235635.86 | 166856934 | 99132568 | 49935890 | 0.000000 | 22444597 | 16640094 | 0.000000
09-04-2025 23:00:00000 | -6841646 | 68.4165 | 91558682 | 235670.70 | 169124451 | 99116386 | 49919918 | 0.000000 | 22571299 | 16734525 | 0.000000
09-04-2025 23:00:05000 | -6835598 | 68.356 | 91864590 | 235720.91 | 168949142 | 99109001 | 49923744 | 0.000000 | 12803555 | 94999023 | 0.000000
09-04-2025 23:00:10000 | -6738413 | 67.3841 | 89333809 | 235699.45 | 166524384 | 99132622 | 49924759 | 0.000000 | 25411322 | 189088379 | 0.000000
09-04-2025 23:00:15000 | -6772714 | 67.7271 | 87615674 | 235611.16 | 167370621 | 99173584 | 49915649 | 0.000000 | 37675591 | 282875092 | 0.000000
09-04-2025 23:00:20000 | -6809665 | 68.0966 | 89055742 | 235648.64 | 168284058 | 99155663 | 49910610 | 0.000000 | 49907059 | 377599243 | 0.000000
09-04-2025 23:00:25000 | -6761316 | 67.6132 | 86266377 | 235618.34 | 167042282 | 99195869 | 49899967 | 0.000000 | 62001774 | 471665375 | 0.000000
09-04-2025 23:00:30000 | -6804696 | 68.047 | 84816260 | 235530.28 | 168114288 | 99232132 | 49890488 | 0.000000 | 73866333 | 565643005 | 0.000000
09-04-2025 23:00:35000 | -6858709 | 68.5871 | 85728496 | 235563.47 | 169435272 | 99227882 | 49872135 | 0.000000 | 85680954 | 660364258 | 0.000000
09-04-2025 23:00:40000 | -6866195 | 68.662 | 86508906 | 235539.73 | 169654205 | 99215622 | 49859196 | 0.000000 | 97768768 | 755788147 | 0.000000
09-04-2025 23:00:45000 | -6756923 | 67.5692 | 86431309 | 235664.84 | 166907166 | 99191788 | 49872559 | 0.000000 | 109729561 | 850556946 | 0.000000
09-04-2025 23:00:50000 | -6664395 | 66.644 | 82738135 | 235567.80 | 164613922 | 99238144 | 49879704 | 0.000000 | 121455505 | 943381348 | 0.000000
09-04-2025 23:00:55000 | -6692389 | 66.9239 | 84230576 | 235611.02 | 165312668 | 99217247 | 49876625 | 0.000000 | 133037643 | 10365436 | 0.000000
09-04-2025 23:01:00000 | -6683173 | 66.8317 | 83949463 | 235581.83 | 165096985 | 99220284 | 49874489 | 0.000000 | 144721970 | 11293475 | 0.000000
09-04-2025 23:01:05000 | -6732221 | 67.3222 | 84513184 | 235549.38 | 166329941 | 99221237 | 49863647 | 0.000000 | 156450317 | 12224359 | 0.000000
09-04-2025 23:01:10000 | -6783413 | 67.8341 | 87686494 | 235625.31 | 167617035 | 99174843 | 49858677 | 0.000000 | 168394394 | 13164844 | 0.000000
09-04-2025 23:01:15000 | -6770510 | 67.7051 | 86487148 | 235618.45 | 167272324 | 99193962 | 49856339 | 0.000000 | 180459305 | 14105374 | 0.000000
09-04-2025 23:01:20000 | -6714242 | 67.1424 | 85649219 | 235618.69 | 165878113 | 99196175 | 49868946 | 0.000000 | 192410065 | 15044729 | 0.000000
09-04-2025 23:01:25000 | -6670470 | 66.7047 | 84679014 | 235609.03 | 164793549 | 99203842 | 49882286 | 0.000000 | 204229080 | 15973800 | 0.000000
09-04-2025 23:01:30000 | -6710302 | 67.103 | 83807246 | 235550.52 | 165774628 | 99229088 | 49865368 | 0.000000 | 215887939 | 16902009 | 0.000000
09-04-2025 23:01:35000 | -6730886 | 67.3089 | 85438828 | 235581.64 | 166302399 | 99203979 | 49861530 | 0.000000 | 227736099 | 17837307 | 0.000000
09-04-2025 23:01:40000 | -6834221 | 68.3422 | 86964287 | 235541.95 | 168890717 | 99200096 | 49848083 | 0.000000 | 239656509 | 18779523 | 0.000000
09-04-2025 23:01:45000 | -6885053 | 68.8505 | 85436670 | 235515.47 | 170098297 | 99238861 | 49824039 | 0.000000 | 251530319 | 19732487 | 0.000000
09-04-2025 23:01:50000 | -6807714 | 68.0771 | 85465547 | 235572.03 | 168180359 | 99221153 | 49825768 | 0.000000 | 263454651 | 20682664 | 0.000000
09-04-2025 23:01:55000 | -6707555 | 67.0756 | 82249951 | 235549.52 | 165663361 | 99256554 | 49838181 | 0.000000 | 275044159 | 21620767 | 0.000000
09-04-2025 23:02:00000 | -6615723 | 66.1572 | 81625654 | 235585.47 | 163387329 | 99247437 | 49859653 | 0.000000 | 286424835 | 22547271 | 0.000000
09-04-2025 23:02:05000 | -6554152 | 65.5415 | 80950435 | 235541.25 | 161896606 | 99245880 | 49873703 | 0.000000 | 297635193 | 23460857 | 0.000000
09-04-2025 23:02:10000 | -6531286 | 65.3129 | 81933682 | 235591.41 | 161338455 | 99222305 | 49876408 | 0.000000 | 308841309 | 24368196 | 0.000000
09-04-2025 23:02:15000 | -6621041 | 66.2104 | 84368545 | 235573.78 | 163605591 | 99197899 | 49865311 | 0.000000 | 320413788 | 25283962 | 0.000000
09-04-2025 23:02:20000 | -6607230 | 66.0723 | 86987793 | 235654.95 | 163295624 | 99144447 | 49881847 | 0.000000 | 332361206 | 26203564 | 0.000000
09-04-2025 23:02:25000 | -6552091 | 65.5209 | 82697910 | 235539.39 | 161905273 | 99212868 | 49882992 | 0.000000 | 344124786 | 27114734 | 0.000000
09-04-2025 23:02:30000 | -6462500 | 64.625 | 86637490 | 235719.08 | 159726105 | 99113304 | 49919674 | 0.000000 | 356210571 | 28016780 | 0.000000
09-04-2025 23:02:35000 | -6581759 | 65.8176 | 85990752 | 235606.80 | 162678833 | 99157303 | 49896774 | 0.000000 | 368011871 | 28924587 | 0.000000
09-04-2025 23:02:40000 | -6536925 | 65.3692 | 90253877 | 235767.41 | 161617691 | 99060280 | 49923759 | 0.000000 | 380321655 | 29838438 | 0.000000
09-04-2025 23:02:45000 | -6519489 | 65.1949 | 84732529 | 235643.28 | 161097641 | 99165970 | 49923969 | 0.000000 | 392236786 | 30742444 | 0.000000
09-04-2025 23:02:50000 | -6617255 | 66.1726 | 86744922 | 235633.53 | 163545212 | 99151703 | 49915867 | 0.000000 | 404071075 | 31655359 | 0.000000
09-04-2025 23:02:55000 | -6768420 | 67.6842 | 86049941 | 235516.44 | 167281326 | 99201508 | 49890041 | 0.000000 | 416165955 | 32585964 | 0.000000
09-04-2025 23:03:00000 | -6889507 | 68.8951 | 90305332 | 235608.80 | 170288040 | 99151863 | 49863659 | 0.000000 | 428477539 | 33534082 | 0.000000
09-04-2025 23:03:05000 | -6825753 | 68.2575 | 88266406 | 235598.89 | 168684250 | 99174240 | 49866516 | 0.000000 | 440930389 | 34488010 | 0.000000
09-04-2025 23:03:10000 | -6708619 | 67.0862 | 83547031 | 235591.67 | 165703705 | 99233437 | 49884491 | 0.000000 | 452666901 | 35428464 | 0.000000
09-04-2025 23:03:15000 | -6688889 | 66.8889 | 80002642 | 235478.67 | 165193054 | 99292313 | 49881023 | 0.000000 | 463908539 | 36358491 | 0.000000
09-04-2025 23:03:20000 | -6640947 | 66.4095 | 83063730 | 235578.02 | 164049866 | 99226830 | 49897575 | 0.000000 | 475278656 | 37285801 | 0.000000
09-04-2025 23:03:25000 | -6655212 | 66.5521 | 81311758 | 235511.44 | 164385162 | 99261887 | 49885208 | 0.000000 | 486569092 | 38207305 | 0.000000
09-04-2025 23:03:30000 | -6777177 | 67.7718 | 83477842 | 235455.36 | 167457596 | 99249924 | 49858498 | 0.000000 | 498140686 | 39143679 | 0.000000
09-04-2025 23:03:35000 | -6853150 | 68.5315 | 85739238 | 235556.69 | 169301514 | 99226456 | 49850018 | 0.000000 | 509854401 | 40093293 | 0.000000
09-04-2025 23:03:40000 | -6714138 | 67.1414 | 84262588 | 235603.72 | 165842087 | 99221664 | 49869339 | 0.000000 | 521698181 | 41032402 | 0.000000
09-04-2025 23:03:45000 | -6567827 | 65.6783 | 80815376 | 235542.22 | 162228455 | 99251457 | 49893497 | 0.000000 | 533099670 | 41952813 | 0.000000
09-04-2025 23:03:50000 | -6554368 | 65.5437 | 81481230 | 235590.98 | 161885773 | 99236122 | 49903030 | 0.000000 | 544375854 | 42861465 | 0.000000
09-04-2025 23:03:55000 | -6667922 | 66.6792 | 83234023 | 235521.30 | 164744461 | 99229889 | 49875538 | 0.000000 | 555773376 | 43782925 | 0.000000
09-04-2025 23:04:00000 | -6773803 | 67.738 | 84327754 | 235506.52 | 167365860 | 99233994 | 49855347 | 0.000000 | 567393738 | 44720117 | 0.000000
09-04-2025 23:04:05000 | -6752856 | 67.5286 | 83950430 | 235553.03 | 166812256 | 99236092 | 49857590 | 0.000000 | 579021790 | 45659336 | 0.000000
09-04-2025 23:04:10000 | -6757200 | 67.572 | 81878110 | 235472.66 | 166911255 | 99273857 | 49860252 | 0.000000 | 590593750 | 46597085 | 0.000000
09-04-2025 23:04:15000 | -6739251 | 67.3925 | 84640107 | 235586.06 | 166475876 | 99220535 | 49862312 | 0.000000 | 602191833 | 47535908 | 0.000000
09-04-2025 23:04:20000 | -6686195 | 66.8619 | 82368682 | 235565.14 | 165132645 | 99249710 | 49875717 | 0.000000 | 613707947 | 48465146 | 0.000000
09-04-2025 23:04:25000 | -6650342 | 66.5034 | 82424248 | 235529.45 | 164289505 | 99240685 | 49873806 | 0.000000 | 625237366 | 49390898 | 0.000000
09-04-2025 23:04:30000 | -6632407 | 66.3241 | 83001641 | 235556.09 | 163855591 | 99226006 | 49878479 | 0.000000 | 636845947 | 50313286 | 0.000000
09-04-2025 23:04:35000 | -6629279 | 66.2928 | 83897588 | 235589.17 | 163778885 | 99208672 | 49883343 | 0.000000 | 648481995 | 51233564 | 0.000000
09-04-2025 23:04:40000 | -6771704 | 67.717 | 84514238 | 235514.94 | 167313705 | 99230171 | 49849083 | 0.000000 | 660170471 | 52167607 | 0.000000
09-04-2025 23:04:45000 | -6819667 | 68.1967 | 86625811 | 235568.23 | 168504333 | 99202881 | 49842426 | 0.000000 | 672147461 | 53111606 | 0.000000
09-04-2025 23:04:50000 | -6718474 | 67.1847 | 86882559 | 235650.16 | 165996674 | 99174171 | 49869469 | 0.000000 | 684233154 | 54051040 | 0.000000
09-04-2025 23:04:55000 | -6640559 | 66.4056 | 83458662 | 235589.19 | 164039749 | 99219460 | 49884796 | 0.000000 | 695983826 | 54979668 | 0.000000
09-04-2025 23:05:00000 | -6583005 | 65.83 | 83927520 | 235638.44 | 162623627 | 99197075 | 49903294 | 0.000000 | 707564331 | 55894712 | 0.000000
09-04-2025 23:05:05000 | -6555453 | 65.5545 | 84062363 | 235638.03 | 161957077 | 99187820 | 49902836 | 0.000000 | 719224182 | 56807397 | 0.000000
09-04-2025 23:05:10000 | -6626603 | 66.266 | 84592432 | 235594.33 | 163733521 | 99195023 | 49890690 | 0.000000 | 730900391 | 57720815 | 0.000000
09-04-2025 23:05:15000 | -6637148 | 66.3715 | 87139736 | 235621.45 | 164056244 | 99149117 | 49882389 | 0.000000 | 742967285 | 58641870 | 0.000000
09-04-2025 23:05:20000 | -6646361 | 66.4636 | 87033164 | 235656.58 | 164245193 | 99153496 | 49886913 | 0.000000 | 755003113 | 59564321 | 0.000000
09-04-2025 23:05:25000 | -6567677 | 65.6768 | 85861133 | 235620.05 | 162320221 | 99156242 | 49914238 | 0.000000 | 767168762 | 60476035 | 0.000000
09-04-2025 23:05:30000 | -6670157 | 66.7016 | 85862734 | 235576.94 | 164843155 | 99181625 | 49894474 | 0.000000 | 779036133 | 61396831 | 0.000000
09-04-2025 23:05:35000 | -6592137 | 65.9214 | 88221709 | 235706.81 | 162933670 | 99116348 | 49914169 | 0.000000 | 791264893 | 62319224 | 0.000000
09-04-2025 23:05:40000 | -6552463 | 65.5246 | 84247021 | 235609.61 | 161908295 | 99183556 | 49924671 | 0.000000 | 803118225 | 63228379 | 0.000000
09-04-2025 23:05:45000 | -6652564 | 66.5256 | 85054932 | 235597.45 | 164375137 | 99192566 | 49899136 | 0.000000 | 814736206 | 64149355 | 0.000000
09-04-2025 23:05:50000 | -6710869 | 67.1087 | 85025947 | 235555.50 | 165823730 | 99206909 | 49897644 | 0.000000 | 826603821 | 65075938 | 0.000000
09-04-2025 23:05:55000 | -6684362 | 66.8436 | 85434063 | 235584.67 | 165167969 | 99193077 | 49904015 | 0.000000 | 838544678 | 66006494 | 0.000000
09-04-2025 23:06:00000 | -6710505 | 67.1051 | 82741328 | 235534.70 | 165758530 | 99248398 | 49892963 | 0.000000 | 850115906 | 66935396 | 0.000000
09-04-2025 23:06:05000 | -6664088 | 66.6409 | 84037256 | 235557.95 | 164651138 | 99214241 | 49909298 | 0.000000 | 861899353 | 67864727 | 0.000000
09-04-2025 23:06:10000 | -6601077 | 66.0108 | 80522295 | 235508.94 | 163045303 | 99264198 | 49914165 | 0.000000 | 873233887 | 68783672 | 0.000000
09-04-2025 23:06:15000 | -6538455 | 65.3846 | 79439980 | 235506.31 | 161492722 | 99270004 | 49929451 | 0.000000 | 884358643 | 69695308 | 0.000000
09-04-2025 23:06:20000 | -6615444 | 66.1544 | 80634019 | 235480.00 | 163421432 | 99265350 | 49919357 | 0.000000 | 895411316 | 70611401 | 0.000000
09-04-2025 23:06:25000 | -6644408 | 66.4441 | 83591572 | 235585.81 | 164141357 | 99217896 | 49921997 | 0.000000 | 906808472 | 71534175 | 0.000000
09-04-2025 23:06:30000 | -6587278 | 65.8728 | 82049746 | 235557.41 | 162722214 | 99233177 | 49932697 | 0.000000 | 918417725 | 72453916 | 0.000000
09-04-2025 23:06:35000 | -6605805 | 66.058 | 81430352 | 235544.31 | 163166916 | 99248764 | 49919830 | 0.000000 | 929701538 | 73370723 | 0.000000
09-04-2025 23:06:40000 | -6588725 | 65.8872 | 83820098 | 235600.59 | 162781631 | 99200478 | 49934734 | 0.000000 | 941243225 | 74289019 | 0.000000
09-04-2025 23:06:45000 | -6525120 | 65.2512 | 82433564 | 235574.17 | 161214066 | 99211433 | 49953438 | 0.000000 | 952785217 | 75196675 | 0.000000
09-04-2025 23:06:50000 | -6512523 | 65.1252 | 83547295 | 235630.70 | 160901794 | 99187141 | 49962158 | 0.000000 | 964219543 | 76101631 | 0.000000
09-04-2025 23:06:55000 | -6483847 | 64.8385 | 83864414 | 235639.58 | 160207352 | 99173866 | 49984730 | 0.000000 | 975921814 | 77001953 | 0.000000
09-04-2025 23:07:00000 | -6561725 | 65.6172 | 85326582 | 235630.20 | 162154083 | 99165092 | 49976204 | 0.000000 | 987605530 | 77907646 | 0.000000
09-04-2025 23:07:05000 | -6424827 | 64.2483 | 86244121 | 235682.59 | 158823883 | 99111038 | 50022297 | 0.000000 | 999838989 | 78804873 | 0.000000
09-04-2025 23:07:10000 | -6526361 | 65.2636 | 84967979 | 235610.42 | 161298874 | 99163124 | 50013180 | 0.000000 | 10117139 | 79703159 | 0.000000
09-04-2025 23:07:15000 | -6705182 | 67.0518 | 88179414 | 235571.30 | 165781113 | 99146324 | 49976460 | 0.000000 | 10238334 | 80622729 | 0.000000
09-04-2025 23:07:20000 | -6879835 | 68.7983 | 89253711 | 235574.34 | 170044907 | 99168953 | 49940670 | 0.000000 | 10362117 | 81573506 | 0.000000
09-04-2025 23:07:25000 | -6842335 | 68.4233 | 90624844 | 235683.72 | 169099854 | 99134262 | 49953007 | 0.000000 | 10487574 | 82527686 | 0.000000
09-04-2025 23:07:30000 | -6764786 | 67.6479 | 85962773 | 235595.23 | 167130661 | 99202263 | 49953445 | 0.000000 | 10609343 | 83470820 | 0.000000
09-04-2025 23:07:35000 | -6812168 | 68.1217 | 83796123 | 235518.77 | 168273605 | 99251915 | 49922306 | 0.000000 | 10725642 | 84412939 | 0.000000
09-04-2025 23:07:40000 | -6832002 | 68.32 | 85910820 | 235551.02 | 168796967 | 99218628 | 49928154 | 0.000000 | 10844703 | 85358984 | 0.000000
09-04-2025 23:07:45000 | -6752439 | 67.5244 | 86242129 | 235644.58 | 166815018 | 99194221 | 49936951 | 0.000000 | 10964141 | 86303994 | 0.000000
09-04-2025 23:07:50000 | -6651278 | 66.5128 | 84277227 | 235639.81 | 164288101 | 99206787 | 49954636 | 0.000000 | 11081759 | 87234414 | 0.000000
09-04-2025 23:07:55000 | -6511937 | 65.1194 | 82419121 | 235636.22 | 160851913 | 99208549 | 49982227 | 0.000000 | 11197744 | 88146084 | 0.000000
09-04-2025 23:08:00000 | -6564624 | 65.6462 | 83629883 | 235597.00 | 162193939 | 99198273 | 49983665 | 0.000000 | 11312891 | 89053506 | 0.000000
09-04-2025 23:08:05000 | -6622673 | 66.2267 | 85971875 | 235630.48 | 163660812 | 99167915 | 49971279 | 0.000000 | 11431001 | 89972471 | 0.000000
09-04-2025 23:08:10000 | -6594973 | 65.9497 | 85486094 | 235626.36 | 162967651 | 99170334 | 49989235 | 0.000000 | 11550894 | 90891250 | 0.000000
09-04-2025 23:08:15000 | -6674127 | 66.7413 | 83691152 | 235538.05 | 164904678 | 99222939 | 49971123 | 0.000000 | 11667948 | 91810840 | 0.000000
09-04-2025 23:08:20000 | -6747057 | 67.4706 | 86362119 | 235599.58 | 166715027 | 99190735 | 49955524 | 0.000000 | 11785975 | 92742656 | 0.000000
09-04-2025 23:08:25000 | -6682999 | 66.83 | 85355088 | 235617.36 | 165113663 | 99194229 | 49958241 | 0.000000 | 11904370 | 93676143 | 0.000000
09-04-2025 23:08:30000 | -6725107 | 67.2511 | 82924912 | 235506.48 | 166136978 | 99248337 | 49955845 | 0.000000 | 12021600 | 94608809 | 0.000000
09-04-2025 23:08:35000 | -6826119 | 68.2612 | 83428896 | 235496.28 | 168621063 | 99261375 | 49940010 | 0.000000 | 12136362 | 95548281 | 0.000000
09-04-2025 23:08:40000 | -6727049 | 67.2705 | 83434854 | 235564.80 | 166161774 | 99239601 | 49957985 | 0.000000 | 12253693 | 96489180 | 0.000000
09-04-2025 23:08:45000 | -6653659 | 66.5366 | 80245952 | 235503.83 | 164322586 | 99280571 | 49967899 | 0.000000 | 12366567 | 97416689 | 0.000000
09-04-2025 23:08:50000 | -6707667 | 67.0767 | 81158120 | 235480.77 | 165679459 | 99275970 | 49944393 | 0.000000 | 12478232 | 98346270 | 0.000000
09-04-2025 23:08:55000 | -6700685 | 67.0069 | 82997617 | 235561.06 | 165511887 | 99241600 | 49957939 | 0.000000 | 12593002 | 99278682 | 0.000000
09-04-2025 23:09:00000 | -6641156 | 66.4116 | 83202354 | 235583.88 | 164051346 | 99224327 | 49974384 | 0.000000 | 12708304 | 10020441 | 0.000000
09-04-2025 23:09:05000 | -6659550 | 66.5955 | 80675947 | 235494.91 | 164484680 | 99274193 | 49970730 | 0.000000 | 12821506 | 10112790 | 0.000000
09-04-2025 23:09:10000 | -6640663 | 66.4066 | 81036685 | 235515.52 | 164021194 | 99263634 | 49963501 | 0.000000 | 12933837 | 10205122 | 0.000000
09-04-2025 23:09:15000 | -6668113 | 66.6811 | 81204146 | 235482.55 | 164716583 | 99266632 | 49960381 | 0.000000 | 13047225 | 10297660 | 0.000000
09-04-2025 23:09:20000 | -6715292 | 67.1529 | 80761992 | 235474.59 | 165856812 | 99284561 | 49949444 | 0.000000 | 13158795 | 10390662 | 0.000000
09-04-2025 23:09:25000 | -6581829 | 65.8183 | 81926602 | 235570.97 | 162580551 | 99234200 | 49980690 | 0.000000 | 13272402 | 10482924 | 0.000000
09-04-2025 23:09:30000 | -6530413 | 65.3041 | 81418745 | 235605.05 | 161291702 | 99231735 | 50002262 | 0.000000 | 13384833 | 10574001 | 0.000000
09-04-2025 23:09:35000 | -6577260 | 65.7726 | 80691094 | 235511.23 | 162471756 | 99255844 | 49998302 | 0.000000 | 13497019 | 10664893 | 0.000000
09-04-2025 23:09:40000 | -6637602 | 66.376 | 82454277 | 235512.63 | 163989807 | 99237251 | 49990753 | 0.000000 | 13611350 | 10756896 | 0.000000
09-04-2025 23:09:45000 | -6810335 | 68.1034 | 82265918 | 235421.61 | 168252747 | 99278305 | 49960430 | 0.000000 | 13725105 | 10850510 | 0.000000
09-04-2025 23:09:50000 | -6786145 | 67.8615 | 84254805 | 235508.20 | 167662094 | 99238052 | 49972424 | 0.000000 | 13842205 | 10944734 | 0.000000
09-04-2025 23:09:55000 | -6797351 | 67.9735 | 81387261 | 235460.31 | 167885544 | 99290810 | 49965267 | 0.000000 | 13956226 | 11038960 | 0.000000
09-04-2025 23:10:00000 | -6728009 | 67.2801 | 82790576 | 235562.20 | 166166382 | 99251381 | 49983665 | 0.000000 | 14070243 | 11132908 | 0.000000
09-04-2025 23:10:05000 | -6643428 | 66.4343 | 80968467 | 235530.78 | 164077530 | 99265465 | 50001743 | 0.000000 | 14184395 | 11225635 | 0.000000
09-04-2025 23:10:10000 | -6494334 | 64.9433 | 81684219 | 235647.81 | 160387039 | 99218262 | 50026814 | 0.000000 | 14297308 | 11316910 | 0.000000
09-04-2025 23:10:15000 | -6494143 | 64.9414 | 81243770 | 235563.20 | 160429199 | 99226524 | 50031223 | 0.000000 | 14410294 | 11407109 | 0.000000
09-04-2025 23:10:20000 | -6521912 | 65.2191 | 84734834 | 235661.88 | 161141052 | 99166534 | 50038742 | 0.000000 | 14525363 | 11497701 | 0.000000
09-04-2025 23:10:25000 | -6636603 | 66.366 | 84887090 | 235558.94 | 164005630 | 99191887 | 50031212 | 0.000000 | 14643519 | 11589233 | 0.000000
09-04-2025 23:10:30000 | -6753884 | 67.5388 | 84878203 | 235487.88 | 166907883 | 99219543 | 50007923 | 0.000000 | 14761069 | 11682117 | 0.000000
09-04-2025 23:10:35000 | -6814936 | 68.1494 | 85636387 | 235550.94 | 168372787 | 99219711 | 49995274 | 0.000000 | 14879047 | 11776706 | 0.000000
09-04-2025 23:10:40000 | -6789942 | 67.8994 | 83970410 | 235503.16 | 167749908 | 99243965 | 50005859 | 0.000000 | 14997944 | 11871039 | 0.000000
09-04-2025 23:10:45000 | -6834526 | 68.3453 | 83508789 | 235475.47 | 168839890 | 99261780 | 49989426 | 0.000000 | 15113738 | 11965821 | 0.000000
09-04-2025 23:10:50000 | -6909338 | 69.0934 | 84847061 | 235514.23 | 170671082 | 99254425 | 49964455 | 0.000000 | 15229690 | 12061670 | 0.000000
09-04-2025 23:10:55000 | -6906048 | 69.0605 | 83093662 | 235481.06 | 170569382 | 99283920 | 49959286 | 0.000000 | 15346259 | 12157635 | 0.000000
09-04-2025 23:11:00000 | -6831180 | 68.3118 | 81515879 | 235486.69 | 168691620 | 99295540 | 49963779 | 0.000000 | 15460645 | 12252998 | 0.000000
09-04-2025 23:11:05000 | -6775291 | 67.7529 | 80484019 | 235472.33 | 167309174 | 99301819 | 49954475 | 0.000000 | 15572701 | 12347547 | 0.000000
09-04-2025 23:11:10000 | -6666435 | 66.6643 | 80236396 | 235545.17 | 164606522 | 99283463 | 49970558 | 0.000000 | 15684247 | 12440726 | 0.000000
09-04-2025 23:11:15000 | -6517970 | 65.1797 | 79030610 | 235559.39 | 160952621 | 99272926 | 49996399 | 0.000000 | 15795356 | 12532045 | 0.000000
09-04-2025 23:11:20000 | -6571275 | 65.7127 | 80024521 | 235531.03 | 162295013 | 99266640 | 49991222 | 0.000000 | 15904658 | 12623118 | 0.000000
09-04-2025 23:11:25000 | -6612002 | 66.12 | 82453711 | 235571.61 | 163326431 | 99231407 | 49985165 | 0.000000 | 16017443 | 12714798 | 0.000000
09-04-2025 23:11:30000 | -6511988 | 65.1199 | 82800752 | 235603.84 | 160883209 | 99201302 | 50003941 | 0.000000 | 16133578 | 12806019 | 0.000000
09-04-2025 23:11:35000 | -6591134 | 65.9113 | 83048281 | 235583.75 | 162828094 | 99215530 | 49997692 | 0.000000 | 16246877 | 12897331 | 0.000000
09-04-2025 23:11:40000 | -6694440 | 66.9444 | 83754805 | 235532.83 | 165405350 | 99226433 | 49988400 | 0.000000 | 16362795 | 12989701 | 0.000000
09-04-2025 23:11:45000 | -6771024 | 67.7102 | 82926582 | 235482.94 | 167274963 | 99258354 | 49962364 | 0.000000 | 16477629 | 13083338 | 0.000000
09-04-2025 23:11:50000 | -6789463 | 67.8946 | 87575771 | 235634.44 | 167753708 | 99178345 | 49972828 | 0.000000 | 16596386 | 13178045 | 0.000000
09-04-2025 23:11:55000 | -6721456 | 67.2146 | 81593774 | 235521.69 | 166002090 | 99271233 | 49967983 | 0.000000 | 16711588 | 13271784 | 0.000000
09-04-2025 23:12:00000 | -6663639 | 66.6364 | 81990635 | 235544.52 | 164592667 | 99251526 | 49966751 | 0.000000 | 16825321 | 13364923 | 0.000000
09-04-2025 23:12:05000 | -6708388 | 67.0839 | 79150781 | 235425.86 | 165679367 | 99311127 | 49941185 | 0.000000 | 16936584 | 13457696 | 0.000000
09-04-2025 23:12:10000 | -6669848 | 66.6985 | 82579316 | 235579.33 | 164734436 | 99242256 | 49939831 | 0.000000 | 17048796 | 13550698 | 0.000000
09-04-2025 23:12:15000 | -6576116 | 65.7612 | 79725547 | 235508.78 | 162414200 | 99273109 | 49945675 | 0.000000 | 17161473 | 13642761 | 0.000000
09-04-2025 23:12:20000 | -6445317 | 64.4532 | 77100430 | 235498.66 | 159166092 | 99292114 | 49955524 | 0.000000 | 17269791 | 13733070 | 0.000000
09-04-2025 23:12:25000 | -6373841 | 63.7384 | 74217373 | 235466.30 | 157363480 | 99328896 | 49955372 | 0.000000 | 17374594 | 13821704 | 0.000000
09-04-2025 23:12:30000 | -6343321 | 63.4332 | 76212939 | 235482.23 | 156666748 | 99285957 | 49942051 | 0.000000 | 17479238 | 13909852 | 0.000000
09-04-2025 23:12:35000 | -6315572 | 63.1557 | 76032769 | 235490.55 | 155979248 | 99283104 | 49931362 | 0.000000 | 17585201 | 13997862 | 0.000000
09-04-2025 23:12:40000 | -6040725 | 60.4072 | 76423105 | 235607.73 | 149230331 | 99209198 | 49978348 | 0.000000 | 17691932 | 14083396 | 0.000000
09-04-2025 23:12:45000 | -5843603 | 58.436 | 71223638 | 235534.00 | 144326859 | 99265404 | 49999203 | 0.000000 | 17793389 | 14165539 | 0.000000
09-04-2025 23:12:50000 | -5743534 | 57.4353 | 71638115 | 235519.67 | 141914368 | 99231102 | 50001686 | 0.000000 | 17892738 | 14245595 | 0.000000
09-04-2025 23:12:55000 | -5452113 | 54.5211 | 73868423 | 235709.06 | 134790283 | 99094627 | 50040867 | 0.000000 | 17995023 | 14322957 | 0.000000
09-04-2025 23:13:00000 | -5328656 | 53.2866 | 71971455 | 235644.70 | 131771515 | 99100166 | 50052734 | 0.000000 | 18095596 | 14397517 | 0.000000
09-04-2025 23:13:05000 | -5150030 | 51.5003 | 73614937 | 235707.42 | 127454124 | 98993790 | 50065018 | 0.000000 | 18197976 | 14470049 | 0.000000
09-04-2025 23:13:10000 | -5028198 | 50.282 | 71883794 | 235677.80 | 124461235 | 98993507 | 50069183 | 0.000000 | 18298488 | 14540445 | 0.000000
09-04-2025 23:13:15000 | -4996673 | 49.9667 | 72136431 | 235642.55 | 123722031 | 98973892 | 50054077 | 0.000000 | 18398295 | 14610004 | 0.000000
09-04-2025 23:13:20000 | -4994268 | 49.9427 | 73526260 | 235638.38 | 123713280 | 98933601 | 50042397 | 0.000000 | 18500074 | 14679403 | 0.000000
09-04-2025 23:13:25000 | -4868779 | 48.6878 | 74832900 | 235758.38 | 120663727 | 98839348 | 50048443 | 0.000000 | 18603711 | 14747771 | 0.000000
09-04-2025 23:13:30000 | -4894745 | 48.9475 | 73292300 | 235666.31 | 121279663 | 98897453 | 50043804 | 0.000000 | 18705967 | 14815335 | 0.000000
09-04-2025 23:13:35000 | -4908618 | 49.0862 | 76815044 | 235780.31 | 121688148 | 98797585 | 50029079 | 0.000000 | 18810032 | 14883986 | 0.000000
09-04-2025 23:13:40000 | -4831030 | 48.3103 | 76107529 | 235758.66 | 119792587 | 98781708 | 50047550 | 0.000000 | 18915481 | 14951552 | 0.000000
09-04-2025 23:13:45000 | -4941211 | 49.4121 | 71882373 | 235586.84 | 122401230 | 98958351 | 50010204 | 0.000000 | 19014791 | 15019104 | 0.000000
09-04-2025 23:13:50000 | -4932511 | 49.3251 | 75155449 | 235688.27 | 122248650 | 98859032 | 49999760 | 0.000000 | 19118389 | 15087646 | 0.000000
09-04-2025 23:13:55000 | -4885067 | 48.8507 | 72033784 | 235605.22 | 121029655 | 98930237 | 49995396 | 0.000000 | 19220597 | 15155852 | 0.000000
09-04-2025 23:14:00000 | -4851412 | 48.5141 | 71450347 | 235624.50 | 120182564 | 98932800 | 49997807 | 0.000000 | 19320240 | 15223234 | 0.000000
09-04-2025 23:14:05000 | -4836719 | 48.3672 | 71097764 | 235620.69 | 119815918 | 98936813 | 49995979 | 0.000000 | 19418998 | 15290362 | 0.000000
09-04-2025 23:14:10000 | -4820881 | 48.2088 | 70861084 | 235626.56 | 119421448 | 98936928 | 49999809 | 0.000000 | 19518127 | 15357654 | 0.000000
09-04-2025 23:14:15000 | -4771371 | 47.7137 | 69623232 | 235621.25 | 118181648 | 98952095 | 50018147 | 0.000000 | 19616520 | 15424145 | 0.000000
09-04-2025 23:14:20000 | -4689985 | 46.8999 | 69332637 | 235639.78 | 116187302 | 98924889 | 50027966 | 0.000000 | 19713070 | 15489379 | 0.000000
09-04-2025 23:14:25000 | -4621249 | 46.2125 | 69779653 | 235698.59 | 114513985 | 98879120 | 50042309 | 0.000000 | 19808883 | 15553888 | 0.000000
09-04-2025 23:14:30000 | -4606798 | 46.068 | 71720420 | 235677.13 | 114241745 | 98809723 | 50060284 | 0.000000 | 19908276 | 15617977 | 0.000000
09-04-2025 23:14:35000 | -4745361 | 47.4536 | 73109453 | 235653.03 | 117659515 | 98833916 | 50048016 | 0.000000 | 20007523 | 15683033 | 0.000000
09-04-2025 23:14:40000 | -4787827 | 47.8783 | 72277256 | 235639.42 | 118667320 | 98879662 | 50038162 | 0.000000 | 20108303 | 15749414 | 0.000000
09-04-2025 23:14:45000 | -4745962 | 47.4596 | 71026025 | 235632.30 | 117609627 | 98898628 | 50053303 | 0.000000 | 20208462 | 15815638 | 0.000000
09-04-2025 23:14:50000 | -4692300 | 46.923 | 72825933 | 235730.34 | 116331482 | 98816933 | 50067165 | 0.000000 | 20309049 | 15881040 | 0.000000
09-04-2025 23:14:55000 | -4741765 | 47.4177 | 73675962 | 235690.00 | 117578453 | 98814331 | 50067760 | 0.000000 | 20411589 | 15946441 | 0.000000
09-04-2025 23:15:00000 | -4824671 | 48.2467 | 74474434 | 235701.98 | 119607414 | 98829498 | 50047997 | 0.000000 | 20513037 | 16012664 | 0.000000
09-04-2025 23:15:05000 | -4871642 | 48.7164 | 75375146 | 235693.38 | 120783203 | 98824120 | 50044937 | 0.000000 | 10594049 | 67674774 | 0.000000
09-04-2025 23:15:10000 | -4862219 | 48.6222 | 76271001 | 235742.98 | 120561462 | 98791924 | 50057064 | 0.000000 | 21044495 | 135225296 | 0.000000
09-04-2025 23:15:15000 | -4841129 | 48.4113 | 73178950 | 235673.73 | 119971550 | 98876732 | 50047108 | 0.000000 | 31367176 | 202406754 | 0.000000
09-04-2025 23:15:20000 | -4868821 | 48.6882 | 73268530 | 235655.77 | 120655075 | 98886589 | 50040798 | 0.000000 | 41554970 | 269789276 | 0.000000
09-04-2025 23:15:25000 | -4975600 | 49.756 | 74620239 | 235641.25 | 123306458 | 98894035 | 50015919 | 0.000000 | 51805103 | 338608307 | 0.000000
09-04-2025 23:15:30000 | -4949716 | 49.4972 | 73895640 | 235654.34 | 122637794 | 98903877 | 50014908 | 0.000000 | 62081333 | 407620361 | 0.000000
09-04-2025 23:15:35000 | -4906905 | 49.069 | 70390210 | 235594.27 | 121505501 | 98986702 | 50001816 | 0.000000 | 72030609 | 476083649 | 0.000000
09-04-2025 23:15:40000 | -4908013 | 49.0801 | 72632109 | 235650.59 | 121582802 | 98922661 | 49991882 | 0.000000 | 82067207 | 544565063 | 0.000000
09-04-2025 23:15:45000 | -4745934 | 47.4593 | 72285156 | 235722.36 | 117611671 | 98859886 | 50022038 | 0.000000 | 92099770 | 611502747 | 0.000000
09-04-2025 23:15:50000 | -4625798 | 46.258 | 71559204 | 235733.50 | 114674438 | 98824516 | 50042213 | 0.000000 | 101982346 | 676269714 | 0.000000
09-04-2025 23:15:55000 | -4610827 | 46.1083 | 69400347 | 235649.63 | 114269806 | 98886139 | 50051910 | 0.000000 | 111680466 | 740561218 | 0.000000
09-04-2025 23:16:00000 | -4699335 | 46.9933 | 71297607 | 235644.30 | 116482689 | 98868568 | 50041153 | 0.000000 | 121491966 | 805256775 | 0.000000
09-04-2025 23:16:05000 | -4795331 | 47.9533 | 73761504 | 235671.56 | 118885437 | 98837570 | 50041306 | 0.000000 | 131659409 | 871429688 | 0.000000
09-04-2025 23:16:10000 | -4666878 | 46.6688 | 72949248 | 235729.48 | 115717133 | 98800255 | 50067566 | 0.000000 | 141906433 | 936795349 | 0.000000
09-04-2025 23:16:15000 | -4581286 | 45.8129 | 69902598 | 235652.47 | 113568031 | 98855865 | 50075176 | 0.000000 | 151813843 | 10010726 | 0.000000
09-04-2025 23:16:20000 | -4625634 | 46.2563 | 71817490 | 235698.31 | 114691833 | 98816086 | 50091366 | 0.000000 | 161619507 | 10649922 | 0.000000
09-04-2025 23:16:25000 | -4716532 | 47.1653 | 71279985 | 235629.28 | 116910408 | 98877213 | 50079227 | 0.000000 | 171541275 | 11297057 | 0.000000
09-04-2025 23:16:30000 | -4792433 | 47.9243 | 75386284 | 235714.52 | 118860390 | 98785286 | 50067581 | 0.000000 | 181759979 | 11960771 | 0.000000
09-04-2025 23:16:35000 | -4802666 | 48.0267 | 76827393 | 235750.02 | 119139069 | 98744553 | 50078175 | 0.000000 | 192439011 | 12627747 | 0.000000
09-04-2025 23:16:40000 | -4839974 | 48.3997 | 70142129 | 235563.69 | 119893341 | 98966133 | 50058918 | 0.000000 | 202462265 | 13294098 | 0.000000
09-04-2025 23:16:45000 | -5016959 | 50.1696 | 73608491 | 235603.50 | 124284554 | 98940742 | 50017929 | 0.000000 | 212432037 | 13983326 | 0.000000
09-04-2025 23:16:50000 | -5064147 | 50.6415 | 73662075 | 235561.31 | 125455544 | 98958595 | 50002258 | 0.000000 | 222788498 | 14686198 | 0.000000
09-04-2025 23:16:55000 | -5121630 | 51.2163 | 69906528 | 235491.81 | 126762787 | 99081306 | 49980202 | 0.000000 | 232764801 | 15392672 | 0.000000
09-04-2025 23:17:00000 | -4786309 | 47.8631 | 76353579 | 235886.52 | 118657486 | 98751373 | 50052776 | 0.000000 | 243075577 | 16078727 | 0.000000
09-04-2025 23:17:05000 | -4525330 | 45.2533 | 71546582 | 235786.52 | 112215996 | 98773132 | 50097340 | 0.000000 | 253201035 | 16717473 | 0.000000
09-04-2025 23:17:10000 | -4611636 | 46.1164 | 69291982 | 235635.31 | 114290688 | 98889938 | 50070072 | 0.000000 | 262829041 | 17350754 | 0.000000
09-04-2025 23:17:15000 | -4811345 | 48.1135 | 72023184 | 235593.81 | 119249725 | 98898064 | 50049183 | 0.000000 | 272744904 | 18008818 | 0.000000
09-04-2025 23:17:20000 | -4860677 | 48.6068 | 72782090 | 235642.19 | 120447525 | 98897453 | 50041451 | 0.000000 | 282854797 | 18681298 | 0.000000
09-04-2025 23:17:25000 | -4818303 | 48.183 | 73218867 | 235665.16 | 119424232 | 98865028 | 50051178 | 0.000000 | 293115662 | 19356630 | 0.000000
09-04-2025 23:17:30000 | -4776782 | 47.7678 | 69947061 | 235609.03 | 118330132 | 98944832 | 50060730 | 0.000000 | 302891785 | 20021886 | 0.000000
09-04-2025 23:17:35000 | -4829056 | 48.2906 | 71669897 | 235689.20 | 119622635 | 98916534 | 50051132 | 0.000000 | 312537445 | 20688428 | 0.000000
09-04-2025 23:17:40000 | -4775141 | 47.7514 | 73321113 | 235731.70 | 118352226 | 98841599 | 50062775 | 0.000000 | 322641998 | 21355029 | 0.000000
09-04-2025 23:17:45000 | -4704140 | 47.0414 | 71214067 | 235651.39 | 116591942 | 98873444 | 50067020 | 0.000000 | 332677887 | 22012957 | 0.000000
09-04-2025 23:17:50000 | -5054498 | 50.545 | 67889995 | 235386.69 | 125121529 | 99109985 | 49996662 | 0.000000 | 342176758 | 22692029 | 0.000000
09-04-2025 23:17:55000 | -5122723 | 51.2272 | 73573809 | 235577.16 | 126863922 | 98984314 | 49979210 | 0.000000 | 352208221 | 23401536 | 0.000000
09-04-2025 23:18:00000 | -5088028 | 50.8803 | 70465234 | 235549.39 | 125930168 | 99054573 | 49975582 | 0.000000 | 362016754 | 24111958 | 0.000000
09-04-2025 23:18:05000 | -5030731 | 50.3073 | 68123857 | 235535.88 | 124464912 | 99095551 | 49974854 | 0.000000 | 371648529 | 24814707 | 0.000000
09-04-2025 23:18:10000 | -4955077 | 49.5508 | 66458647 | 235512.22 | 122591110 | 99112518 | 49972553 | 0.000000 | 380946533 | 25505942 | 0.000000
09-04-2025 23:18:15000 | -4947630 | 49.4763 | 66073608 | 235488.27 | 122406532 | 99120026 | 49961361 | 0.000000 | 390093872 | 26196692 | 0.000000
09-04-2025 23:18:20000 | -4860127 | 48.6013 | 64522466 | 235516.36 | 120220474 | 99130234 | 49972687 | 0.000000 | 399089508 | 26875955 | 0.000000
09-04-2025 23:18:25000 | -4569529 | 45.6953 | 65324717 | 235628.28 | 113138580 | 98993561 | 50023582 | 0.000000 | 408144897 | 27528828 | 0.000000
09-04-2025 23:18:30000 | -4459143 | 44.5914 | 65867314 | 235657.13 | 110462547 | 98926575 | 50060482 | 0.000000 | 417264862 | 28154182 | 0.000000
09-04-2025 23:18:35000 | -4446993 | 44.4699 | 66753535 | 235635.11 | 110210564 | 98892044 | 50058167 | 0.000000 | 426344116 | 28773779 | 0.000000
09-04-2025 23:18:40000 | -4475727 | 44.7573 | 68727974 | 235663.67 | 110964149 | 98841461 | 50070190 | 0.000000 | 435791901 | 29393604 | 0.000000
09-04-2025 23:18:45000 | -4447543 | 44.4754 | 69456343 | 235640.86 | 110319504 | 98802437 | 50093777 | 0.000000 | 445508881 | 30012734 | 0.000000
09-04-2025 23:18:50000 | -4554741 | 45.5474 | 69130215 | 235626.48 | 112908875 | 98867722 | 50074512 | 0.000000 | 454952850 | 30639436 | 0.000000
09-04-2025 23:18:55000 | -4687654 | 46.8765 | 72311704 | 235638.34 | 116240768 | 98831017 | 50070351 | 0.000000 | 464789978 | 31283037 | 0.000000
09-04-2025 23:19:00000 | -4749374 | 47.4937 | 72457578 | 235647.55 | 117737816 | 98856163 | 50067848 | 0.000000 | 474887665 | 31942849 | 0.000000
09-04-2025 23:19:05000 | -4763764 | 47.6376 | 73033945 | 235667.53 | 118095024 | 98845100 | 50060436 | 0.000000 | 485006622 | 32605645 | 0.000000
09-04-2025 23:19:10000 | -4833945 | 48.3394 | 74529399 | 235703.59 | 119831833 | 98832214 | 50054726 | 0.000000 | 495243988 | 33276162 | 0.000000
09-04-2025 23:19:15000 | -4828805 | 48.288 | 72630156 | 235657.28 | 119661789 | 98887680 | 50060371 | 0.000000 | 505338593 | 33947373 | 0.000000
09-04-2025 23:19:20000 | -4787294 | 47.8729 | 73146631 | 235688.97 | 118658440 | 98852760 | 50060654 | 0.000000 | 515417419 | 34615427 | 0.000000
09-04-2025 23:19:25000 | -4812613 | 48.1261 | 72595132 | 235665.20 | 119264168 | 98881363 | 50061291 | 0.000000 | 525481628 | 35280732 | 0.000000
09-04-2025 23:19:30000 | -4768695 | 47.687 | 73920771 | 235745.14 | 118208366 | 98819778 | 50071896 | 0.000000 | 535719849 | 35943491 | 0.000000
09-04-2025 23:19:35000 | -4688325 | 46.8832 | 73993174 | 235741.67 | 116270378 | 98777367 | 50076004 | 0.000000 | 545981506 | 36599590 | 0.000000
09-04-2025 23:19:40000 | -4685891 | 46.8589 | 75341245 | 235771.27 | 116247917 | 98731972 | 50084438 | 0.000000 | 556355530 | 37251880 | 0.000000
09-04-2025 23:19:45000 | -4661833 | 46.6183 | 74210479 | 235743.55 | 115635735 | 98756554 | 50086670 | 0.000000 | 566654236 | 37899983 | 0.000000
09-04-2025 23:19:50000 | -4748747 | 47.4875 | 71193433 | 235615.70 | 117694099 | 98894791 | 50062000 | 0.000000 | 576734070 | 38552437 | 0.000000
09-04-2025 23:19:55000 | -4823824 | 48.2382 | 75017900 | 235717.91 | 119599571 | 98812248 | 50053818 | 0.000000 | 586891968 | 39223250 | 0.000000
09-04-2025 23:20:00000 | -4890120 | 48.9012 | 74769795 | 235683.73 | 121213028 | 98851189 | 50049572 | 0.000000 | 597397583 | 39897996 | 0.000000
09-04-2025 23:20:05000 | -4881185 | 48.8118 | 75030356 | 235698.25 | 121000374 | 98839142 | 50037464 | 0.000000 | 607806580 | 40575459 | 0.000000
09-04-2025 23:20:10000 | -5009622 | 50.0962 | 69899526 | 235483.11 | 124039474 | 99040550 | 50005367 | 0.000000 | 617783813 | 41264795 | 0.000000
09-04-2025 23:20:15000 | -5020448 | 50.2045 | 72523745 | 235593.97 | 124334076 | 98972664 | 50003025 | 0.000000 | 627911194 | 41961401 | 0.000000
09-04-2025 23:20:20000 | -4920346 | 49.2035 | 71045317 | 235639.39 | 121831726 | 98973587 | 50007103 | 0.000000 | 637820190 | 42652749 | 0.000000
09-04-2025 23:20:25000 | -4754427 | 47.5443 | 68383022 | 235651.06 | 117707832 | 98981422 | 50032524 | 0.000000 | 647407227 | 43323306 | 0.000000
09-04-2025 23:20:30000 | -4645734 | 46.4573 | 69203604 | 235664.16 | 115104675 | 98908653 | 50066750 | 0.000000 | 657080627 | 43969761 | 0.000000
09-04-2025 23:20:35000 | -4662536 | 46.6254 | 67619170 | 235591.16 | 115483017 | 98964668 | 50051231 | 0.000000 | 666548767 | 44615361 | 0.000000
09-04-2025 23:20:40000 | -4823900 | 48.239 | 66907456 | 235462.80 | 119438950 | 99051773 | 50028374 | 0.000000 | 675995056 | 45278496 | 0.000000
09-04-2025 23:20:45000 | -4894016 | 48.9402 | 68733599 | 235517.25 | 121175797 | 99028130 | 50029194 | 0.000000 | 685473999 | 45954897 | 0.000000
09-04-2025 23:20:50000 | -4832382 | 48.3238 | 67807007 | 235543.33 | 119636879 | 99029846 | 50037636 | 0.000000 | 695000061 | 46629712 | 0.000000
09-04-2025 23:20:55000 | -4796148 | 47.9615 | 68133252 | 235560.75 | 118757576 | 99005989 | 50046951 | 0.000000 | 704536255 | 47300142 | 0.000000
09-04-2025 23:21:00000 | -4826477 | 48.2648 | 68510083 | 235565.56 | 119503952 | 99007538 | 50037193 | 0.000000 | 713920227 | 47967261 | 0.000000
09-04-2025 23:21:05000 | -4816022 | 48.1602 | 69958633 | 235618.81 | 119276199 | 98961349 | 50037224 | 0.000000 | 723594482 | 48635034 | 0.000000
09-04-2025 23:21:10000 | -4714646 | 47.1465 | 69662549 | 235635.88 | 116803131 | 98925941 | 50064949 | 0.000000 | 733378296 | 49296904 | 0.000000
09-04-2025 23:21:15000 | -4746159 | 47.4616 | 67215234 | 235527.84 | 117537918 | 99012024 | 50053493 | 0.000000 | 742867065 | 49954448 | 0.000000
09-04-2025 23:21:20000 | -4850588 | 48.5059 | 67317241 | 235494.41 | 120085472 | 99050674 | 50028065 | 0.000000 | 752226318 | 50618574 | 0.000000
09-04-2025 23:21:25000 | -4805797 | 48.058 | 71173696 | 235641.03 | 119058762 | 98921043 | 50041576 | 0.000000 | 762003967 | 51292095 | 0.000000
09-04-2025 23:21:30000 | -4655687 | 46.5569 | 69935366 | 235642.13 | 115388252 | 98890518 | 50079170 | 0.000000 | 771863586 | 51945298 | 0.000000
09-04-2025 23:21:35000 | -4688279 | 46.8828 | 70496724 | 235665.06 | 116177025 | 98888290 | 50081280 | 0.000000 | 781545959 | 52590161 | 0.000000
09-04-2025 23:21:40000 | -4716051 | 47.1605 | 72362881 | 235654.28 | 116933060 | 98843201 | 50076038 | 0.000000 | 791690125 | 53241499 | 0.000000
09-04-2025 23:21:45000 | -4757013 | 47.5701 | 72210547 | 235657.77 | 117908554 | 98867401 | 50072483 | 0.000000 | 801706360 | 53903516 | 0.000000
09-04-2025 23:21:50000 | -4797295 | 47.9729 | 70647549 | 235571.58 | 118871620 | 98932968 | 50067707 | 0.000000 | 811676208 | 54566187 | 0.000000
09-04-2025 23:21:55000 | -5134827 | 51.3483 | 67729897 | 235351.72 | 127081589 | 99141266 | 49983246 | 0.000000 | 821044861 | 55260723 | 0.000000
09-04-2025 23:22:00000 | -5228561 | 52.2856 | 72162769 | 235481.36 | 129435516 | 99060966 | 49959923 | 0.000000 | 830927307 | 55986787 | 0.000000
09-04-2025 23:22:05000 | -5180657 | 51.8066 | 70831538 | 235560.31 | 128182037 | 99078239 | 49972126 | 0.000000 | 840791748 | 56711299 | 0.000000
09-04-2025 23:22:10000 | -5125620 | 51.2562 | 67651133 | 235473.50 | 126787605 | 99140198 | 49966423 | 0.000000 | 850383728 | 57425645 | 0.000000
09-04-2025 23:22:15000 | -5134365 | 51.3436 | 67470708 | 235475.75 | 126996231 | 99147591 | 49956978 | 0.000000 | 859706055 | 58140371 | 0.000000
09-04-2025 23:22:20000 | -5041591 | 50.4159 | 64171758 | 235440.48 | 124657173 | 99199638 | 49956657 | 0.000000 | 868872131 | 58846294 | 0.000000
09-04-2025 23:22:25000 | -4779366 | 47.7937 | 65953232 | 235630.00 | 118242111 | 99061241 | 49998257 | 0.000000 | 877903442 | 59526987 | 0.000000
09-04-2025 23:22:30000 | -4651503 | 46.515 | 59643330 | 235421.34 | 115037773 | 99187935 | 50013885 | 0.000000 | 886528809 | 60177842 | 0.000000
09-04-2025 23:22:35000 | -4605400 | 46.054 | 63347764 | 235550.97 | 113968781 | 99067200 | 50024792 | 0.000000 | 895005981 | 60820151 | 0.000000
09-04-2025 23:22:40000 | -4637353 | 46.3735 | 63460610 | 235505.53 | 114772881 | 99076599 | 50030460 | 0.000000 | 903802612 | 61460732 | 0.000000
09-04-2025 23:22:45000 | -4760220 | 47.6022 | 65785864 | 235502.38 | 117838753 | 99058517 | 50018738 | 0.000000 | 912668945 | 62116396 | 0.000000
09-04-2025 23:22:50000 | -4608891 | 46.0889 | 66603442 | 235593.63 | 114151268 | 98971909 | 50053795 | 0.000000 | 921863159 | 62769360 | 0.000000
09-04-2025 23:22:55000 | -4526714 | 45.2671 | 64478008 | 235566.95 | 112096962 | 99000740 | 50079697 | 0.000000 | 930883301 | 63400957 | 0.000000
09-04-2025 23:23:00000 | -4623621 | 46.2362 | 64759536 | 235519.25 | 114477112 | 99033325 | 50068668 | 0.000000 | 939745239 | 64034341 | 0.000000
09-04-2025 23:23:05000 | -4669711 | 46.6971 | 66923867 | 235562.70 | 115647285 | 98988594 | 50069637 | 0.000000 | 948861084 | 64683276 | 0.000000
09-04-2025 23:23:10000 | -4791295 | 47.913 | 68407720 | 235520.88 | 118670067 | 98996086 | 50062355 | 0.000000 | 958286926 | 65340879 | 0.000000
09-04-2025 23:23:15000 | -4900370 | 49.0037 | 66925586 | 235445.95 | 121310410 | 99080246 | 50046925 | 0.000000 | 967837097 | 66011528 | 0.000000
09-04-2025 23:23:20000 | -4994062 | 49.9406 | 67654414 | 235449.39 | 123604286 | 99094841 | 50023590 | 0.000000 | 977177979 | 66702808 | 0.000000
09-04-2025 23:23:25000 | -5029368 | 50.2937 | 66538940 | 235447.19 | 124429810 | 99136147 | 50007290 | 0.000000 | 986455872 | 67397788 | 0.000000
09-04-2025 23:23:30000 | -4968053 | 49.6805 | 66215146 | 235483.47 | 122908028 | 99123459 | 49999969 | 0.000000 | 995685120 | 68088237 | 0.000000
09-04-2025 23:23:35000 | -4938643 | 49.3864 | 66696016 | 235503.92 | 122197998 | 99100372 | 49986042 | 0.000000 | 10048271 | 68779399 | 0.000000
09-04-2025 23:23:40000 | -4867491 | 48.6749 | 66332031 | 235510.30 | 120454231 | 99084183 | 49995392 | 0.000000 | 10141291 | 69462051 | 0.000000
09-04-2025 23:23:45000 | -4655382 | 46.5538 | 65236992 | 235589.39 | 115230438 | 99032372 | 50031857 | 0.000000 | 10232563 | 70119751 | 0.000000
09-04-2025 23:23:50000 | -4646553 | 46.4655 | 60557695 | 235381.33 | 114964294 | 99161392 | 50027092 | 0.000000 | 10319930 | 70764146 | 0.000000
09-04-2025 23:23:55000 | -4719830 | 47.1983 | 66175952 | 235539.19 | 116854294 | 99031342 | 50030907 | 0.000000 | 10409705 | 71417246 | 0.000000
09-04-2025 23:24:00000 | -4712281 | 47.1228 | 63644199 | 235416.66 | 116644257 | 99100227 | 50039402 | 0.000000 | 10499932 | 72073550 | 0.000000
09-04-2025 23:24:05000 | -4651912 | 46.5191 | 60682173 | 235389.16 | 115094353 | 99159904 | 50046165 | 0.000000 | 10586300 | 72724888 | 0.000000
09-04-2025 23:24:10000 | -4667200 | 46.672 | 60617031 | 235416.25 | 115457199 | 99167099 | 50048286 | 0.000000 | 10669369 | 73375161 | 0.000000
09-04-2025 23:24:15000 | -4454902 | 44.549 | 64257437 | 235615.77 | 110322464 | 98975700 | 50113804 | 0.000000 | 10757391 | 74003022 | 0.000000
09-04-2025 23:24:20000 | -4599537 | 45.9954 | 63594590 | 235476.31 | 113879776 | 99057655 | 50084152 | 0.000000 | 10845591 | 74634170 | 0.000000
09-04-2025 23:24:25000 | -4726640 | 47.2664 | 70617764 | 235607.42 | 117138428 | 98902267 | 50070908 | 0.000000 | 10940519 | 75284307 | 0.000000
09-04-2025 23:24:30000 | -4796616 | 47.9662 | 71827266 | 235603.11 | 118882309 | 98897324 | 50073799 | 0.000000 | 11041100 | 75945459 | 0.000000
09-04-2025 23:24:35000 | -4741862 | 47.4186 | 71097256 | 235649.50 | 117505936 | 98894577 | 50084137 | 0.000000 | 11138718 | 76610928 | 0.000000
09-04-2025 23:24:40000 | -4783590 | 47.8359 | 68005039 | 235529.23 | 118464302 | 99004547 | 50073330 | 0.000000 | 11235165 | 77270981 | 0.000000
09-04-2025 23:24:45000 | -4962381 | 49.6238 | 69884053 | 235521.05 | 122871735 | 99022888 | 50042007 | 0.000000 | 11329901 | 77948145 | 0.000000
09-04-2025 23:24:50000 | -4867123 | 48.6712 | 73017612 | 235677.52 | 120591774 | 98893311 | 50055531 | 0.000000 | 11430233 | 78632773 | 0.000000
09-04-2025 23:24:55000 | -4786853 | 47.8685 | 69487930 | 235614.03 | 118552544 | 98962730 | 50067406 | 0.000000 | 11527959 | 79300264 | 0.000000
09-04-2025 23:25:00000 | -4870102 | 48.701 | 68207837 | 235553.50 | 120560501 | 99033440 | 50043541 | 0.000000 | 11621895 | 79969937 | 0.000000
09-04-2025 23:25:05000 | -4913202 | 49.132 | 68282939 | 235524.83 | 121622414 | 99048019 | 50041565 | 0.000000 | 11717712 | 80648145 | 0.000000
09-04-2025 23:25:10000 | -4891541 | 48.9154 | 69331274 | 235544.91 | 121123238 | 99010414 | 50043289 | 0.000000 | 11814637 | 81329907 | 0.000000
09-04-2025 23:25:15000 | -4870962 | 48.7096 | 69039409 | 235578.81 | 120594681 | 99010422 | 50048607 | 0.000000 | 11910826 | 82005830 | 0.000000
09-04-2025 23:25:20000 | -4908874 | 49.0887 | 67032412 | 235517.84 | 121479065 | 99080498 | 50031609 | 0.000000 | 12004535 | 82684863 | 0.000000
09-04-2025 23:25:25000 | -4840498 | 48.405 | 68873921 | 235601.58 | 119840355 | 99002838 | 50056652 | 0.000000 | 12100164 | 83364297 | 0.000000
09-04-2025 23:25:30000 | -4768163 | 47.6816 | 66089023 | 235517.42 | 118031036 | 99053055 | 50071712 | 0.000000 | 12194484 | 84029229 | 0.000000
09-04-2025 23:25:35000 | -4813553 | 48.1355 | 65824922 | 235516.02 | 119125145 | 99077896 | 50049068 | 0.000000 | 12284823 | 84693027 | 0.000000
09-04-2025 23:25:40000 | -4752896 | 47.529 | 70027861 | 235623.80 | 117744522 | 98931946 | 50068165 | 0.000000 | 12380958 | 85358730 | 0.000000
09-04-2025 23:25:45000 | -4767649 | 47.6765 | 67731401 | 235548.38 | 118058716 | 99005905 | 50066177 | 0.000000 | 12476483 | 86019883 | 0.000000
09-04-2025 23:25:50000 | -4779954 | 47.7995 | 68902725 | 235595.64 | 118376030 | 98976967 | 50058083 | 0.000000 | 12571643 | 86680176 | 0.000000
09-04-2025 23:25:55000 | -4770132 | 47.7013 | 69713931 | 235598.88 | 118164085 | 98948868 | 50065422 | 0.000000 | 12668097 | 87345391 | 0.000000
09-04-2025 23:26:00000 | -4786833 | 47.8683 | 69689512 | 235592.22 | 118571434 | 98956795 | 50064877 | 0.000000 | 12764154 | 88010801 | 0.000000
09-04-2025 23:26:05000 | -4688054 | 46.8805 | 68261113 | 235598.58 | 116121002 | 98956505 | 50079449 | 0.000000 | 12860592 | 88666533 | 0.000000
09-04-2025 23:26:10000 | -4683675 | 46.8368 | 67062749 | 235569.25 | 115993828 | 98990417 | 50079006 | 0.000000 | 12954370 | 89317656 | 0.000000
09-04-2025 23:26:15000 | -4755769 | 47.5577 | 69309932 | 235603.19 | 117798096 | 98954636 | 50067616 | 0.000000 | 13049302 | 89976279 | 0.000000
09-04-2025 23:26:20000 | -4751620 | 47.5162 | 70256040 | 235635.33 | 117719475 | 98924515 | 50078114 | 0.000000 | 13145857 | 90634639 | 0.000000
09-04-2025 23:26:25000 | -4688563 | 46.8856 | 70179521 | 235626.44 | 116192307 | 98898239 | 50087425 | 0.000000 | 13243906 | 91288750 | 0.000000
09-04-2025 23:26:30000 | -4730837 | 47.3084 | 69335225 | 235604.36 | 117193817 | 98943001 | 50075127 | 0.000000 | 13339579 | 91943330 | 0.000000
09-04-2025 23:26:35000 | -4766498 | 47.665 | 69042095 | 235572.97 | 118064919 | 98967171 | 50077354 | 0.000000 | 13435455 | 92598770 | 0.000000
09-04-2025 23:26:40000 | -4706565 | 47.0656 | 71396582 | 235672.38 | 116648079 | 98868904 | 50081932 | 0.000000 | 13533141 | 93255059 | 0.000000
09-04-2025 23:26:45000 | -4722486 | 47.2249 | 69181162 | 235594.52 | 116998047 | 98943954 | 50076225 | 0.000000 | 13629431 | 93910781 | 0.000000
09-04-2025 23:26:50000 | -4812345 | 48.1234 | 69069307 | 235544.66 | 119193985 | 98985672 | 50065273 | 0.000000 | 13725570 | 94570801 | 0.000000
09-04-2025 23:26:55000 | -4799743 | 47.9974 | 70496514 | 235611.86 | 118901428 | 98938522 | 50056465 | 0.000000 | 13822888 | 95239053 | 0.000000
09-04-2025 23:27:00000 | -4749353 | 47.4935 | 71525859 | 235665.47 | 117691940 | 98884895 | 50082737 | 0.000000 | 13922814 | 95901846 | 0.000000
09-04-2025 23:27:05000 | -4742156 | 47.4216 | 68751836 | 235597.25 | 117454163 | 98965324 | 50075054 | 0.000000 | 14019911 | 96558027 | 0.000000
09-04-2025 23:27:10000 | -4697599 | 46.976 | 71032725 | 235694.38 | 116404991 | 98876007 | 50079868 | 0.000000 | 14117373 | 97213818 | 0.000000
09-04-2025 23:27:15000 | -4701707 | 47.0171 | 71199517 | 235626.81 | 116548378 | 98872749 | 50076572 | 0.000000 | 14215768 | 97870225 | 0.000000
09-04-2025 23:27:20000 | -4802562 | 48.0256 | 69722490 | 235574.45 | 118961807 | 98962540 | 50057949 | 0.000000 | 14312410 | 98533701 | 0.000000
09-04-2025 23:27:25000 | -4777954 | 47.7795 | 68811851 | 235588.91 | 118324707 | 98978775 | 50072289 | 0.000000 | 14408683 | 99197891 | 0.000000
09-04-2025 23:27:30000 | -4726634 | 47.2663 | 68226377 | 235584.19 | 117064018 | 98974236 | 50084820 | 0.000000 | 14503257 | 99857813 | 0.000000
09-04-2025 23:27:35000 | -4682907 | 46.8291 | 68086011 | 235619.09 | 115980255 | 98959518 | 50088207 | 0.000000 | 14597178 | 10050830 | 0.000000
09-04-2025 23:27:40000 | -4671461 | 46.7146 | 69890068 | 235659.91 | 115748917 | 98899277 | 50112862 | 0.000000 | 14694219 | 10115641 | 0.000000
09-04-2025 23:27:45000 | -4650598 | 46.506 | 69855283 | 235639.69 | 115250389 | 98890625 | 50111752 | 0.000000 | 14789945 | 10180623 | 0.000000
09-04-2025 23:27:50000 | -4783631 | 47.8363 | 71642388 | 235629.06 | 118547432 | 98897034 | 50111992 | 0.000000 | 14888535 | 10246378 | 0.000000
09-04-2025 23:27:55000 | -4889708 | 48.8971 | 70613335 | 235570.16 | 121111267 | 98973289 | 50079151 | 0.000000 | 14986373 | 10313437 | 0.000000
09-04-2025 23:28:00000 | -4943062 | 49.4306 | 71777461 | 235563.25 | 122448662 | 98962112 | 50083530 | 0.000000 | 15087307 | 10381938 | 0.000000
09-04-2025 23:28:05000 | -4889066 | 48.8907 | 69454893 | 235562.34 | 121058990 | 99005943 | 50075733 | 0.000000 | 15184417 | 10450212 | 0.000000
09-04-2025 23:28:10000 | -4858199 | 48.582 | 70279414 | 235613.33 | 120309723 | 98969795 | 50068138 | 0.000000 | 15281405 | 10517770 | 0.000000
09-04-2025 23:28:15000 | -4796790 | 47.9679 | 73291904 | 235700.80 | 118887100 | 98852753 | 50084782 | 0.000000 | 15382076 | 10585126 | 0.000000
09-04-2025 23:28:20000 | -4780492 | 47.8049 | 70611675 | 235636.34 | 118427170 | 98926651 | 50085819 | 0.000000 | 15480754 | 10651415 | 0.000000
09-04-2025 23:28:25000 | -4851850 | 48.5185 | 70144482 | 235584.45 | 120168198 | 98971039 | 50072311 | 0.000000 | 15578186 | 10718290 | 0.000000
09-04-2025 23:28:30000 | -4859713 | 48.5971 | 71676914 | 235633.42 | 120386520 | 98929733 | 50066490 | 0.000000 | 15676924 | 10786052 | 0.000000
09-04-2025 23:28:35000 | -4767232 | 47.6723 | 70808926 | 235663.25 | 118102921 | 98914825 | 50095295 | 0.000000 | 15775961 | 10852950 | 0.000000
09-04-2025 23:28:40000 | -4683869 | 46.8387 | 68390781 | 235583.25 | 116035110 | 98950752 | 50101139 | 0.000000 | 15872991 | 10918301 | 0.000000
09-04-2025 23:28:45000 | -4837424 | 48.3742 | 67394619 | 235499.23 | 119765671 | 99043411 | 50064396 | 0.000000 | 15966449 | 10984604 | 0.000000
09-04-2025 23:28:50000 | -4946672 | 49.4667 | 72209326 | 235614.17 | 122524353 | 98951286 | 50056854 | 0.000000 | 16064125 | 11052952 | 0.000000
09-04-2025 23:28:55000 | -4748539 | 47.4854 | 70514980 | 235648.45 | 117647491 | 98915321 | 50097412 | 0.000000 | 16165197 | 11119984 | 0.000000
09-04-2025 23:29:00000 | -4684795 | 46.8479 | 68495874 | 235625.95 | 116037537 | 98947983 | 50105701 | 0.000000 | 16261007 | 11185518 | 0.000000
09-04-2025 23:29:05000 | -4626899 | 46.269 | 69523506 | 235636.44 | 114666046 | 98889870 | 50112637 | 0.000000 | 16357583 | 11250072 | 0.000000
09-04-2025 23:29:10000 | -4807740 | 48.0774 | 69628784 | 235556.31 | 119094162 | 98967484 | 50084534 | 0.000000 | 16453467 | 11315418 | 0.000000
09-04-2025 23:29:15000 | -4813163 | 48.1316 | 73953169 | 235719.94 | 119297180 | 98840118 | 50083679 | 0.000000 | 16554114 | 11382693 | 0.000000
09-04-2025 23:29:20000 | -4804586 | 48.0459 | 71271040 | 235622.72 | 119043427 | 98917603 | 50095345 | 0.000000 | 16655161 | 11449406 | 0.000000
09-04-2025 23:29:25000 | -4786192 | 47.8619 | 70874873 | 235627.67 | 118587875 | 98921295 | 50093006 | 0.000000 | 16754609 | 11515787 | 0.000000
09-04-2025 23:29:30000 | -4970244 | 49.7024 | 67853384 | 235463.94 | 123026337 | 99080956 | 50042271 | 0.000000 | 16849431 | 11583945 | 0.000000
09-04-2025 23:29:35000 | -5073918 | 50.7392 | 68632749 | 235457.34 | 125573441 | 99097527 | 50028172 | 0.000000 | 16945621 | 11653804 | 0.000000
09-04-2025 23:29:40000 | -5045796 | 50.458 | 67701899 | 235474.09 | 124849304 | 99111832 | 50024105 | 0.000000 | 17041593 | 11723962 | 0.000000
09-04-2025 23:29:45000 | -4954790 | 49.5479 | 65222495 | 235459.81 | 122570801 | 99144707 | 50022541 | 0.000000 | 17133535 | 11793240 | 0.000000
09-04-2025 23:29:50000 | -4821239 | 48.2124 | 64955000 | 235546.66 | 119274315 | 99104607 | 50028988 | 0.000000 | 17223351 | 11861110 | 0.000000
09-04-2025 23:29:55000 | -4879392 | 48.7939 | 63065425 | 235430.08 | 120682251 | 99175064 | 50015408 | 0.000000 | 17311105 | 11928438 | 0.000000
09-04-2025 23:30:00000 | -4873251 | 48.7325 | 66710581 | 235528.34 | 120600914 | 99076004 | 50023479 | 0.000000 | 17401428 | 11996086 | 0.000000
09-04-2025 23:30:05000 | -4712559 | 47.1256 | 65054570 | 235536.89 | 116638268 | 99060585 | 50053852 | 0.000000 | 9158684 | 66462761 | 0.000000
09-04-2025 23:30:10000 | -4682602 | 46.826 | 66393511 | 235575.52 | 115938103 | 99009720 | 50059578 | 0.000000 | 18147743 | 131358978 | 0.000000
09-04-2025 23:30:15000 | -4759991 | 47.5999 | 67258716 | 235552.81 | 117857536 | 99016418 | 50050541 | 0.000000 | 27475739 | 196741928 | 0.000000
09-04-2025 23:30:20000 | -4832766 | 48.3277 | 65343428 | 235440.78 | 119614983 | 99098267 | 50033329 | 0.000000 | 36598862 | 263534485 | 0.000000
09-04-2025 23:30:25000 | -4809960 | 48.0996 | 66432710 | 235502.28 | 119067245 | 99059647 | 50051483 | 0.000000 | 45699692 | 330678162 | 0.000000
09-04-2025 23:30:30000 | -4802273 | 48.0227 | 64791704 | 235488.81 | 118840279 | 99102089 | 50057976 | 0.000000 | 54682007 | 397210968 | 0.000000
09-04-2025 23:30:35000 | -4719020 | 47.1902 | 64950625 | 235500.48 | 116815224 | 99066071 | 50062927 | 0.000000 | 63765388 | 463001465 | 0.000000
09-04-2025 23:30:40000 | -4702954 | 47.0295 | 66849912 | 235585.00 | 116453491 | 99004807 | 50063244 | 0.000000 | 72818466 | 528496826 | 0.000000
09-04-2025 23:30:45000 | -4776381 | 47.7638 | 64860376 | 235486.44 | 118207733 | 99090561 | 50061317 | 0.000000 | 81900269 | 594111755 | 0.000000
09-04-2025 23:30:50000 | -4865454 | 48.6545 | 66368657 | 235468.95 | 120425575 | 99082428 | 50027653 | 0.000000 | 90940697 | 661356018 | 0.000000
09-04-2025 23:30:55000 | -4880145 | 48.8015 | 69422095 | 235581.55 | 120835350 | 99003288 | 50032940 | 0.000000 | 100386665 | 729619324 | 0.000000
09-04-2025 23:31:00000 | -4769921 | 47.6992 | 67991338 | 235595.45 | 118104897 | 98999313 | 50066475 | 0.000000 | 109887001 | 796361206 | 0.000000
09-04-2025 23:31:05000 | -4742609 | 47.4261 | 66743745 | 235563.81 | 117410919 | 99024193 | 50056679 | 0.000000 | 119051521 | 862114685 | 0.000000
09-04-2025 23:31:10000 | -4688597 | 46.886 | 68177432 | 235600.41 | 116130646 | 98959259 | 50069027 | 0.000000 | 128475540 | 928122559 | 0.000000
09-04-2025 23:31:15000 | -4709592 | 47.0959 | 65786943 | 235504.45 | 116607803 | 99038422 | 50064457 | 0.000000 | 137730713 | 993216858 | 0.000000
09-04-2025 23:31:20000 | -4785723 | 47.8572 | 66405220 | 235512.09 | 118474030 | 99051010 | 50043659 | 0.000000 | 146915237 | 10590330 | 0.000000
09-04-2025 23:31:25000 | -4810625 | 48.1063 | 69755054 | 235594.48 | 119153961 | 98965012 | 50053787 | 0.000000 | 156456879 | 11260657 | 0.000000
09-04-2025 23:31:30000 | -4700391 | 47.0039 | 67227017 | 235565.41 | 116409683 | 98992630 | 50068310 | 0.000000 | 165929581 | 11920199 | 0.000000
09-04-2025 23:31:35000 | -4611998 | 46.12 | 66827573 | 235593.31 | 114230270 | 98966454 | 50088715 | 0.000000 | 175157272 | 12565900 | 0.000000
09-04-2025 23:31:40000 | -4758002 | 47.58 | 65070435 | 235439.53 | 117794212 | 99077751 | 50060143 | 0.000000 | 184161804 | 13220846 | 0.000000
09-04-2025 23:31:45000 | -4789621 | 47.8962 | 68752661 | 235583.61 | 118611038 | 98985390 | 50062569 | 0.000000 | 193631958 | 13882810 | 0.000000
09-04-2025 23:31:50000 | -4898610 | 48.9861 | 68964507 | 235516.31 | 121296013 | 99023491 | 50038208 | 0.000000 | 203193665 | 14556300 | 0.000000
09-04-2025 23:31:55000 | -4928628 | 49.2863 | 69122168 | 235553.78 | 122009499 | 99030823 | 50041431 | 0.000000 | 212762375 | 15241420 | 0.000000
09-04-2025 23:32:00000 | -4723103 | 47.231 | 70470723 | 235700.47 | 117004349 | 98905151 | 50079525 | 0.000000 | 222492477 | 15910265 | 0.000000
09-04-2025 23:32:05000 | -4734632 | 47.3463 | 63053740 | 235441.77 | 117158218 | 99124840 | 50075577 | 0.000000 | 231668671 | 16558770 | 0.000000
09-04-2025 23:32:10000 | -4879589 | 48.7959 | 66222856 | 235468.31 | 120766556 | 99091614 | 50043163 | 0.000000 | 240709274 | 17228722 | 0.000000
09-04-2025 23:32:15000 | -4787865 | 47.8787 | 69821406 | 235612.27 | 118595978 | 98953346 | 50073643 | 0.000000 | 250278000 | 17901747 | 0.000000
09-04-2025 23:32:20000 | -4800461 | 48.0046 | 65039116 | 235511.39 | 118787544 | 99094635 | 50061100 | 0.000000 | 259405304 | 18563800 | 0.000000
09-04-2025 23:32:25000 | -4804585 | 48.0459 | 68610454 | 235564.50 | 118973969 | 98995712 | 50071754 | 0.000000 | 268843353 | 19229559 | 0.000000
09-04-2025 23:32:30000 | -4869076 | 48.6908 | 68127759 | 235523.14 | 120555695 | 99035271 | 50046986 | 0.000000 | 278138611 | 19903535 | 0.000000
09-04-2025 23:32:35000 | -4883090 | 48.8309 | 69699014 | 235611.61 | 120899208 | 98996635 | 50040615 | 0.000000 | 287533661 | 20583889 | 0.000000
09-04-2025 23:32:40000 | -4896838 | 48.9684 | 69463662 | 235556.92 | 121253296 | 99008804 | 50052013 | 0.000000 | 297245209 | 21266077 | 0.000000
09-04-2025 23:32:45000 | -4936160 | 49.3616 | 65988135 | 235443.50 | 122154778 | 99118240 | 50040871 | 0.000000 | 306648071 | 21946377 | 0.000000
09-04-2025 23:32:50000 | -4832414 | 48.3241 | 70759160 | 235657.16 | 119685097 | 98944908 | 50052353 | 0.000000 | 316185944 | 22629285 | 0.000000
09-04-2025 23:32:55000 | -4695139 | 46.9514 | 66363428 | 235553.13 | 116261009 | 99015800 | 50080166 | 0.000000 | 325685181 | 23286450 | 0.000000
09-04-2025 23:33:00000 | -4769367 | 47.6937 | 65381543 | 235506.77 | 118043365 | 99073402 | 50060535 | 0.000000 | 334677887 | 23942698 | 0.000000
09-04-2025 23:33:05000 | -4856227 | 48.5623 | 69372310 | 235573.23 | 120250099 | 98995018 | 50044254 | 0.000000 | 344033905 | 24616492 | 0.000000
09-04-2025 23:33:10000 | -4821647 | 48.2165 | 68355815 | 235561.09 | 119385475 | 99009979 | 50050678 | 0.000000 | 353474274 | 25290000 | 0.000000
09-04-2025 23:33:15000 | -4820606 | 48.2061 | 68545649 | 235566.63 | 119361771 | 99004135 | 50058777 | 0.000000 | 362979187 | 25956799 | 0.000000
09-04-2025 23:33:20000 | -4853702 | 48.537 | 65624019 | 235464.23 | 120119766 | 99098335 | 50044941 | 0.000000 | 372348114 | 26624917 | 0.000000
09-04-2025 23:33:25000 | -4944782 | 49.4478 | 69630879 | 235529.70 | 122435715 | 99023033 | 50022285 | 0.000000 | 381727814 | 27310806 | 0.000000
09-04-2025 23:33:30000 | -4781785 | 47.8178 | 69128438 | 235624.94 | 118412186 | 98971130 | 50058460 | 0.000000 | 391525208 | 27984949 | 0.000000
09-04-2025 23:33:35000 | -4694980 | 46.9498 | 67394902 | 235603.17 | 116260323 | 98985374 | 50064304 | 0.000000 | 401004669 | 28637612 | 0.000000
09-04-2025 23:33:40000 | -4743820 | 47.4382 | 67662349 | 235580.92 | 117464859 | 98998062 | 50055904 | 0.000000 | 410420685 | 29291328 | 0.000000
09-04-2025 23:33:45000 | -4729177 | 47.2918 | 69563989 | 235630.30 | 117161217 | 98935394 | 50063660 | 0.000000 | 419985321 | 29946624 | 0.000000
09-04-2025 23:33:50000 | -4687465 | 46.8747 | 70813447 | 235667.56 | 116165756 | 98878059 | 50075138 | 0.000000 | 429705017 | 30595740 | 0.000000
09-04-2025 23:33:55000 | -4813570 | 48.1357 | 70920923 | 235637.70 | 119239021 | 98931969 | 50053951 | 0.000000 | 439390015 | 31257810 | 0.000000
09-04-2025 23:34:00000 | -4888986 | 48.8899 | 71482866 | 235598.20 | 121105499 | 98947937 | 50042843 | 0.000000 | 449282013 | 31932881 | 0.000000
09-04-2025 23:34:05000 | -4870751 | 48.7075 | 70643662 | 235592.02 | 120640572 | 98964531 | 50048668 | 0.000000 | 459176788 | 32610249 | 0.000000
09-04-2025 23:34:10000 | -4895712 | 48.9571 | 71696143 | 235613.72 | 121270134 | 98944611 | 50047203 | 0.000000 | 469013519 | 33289050 | 0.000000
09-04-2025 23:34:15000 | -4928766 | 49.2877 | 72362202 | 235634.08 | 122090721 | 98939369 | 50036182 | 0.000000 | 478924683 | 33970713 | 0.000000
09-04-2025 23:34:20000 | -4899721 | 48.9972 | 70621914 | 235581.67 | 121344795 | 98977173 | 50039307 | 0.000000 | 489020782 | 34654614 | 0.000000
09-04-2025 23:34:25000 | -4807850 | 48.0785 | 72546196 | 235706.16 | 119126190 | 98880669 | 50044331 | 0.000000 | 498955322 | 35327800 | 0.000000
09-04-2025 23:34:30000 | -4773309 | 47.7331 | 71241582 | 235669.00 | 118259895 | 98904495 | 50050438 | 0.000000 | 508842529 | 35990986 | 0.000000
09-04-2025 23:34:35000 | -4755201 | 47.552 | 68955981 | 235583.83 | 117783173 | 98964874 | 50045761 | 0.000000 | 518530884 | 36650728 | 0.000000
09-04-2025 23:34:40000 | -4869835 | 48.6983 | 71455850 | 235585.86 | 120650772 | 98940567 | 50035557 | 0.000000 | 528395569 | 37322654 | 0.000000
09-04-2025 23:34:45000 | -4729993 | 47.2999 | 72097139 | 235709.34 | 117224976 | 98858185 | 50064274 | 0.000000 | 538473572 | 37985129 | 0.000000
09-04-2025 23:34:50000 | -4641897 | 46.419 | 69562554 | 235648.02 | 115023521 | 98895691 | 50065117 | 0.000000 | 548219055 | 38634058 | 0.000000
09-04-2025 23:34:55000 | -4759644 | 47.5964 | 71477646 | 235604.42 | 117970497 | 98891106 | 50069305 | 0.000000 | 558291748 | 39286235 | 0.000000
09-04-2025 23:35:00000 | -4872711 | 48.7271 | 73696567 | 235650.88 | 120766724 | 98875526 | 50040039 | 0.000000 | 568296204 | 39958328 | 0.000000
09-04-2025 23:35:05000 | -4849518 | 48.4952 | 75465488 | 235742.11 | 120233360 | 98810760 | 50049171 | 0.000000 | 578654785 | 40635693 | 0.000000
09-04-2025 23:35:10000 | -4745834 | 47.4583 | 77134014 | 235862.02 | 117720154 | 98704803 | 50075474 | 0.000000 | 588995117 | 41306055 | 0.000000
09-04-2025 23:35:15000 | -4820940 | 48.2094 | 72115352 | 235650.30 | 119458275 | 98899605 | 50059280 | 0.000000 | 599183228 | 41967642 | 0.000000
09-04-2025 23:35:20000 | -4902595 | 49.026 | 72207686 | 235604.38 | 121461082 | 98932693 | 50031071 | 0.000000 | 609211243 | 42644048 | 0.000000
09-04-2025 23:35:25000 | -4922018 | 49.2202 | 74086934 | 235689.44 | 121962021 | 98886055 | 50041782 | 0.000000 | 619507690 | 43325742 | 0.000000
09-04-2025 23:35:30000 | -4813623 | 48.1362 | 74194673 | 235763.23 | 119309387 | 98832878 | 50066349 | 0.000000 | 629738647 | 43999893 | 0.000000
09-04-2025 23:35:35000 | -4892658 | 48.9266 | 72373818 | 235638.41 | 121210724 | 98923569 | 50040470 | 0.000000 | 639778076 | 44673267 | 0.000000
09-04-2025 23:35:40000 | -5014253 | 50.1425 | 73388716 | 235598.22 | 124217216 | 98945839 | 50007732 | 0.000000 | 649915466 | 45362397 | 0.000000
09-04-2025 23:35:45000 | -4893321 | 48.9332 | 73227290 | 235682.08 | 121242203 | 98898743 | 50024036 | 0.000000 | 660218262 | 46050366 | 0.000000
09-04-2025 23:35:50000 | -4839986 | 48.3999 | 71363545 | 235611.48 | 119909386 | 98930397 | 50032555 | 0.000000 | 670273438 | 46724995 | 0.000000
09-04-2025 23:35:55000 | -4830179 | 48.3018 | 74206909 | 235726.86 | 119718193 | 98840355 | 50036430 | 0.000000 | 680401672 | 47395742 | 0.000000
09-04-2025 23:36:00000 | -4685039 | 46.8504 | 74204937 | 235806.39 | 116165520 | 98768791 | 50060047 | 0.000000 | 690611206 | 48054370 | 0.000000
09-04-2025 23:36:05000 | -4671071 | 46.7107 | 69336079 | 235598.22 | 115753983 | 98916199 | 50057152 | 0.000000 | 700508667 | 48706265 | 0.000000
09-04-2025 23:36:10000 | -4767659 | 47.6766 | 70428770 | 235608.19 | 118123627 | 98926453 | 50043392 | 0.000000 | 710245422 | 49359277 | 0.000000
09-04-2025 23:36:15000 | -4757110 | 47.5711 | 73876885 | 235703.22 | 117947586 | 98815514 | 50047646 | 0.000000 | 720373047 | 50023086 | 0.000000
09-04-2025 23:36:20000 | -4781253 | 47.8125 | 71903853 | 235629.42 | 118504089 | 98888016 | 50047279 | 0.000000 | 730436951 | 50688398 | 0.000000
09-04-2025 23:36:25000 | -4907436 | 49.0744 | 70268848 | 235553.67 | 121538101 | 98990349 | 50025307 | 0.000000 | 740281921 | 51361167 | 0.000000
09-04-2025 23:36:30000 | -4819980 | 48.1998 | 71720923 | 235632.14 | 119433891 | 98910988 | 50043373 | 0.000000 | 750367065 | 52035044 | 0.000000
09-04-2025 23:36:35000 | -4716704 | 47.167 | 72151553 | 235714.70 | 116901825 | 98850143 | 50064941 | 0.000000 | 760377136 | 52695005 | 0.000000
09-04-2025 23:36:40000 | -4664010 | 46.6401 | 72106685 | 235734.70 | 115614586 | 98825912 | 50079338 | 0.000000 | 770371399 | 53343003 | 0.000000
09-04-2025 23:36:45000 | -4715201 | 47.152 | 74340488 | 235738.45 | 116938232 | 98779846 | 50067436 | 0.000000 | 780495239 | 53994053 | 0.000000
09-04-2025 23:36:50000 | -4845741 | 48.4574 | 74597808 | 235650.33 | 120147461 | 98835701 | 50046280 | 0.000000 | 790729065 | 54662715 | 0.000000
09-04-2025 23:36:55000 | -4916142 | 49.1614 | 74774951 | 235694.38 | 121842331 | 98862961 | 50044121 | 0.000000 | 801100159 | 55343442 | 0.000000
09-04-2025 23:37:00000 | -4860998 | 48.61 | 74563794 | 235657.67 | 120511681 | 98843910 | 50055637 | 0.000000 | 811524963 | 56021460 | 0.000000
09-04-2025 23:37:05000 | -4822031 | 48.2203 | 72141924 | 235659.78 | 119478622 | 98899300 | 50057903 | 0.000000 | 821680420 | 56692456 | 0.000000
09-04-2025 23:37:10000 | -4868927 | 48.6893 | 72831050 | 235653.91 | 120643730 | 98899673 | 50047672 | 0.000000 | 831631226 | 57364233 | 0.000000
09-04-2025 23:37:15000 | -4844644 | 48.4464 | 74168882 | 235723.38 | 120069138 | 98848305 | 50056835 | 0.000000 | 841851929 | 58039380 | 0.000000
09-04-2025 23:37:20000 | -4849229 | 48.4923 | 71376113 | 235635.61 | 120129990 | 98934036 | 50055775 | 0.000000 | 851874268 | 58714014 | 0.000000
09-04-2025 23:37:25000 | -4849771 | 48.4977 | 72470195 | 235678.63 | 120156067 | 98901886 | 50049545 | 0.000000 | 861770142 | 59385527 | 0.000000
09-04-2025 23:37:30000 | -4904001 | 49.04 | 72977856 | 235660.33 | 121498833 | 98910797 | 50045151 | 0.000000 | 871892639 | 60065791 | 0.000000
09-04-2025 23:37:35000 | -4873409 | 48.7341 | 73265332 | 235662.67 | 120763321 | 98888741 | 50057816 | 0.000000 | 882115845 | 60743740 | 0.000000
09-04-2025 23:37:40000 | -4880442 | 48.8044 | 71077871 | 235627.63 | 120872887 | 98956055 | 50048615 | 0.000000 | 892056824 | 61419658 | 0.000000
09-04-2025 23:37:45000 | -4816961 | 48.1696 | 70504502 | 235625.77 | 119314171 | 98945740 | 50057247 | 0.000000 | 901965759 | 62091274 | 0.000000
09-04-2025 23:37:50000 | -4805735 | 48.0573 | 73175132 | 235708.92 | 119099289 | 98860527 | 50066025 | 0.000000 | 912004333 | 62759956 | 0.000000
09-04-2025 23:37:55000 | -4815038 | 48.1504 | 72025791 | 235647.16 | 119307640 | 98899651 | 50060753 | 0.000000 | 922004944 | 63425557 | 0.000000
09-04-2025 23:38:00000 | -4840245 | 48.4025 | 70869873 | 235596.16 | 119907761 | 98945023 | 50047020 | 0.000000 | 931926208 | 64097393 | 0.000000
09-04-2025 23:38:05000 | -4951808 | 49.5181 | 72786191 | 235602.00 | 122674828 | 98936905 | 50034206 | 0.000000 | 941866028 | 64778940 | 0.000000
09-04-2025 23:38:10000 | -4914899 | 49.149 | 72108950 | 235603.42 | 121757782 | 98940804 | 50039715 | 0.000000 | 951967529 | 65463853 | 0.000000
09-04-2025 23:38:15000 | -4750500 | 47.505 | 71845654 | 235691.05 | 117719826 | 98875603 | 50060001 | 0.000000 | 962005249 | 66134937 | 0.000000
09-04-2025 23:38:20000 | -4603868 | 46.0387 | 71381533 | 235762.84 | 114123642 | 98819267 | 50088562 | 0.000000 | 971771301 | 66783813 | 0.000000
09-04-2025 23:38:25000 | -4605016 | 46.0502 | 69046445 | 235641.03 | 114120720 | 98894539 | 50093742 | 0.000000 | 981496155 | 67419790 | 0.000000
09-04-2025 23:38:30000 | -4812544 | 48.1254 | 70969204 | 235558.55 | 119256699 | 98930092 | 50048195 | 0.000000 | 991151245 | 68079497 | 0.000000
09-04-2025 23:38:35000 | -4910006 | 49.1001 | 74543291 | 235663.06 | 121693352 | 98867096 | 50045628 | 0.000000 | 10012857 | 68757378 | 0.000000
09-04-2025 23:38:40000 | -4875664 | 48.7566 | 75934727 | 235750.88 | 120870750 | 98808846 | 50061100 | 0.000000 | 10117075 | 69437705 | 0.000000
09-04-2025 23:38:45000 | -4736453 | 47.3645 | 73652280 | 235717.42 | 117441147 | 98812469 | 50084892 | 0.000000 | 10220859 | 70106797 | 0.000000
09-04-2025 23:38:50000 | -4703240 | 47.0324 | 70565415 | 235643.69 | 116549683 | 98893120 | 50093842 | 0.000000 | 10321573 | 70755425 | 0.000000
09-04-2025 23:38:55000 | -4866669 | 48.6667 | 73306191 | 235671.56 | 120604004 | 98884491 | 50064831 | 0.000000 | 10419891 | 71423335 | 0.000000
09-04-2025 23:39:00000 | -4880439 | 48.8044 | 72613809 | 235627.34 | 120930946 | 98911186 | 50057854 | 0.000000 | 10520148 | 72102656 | 0.000000
09-04-2025 23:39:05000 | -4939838 | 49.3984 | 72396055 | 235619.39 | 122364449 | 98943069 | 50049843 | 0.000000 | 10620389 | 72785498 | 0.000000
09-04-2025 23:39:10000 | -4849400 | 48.494 | 73973501 | 235713.36 | 120186394 | 98856476 | 50065369 | 0.000000 | 10722930 | 73463564 | 0.000000
09-04-2025 23:39:15000 | -4905827 | 49.0583 | 72889473 | 235631.61 | 121549988 | 98914185 | 50041569 | 0.000000 | 10824332 | 74143027 | 0.000000
09-04-2025 23:39:20000 | -4915441 | 49.1544 | 72712148 | 235644.14 | 121775497 | 98923531 | 50044331 | 0.000000 | 10925641 | 74825146 | 0.000000
09-04-2025 23:39:25000 | -4896871 | 48.9687 | 72689424 | 235645.30 | 121318932 | 98916145 | 50048298 | 0.000000 | 11026770 | 75505332 | 0.000000
09-04-2025 23:39:30000 | -4845883 | 48.4588 | 76526914 | 235788.86 | 120152664 | 98775887 | 50052628 | 0.000000 | 11129429 | 76185244 | 0.000000
09-04-2025 23:39:35000 | -4712027 | 47.1203 | 74376772 | 235784.53 | 116837975 | 98777061 | 50093914 | 0.000000 | 11235408 | 76846084 | 0.000000
09-04-2025 23:39:40000 | -4628324 | 46.2832 | 74787158 | 235810.08 | 114818825 | 98719521 | 50099934 | 0.000000 | 11338196 | 77491318 | 0.000000
09-04-2025 23:39:45000 | -4601625 | 46.0162 | 76923945 | 235825.11 | 114247429 | 98631378 | 50114902 | 0.000000 | 11444601 | 78133887 | 0.000000
09-04-2025 23:39:50000 | -4636586 | 46.3659 | 78325195 | 235859.05 | 115132896 | 98602989 | 50133984 | 0.000000 | 11552188 | 78772666 | 0.000000
09-04-2025 23:39:55000 | -4712388 | 47.1239 | 79068271 | 235827.66 | 117008942 | 98621399 | 50113728 | 0.000000 | 11660707 | 79422793 | 0.000000
09-04-2025 23:40:00000 | -4922044 | 49.2204 | 82137256 | 235821.44 | 122196495 | 98636040 | 50086792 | 0.000000 | 11772145 | 80099785 | 0.000000
09-04-2025 23:40:05000 | -4877838 | 48.7784 | 81877295 | 235862.91 | 121098358 | 98620308 | 50095703 | 0.000000 | 11886425 | 80779761 | 0.000000
09-04-2025 23:40:10000 | -4939638 | 49.3964 | 78370020 | 235739.23 | 122514885 | 98764694 | 50081612 | 0.000000 | 11997644 | 81461133 | 0.000000
09-04-2025 23:40:15000 | -4942624 | 49.4262 | 81427085 | 235861.95 | 122644417 | 98669975 | 50084656 | 0.000000 | 12108914 | 82147480 | 0.000000
09-04-2025 23:40:20000 | -4824223 | 48.2422 | 79460376 | 235880.14 | 119696648 | 98670502 | 50111134 | 0.000000 | 12220620 | 82824561 | 0.000000
09-04-2025 23:40:25000 | -4816679 | 48.1668 | 77650225 | 235812.58 | 119475464 | 98725342 | 50101524 | 0.000000 | 12328413 | 83497432 | 0.000000
09-04-2025 23:40:30000 | -4950105 | 49.501 | 75495283 | 235646.23 | 122710777 | 98856903 | 50080391 | 0.000000 | 12435985 | 84171924 | 0.000000
09-04-2025 23:40:35000 | -4937948 | 49.3795 | 76174312 | 235739.88 | 122394379 | 98830971 | 50067223 | 0.000000 | 12541566 | 84860557 | 0.000000
09-04-2025 23:40:40000 | -4897815 | 48.9781 | 75208740 | 235704.84 | 121402405 | 98841484 | 50069260 | 0.000000 | 12647041 | 85542012 | 0.000000
09-04-2025 23:40:45000 | -4926577 | 49.2658 | 72226104 | 235598.25 | 122047119 | 98942368 | 50048405 | 0.000000 | 12749098 | 86221455 | 0.000000
09-04-2025 23:40:50000 | -4846918 | 48.4692 | 74911514 | 235752.44 | 120137718 | 98826622 | 50059074 | 0.000000 | 12851838 | 86904268 | 0.000000
09-04-2025 23:40:55000 | -4806577 | 48.0658 | 72296812 | 235671.00 | 119104233 | 98887650 | 50062527 | 0.000000 | 12952979 | 87573936 | 0.000000
09-04-2025 23:41:00000 | -4884083 | 48.8408 | 73069585 | 235666.47 | 121014175 | 98899323 | 50041409 | 0.000000 | 13052825 | 88246846 | 0.000000
09-04-2025 23:41:05000 | -4807358 | 48.0736 | 76615913 | 235811.13 | 119215614 | 98753716 | 50069008 | 0.000000 | 13157216 | 88922002 | 0.000000
09-04-2025 23:41:10000 | -4667886 | 46.6789 | 73476455 | 235731.70 | 115761505 | 98783684 | 50088352 | 0.000000 | 13260372 | 89577168 | 0.000000
09-04-2025 23:41:15000 | -4683155 | 46.8316 | 74279795 | 235760.77 | 116150383 | 98765381 | 50088608 | 0.000000 | 13362926 | 90223857 | 0.000000
09-04-2025 23:41:20000 | -4730204 | 47.302 | 74601104 | 235702.05 | 117328957 | 98779076 | 50087944 | 0.000000 | 13466947 | 90878242 | 0.000000
09-04-2025 23:41:25000 | -4881607 | 48.8161 | 77254072 | 235730.14 | 121080978 | 98770805 | 50064030 | 0.000000 | 13571516 | 91550908 | 0.000000
09-04-2025 23:41:30000 | -4957187 | 49.5719 | 77840259 | 235716.88 | 122939919 | 98789497 | 50057762 | 0.000000 | 13679918 | 92234326 | 0.000000
09-04-2025 23:41:35000 | -4841175 | 48.4117 | 76842490 | 235766.89 | 120064377 | 98763603 | 50071098 | 0.000000 | 13788531 | 92912217 | 0.000000
09-04-2025 23:41:40000 | -4866822 | 48.6682 | 74377441 | 235690.77 | 120629768 | 98852287 | 50058018 | 0.000000 | 13893046 | 93582617 | 0.000000
09-04-2025 23:41:45000 | -4875081 | 48.7508 | 78139233 | 235798.03 | 120917976 | 98739700 | 50065098 | 0.000000 | 13999565 | 94261807 | 0.000000
09-04-2025 23:41:50000 | -4858722 | 48.5872 | 75883101 | 235743.27 | 120465172 | 98802269 | 50064049 | 0.000000 | 14105657 | 94937676 | 0.000000
09-04-2025 23:41:55000 | -4863737 | 48.6374 | 74152617 | 235701.25 | 120547745 | 98857674 | 50057465 | 0.000000 | 14208196 | 95611133 | 0.000000
09-04-2025 23:42:00000 | -4828870 | 48.2887 | 74701787 | 235741.16 | 119698860 | 98824478 | 50071869 | 0.000000 | 14311976 | 96283281 | 0.000000
09-04-2025 23:42:05000 | -4844851 | 48.4485 | 72906025 | 235626.94 | 120072983 | 98886642 | 50055836 | 0.000000 | 14414917 | 96951631 | 0.000000
09-04-2025 23:42:10000 | -4958397 | 49.584 | 75641782 | 235691.17 | 122897141 | 98856308 | 50036018 | 0.000000 | 14518309 | 97634746 | 0.000000
09-04-2025 23:42:15000 | -4814889 | 48.1489 | 77963691 | 235836.61 | 119442070 | 98714287 | 50064442 | 0.000000 | 14625317 | 98318232 | 0.000000
09-04-2025 23:42:20000 | -4691106 | 46.9111 | 74375313 | 235788.59 | 116342789 | 98766380 | 50094105 | 0.000000 | 14728815 | 98978291 | 0.000000
09-04-2025 23:42:25000 | -4797993 | 47.9799 | 71262119 | 235656.31 | 118862198 | 98914940 | 50058590 | 0.000000 | 14827106 | 99635713 | 0.000000
09-04-2025 23:42:30000 | -4924928 | 49.2493 | 74420947 | 235650.16 | 122057060 | 98877464 | 50040367 | 0.000000 | 14928864 | 10031510 | 0.000000
09-04-2025 23:42:35000 | -4939953 | 49.3995 | 75381538 | 235681.20 | 122447006 | 98855675 | 50055424 | 0.000000 | 15033876 | 10100134 | 0.000000
09-04-2025 23:42:40000 | -4826881 | 48.2688 | 72270259 | 235662.28 | 119602074 | 98897629 | 50064968 | 0.000000 | 15137328 | 10167586 | 0.000000
09-04-2025 23:42:45000 | -4850288 | 48.5029 | 71799512 | 235632.05 | 120168060 | 98922020 | 50059582 | 0.000000 | 15237214 | 10234615 | 0.000000
09-04-2025 23:42:50000 | -4902079 | 49.0208 | 73465063 | 235671.14 | 121462524 | 98895592 | 50057022 | 0.000000 | 15338318 | 10302313 | 0.000000
09-04-2025 23:42:55000 | -4814094 | 48.1409 | 73702080 | 235704.23 | 119320503 | 98848282 | 50067829 | 0.000000 | 15441993 | 10369642 | 0.000000
09-04-2025 23:43:00000 | -4852579 | 48.5258 | 72979072 | 235664.05 | 120245903 | 98887939 | 50063004 | 0.000000 | 15542916 | 10436479 | 0.000000
09-04-2025 23:43:05000 | -4894980 | 48.9498 | 75529741 | 235738.95 | 121337997 | 98830414 | 50051449 | 0.000000 | 15646234 | 10504170 | 0.000000
09-04-2025 23:43:10000 | -4826041 | 48.2604 | 76903125 | 235769.55 | 119699684 | 98754051 | 50071014 | 0.000000 | 15752189 | 10571925 | 0.000000
09-04-2025 23:43:15000 | -4810311 | 48.1031 | 72996787 | 235678.33 | 119218964 | 98868095 | 50066257 | 0.000000 | 15855297 | 10638402 | 0.000000
09-04-2025 23:43:20000 | -4802011 | 48.0201 | 75249575 | 235739.48 | 119077805 | 98794350 | 50069855 | 0.000000 | 15959492 | 10705274 | 0.000000
09-04-2025 23:43:25000 | -4790962 | 47.9096 | 74248311 | 235688.48 | 118791969 | 98820335 | 50068680 | 0.000000 | 16062843 | 10772061 | 0.000000
09-04-2025 23:43:30000 | -4743096 | 47.431 | 76445029 | 235812.64 | 117656029 | 98725960 | 50084293 | 0.000000 | 16167413 | 10838153 | 0.000000
09-04-2025 23:43:35000 | -4659166 | 46.5917 | 74482534 | 235774.59 | 115572433 | 98746185 | 50096172 | 0.000000 | 16271530 | 10903604 | 0.000000
09-04-2025 23:43:40000 | -4740938 | 47.4094 | 74493354 | 235731.00 | 117564400 | 98787941 | 50082645 | 0.000000 | 16374496 | 10968631 | 0.000000
09-04-2025 23:43:45000 | -4878103 | 48.781 | 76513789 | 235729.81 | 120963432 | 98792122 | 50068588 | 0.000000 | 16479121 | 11035705 | 0.000000
09-04-2025 23:43:50000 | -4805274 | 48.0527 | 75113750 | 235685.11 | 119169670 | 98800217 | 50077858 | 0.000000 | 16586213 | 11102675 | 0.000000
09-04-2025 23:43:55000 | -4974970 | 49.7497 | 75308286 | 235645.08 | 123311447 | 98873611 | 50035717 | 0.000000 | 16690435 | 11170940 | 0.000000
09-04-2025 23:44:00000 | -4956484 | 49.5648 | 76947910 | 235740.33 | 122867722 | 98816277 | 50031857 | 0.000000 | 16796521 | 11239947 | 0.000000
09-04-2025 23:44:05000 | -4838356 | 48.3836 | 75688169 | 235755.53 | 119960419 | 98798431 | 50058968 | 0.000000 | 16903088 | 11307942 | 0.000000
09-04-2025 23:44:10000 | -4625598 | 46.256 | 73947739 | 235808.69 | 114716789 | 98746124 | 50089741 | 0.000000 | 17006305 | 11373196 | 0.000000
09-04-2025 23:44:15000 | -4693182 | 46.9318 | 74092227 | 235752.30 | 116388359 | 98776642 | 50075500 | 0.000000 | 17107045 | 11438098 | 0.000000
09-04-2025 23:44:20000 | -4771835 | 47.7184 | 76644541 | 235785.56 | 118369781 | 98734520 | 50085098 | 0.000000 | 17212694 | 11503877 | 0.000000
09-04-2025 23:44:25000 | -4810468 | 48.1047 | 76782349 | 235766.73 | 119316658 | 98749985 | 50063320 | 0.000000 | 17318015 | 11570304 | 0.000000
09-04-2025 23:44:30000 | -4864754 | 48.6475 | 78192314 | 235758.16 | 120694687 | 98732758 | 50073425 | 0.000000 | 17426561 | 11637838 | 0.000000
09-04-2025 23:44:35000 | -4823934 | 48.2393 | 75140908 | 235733.53 | 119600052 | 98808472 | 50070068 | 0.000000 | 17532217 | 11704963 | 0.000000
09-04-2025 23:44:40000 | -4861332 | 48.6133 | 74503379 | 235699.95 | 120497620 | 98845901 | 50062332 | 0.000000 | 17635464 | 11772209 | 0.000000
09-04-2025 23:44:45000 | -4801762 | 48.0176 | 76111304 | 235748.53 | 119103577 | 98766960 | 50084503 | 0.000000 | 17741788 | 11839339 | 0.000000
09-04-2025 23:44:50000 | -4766916 | 47.6692 | 74323574 | 235739.94 | 118186752 | 98806244 | 50084503 | 0.000000 | 17845126 | 11905544 | 0.000000
09-04-2025 23:44:55000 | -4763772 | 47.6377 | 74193794 | 235754.11 | 118101212 | 98808792 | 50086029 | 0.000000 | 17948429 | 11971670 | 0.000000
09-04-2025 23:45:00000 | -4700791 | 47.0079 | 76284189 | 235793.59 | 116641754 | 98708717 | 50090111 | 0.000000 | 18053833 | 12037593 | 0.000000
09-04-2025 23:45:05000 | -4756206 | 47.5621 | 77822700 | 235821.16 | 118017052 | 98687660 | 50095406 | 0.000000 | 10608975 | 65556694 | 0.000000
09-04-2025 23:45:10000 | -4797246 | 47.9725 | 77622261 | 235776.28 | 119033371 | 98716103 | 50079552 | 0.000000 | 21414848 | 132057526 | 0.000000
09-04-2025 23:45:15000 | -4784368 | 47.8437 | 80723081 | 235892.75 | 118783890 | 98606323 | 50088581 | 0.000000 | 32431141 | 198914429 | 0.000000
09-04-2025 23:45:20000 | -4706286 | 47.0629 | 78201919 | 235847.58 | 116819237 | 98647408 | 50106487 | 0.000000 | 43284821 | 264817017 | 0.000000
09-04-2025 23:45:25000 | -4668110 | 46.6811 | 74584600 | 235743.72 | 115805191 | 98747528 | 50114777 | 0.000000 | 53837776 | 329456482 | 0.000000
09-04-2025 23:45:30000 | -4846707 | 48.4671 | 76972559 | 235713.22 | 120230759 | 98762268 | 50081402 | 0.000000 | 64470444 | 395832947 | 0.000000
09-04-2025 23:45:35000 | -4901160 | 49.0116 | 81160547 | 235829.16 | 121651695 | 98656487 | 50081219 | 0.000000 | 75536484 | 463571869 | 0.000000
09-04-2025 23:45:40000 | -4796602 | 47.966 | 78509600 | 235789.05 | 119039642 | 98686813 | 50104172 | 0.000000 | 86790359 | 530667297 | 0.000000
09-04-2025 23:45:45000 | -4886195 | 48.862 | 74853862 | 235667.61 | 121134140 | 98846832 | 50084225 | 0.000000 | 97346855 | 597729797 | 0.000000
09-04-2025 23:45:50000 | -4960539 | 49.6054 | 77114292 | 235611.86 | 123043198 | 98813148 | 50067028 | 0.000000 | 108035851 | 665912598 | 0.000000
09-04-2025 23:45:55000 | -4935054 | 49.3505 | 77693599 | 235727.53 | 122390961 | 98783325 | 50058876 | 0.000000 | 118812019 | 735041260 | 0.000000
09-04-2025 23:46:00000 | -4844121 | 48.4412 | 77184385 | 235787.80 | 120139648 | 98754272 | 50078949 | 0.000000 | 129485764 | 802968567 | 0.000000
09-04-2025 23:46:05000 | -4714711 | 47.1471 | 74343213 | 235721.89 | 116939697 | 98779510 | 50094402 | 0.000000 | 139994308 | 869246643 | 0.000000
09-04-2025 23:46:10000 | -4689332 | 46.8933 | 74556235 | 235739.97 | 116316246 | 98759560 | 50100529 | 0.000000 | 150300400 | 934439331 | 0.000000
09-04-2025 23:46:15000 | -4755139 | 47.5514 | 74833574 | 235699.55 | 117943207 | 98784210 | 50097942 | 0.000000 | 160745392 | 999868652 | 0.000000
09-04-2025 23:46:20000 | -4754189 | 47.5419 | 77529053 | 235752.20 | 118005013 | 98696266 | 50094151 | 0.000000 | 171273666 | 10660991 | 0.000000
09-04-2025 23:46:25000 | -4772737 | 47.7274 | 78100854 | 235762.03 | 118467819 | 98687408 | 50105907 | 0.000000 | 182128952 | 11324674 | 0.000000
09-04-2025 23:46:30000 | -4706070 | 47.0607 | 75785933 | 235706.28 | 116791878 | 98728012 | 50115292 | 0.000000 | 192925003 | 11975603 | 0.000000
09-04-2025 23:46:35000 | -4689559 | 46.8956 | 79004277 | 235857.14 | 116438889 | 98610428 | 50108627 | 0.000000 | 203677628 | 12630010 | 0.000000
09-04-2025 23:46:40000 | -4700825 | 47.0082 | 79236758 | 235827.25 | 116734940 | 98608963 | 50112057 | 0.000000 | 214713608 | 13281624 | 0.000000
09-04-2025 23:46:45000 | -4718875 | 47.1887 | 78866748 | 235834.03 | 117154106 | 98631966 | 50107327 | 0.000000 | 225573990 | 13934707 | 0.000000
09-04-2025 23:46:50000 | -4778568 | 47.7857 | 78603818 | 235810.77 | 118599792 | 98673965 | 50089424 | 0.000000 | 236449661 | 14594773 | 0.000000
09-04-2025 23:46:55000 | -4758167 | 47.5817 | 78625884 | 235788.73 | 118115799 | 98662056 | 50101414 | 0.000000 | 247519165 | 15259835 | 0.000000
09-04-2025 23:47:00000 | -4741411 | 47.4141 | 76053936 | 235765.91 | 117620148 | 98737839 | 50097713 | 0.000000 | 258149933 | 15917759 | 0.000000
09-04-2025 23:47:05000 | -4723613 | 47.2361 | 78955767 | 235828.25 | 117271988 | 98631630 | 50098793 | 0.000000 | 269087555 | 16579810 | 0.000000
09-04-2025 23:47:10000 | -4846573 | 48.4657 | 76793086 | 235752.09 | 120199524 | 98767860 | 50081711 | 0.000000 | 279689789 | 17248334 | 0.000000
09-04-2025 23:47:15000 | -4649294 | 46.4929 | 79169971 | 235908.58 | 115450226 | 98580956 | 50133312 | 0.000000 | 290840759 | 17906532 | 0.000000
09-04-2025 23:47:20000 | -4735446 | 47.3545 | 76902578 | 235811.67 | 117487610 | 98706871 | 50107792 | 0.000000 | 301361267 | 18561447 | 0.000000
09-04-2025 23:47:25000 | -4715045 | 47.1504 | 79280181 | 235859.09 | 117063828 | 98615685 | 50122444 | 0.000000 | 312377747 | 19217401 | 0.000000
09-04-2025 23:47:30000 | -4746284 | 47.4628 | 77464131 | 235783.61 | 117788658 | 98694153 | 50102051 | 0.000000 | 323121552 | 19875189 | 0.000000
09-04-2025 23:47:35000 | -4758921 | 47.5892 | 78617212 | 235824.84 | 118117584 | 98662766 | 50103756 | 0.000000 | 334051056 | 20537903 | 0.000000
09-04-2025 23:47:40000 | -4832875 | 48.3287 | 79730640 | 235807.30 | 119960289 | 98666313 | 50101563 | 0.000000 | 344973389 | 21206631 | 0.000000
09-04-2025 23:47:45000 | -4822246 | 48.2225 | 77378477 | 235763.19 | 119627724 | 98736946 | 50105198 | 0.000000 | 355929932 | 21871943 | 0.000000
09-04-2025 23:47:50000 | -4905250 | 49.0525 | 78015664 | 235725.00 | 121678818 | 98758728 | 50077705 | 0.000000 | 366826782 | 22547139 | 0.000000
09-04-2025 23:47:55000 | -4959680 | 49.5968 | 80782803 | 235850.22 | 123038261 | 98699341 | 50065998 | 0.000000 | 377860809 | 23235610 | 0.000000
09-04-2025 23:48:00000 | -4845384 | 48.4538 | 78807568 | 235831.63 | 120207726 | 98703011 | 50082317 | 0.000000 | 388979462 | 23915044 | 0.000000
09-04-2025 23:48:05000 | -4833505 | 48.3351 | 76526914 | 235783.75 | 119862793 | 98769730 | 50074268 | 0.000000 | 399673126 | 24585193 | 0.000000
09-04-2025 23:48:10000 | -4787055 | 47.8706 | 78950996 | 235860.11 | 118792580 | 98667099 | 50086468 | 0.000000 | 410486969 | 25254846 | 0.000000
09-04-2025 23:48:15000 | -4732500 | 47.325 | 79063311 | 235859.25 | 117477203 | 98633018 | 50103226 | 0.000000 | 421360718 | 25916448 | 0.000000
09-04-2025 23:48:20000 | -4714407 | 47.1441 | 76764331 | 235790.03 | 116983147 | 98700127 | 50105049 | 0.000000 | 432080292 | 26566086 | 0.000000
09-04-2025 23:48:25000 | -4795530 | 47.9553 | 79304463 | 235816.69 | 119035736 | 98660034 | 50090786 | 0.000000 | 442982178 | 27231575 | 0.000000
09-04-2025 23:48:30000 | -4879700 | 48.797 | 78995830 | 235813.16 | 121054688 | 98714844 | 50078091 | 0.000000 | 453857666 | 27906624 | 0.000000
09-04-2025 23:48:35000 | -4925374 | 49.2537 | 78446265 | 235772.13 | 122156822 | 98755287 | 50077000 | 0.000000 | 464896393 | 28585281 | 0.000000
09-04-2025 23:48:40000 | -4881273 | 48.8127 | 78016499 | 235788.98 | 121066193 | 98746712 | 50071438 | 0.000000 | 475841980 | 29267434 | 0.000000
09-04-2025 23:48:45000 | -4860559 | 48.6056 | 78788271 | 235847.83 | 120563248 | 98711563 | 50089523 | 0.000000 | 486778198 | 29947058 | 0.000000
09-04-2025 23:48:50000 | -4767590 | 47.6759 | 75051040 | 235751.66 | 118220680 | 98783524 | 50099014 | 0.000000 | 497446594 | 30613550 | 0.000000
09-04-2025 23:48:55000 | -4846011 | 48.4601 | 77151636 | 235761.97 | 120196053 | 98756256 | 50079563 | 0.000000 | 507960999 | 31284341 | 0.000000
09-04-2025 23:49:00000 | -4790886 | 47.9089 | 79658389 | 235891.16 | 118899529 | 98645721 | 50101463 | 0.000000 | 518904175 | 31956853 | 0.000000
09-04-2025 23:49:05000 | -4670840 | 46.7084 | 76993232 | 235843.94 | 115916893 | 98668495 | 50123726 | 0.000000 | 529774109 | 32609753 | 0.000000
09-04-2025 23:49:10000 | -4690595 | 46.9059 | 76436670 | 235772.42 | 116403252 | 98698120 | 50104919 | 0.000000 | 540350586 | 33261772 | 0.000000
09-04-2025 23:49:15000 | -4830027 | 48.3003 | 81138208 | 235884.70 | 119907364 | 98618195 | 50080551 | 0.000000 | 551238586 | 33926104 | 0.000000
09-04-2025 23:49:20000 | -4600597 | 46.006 | 82855762 | 235987.11 | 114392853 | 98416649 | 50134232 | 0.000000 | 562991150 | 34581174 | 0.000000
09-04-2025 23:49:25000 | -4569323 | 45.6932 | 80885786 | 235928.22 | 113587845 | 98469093 | 50151001 | 0.000000 | 574216797 | 35217502 | 0.000000
09-04-2025 23:49:30000 | -4634679 | 46.3468 | 82019375 | 235953.34 | 115194984 | 98469948 | 50149155 | 0.000000 | 585513000 | 35854153 | 0.000000
09-04-2025 23:49:35000 | -4597174 | 45.9717 | 83955449 | 236002.13 | 114351372 | 98373009 | 50164227 | 0.000000 | 597177185 | 36494617 | 0.000000
09-04-2025 23:49:40000 | -4728554 | 47.2855 | 84449766 | 235951.95 | 117560463 | 98442352 | 50155052 | 0.000000 | 608766602 | 37147639 | 0.000000
09-04-2025 23:49:45000 | -4843658 | 48.4366 | 86442412 | 235960.13 | 120413002 | 98444565 | 50140430 | 0.000000 | 620618835 | 37815508 | 0.000000
09-04-2025 23:49:50000 | -4897410 | 48.9741 | 84920430 | 235930.30 | 121663086 | 98529716 | 50137833 | 0.000000 | 632548035 | 38491350 | 0.000000
09-04-2025 23:49:55000 | -4852417 | 48.5242 | 85254600 | 235971.50 | 120572205 | 98491402 | 50148228 | 0.000000 | 644466858 | 39166589 | 0.000000
09-04-2025 23:50:00000 | -4794765 | 47.9477 | 88463271 | 236089.48 | 119259178 | 98340248 | 50149330 | 0.000000 | 656483215 | 39836526 | 0.000000
09-04-2025 23:50:05000 | -4869746 | 48.6975 | 88586650 | 236040.97 | 121093910 | 98385361 | 50133553 | 0.000000 | 668789551 | 40511018 | 0.000000
09-04-2025 23:50:10000 | -4864407 | 48.6441 | 90545879 | 236122.06 | 121010757 | 98311356 | 50144547 | 0.000000 | 681230286 | 41186606 | 0.000000
09-04-2025 23:50:15000 | -4710827 | 47.1083 | 89901211 | 236159.34 | 117271690 | 98227287 | 50173527 | 0.000000 | 693717529 | 41851235 | 0.000000
09-04-2025 23:50:20000 | -4663273 | 46.6327 | 88605176 | 236097.39 | 116106056 | 98242332 | 50173367 | 0.000000 | 706046875 | 42503174 | 0.000000
09-04-2025 23:50:25000 | -4805941 | 48.0594 | 89850215 | 236078.55 | 119596199 | 98296883 | 50155937 | 0.000000 | 718309448 | 43162803 | 0.000000
09-04-2025 23:50:30000 | -4963539 | 49.6354 | 88627061 | 235960.75 | 123395294 | 98443016 | 50127754 | 0.000000 | 730721985 | 43842246 | 0.000000
09-04-2025 23:50:35000 | -4953583 | 49.5358 | 88815137 | 236006.77 | 123137802 | 98430412 | 50118496 | 0.000000 | 743000488 | 44529746 | 0.000000
09-04-2025 23:50:40000 | -4866669 | 48.6667 | 87884395 | 236075.02 | 120976799 | 98408295 | 50116184 | 0.000000 | 755223755 | 45212578 | 0.000000
09-04-2025 23:50:45000 | -4651296 | 46.513 | 87325908 | 236145.47 | 115739151 | 98282852 | 50169819 | 0.000000 | 767448303 | 45872466 | 0.000000
09-04-2025 23:50:50000 | -4585163 | 45.8516 | 85610469 | 236086.38 | 114095139 | 98301224 | 50186203 | 0.000000 | 779353088 | 46507637 | 0.000000
09-04-2025 23:50:55000 | -4689258 | 46.8926 | 87438389 | 236059.34 | 116693481 | 98305595 | 50169918 | 0.000000 | 791387695 | 47149214 | 0.000000
09-04-2025 23:51:00000 | -4799370 | 47.9937 | 92079893 | 236123.73 | 119519585 | 98208817 | 50155590 | 0.000000 | 803960510 | 47810967 | 0.000000
09-04-2025 23:51:05000 | -4746127 | 47.4613 | 93749580 | 236214.16 | 118275383 | 98104416 | 50174526 | 0.000000 | 816842102 | 48475308 | 0.000000
09-04-2025 23:51:10000 | -4752333 | 47.5233 | 87543574 | 236042.09 | 118223831 | 98345299 | 50166134 | 0.000000 | 829358032 | 49135479 | 0.000000
09-04-2025 23:51:15000 | -4808890 | 48.0889 | 92152773 | 236176.44 | 119723221 | 98212967 | 50158848 | 0.000000 | 841942383 | 49802827 | 0.000000
09-04-2025 23:51:20000 | -4816004 | 48.16 | 90911172 | 236133.55 | 119857773 | 98264557 | 50161236 | 0.000000 | 854656006 | 50468203 | 0.000000
09-04-2025 23:51:25000 | -4790832 | 47.9083 | 90307617 | 236112.39 | 119237793 | 98269356 | 50156654 | 0.000000 | 867284729 | 51134629 | 0.000000
09-04-2025 23:51:30000 | -4787441 | 47.8744 | 91988242 | 236164.69 | 119210434 | 98203606 | 50165176 | 0.000000 | 880005493 | 51803706 | 0.000000
09-04-2025 23:51:35000 | -4783053 | 47.8305 | 89241426 | 236089.61 | 119015640 | 98303589 | 50166130 | 0.000000 | 892579529 | 52466387 | 0.000000
09-04-2025 23:51:40000 | -4658609 | 46.5861 | 90754912 | 236181.63 | 116048836 | 98154785 | 50184391 | 0.000000 | 905266235 | 53120078 | 0.000000
09-04-2025 23:51:45000 | -4746723 | 47.4672 | 90564570 | 236112.75 | 118191330 | 98228119 | 50163391 | 0.000000 | 917798462 | 53776416 | 0.000000
09-04-2025 23:51:50000 | -4870865 | 48.7086 | 92777559 | 236129.97 | 121266304 | 98233887 | 50148983 | 0.000000 | 930569580 | 54442129 | 0.000000
09-04-2025 23:51:55000 | -4899998 | 49 | 93806816 | 236133.83 | 122006409 | 98216370 | 50143829 | 0.000000 | 943713928 | 55117964 | 0.000000
09-04-2025 23:52:00000 | -4937165 | 49.3717 | 93962422 | 236140.64 | 122905365 | 98236740 | 50137676 | 0.000000 | 956763611 | 55800767 | 0.000000
09-04-2025 23:52:05000 | -4878789 | 48.7879 | 94227393 | 236201.41 | 121483482 | 98185516 | 50148239 | 0.000000 | 969802490 | 56481030 | 0.000000
09-04-2025 23:52:10000 | -4805256 | 48.0526 | 91259473 | 236172.94 | 119596718 | 98243958 | 50160923 | 0.000000 | 982587280 | 57153086 | 0.000000
09-04-2025 23:52:15000 | -4770681 | 47.7068 | 90780029 | 236146.52 | 118756752 | 98237267 | 50172653 | 0.000000 | 995241821 | 57817012 | 0.000000
09-04-2025 23:52:20000 | -4781756 | 47.8176 | 89152998 | 236084.25 | 118981026 | 98305969 | 50159569 | 0.000000 | 10077349 | 58477744 | 0.000000
09-04-2025 23:52:25000 | -4872244 | 48.7224 | 90680625 | 236108.06 | 121211403 | 98311760 | 50141602 | 0.000000 | 10201995 | 59150601 | 0.000000
09-04-2025 23:52:30000 | -4801169 | 48.0117 | 90122754 | 236115.56 | 119476463 | 98283478 | 50168262 | 0.000000 | 10328367 | 59819785 | 0.000000
09-04-2025 23:52:35000 | -4666863 | 46.6686 | 89087490 | 236137.91 | 116189766 | 98226311 | 50194004 | 0.000000 | 10453156 | 60474019 | 0.000000
09-04-2025 23:52:40000 | -4717745 | 47.1775 | 89701758 | 236130.38 | 117443794 | 98239975 | 50183723 | 0.000000 | 10576138 | 61123516 | 0.000000
09-04-2025 23:52:45000 | -4804377 | 48.0438 | 90807090 | 236122.63 | 119578491 | 98260254 | 50171825 | 0.000000 | 10702001 | 61782041 | 0.000000
09-04-2025 23:52:50000 | -4762597 | 47.626 | 93534697 | 236225.94 | 118655830 | 98125519 | 50172306 | 0.000000 | 10830669 | 62448638 | 0.000000
09-04-2025 23:52:55000 | -4796059 | 47.9606 | 89104375 | 236070.20 | 119328568 | 98317596 | 50179577 | 0.000000 | 10955977 | 63114023 | 0.000000
09-04-2025 23:53:00000 | -4748233 | 47.4823 | 91381523 | 236205.70 | 118218346 | 98197983 | 50180752 | 0.000000 | 11080519 | 63775938 | 0.000000
09-04-2025 23:53:05000 | -4723863 | 47.2386 | 93486377 | 236225.44 | 117718140 | 98097443 | 50183659 | 0.000000 | 11209901 | 64436963 | 0.000000
09-04-2025 23:53:10000 | -4716008 | 47.1601 | 94555029 | 236254.88 | 117569687 | 98048668 | 50189194 | 0.000000 | 11339800 | 65094819 | 0.000000
09-04-2025 23:53:15000 | -4698788 | 46.9879 | 94195078 | 236227.88 | 117151733 | 98049255 | 50191650 | 0.000000 | 11471527 | 65747876 | 0.000000
09-04-2025 23:53:20000 | -4720242 | 47.2024 | 94298779 | 236206.81 | 117679924 | 98062302 | 50182083 | 0.000000 | 11601353 | 66404971 | 0.000000
09-04-2025 23:53:25000 | -4724584 | 47.2458 | 93487432 | 236207.56 | 117748878 | 98097961 | 50189186 | 0.000000 | 11731508 | 67060254 | 0.000000
09-04-2025 23:53:30000 | -4686178 | 46.8618 | 94413623 | 236231.91 | 116858421 | 98030212 | 50193623 | 0.000000 | 11862423 | 67711616 | 0.000000
09-04-2025 23:53:35000 | -4620095 | 46.2009 | 94975840 | 236258.23 | 115294350 | 97951721 | 50206001 | 0.000000 | 11993804 | 68358677 | 0.000000
09-04-2025 23:53:40000 | -4700545 | 47.0055 | 96171611 | 236292.89 | 117257515 | 97970505 | 50208725 | 0.000000 | 12125687 | 69005327 | 0.000000
09-04-2025 23:53:45000 | -4742535 | 47.4254 | 97401914 | 236265.89 | 118335594 | 97955421 | 50200226 | 0.000000 | 12259365 | 69662998 | 0.000000
09-04-2025 23:53:50000 | -4764640 | 47.6464 | 95960459 | 236247.52 | 118810829 | 98031563 | 50199486 | 0.000000 | 12393643 | 70324702 | 0.000000
09-04-2025 23:53:55000 | -4794259 | 47.9426 | 97047715 | 236263.97 | 119558502 | 98012100 | 50198582 | 0.000000 | 12527819 | 70988350 | 0.000000
09-04-2025 23:54:00000 | -4819821 | 48.1982 | 95765596 | 236223.23 | 120131378 | 98082680 | 50182896 | 0.000000 | 12660695 | 71658086 | 0.000000
09-04-2025 23:54:05000 | -4820587 | 48.2059 | 96044609 | 236234.03 | 120155685 | 98072403 | 50197178 | 0.000000 | 12794447 | 72329287 | 0.000000
09-04-2025 23:54:10000 | -4772230 | 47.7223 | 95561846 | 236253.92 | 118963089 | 98053436 | 50202801 | 0.000000 | 12927257 | 72992930 | 0.000000
09-04-2025 23:54:15000 | -4723004 | 47.23 | 95743730 | 236260.97 | 117788361 | 98006508 | 50209934 | 0.000000 | 13059633 | 73651172 | 0.000000
09-04-2025 23:54:20000 | -4763067 | 47.6307 | 95048223 | 236234.02 | 118728409 | 98066498 | 50201725 | 0.000000 | 13191427 | 74309297 | 0.000000
09-04-2025 23:54:25000 | -4771004 | 47.71 | 96947852 | 236281.36 | 118988388 | 97997253 | 50197521 | 0.000000 | 13324135 | 74971484 | 0.000000
09-04-2025 23:54:30000 | -4757101 | 47.571 | 95298047 | 236231.09 | 118600067 | 98051880 | 50201660 | 0.000000 | 13458330 | 75633457 | 0.000000
09-04-2025 23:54:35000 | -4862733 | 48.6273 | 95595703 | 236198.84 | 121161179 | 98121918 | 50176071 | 0.000000 | 13590629 | 76304312 | 0.000000
09-04-2025 23:54:40000 | -4912436 | 49.1244 | 97818340 | 236236.02 | 122439751 | 98074554 | 50176735 | 0.000000 | 13725800 | 76982842 | 0.000000
09-04-2025 23:54:45000 | -4920834 | 49.2083 | 95234932 | 236187.42 | 122544998 | 98178246 | 50174000 | 0.000000 | 13859268 | 77665410 | 0.000000
09-04-2025 23:54:50000 | -4900035 | 49.0003 | 95836494 | 236227.80 | 122054802 | 98140541 | 50179451 | 0.000000 | 13991779 | 78346431 | 0.000000
09-04-2025 23:54:55000 | -4793730 | 47.9373 | 94009434 | 236219.72 | 119429955 | 98130806 | 50202347 | 0.000000 | 14124604 | 79017422 | 0.000000
09-04-2025 23:55:00000 | -4817455 | 48.1746 | 94216289 | 236216.45 | 120003365 | 98140732 | 50193794 | 0.000000 | 14253982 | 79684624 | 0.000000
09-04-2025 23:55:05000 | -4798197 | 47.982 | 96004834 | 236265.25 | 119605980 | 98056458 | 50196735 | 0.000000 | 14386610 | 80350371 | 0.000000
09-04-2025 23:55:10000 | -4745510 | 47.4551 | 94158193 | 236243.55 | 118264107 | 98087845 | 50205093 | 0.000000 | 14517729 | 81014312 | 0.000000
09-04-2025 23:55:15000 | -4794229 | 47.9423 | 95036846 | 236232.52 | 119479691 | 98091278 | 50195763 | 0.000000 | 14649049 | 81675986 | 0.000000
09-04-2025 23:55:20000 | -4881736 | 48.8174 | 95087031 | 236186.19 | 121605492 | 98155342 | 50173706 | 0.000000 | 14780675 | 82347383 | 0.000000
09-04-2025 23:55:25000 | -4894939 | 48.9494 | 97228203 | 236263.08 | 121977913 | 98083824 | 50173210 | 0.000000 | 14914844 | 83030098 | 0.000000
09-04-2025 23:55:30000 | -4798520 | 47.9852 | 94659375 | 236209.61 | 119573318 | 98109276 | 50202400 | 0.000000 | 15049127 | 83702559 | 0.000000
09-04-2025 23:55:35000 | -4840380 | 48.4038 | 91001563 | 236131.53 | 120454033 | 98278214 | 50183022 | 0.000000 | 15176594 | 84370635 | 0.000000
09-04-2025 23:55:40000 | -4819555 | 48.1955 | 95500322 | 236255.13 | 120101456 | 98092781 | 50191059 | 0.000000 | 15308285 | 85043301 | 0.000000
09-04-2025 23:55:45000 | -4833818 | 48.3382 | 93074697 | 236156.28 | 120374252 | 98196251 | 50189907 | 0.000000 | 15438914 | 85712471 | 0.000000
09-04-2025 23:55:50000 | -4853678 | 48.5368 | 95666484 | 236251.69 | 120926559 | 98112381 | 50179317 | 0.000000 | 15570614 | 86386416 | 0.000000
09-04-2025 23:55:55000 | -4828070 | 48.2807 | 97422676 | 236280.09 | 120383102 | 98024292 | 50193184 | 0.000000 | 15704331 | 87060664 | 0.000000
09-04-2025 23:56:00000 | -4755899 | 47.559 | 95625840 | 236277.67 | 118567223 | 98037880 | 50209236 | 0.000000 | 15838135 | 87723848 | 0.000000
09-04-2025 23:56:05000 | -4777529 | 47.7753 | 94340273 | 236210.44 | 119055847 | 98105568 | 50184124 | 0.000000 | 15969330 | 88386611 | 0.000000
09-04-2025 23:56:10000 | -4863757 | 48.6376 | 96740479 | 236238.47 | 121223274 | 98078743 | 50179878 | 0.000000 | 16102512 | 89062656 | 0.000000
09-04-2025 23:56:15000 | -4793310 | 47.9331 | 97640957 | 236300.83 | 119547424 | 97987679 | 50199535 | 0.000000 | 16237615 | 89732842 | 0.000000
09-04-2025 23:56:20000 | -4728041 | 47.2804 | 95055107 | 236262.55 | 117876556 | 98038307 | 50208458 | 0.000000 | 16371459 | 90392910 | 0.000000
09-04-2025 23:56:25000 | -4753588 | 47.5359 | 97950020 | 236308.94 | 118609985 | 97942368 | 50201698 | 0.000000 | 16504386 | 91052324 | 0.000000
09-04-2025 23:56:30000 | -4810174 | 48.1017 | 95803447 | 236217.88 | 119905014 | 98073723 | 50189590 | 0.000000 | 16638983 | 91715859 | 0.000000
09-04-2025 23:56:35000 | -4764817 | 47.6482 | 97477529 | 236305.97 | 118853836 | 97970871 | 50198181 | 0.000000 | 16773289 | 92383369 | 0.000000
09-04-2025 23:56:40000 | -4697301 | 46.973 | 96569678 | 236302.66 | 117196198 | 97951447 | 50217258 | 0.000000 | 16908430 | 93039375 | 0.000000
09-04-2025 23:56:45000 | -4737680 | 47.3768 | 97628740 | 236328.45 | 118207596 | 97942101 | 50196583 | 0.000000 | 17042003 | 93695029 | 0.000000
09-04-2025 23:56:50000 | -4711754 | 47.1175 | 98857979 | 236333.08 | 117642006 | 97869057 | 50206165 | 0.000000 | 17179304 | 94354814 | 0.000000
09-04-2025 23:56:55000 | -4681829 | 46.8183 | 95919873 | 236249.30 | 116819962 | 97965111 | 50213898 | 0.000000 | 17314916 | 95007500 | 0.000000
09-04-2025 23:57:00000 | -4676433 | 46.7643 | 95916934 | 236303.84 | 116662308 | 97960678 | 50210365 | 0.000000 | 17448127 | 95657822 | 0.000000
09-04-2025 23:57:05000 | -4632000 | 46.32 | 96730117 | 236326.70 | 115629333 | 97888321 | 50225155 | 0.000000 | 17582871 | 96306611 | 0.000000
09-04-2025 23:57:10000 | -4659300 | 46.593 | 95070186 | 236255.73 | 116238220 | 97981133 | 50227474 | 0.000000 | 17715911 | 96950830 | 0.000000
09-04-2025 23:57:15000 | -4786537 | 47.8654 | 97316982 | 236285.05 | 119377998 | 97995117 | 50213078 | 0.000000 | 17850044 | 97606426 | 0.000000
09-04-2025 23:57:20000 | -4788231 | 47.8823 | 99287402 | 236328.31 | 119497559 | 97917084 | 50217766 | 0.000000 | 17987754 | 98272549 | 0.000000
09-04-2025 23:57:25000 | -4783327 | 47.8333 | 99248359 | 236347.59 | 119361694 | 97914536 | 50225647 | 0.000000 | 18125538 | 98935967 | 0.000000
09-04-2025 23:57:30000 | -4755206 | 47.5521 | 95595293 | 236229.75 | 118569489 | 98038544 | 50215427 | 0.000000 | 18260693 | 99596748 | 0.000000
09-04-2025 23:57:35000 | -4838697 | 48.387 | 95894180 | 236205.86 | 120597740 | 98092216 | 50199932 | 0.000000 | 18393479 | 10026783 | 0.000000
09-04-2025 23:57:40000 | -4853213 | 48.5321 | 96758418 | 236253.89 | 120963264 | 98069931 | 50208000 | 0.000000 | 18526902 | 10094305 | 0.000000
09-04-2025 23:57:45000 | -4794859 | 47.9486 | 94362979 | 236218.48 | 119466248 | 98117981 | 50217342 | 0.000000 | 18660253 | 10161259 | 0.000000
09-04-2025 23:57:50000 | -4835953 | 48.3595 | 93503428 | 236147.59 | 120450272 | 98181610 | 50202473 | 0.000000 | 18790552 | 10228231 | 0.000000
09-04-2025 23:57:55000 | -4865613 | 48.6561 | 95438252 | 236240.00 | 121213821 | 98130074 | 50204464 | 0.000000 | 18921533 | 10295841 | 0.000000
09-04-2025 23:58:00000 | -4769819 | 47.6982 | 95512979 | 236276.22 | 118896202 | 98053452 | 50220612 | 0.000000 | 19054456 | 10362827 | 0.000000
09-04-2025 23:58:05000 | -4762526 | 47.6253 | 94345996 | 236221.42 | 118690536 | 98093735 | 50218452 | 0.000000 | 19186653 | 10429176 | 0.000000
09-04-2025 23:58:10000 | -4834794 | 48.3479 | 92196650 | 236162.77 | 120353836 | 98229919 | 50206345 | 0.000000 | 19314971 | 10495932 | 0.000000
09-04-2025 23:58:15000 | -4888359 | 48.8836 | 95542109 | 236194.89 | 121778023 | 98143036 | 50190613 | 0.000000 | 19445746 | 10563834 | 0.000000
09-04-2025 23:58:20000 | -4970244 | 49.7024 | 94427363 | 236183.73 | 123697144 | 98242706 | 50183895 | 0.000000 | 19576812 | 10632547 | 0.000000
09-04-2025 23:58:25000 | -4829396 | 48.294 | 93701016 | 236228.25 | 120260628 | 98169296 | 50205704 | 0.000000 | 19707922 | 10700674 | 0.000000
09-04-2025 23:58:30000 | -4813582 | 48.1358 | 90590791 | 236106.08 | 119803482 | 98274765 | 50206959 | 0.000000 | 19835935 | 10767550 | 0.000000
09-04-2025 23:58:35000 | -4751612 | 47.5161 | 91863457 | 236168.63 | 118339371 | 98181961 | 50217354 | 0.000000 | 19962903 | 10833671 | 0.000000
09-04-2025 23:58:40000 | -4785677 | 47.8568 | 93143896 | 236199.42 | 119200417 | 98158112 | 50206005 | 0.000000 | 20091465 | 10899868 | 0.000000
09-04-2025 23:58:45000 | -4800482 | 48.0048 | 94082471 | 236243.98 | 119576759 | 98133095 | 50204563 | 0.000000 | 20220839 | 10966651 | 0.000000
09-04-2025 23:58:50000 | -4814780 | 48.1478 | 92655361 | 236160.34 | 119900040 | 98198242 | 50200802 | 0.000000 | 20350566 | 11033278 | 0.000000
09-04-2025 23:58:55000 | -4829509 | 48.2951 | 94289434 | 236224.50 | 120295227 | 98146950 | 50199486 | 0.000000 | 20480442 | 11100535 | 0.000000
09-04-2025 23:59:00000 | -4805138 | 48.0514 | 95182910 | 236249.06 | 119738525 | 98094009 | 50214169 | 0.000000 | 20611763 | 11167325 | 0.000000
09-04-2025 23:59:05000 | -4802595 | 48.026 | 92934492 | 236174.56 | 119612427 | 98178711 | 50205402 | 0.000000 | 20742317 | 11233732 | 0.000000
09-04-2025 23:59:10000 | -4807107 | 48.0711 | 91783828 | 236143.67 | 119681725 | 98225586 | 50205681 | 0.000000 | 20869819 | 11300664 | 0.000000
09-04-2025 23:59:15000 | -4824130 | 48.2413 | 89145977 | 236056.77 | 120016594 | 98335121 | 50203014 | 0.000000 | 20995188 | 11367274 | 0.000000
09-04-2025 23:59:20000 | -4929922 | 49.2992 | 89758516 | 236060.09 | 122587692 | 98382645 | 50176987 | 0.000000 | 21118831 | 11435097 | 0.000000
09-04-2025 23:59:25000 | -4856920 | 48.5692 | 91407109 | 236157.42 | 120849625 | 98274742 | 50189999 | 0.000000 | 21246184 | 11503049 | 0.000000
09-04-2025 23:59:30000 | -4710673 | 47.1067 | 89403115 | 236182.00 | 117235313 | 98246254 | 50220093 | 0.000000 | 21372459 | 11568798 | 0.000000
09-04-2025 23:59:35000 | -4748177 | 47.4818 | 89537070 | 236108.44 | 118182098 | 98268097 | 50212868 | 0.000000 | 21496655 | 11634260 | 0.000000
09-04-2025 23:59:40000 | -4770046 | 47.7005 | 93970684 | 236247.31 | 118838356 | 98114235 | 50215561 | 0.000000 | 21623892 | 11700530 | 0.000000
09-04-2025 23:59:45000 | -4702104 | 47.021 | 92184268 | 236203.98 | 117149170 | 98131920 | 50223606 | 0.000000 | 21752158 | 11766062 | 0.000000
09-04-2025 23:59:50000 | -4731634 | 47.3163 | 91396621 | 236109.64 | 117870445 | 98185074 | 50210976 | 0.000000 | 21880293 | 11831771 | 0.000000
09-04-2025 23:59:55000 | -4847261 | 48.4726 | 93962471 | 236167.00 | 120730507 | 98172523 | 50199200 | 0.000000 | 22008911 | 11898545 | 0.000000
10-04-2025 0:00:00000 | -4722804 | 47.228 | 87813721 | 235969.77 | 117587814 | 98314964 | 50218292 | 0.000000 | 22137676 | 11965070 | 0.000000
10-04-2025 0:00:05000 | -4743179 | 47.4318 | 72733145 | 235645.52 | 117596863 | 98844635 | 50220631 | 0.000000 | 10558481 | 66238197 | 0.000000
10-04-2025 0:00:10000 | -4710413 | 47.1041 | 70148496 | 235637.59 | 116711021 | 98909218 | 50226028 | 0.000000 | 20454178 | 131683624 | 0.000000
10-04-2025 0:00:15000 | -4690796 | 46.908 | 69950820 | 235634.23 | 116231277 | 98906319 | 50230572 | 0.000000 | 30184879 | 196793106 | 0.000000
10-04-2025 0:00:20000 | -4775910 | 47.7591 | 69008003 | 235570.23 | 118290642 | 98972176 | 50220413 | 0.000000 | 39870537 | 262584259 | 0.000000
10-04-2025 0:00:25000 | -4781895 | 47.819 | 70546836 | 235619.03 | 118465538 | 98929207 | 50220852 | 0.000000 | 49612232 | 328694183 | 0.000000
10-04-2025 0:00:30000 | -4713248 | 47.1325 | 71391582 | 235683.95 | 116803757 | 98872208 | 50235188 | 0.000000 | 59546669 | 394623718 | 0.000000
10-04-2025 0:00:35000 | -4716016 | 47.1602 | 71637935 | 235687.92 | 116880493 | 98865860 | 50228447 | 0.000000 | 69389603 | 460259308 | 0.000000
10-04-2025 0:00:40000 | -4628041 | 46.2804 | 74415928 | 235790.66 | 114801552 | 98731812 | 50249130 | 0.000000 | 79629082 | 525294861 | 0.000000
10-04-2025 0:00:45000 | -4574104 | 45.741 | 72788457 | 235764.73 | 113447762 | 98757408 | 50269508 | 0.000000 | 89783569 | 589138062 | 0.000000
10-04-2025 0:00:50000 | -4596116 | 45.9612 | 74144292 | 235759.50 | 114033417 | 98723663 | 50274376 | 0.000000 | 99970757 | 652905457 | 0.000000
10-04-2025 0:00:55000 | -4632664 | 46.3266 | 73028740 | 235682.52 | 114914230 | 98780190 | 50281975 | 0.000000 | 110335136 | 716902832 | 0.000000
10-04-2025 0:01:00000 | -4690863 | 46.9086 | 73072275 | 235712.80 | 116311218 | 98808342 | 50288120 | 0.000000 | 120395340 | 781806458 | 0.000000
10-04-2025 0:01:05000 | -4843467 | 48.4347 | 75439561 | 235671.69 | 120110123 | 98808647 | 50263142 | 0.000000 | 130757645 | 848144653 | 0.000000
10-04-2025 0:01:10000 | -4911914 | 49.1191 | 75736055 | 235693.28 | 121771774 | 98832077 | 50254646 | 0.000000 | 141279480 | 916140015 | 0.000000
10-04-2025 0:01:15000 | -4883076 | 48.8308 | 77526260 | 235781.02 | 121092896 | 98763016 | 50268181 | 0.000000 | 151887634 | 984349243 | 0.000000
10-04-2025 0:01:20000 | -4881247 | 48.8125 | 75441836 | 235732.89 | 120995705 | 98826630 | 50263767 | 0.000000 | 162381683 | 10520137 | 0.000000
10-04-2025 0:01:25000 | -4857834 | 48.5783 | 74627646 | 235722.83 | 120402031 | 98840477 | 50264900 | 0.000000 | 172814774 | 11198429 | 0.000000
10-04-2025 0:01:30000 | -4883111 | 48.8311 | 75169023 | 235730.67 | 121028656 | 98835823 | 50267056 | 0.000000 | 183229462 | 11874959 | 0.000000
10-04-2025 0:01:35000 | -4731106 | 47.3111 | 76162114 | 235822.02 | 117346420 | 98728897 | 50292431 | 0.000000 | 193844208 | 12540825 | 0.000000
10-04-2025 0:01:40000 | -4750481 | 47.5048 | 75865566 | 235767.80 | 117830353 | 98748665 | 50286327 | 0.000000 | 204312271 | 13201420 | 0.000000
10-04-2025 0:01:45000 | -4791579 | 47.9158 | 75704912 | 235731.42 | 118833382 | 98774757 | 50278416 | 0.000000 | 214810654 | 13861086 | 0.000000
10-04-2025 0:01:50000 | -4861055 | 48.6106 | 77011479 | 235742.09 | 120558846 | 98768211 | 50257813 | 0.000000 | 225465164 | 14532632 | 0.000000
10-04-2025 0:01:55000 | -4948658 | 49.4866 | 78408618 | 235781.47 | 122714493 | 98767921 | 50251453 | 0.000000 | 236282120 | 15218379 | 0.000000
10-04-2025 0:02:00000 | -4865071 | 48.6507 | 76857412 | 235791.45 | 120624435 | 98775032 | 50257626 | 0.000000 | 247107361 | 15898417 | 0.000000
10-04-2025 0:02:05000 | -4820202 | 48.202 | 75560908 | 235768.25 | 119505875 | 98793526 | 50248856 | 0.000000 | 257650574 | 16573407 | 0.000000
10-04-2025 0:02:10000 | -4841512 | 48.4151 | 75131650 | 235724.89 | 120023865 | 98817245 | 50245815 | 0.000000 | 268047913 | 17244753 | 0.000000
10-04-2025 0:02:15000 | -4843501 | 48.435 | 75625562 | 235743.42 | 120085098 | 98802887 | 50245579 | 0.000000 | 278538727 | 17916570 | 0.000000
10-04-2025 0:02:20000 | -4859132 | 48.5913 | 75693364 | 235704.22 | 120485260 | 98808342 | 50244373 | 0.000000 | 289131378 | 18589871 | 0.000000
10-04-2025 0:02:25000 | -4987932 | 49.8793 | 76559380 | 235704.91 | 123632057 | 98842468 | 50215626 | 0.000000 | 299582642 | 19275515 | 0.000000
10-04-2025 0:02:30000 | -5029465 | 50.2946 | 77342900 | 235720.83 | 124657227 | 98838158 | 50193504 | 0.000000 | 310272217 | 19975331 | 0.000000
10-04-2025 0:02:35000 | -4921863 | 49.2186 | 74906289 | 235722.53 | 121962318 | 98861633 | 50211285 | 0.000000 | 320891052 | 20665129 | 0.000000
10-04-2025 0:02:40000 | -4888950 | 48.8895 | 71662539 | 235641.81 | 121090408 | 98942711 | 50191437 | 0.000000 | 330966278 | 21347905 | 0.000000
10-04-2025 0:02:45000 | -4875998 | 48.76 | 71726377 | 235656.69 | 120769600 | 98935310 | 50188454 | 0.000000 | 340936646 | 22027786 | 0.000000
10-04-2025 0:02:50000 | -4808487 | 48.0849 | 70327754 | 235635.03 | 119093925 | 98947296 | 50191048 | 0.000000 | 350762268 | 22699841 | 0.000000
10-04-2025 0:02:55000 | -4809001 | 48.09 | 70200029 | 235603.80 | 119118828 | 98951279 | 50193825 | 0.000000 | 360554993 | 23368372 | 0.000000
10-04-2025 0:03:00000 | -4810866 | 48.1087 | 69201489 | 235569.52 | 119152664 | 98981224 | 50189983 | 0.000000 | 370157898 | 24035508 | 0.000000
10-04-2025 0:03:05000 | -4912264 | 49.1226 | 71646592 | 235590.22 | 121680420 | 98953026 | 50166576 | 0.000000 | 379887604 | 24716843 | 0.000000
10-04-2025 0:03:10000 | -4971946 | 49.7195 | 72660396 | 235631.20 | 123142319 | 98948952 | 50168213 | 0.000000 | 389807373 | 25404360 | 0.000000
10-04-2025 0:03:15000 | -4871799 | 48.718 | 69728853 | 235580.94 | 120637993 | 98991196 | 50172714 | 0.000000 | 399745972 | 26084719 | 0.000000
10-04-2025 0:03:20000 | -4811238 | 48.1124 | 68729453 | 235613.25 | 119116631 | 98995026 | 50183983 | 0.000000 | 409321350 | 26757075 | 0.000000
10-04-2025 0:03:25000 | -4742679 | 47.4268 | 67221807 | 235597.11 | 117410118 | 99010399 | 50198540 | 0.000000 | 418816437 | 27413621 | 0.000000
10-04-2025 0:03:30000 | -4841563 | 48.4156 | 68717563 | 235564.69 | 119875053 | 99007721 | 50163185 | 0.000000 | 428255096 | 28079819 | 0.000000
10-04-2025 0:03:35000 | -4858002 | 48.58 | 69950977 | 235577.67 | 120309906 | 98979172 | 50170452 | 0.000000 | 437999664 | 28756274 | 0.000000
10-04-2025 0:03:40000 | -4841727 | 48.4173 | 68912310 | 235548.53 | 119893944 | 99002243 | 50167442 | 0.000000 | 447619934 | 29429556 | 0.000000
10-04-2025 0:03:45000 | -4917652 | 49.1765 | 69206543 | 235545.25 | 121748444 | 99024208 | 50151234 | 0.000000 | 457138702 | 30113779 | 0.000000
10-04-2025 0:03:50000 | -4837770 | 48.3777 | 69393511 | 235600.95 | 119788620 | 98986839 | 50173344 | 0.000000 | 466758789 | 30788809 | 0.000000
10-04-2025 0:03:55000 | -4756730 | 47.5673 | 66345254 | 235520.77 | 117758301 | 99041283 | 50178795 | 0.000000 | 476152222 | 31450669 | 0.000000
10-04-2025 0:04:00000 | -4754635 | 47.5463 | 67162656 | 235561.14 | 117722488 | 99017006 | 50176369 | 0.000000 | 485394867 | 32113376 | 0.000000
10-04-2025 0:04:05000 | -4694060 | 46.9406 | 67524893 | 235593.09 | 116241898 | 98981117 | 50197540 | 0.000000 | 494735535 | 32767742 | 0.000000
10-04-2025 0:04:10000 | -4623928 | 46.2393 | 64565156 | 235520.06 | 114476860 | 99039162 | 50202797 | 0.000000 | 503892120 | 33412878 | 0.000000
10-04-2025 0:04:15000 | -4652561 | 46.5256 | 66337588 | 235564.64 | 115208145 | 98998749 | 50211254 | 0.000000 | 512986877 | 34059072 | 0.000000
10-04-2025 0:04:20000 | -4708891 | 47.0889 | 64940327 | 235482.20 | 116575752 | 99062393 | 50212734 | 0.000000 | 522234497 | 34706797 | 0.000000
10-04-2025 0:04:25000 | -4894917 | 48.9492 | 67494414 | 235481.59 | 121175064 | 99062706 | 50181919 | 0.000000 | 531510254 | 35376577 | 0.000000
10-04-2025 0:04:30000 | -4904762 | 49.0476 | 70889385 | 235612.73 | 121461151 | 98971611 | 50186245 | 0.000000 | 541275146 | 36056917 | 0.000000
10-04-2025 0:04:35000 | -4874996 | 48.75 | 69162925 | 235565.91 | 120701263 | 99008545 | 50188580 | 0.000000 | 551022156 | 36734648 | 0.000000
10-04-2025 0:04:40000 | -4908259 | 49.0826 | 70933213 | 235587.69 | 121559601 | 98971802 | 50182224 | 0.000000 | 560768860 | 37416248 | 0.000000
10-04-2025 0:04:45000 | -4977346 | 49.7735 | 71617383 | 235619.55 | 123240692 | 98980629 | 50167206 | 0.000000 | 570615967 | 38106248 | 0.000000
10-04-2025 0:04:50000 | -4917756 | 49.1776 | 72385063 | 235649.33 | 121807541 | 98934029 | 50159100 | 0.000000 | 580688538 | 38794336 | 0.000000
10-04-2025 0:04:55000 | -4952126 | 49.5213 | 70538574 | 235582.02 | 122616264 | 99000710 | 50146751 | 0.000000 | 590509399 | 39478828 | 0.000000
10-04-2025 0:05:00000 | -4885559 | 48.8556 | 71976772 | 235685.28 | 120995323 | 98932114 | 50153767 | 0.000000 | 600494385 | 40160190 | 0.000000
10-04-2025 0:05:05000 | -4877192 | 48.7719 | 67876528 | 235522.14 | 120735153 | 99045410 | 50137589 | 0.000000 | 610249512 | 40835879 | 0.000000
10-04-2025 0:05:10000 | -4995593 | 49.9559 | 69717305 | 235518.23 | 123671783 | 99040184 | 50108421 | 0.000000 | 619820740 | 41523672 | 0.000000
10-04-2025 0:05:15000 | -4977350 | 49.7735 | 74313564 | 235712.78 | 123290909 | 98903717 | 50106335 | 0.000000 | 629827271 | 42217729 | 0.000000
10-04-2025 0:05:20000 | -4891024 | 48.9102 | 72647900 | 235687.48 | 121151566 | 98914818 | 50113052 | 0.000000 | 640081360 | 42903853 | 0.000000
10-04-2025 0:05:25000 | -4889857 | 48.8986 | 69527090 | 235574.44 | 121071426 | 99004227 | 50103230 | 0.000000 | 649851990 | 43580234 | 0.000000
10-04-2025 0:05:30000 | -4953050 | 49.5305 | 71229272 | 235599.86 | 122648552 | 98981720 | 50083805 | 0.000000 | 659556519 | 44268242 | 0.000000
10-04-2025 0:05:35000 | -4832259 | 48.3226 | 68931172 | 235608.31 | 119638237 | 98997849 | 50113571 | 0.000000 | 669366516 | 44944634 | 0.000000
10-04-2025 0:05:40000 | -4710866 | 47.1087 | 67577900 | 235622.36 | 116637207 | 98986702 | 50124565 | 0.000000 | 678804260 | 45607119 | 0.000000
10-04-2025 0:05:45000 | -4660944 | 46.6094 | 66620591 | 235563.39 | 115425621 | 98993889 | 50143707 | 0.000000 | 688121399 | 46253926 | 0.000000
10-04-2025 0:05:50000 | -4726391 | 47.2639 | 68022437 | 235554.86 | 117063881 | 98980164 | 50139069 | 0.000000 | 697485901 | 46903149 | 0.000000
10-04-2025 0:05:55000 | -4736214 | 47.3621 | 67654204 | 235487.77 | 117323441 | 98995125 | 50138603 | 0.000000 | 707076111 | 47563413 | 0.000000
10-04-2025 0:06:00000 | -4796011 | 47.9601 | 60997925 | 235357.33 | 118622276 | 99200882 | 50136116 | 0.000000 | 715614990 | 48226040 | 0.000000
10-04-2025 0:06:05000 | -4745049 | 47.4505 | 63132861 | 235491.23 | 117389786 | 99126465 | 50144657 | 0.000000 | 724255493 | 48886636 | 0.000000
10-04-2025 0:06:10000 | -4604100 | 46.041 | 66158320 | 235623.66 | 114004044 | 98983315 | 50174812 | 0.000000 | 733329163 | 49534663 | 0.000000
10-04-2025 0:06:15000 | -4610234 | 46.1023 | 63157969 | 235498.94 | 114106544 | 99074623 | 50180630 | 0.000000 | 742344788 | 50173706 | 0.000000
10-04-2025 0:06:20000 | -4647230 | 46.4723 | 63782334 | 235489.27 | 115036293 | 99071251 | 50188873 | 0.000000 | 751257263 | 50816172 | 0.000000
10-04-2025 0:06:25000 | -4772934 | 47.7293 | 65983320 | 235498.75 | 118150223 | 99057899 | 50178284 | 0.000000 | 760318481 | 51473530 | 0.000000
10-04-2025 0:06:30000 | -4978652 | 49.7865 | 67548257 | 235455.95 | 123219421 | 99092117 | 50135975 | 0.000000 | 769628357 | 52153237 | 0.000000
10-04-2025 0:06:35000 | -5036089 | 50.3609 | 69133779 | 235483.72 | 124652924 | 99070869 | 50122326 | 0.000000 | 779125366 | 52853237 | 0.000000
10-04-2025 0:06:40000 | -4958356 | 49.5836 | 64580967 | 235432.81 | 122645271 | 99162430 | 50134605 | 0.000000 | 788359009 | 53546675 | 0.000000
10-04-2025 0:06:45000 | -4818568 | 48.1857 | 62726797 | 235462.55 | 119169983 | 99163315 | 50144279 | 0.000000 | 797195435 | 54223677 | 0.000000
10-04-2025 0:06:50000 | -4667146 | 46.6715 | 62634502 | 235537.23 | 115452065 | 99111465 | 50171425 | 0.000000 | 805894653 | 54883433 | 0.000000
10-04-2025 0:06:55000 | -4604488 | 46.0449 | 58742700 | 235388.42 | 113877892 | 99196007 | 50187912 | 0.000000 | 814291809 | 55526040 | 0.000000
10-04-2025 0:07:00000 | -4847534 | 48.4753 | 57987261 | 235254.70 | 119840637 | 99292114 | 50157982 | 0.000000 | 822304077 | 56179634 | 0.000000
10-04-2025 0:07:05000 | -4980612 | 49.8061 | 62047471 | 235352.63 | 123148659 | 99232933 | 50120354 | 0.000000 | 830644775 | 56863901 | 0.000000
10-04-2025 0:07:10000 | -4907846 | 49.0785 | 64351099 | 235423.52 | 121414230 | 99151321 | 50135944 | 0.000000 | 839589966 | 57556060 | 0.000000
10-04-2025 0:07:15000 | -4799471 | 47.9947 | 58684238 | 235349.45 | 118638710 | 99260750 | 50154354 | 0.000000 | 848013794 | 58227275 | 0.000000
10-04-2025 0:07:20000 | -4660576 | 46.6058 | 55140942 | 235295.19 | 115177864 | 99307358 | 50178631 | 0.000000 | 855856384 | 58877837 | 0.000000
10-04-2025 0:07:25000 | -4604503 | 46.045 | 56361436 | 235350.50 | 113824043 | 99259163 | 50186958 | 0.000000 | 863624817 | 59517412 | 0.000000
10-04-2025 0:07:30000 | -4760147 | 47.6015 | 57720913 | 235303.36 | 117675529 | 99272827 | 50167740 | 0.000000 | 871437073 | 60170322 | 0.000000
10-04-2025 0:07:35000 | -4837212 | 48.3721 | 58509990 | 235296.17 | 119579773 | 99276390 | 50155746 | 0.000000 | 879482727 | 60841382 | 0.000000
10-04-2025 0:07:40000 | -4821442 | 48.2144 | 57371704 | 235276.52 | 119175774 | 99299469 | 50166088 | 0.000000 | 887637817 | 61511938 | 0.000000
10-04-2025 0:07:45000 | -5001997 | 50.02 | 56894688 | 235189.72 | 123603790 | 99359329 | 50126617 | 0.000000 | 895533447 | 62193413 | 0.000000
10-04-2025 0:07:50000 | -5076894 | 50.7689 | 59068174 | 235263.30 | 125453308 | 99329964 | 50100178 | 0.000000 | 903601563 | 62896499 | 0.000000
10-04-2025 0:07:55000 | -4908934 | 49.0893 | 57773345 | 235291.58 | 121311882 | 99314560 | 50130386 | 0.000000 | 911737000 | 63591343 | 0.000000
10-04-2025 0:08:00000 | -4826847 | 48.2685 | 51463857 | 235168.28 | 119198990 | 99436409 | 50150574 | 0.000000 | 919310608 | 64262339 | 0.000000
10-04-2025 0:08:05000 | -4916307 | 49.1631 | 52393047 | 235176.55 | 121400154 | 99436935 | 50111874 | 0.000000 | 926296204 | 64936470 | 0.000000
10-04-2025 0:08:10000 | -4954114 | 49.5411 | 54798794 | 235199.81 | 122373550 | 99393799 | 50106476 | 0.000000 | 933796021 | 65624756 | 0.000000
10-04-2025 0:08:15000 | -4915870 | 49.1587 | 58327598 | 235319.34 | 121478348 | 99303436 | 50121571 | 0.000000 | 941765503 | 66310762 | 0.000000
10-04-2025 0:08:20000 | -4849673 | 48.4967 | 54188633 | 235214.92 | 119804916 | 99381531 | 50115597 | 0.000000 | 949623718 | 66987632 | 0.000000
10-04-2025 0:08:25000 | -5032371 | 50.3237 | 56543608 | 235179.30 | 124340240 | 99374680 | 50083130 | 0.000000 | 957312744 | 67674702 | 0.000000
10-04-2025 0:08:30000 | -4977758 | 49.7776 | 54875830 | 235172.66 | 122965836 | 99397820 | 50081070 | 0.000000 | 965064331 | 68370151 | 0.000000
10-04-2025 0:08:35000 | -4927416 | 49.2742 | 51852065 | 235114.63 | 121687485 | 99450867 | 50082245 | 0.000000 | 972448730 | 69055859 | 0.000000
10-04-2025 0:08:40000 | -4838699 | 48.387 | 52437988 | 235202.36 | 119493500 | 99417900 | 50084461 | 0.000000 | 979607727 | 69733901 | 0.000000
10-04-2025 0:08:45000 | -4858437 | 48.5844 | 49350889 | 235118.81 | 119939804 | 99488060 | 50074116 | 0.000000 | 986571106 | 70407715 | 0.000000
10-04-2025 0:08:50000 | -4874713 | 48.7471 | 52386860 | 235161.84 | 120390915 | 99427498 | 50082954 | 0.000000 | 993689819 | 71083892 | 0.000000
10-04-2025 0:08:55000 | -4835883 | 48.3588 | 42100811 | 234884.94 | 119339951 | 99623177 | 50073860 | 0.000000 | 10000742 | 71753242 | 0.000000
10-04-2025 0:09:00000 | -4950720 | 49.5072 | 47732813 | 235023.69 | 122202728 | 99538414 | 50050758 | 0.000000 | 10063090 | 72439609 | 0.000000
10-04-2025 0:09:05000 | -4961379 | 49.6138 | 49509331 | 235050.28 | 122494400 | 99505791 | 50047955 | 0.000000 | 10131402 | 73129775 | 0.000000
10-04-2025 0:09:10000 | -4900458 | 49.0046 | 44255054 | 234939.66 | 120938843 | 99594704 | 50039146 | 0.000000 | 10195356 | 73813228 | 0.000000
10-04-2025 0:09:15000 | -4940134 | 49.4013 | 43789224 | 234932.22 | 121907532 | 99609451 | 50017033 | 0.000000 | 10256198 | 74495752 | 0.000000
10-04-2025 0:09:20000 | -4864349 | 48.6435 | 42050283 | 234918.03 | 120021385 | 99628433 | 50020081 | 0.000000 | 10316447 | 75174106 | 0.000000
10-04-2025 0:09:25000 | -4919929 | 49.1993 | 41942241 | 234874.66 | 121400185 | 99638596 | 50006660 | 0.000000 | 10374371 | 75858345 | 0.000000
10-04-2025 0:09:30000 | -4924280 | 49.2428 | 43174248 | 234957.72 | 121493668 | 99617844 | 50022537 | 0.000000 | 10432622 | 76542368 | 0.000000
10-04-2025 0:09:35000 | -4877744 | 48.7774 | 38787419 | 234818.91 | 120333054 | 99685326 | 50017227 | 0.000000 | 10489265 | 77219854 | 0.000000
10-04-2025 0:09:40000 | -4976945 | 49.7694 | 43266157 | 234900.13 | 122817467 | 99624260 | 49999702 | 0.000000 | 10545492 | 77909155 | 0.000000
10-04-2025 0:09:45000 | -4864385 | 48.6439 | 41038350 | 234892.45 | 120012299 | 99646019 | 50014858 | 0.000000 | 10603016 | 78590171 | 0.000000
10-04-2025 0:09:50000 | -4850947 | 48.5095 | 38564292 | 234816.78 | 119673355 | 99685486 | 50011024 | 0.000000 | 10657368 | 79264224 | 0.000000
10-04-2025 0:09:55000 | -4942124 | 49.4212 | 40531609 | 234841.45 | 121933533 | 99665382 | 49994900 | 0.000000 | 10711195 | 79947051 | 0.000000
10-04-2025 0:10:00000 | -4914845 | 49.1484 | 39508547 | 234829.91 | 121250267 | 99678459 | 49985195 | 0.000000 | 10767042 | 80630986 | 0.000000
10-04-2025 0:10:05000 | -4876554 | 48.7655 | 37507764 | 234805.02 | 120285027 | 99705513 | 49982552 | 0.000000 | 10820136 | 81310708 | 0.000000
10-04-2025 0:10:10000 | -4936980 | 49.3698 | 37274741 | 234750.69 | 121789612 | 99716194 | 49970318 | 0.000000 | 10872286 | 81990820 | 0.000000
10-04-2025 0:10:15000 | -4952921 | 49.5292 | 38489868 | 234813.48 | 122178253 | 99699409 | 49966099 | 0.000000 | 10924852 | 82676621 | 0.000000
10-04-2025 0:10:20000 | -4926471 | 49.2647 | 37080950 | 234763.14 | 121522438 | 99717926 | 49959225 | 0.000000 | 10976460 | 83365723 | 0.000000
10-04-2025 0:10:25000 | -4840179 | 48.4018 | 38074595 | 234871.33 | 119369530 | 99692032 | 49967937 | 0.000000 | 11028767 | 84041475 | 0.000000
10-04-2025 0:10:30000 | -4749446 | 47.4945 | 35787129 | 234781.05 | 117149582 | 99717323 | 49987614 | 0.000000 | 11080946 | 84704268 | 0.000000
10-04-2025 0:10:35000 | -4810829 | 48.1083 | 37301577 | 234835.05 | 118653397 | 99700752 | 49973808 | 0.000000 | 11129916 | 85366045 | 0.000000
10-04-2025 0:10:40000 | -4917073 | 49.1707 | 45439810 | 234959.86 | 121359268 | 99575714 | 49951050 | 0.000000 | 11190483 | 86043750 | 0.000000
10-04-2025 0:10:45000 | -4937378 | 49.3738 | 44062700 | 234919.58 | 121846329 | 99604149 | 49945675 | 0.000000 | 11252896 | 86730732 | 0.000000
10-04-2025 0:10:50000 | -4863979 | 48.6398 | 41038716 | 234881.02 | 120006912 | 99645950 | 49967144 | 0.000000 | 11312006 | 87409834 | 0.000000
10-04-2025 0:10:55000 | -4775702 | 47.757 | 38505049 | 234849.14 | 117810570 | 99676544 | 49976902 | 0.000000 | 11367623 | 88078838 | 0.000000
10-04-2025 0:11:00000 | -4545005 | 45.45 | 40020098 | 234980.41 | 112127655 | 99614571 | 50035515 | 0.000000 | 11423250 | 88723477 | 0.000000
10-04-2025 0:11:05000 | -4509216 | 45.0922 | 37177354 | 234875.34 | 111240990 | 99661842 | 50046154 | 0.000000 | 11477345 | 89346855 | 0.000000
10-04-2025 0:11:10000 | -4580388 | 45.8039 | 39534795 | 234905.17 | 113018570 | 99629570 | 50039909 | 0.000000 | 11530889 | 89979375 | 0.000000
10-04-2025 0:11:15000 | -4710698 | 47.107 | 40916790 | 234868.28 | 116263191 | 99624893 | 50031979 | 0.000000 | 11586501 | 90626563 | 0.000000
10-04-2025 0:11:20000 | -4871626 | 48.7163 | 43800127 | 234899.84 | 120241425 | 99598259 | 50013577 | 0.000000 | 11645747 | 91295732 | 0.000000
10-04-2025 0:11:25000 | -4905634 | 49.0563 | 44341128 | 234913.67 | 121078377 | 99593987 | 50002720 | 0.000000 | 11707365 | 91977480 | 0.000000
10-04-2025 0:11:30000 | -4941074 | 49.4107 | 44221704 | 234935.77 | 121932335 | 99601891 | 50006161 | 0.000000 | 11769241 | 92661348 | 0.000000
10-04-2025 0:11:35000 | -4934086 | 49.3409 | 43023042 | 234892.69 | 121757515 | 99622002 | 50005405 | 0.000000 | 11830630 | 93342227 | 0.000000
10-04-2025 0:11:40000 | -4963976 | 49.6398 | 44086108 | 234923.06 | 122496826 | 99607941 | 49987827 | 0.000000 | 11891545 | 94031729 | 0.000000
10-04-2025 0:11:45000 | -4923560 | 49.2356 | 44794160 | 234940.88 | 121515129 | 99588692 | 49992649 | 0.000000 | 11953569 | 94719736 | 0.000000
10-04-2025 0:11:50000 | -4793540 | 47.9354 | 40581572 | 234908.50 | 118260895 | 99643562 | 50005558 | 0.000000 | 12012083 | 95391875 | 0.000000
10-04-2025 0:11:55000 | -4834701 | 48.347 | 41498677 | 234919.81 | 119277679 | 99633644 | 49994045 | 0.000000 | 12067975 | 96061074 | 0.000000
10-04-2025 0:12:00000 | -4853727 | 48.5373 | 42928770 | 234936.27 | 119766327 | 99611153 | 49995922 | 0.000000 | 12126528 | 96733125 | 0.000000
10-04-2025 0:12:05000 | -4762792 | 47.6279 | 42408696 | 234957.23 | 117517570 | 99605919 | 50010460 | 0.000000 | 12185392 | 97400996 | 0.000000
10-04-2025 0:12:10000 | -4726757 | 47.2676 | 41018911 | 234911.06 | 116633621 | 99625572 | 50015007 | 0.000000 | 12242843 | 98057295 | 0.000000
10-04-2025 0:12:15000 | -4792773 | 47.9277 | 39990830 | 234842.83 | 118258484 | 99653694 | 49996365 | 0.000000 | 12298635 | 98716260 | 0.000000
10-04-2025 0:12:20000 | -4909937 | 49.0994 | 40740847 | 234805.41 | 121168915 | 99657516 | 49973362 | 0.000000 | 12356090 | 99394463 | 0.000000
10-04-2025 0:12:25000 | -4933085 | 49.3308 | 41594072 | 234879.91 | 121710289 | 99646423 | 49983482 | 0.000000 | 12413560 | 10008063 | 0.000000
10-04-2025 0:12:30000 | -4867027 | 48.6703 | 42546836 | 234928.27 | 120097214 | 99620079 | 49997639 | 0.000000 | 12471812 | 10075983 | 0.000000
10-04-2025 0:12:35000 | -4905893 | 49.0589 | 42188071 | 234911.56 | 121041626 | 99632286 | 49981087 | 0.000000 | 12529822 | 10143926 | 0.000000
10-04-2025 0:12:40000 | -4918134 | 49.1813 | 44437305 | 234934.19 | 121383408 | 99594292 | 49984833 | 0.000000 | 12591019 | 10212196 | 0.000000
10-04-2025 0:12:45000 | -4882983 | 48.8298 | 41142339 | 234869.92 | 120479523 | 99646919 | 49985321 | 0.000000 | 12648859 | 10280284 | 0.000000
10-04-2025 0:12:50000 | -4798838 | 47.9884 | 40066355 | 234879.88 | 118396187 | 99653267 | 50005413 | 0.000000 | 12705116 | 10347663 | 0.000000
10-04-2025 0:12:55000 | -4669951 | 46.6995 | 38528142 | 234920.66 | 115186348 | 99661400 | 50036728 | 0.000000 | 12759716 | 10413031 | 0.000000
10-04-2025 0:13:00000 | -4553387 | 45.5339 | 41697388 | 235019.81 | 112348869 | 99583328 | 50067032 | 0.000000 | 12817500 | 10476705 | 0.000000
10-04-2025 0:13:05000 | -4625279 | 46.2528 | 41631108 | 234919.95 | 114156715 | 99597374 | 50055290 | 0.000000 | 12875165 | 10540146 | 0.000000
10-04-2025 0:13:10000 | -4785247 | 47.8525 | 43985239 | 234929.84 | 118119003 | 99580208 | 50036655 | 0.000000 | 12933354 | 10605775 | 0.000000
10-04-2025 0:13:15000 | -4745641 | 47.4564 | 43635039 | 234966.58 | 117120552 | 99579941 | 50055397 | 0.000000 | 12994131 | 10672128 | 0.000000
10-04-2025 0:13:20000 | -4725965 | 47.2597 | 45527373 | 235024.48 | 116655159 | 99539185 | 50056614 | 0.000000 | 13056400 | 10738044 | 0.000000
10-04-2025 0:13:25000 | -4665329 | 46.6533 | 44331104 | 235043.34 | 115135544 | 99551575 | 50063793 | 0.000000 | 13116654 | 10803121 | 0.000000
10-04-2025 0:13:30000 | -4642113 | 46.4211 | 44391475 | 235005.30 | 114588501 | 99545876 | 50062683 | 0.000000 | 13178376 | 10868036 | 0.000000
10-04-2025 0:13:35000 | -4728924 | 47.2892 | 47416123 | 235043.91 | 116763832 | 99501076 | 50077057 | 0.000000 | 13244462 | 10933356 | 0.000000
10-04-2025 0:13:40000 | -4854394 | 48.5439 | 45966055 | 234962.73 | 119837616 | 99554688 | 50053894 | 0.000000 | 13308009 | 10999666 | 0.000000
10-04-2025 0:13:45000 | -5005159 | 50.0516 | 49971660 | 235010.67 | 123594421 | 99505295 | 50019932 | 0.000000 | 13375371 | 11068827 | 0.000000
10-04-2025 0:13:50000 | -5091888 | 50.9189 | 46820903 | 234910.88 | 125698029 | 99579903 | 49997578 | 0.000000 | 13442112 | 11139296 | 0.000000
10-04-2025 0:13:55000 | -4869758 | 48.6976 | 45806064 | 235044.00 | 120168884 | 99560532 | 50043468 | 0.000000 | 13507065 | 11208240 | 0.000000
10-04-2025 0:14:00000 | -4681958 | 46.8196 | 42853916 | 235010.48 | 115525978 | 99583725 | 50068535 | 0.000000 | 13566868 | 11274431 | 0.000000
10-04-2025 0:14:05000 | -4621532 | 46.2153 | 39897090 | 234936.98 | 114017296 | 99629440 | 50081539 | 0.000000 | 13624093 | 11338605 | 0.000000
10-04-2025 0:14:10000 | -4774715 | 47.7471 | 42755317 | 234922.98 | 117836319 | 99601479 | 50067078 | 0.000000 | 13682393 | 11403842 | 0.000000
10-04-2025 0:14:15000 | -4774206 | 47.7421 | 43800366 | 234945.77 | 117833939 | 99581795 | 50065865 | 0.000000 | 13743951 | 11470106 | 0.000000
10-04-2025 0:14:20000 | -4832262 | 48.3226 | 42694004 | 234890.55 | 119260910 | 99611969 | 50052742 | 0.000000 | 13803688 | 11536800 | 0.000000
10-04-2025 0:14:25000 | -5030552 | 50.3055 | 43098442 | 234825.34 | 124164192 | 99635010 | 50019653 | 0.000000 | 13864354 | 11605457 | 0.000000
10-04-2025 0:14:30000 | -5060295 | 50.6029 | 44479741 | 234889.94 | 124883339 | 99615906 | 50004494 | 0.000000 | 13926633 | 11675659 | 0.000000
10-04-2025 0:14:35000 | -5047667 | 50.4767 | 42999463 | 234859.02 | 124556366 | 99639122 | 49998692 | 0.000000 | 13987736 | 11745852 | 0.000000
10-04-2025 0:14:40000 | -4990975 | 49.9098 | 40556501 | 234823.64 | 123137543 | 99671471 | 49993507 | 0.000000 | 14045602 | 11815563 | 0.000000
10-04-2025 0:14:45000 | -4891847 | 48.9185 | 38880872 | 234828.97 | 120670181 | 99685631 | 50009792 | 0.000000 | 14101834 | 11883751 | 0.000000
10-04-2025 0:14:50000 | -4893511 | 48.9351 | 38356499 | 234817.34 | 120706787 | 99694221 | 49997608 | 0.000000 | 14155474 | 11951472 | 0.000000
10-04-2025 0:14:55000 | -5005460 | 50.0546 | 39356343 | 234759.83 | 123499405 | 99692314 | 49977871 | 0.000000 | 14210623 | 12020378 | 0.000000
10-04-2025 0:15:00000 | -5025955 | 50.2595 | 40180161 | 234778.97 | 124009193 | 99681961 | 49964878 | 0.000000 | 14265908 | 12090124 | 0.000000
10-04-2025 0:15:05000 | -4967364 | 49.6736 | 40123003 | 234856.86 | 122531403 | 99675369 | 49964645 | 0.000000 | 5449661 | 69806305 | 0.000000
10-04-2025 0:15:10000 | -4907370 | 49.0737 | 35054670 | 234730.36 | 121032425 | 99745842 | 49960075 | 0.000000 | 10625352 | 138342010 | 0.000000
10-04-2025 0:15:15000 | -4843082 | 48.4308 | 37363276 | 234831.52 | 119448097 | 99703735 | 49955563 | 0.000000 | 15568449 | 206136597 | 0.000000
10-04-2025 0:15:20000 | -4830050 | 48.3005 | 37295747 | 234785.11 | 119148666 | 99703209 | 49973080 | 0.000000 | 20713810 | 273318665 | 0.000000
10-04-2025 0:15:25000 | -4801093 | 48.0109 | 34969282 | 234754.33 | 118411911 | 99735794 | 49969505 | 0.000000 | 25648119 | 339910706 | 0.000000
10-04-2025 0:15:30000 | -4784695 | 47.8469 | 34517698 | 234716.88 | 118022644 | 99740791 | 49965942 | 0.000000 | 30523602 | 406682129 | 0.000000
10-04-2025 0:15:35000 | -4710540 | 47.1054 | 32350886 | 234708.55 | 116166168 | 99764999 | 49993324 | 0.000000 | 34987621 | 472760010 | 0.000000
10-04-2025 0:15:40000 | -4557968 | 45.5797 | 29767441 | 234729.52 | 112370285 | 99787422 | 50024101 | 0.000000 | 39224125 | 536783875 | 0.000000
10-04-2025 0:15:45000 | -4539818 | 45.3982 | 29307151 | 234691.27 | 111936188 | 99792274 | 50033066 | 0.000000 | 43238499 | 600106567 | 0.000000
10-04-2025 0:15:50000 | -4749302 | 47.493 | 31474426 | 234611.70 | 117152802 | 99781120 | 50011990 | 0.000000 | 47505032 | 664569946 | 0.000000
10-04-2025 0:15:55000 | -4912738 | 49.1274 | 32386282 | 234587.44 | 121191933 | 99783417 | 49983711 | 0.000000 | 51945942 | 731926453 | 0.000000
10-04-2025 0:16:00000 | -4928750 | 49.2875 | 33544043 | 234618.75 | 121590416 | 99769211 | 49990818 | 0.000000 | 56589226 | 800398804 | 0.000000
10-04-2025 0:16:05000 | -4994308 | 49.9431 | 31768411 | 234606.83 | 123176033 | 99798302 | 49975082 | 0.000000 | 60978638 | 869174561 | 0.000000
10-04-2025 0:16:10000 | -4991160 | 49.9116 | 33185703 | 234656.63 | 123094940 | 99779694 | 49960552 | 0.000000 | 65467369 | 938861877 | 0.000000
10-04-2025 0:16:15000 | -4938095 | 49.3809 | 30422007 | 234593.70 | 121784790 | 99810768 | 49963051 | 0.000000 | 69802559 | 10081033 | 0.000000
10-04-2025 0:16:20000 | -4828659 | 48.2866 | 29739922 | 234639.75 | 119063599 | 99810867 | 49970901 | 0.000000 | 73963219 | 10756707 | 0.000000
10-04-2025 0:16:25000 | -4847188 | 48.4719 | 31436262 | 234678.81 | 119521568 | 99790352 | 49970890 | 0.000000 | 78147949 | 11431943 | 0.000000
10-04-2025 0:16:30000 | -4784460 | 47.8446 | 30734578 | 234650.17 | 117985771 | 99794312 | 49991356 | 0.000000 | 82494614 | 12098680 | 0.000000
10-04-2025 0:16:35000 | -4688717 | 46.8872 | 30148586 | 234663.05 | 115624329 | 99793915 | 50006695 | 0.000000 | 86680687 | 12755751 | 0.000000
10-04-2025 0:16:40000 | -4782200 | 47.822 | 29859163 | 234592.94 | 117945778 | 99805641 | 49990528 | 0.000000 | 90791618 | 13413032 | 0.000000
10-04-2025 0:16:45000 | -4741995 | 47.42 | 29835291 | 234606.83 | 116951881 | 99802658 | 50009926 | 0.000000 | 95189941 | 14072870 | 0.000000
10-04-2025 0:16:50000 | -4673838 | 46.7384 | 28298914 | 234590.22 | 115262337 | 99817200 | 50009960 | 0.000000 | 99216034 | 14724962 | 0.000000
10-04-2025 0:16:55000 | -4780887 | 47.8089 | 30287468 | 234581.09 | 117924698 | 99799934 | 49987675 | 0.000000 | 103285179 | 15382227 | 0.000000
10-04-2025 0:17:00000 | -4844866 | 48.4487 | 31508225 | 234640.55 | 119484543 | 99789192 | 49977013 | 0.000000 | 107451614 | 16053539 | 0.000000
10-04-2025 0:17:05000 | -4866031 | 48.6603 | 32977114 | 234646.81 | 120028282 | 99771149 | 49982048 | 0.000000 | 111985962 | 16731202 | 0.000000
10-04-2025 0:17:10000 | -4961823 | 49.6182 | 31078247 | 234579.25 | 122385345 | 99804420 | 49961628 | 0.000000 | 116270500 | 17414475 | 0.000000
10-04-2025 0:17:15000 | -5009834 | 50.0983 | 32069602 | 234572.13 | 123580498 | 99795746 | 49945518 | 0.000000 | 120674019 | 18107463 | 0.000000
10-04-2025 0:17:20000 | -4835568 | 48.3557 | 31171543 | 234656.75 | 119248856 | 99792870 | 49977398 | 0.000000 | 125127838 | 18789426 | 0.000000
10-04-2025 0:17:25000 | -4588436 | 45.8844 | 28151782 | 234679.03 | 113118446 | 99812317 | 50022739 | 0.000000 | 129310486 | 19438842 | 0.000000
10-04-2025 0:17:30000 | -4617025 | 46.1703 | 28355620 | 234661.89 | 113834023 | 99811943 | 50022648 | 0.000000 | 133157211 | 20076516 | 0.000000
10-04-2025 0:17:35000 | -4701753 | 47.0175 | 30095198 | 234621.70 | 115958641 | 99795776 | 50018734 | 0.000000 | 137242630 | 20723540 | 0.000000
10-04-2025 0:17:40000 | -4814341 | 48.1434 | 30912942 | 234577.75 | 118756989 | 99794487 | 50011429 | 0.000000 | 141505127 | 21386133 | 0.000000
10-04-2025 0:17:45000 | -4932239 | 49.3224 | 33400061 | 234606.47 | 121678665 | 99771500 | 49995312 | 0.000000 | 145954636 | 22065278 | 0.000000
10-04-2025 0:17:50000 | -4949459 | 49.4946 | 30251870 | 234505.83 | 122104797 | 99813728 | 49977394 | 0.000000 | 150316940 | 22750789 | 0.000000
10-04-2025 0:17:55000 | -4935035 | 49.3503 | 31964700 | 234617.02 | 121719833 | 99790894 | 49969872 | 0.000000 | 154639175 | 23441660 | 0.000000
10-04-2025 0:18:00000 | -4834163 | 48.3416 | 28562749 | 234580.23 | 119207581 | 99825905 | 49978569 | 0.000000 | 158835220 | 24115449 | 0.000000
10-04-2025 0:18:05000 | -4678997 | 46.79 | 29740359 | 234686.98 | 115362404 | 99798607 | 49985413 | 0.000000 | 162931061 | 24774546 | 0.000000
10-04-2025 0:18:10000 | -4465766 | 44.6577 | 30177739 | 234753.27 | 110107231 | 99772453 | 50018055 | 0.000000 | 167207306 | 25407622 | 0.000000
10-04-2025 0:18:15000 | -4285624 | 42.8562 | 27809314 | 234725.91 | 105657402 | 99790131 | 50038471 | 0.000000 | 171251175 | 26009915 | 0.000000
10-04-2025 0:18:20000 | -4279445 | 42.7944 | 25255742 | 234560.92 | 105543358 | 99826309 | 50007301 | 0.000000 | 175005142 | 26601077 | 0.000000
10-04-2025 0:18:25000 | -4434759 | 44.3476 | 31793730 | 234671.25 | 109412178 | 99743996 | 49966179 | 0.000000 | 178984543 | 27210034 | 0.000000
10-04-2025 0:18:30000 | -4458495 | 44.5849 | 28140872 | 234570.81 | 109977318 | 99801399 | 49946297 | 0.000000 | 182982239 | 27828193 | 0.000000
10-04-2025 0:18:35000 | -4411019 | 44.1102 | 28958652 | 234645.38 | 108793983 | 99785194 | 49950279 | 0.000000 | 186991455 | 28446909 | 0.000000
10-04-2025 0:18:40000 | -4336714 | 43.3671 | 28188657 | 234663.47 | 106950516 | 99789413 | 49959442 | 0.000000 | 190900696 | 29053142 | 0.000000
10-04-2025 0:18:45000 | -4161391 | 41.6139 | 27528679 | 234692.95 | 102618889 | 99781906 | 49971622 | 0.000000 | 194802536 | 29640151 | 0.000000
10-04-2025 0:18:50000 | -4025205 | 40.252 | 28827339 | 234753.84 | 99276779 | 99744530 | 49972683 | 0.000000 | 198662247 | 30211360 | 0.000000
10-04-2025 0:18:55000 | -3880319 | 38.8032 | 27258687 | 234763.61 | 95692879 | 99754166 | 49991566 | 0.000000 | 202542313 | 30757634 | 0.000000
10-04-2025 0:19:00000 | -3822719 | 38.2272 | 27187651 | 234706.98 | 94300453 | 99748047 | 49977070 | 0.000000 | 206350143 | 31291838 | 0.000000
10-04-2025 0:19:05000 | -3921144 | 39.2114 | 26851318 | 234629.97 | 96738014 | 99766357 | 49945637 | 0.000000 | 210145859 | 31830498 | 0.000000
10-04-2025 0:19:10000 | -3856625 | 38.5662 | 27617471 | 234715.86 | 95134155 | 99744576 | 49954407 | 0.000000 | 213927307 | 32368987 | 0.000000
10-04-2025 0:19:15000 | -3731524 | 37.3152 | 23195417 | 234629.97 | 92031174 | 99807358 | 49968758 | 0.000000 | 217342590 | 32895217 | 0.000000
10-04-2025 0:19:20000 | -3683796 | 36.838 | 23142463 | 234632.05 | 90850609 | 99803253 | 49956570 | 0.000000 | 220538254 | 33408042 | 0.000000
10-04-2025 0:19:25000 | -3543403 | 35.434 | 23921128 | 234697.56 | 87406792 | 99772903 | 49964283 | 0.000000 | 223793228 | 33910002 | 0.000000
10-04-2025 0:19:30000 | -3362256 | 33.6226 | 24633140 | 234759.52 | 82941025 | 99732697 | 49990196 | 0.000000 | 227324432 | 34388252 | 0.000000
10-04-2025 0:19:35000 | -3174398 | 31.744 | 23430813 | 234752.27 | 78315651 | 99728699 | 50013592 | 0.000000 | 230622543 | 34838777 | 0.000000
10-04-2025 0:19:40000 | -3079276 | 30.7928 | 22164724 | 234733.48 | 75966446 | 99741943 | 50006931 | 0.000000 | 233709137 | 35270601 | 0.000000
10-04-2025 0:19:45000 | -3086483 | 30.8648 | 19778627 | 234602.42 | 76147980 | 99795311 | 49982624 | 0.000000 | 236570740 | 35699326 | 0.000000
10-04-2025 0:19:50000 | -3058920 | 30.5892 | 22048225 | 234689.78 | 75475349 | 99741241 | 49981640 | 0.000000 | 239425644 | 36126809 | 0.000000
10-04-2025 0:19:55000 | -3076049 | 30.7605 | 20089197 | 234595.52 | 75898598 | 99787422 | 49958828 | 0.000000 | 242296082 | 36551655 | 0.000000
10-04-2025 0:20:00000 | -3090398 | 30.904 | 20415051 | 234607.75 | 76250031 | 99782516 | 49949554 | 0.000000 | 245232681 | 36978489 | 0.000000
10-04-2025 0:20:05000 | -2999977 | 29.9998 | 21204890 | 234665.11 | 74034325 | 99751122 | 49956215 | 0.000000 | 248182465 | 37402590 | 0.000000
10-04-2025 0:20:10000 | -2958303 | 29.583 | 20945579 | 234660.80 | 73001129 | 99750290 | 49959457 | 0.000000 | 251044952 | 37816606 | 0.000000
10-04-2025 0:20:15000 | -2842050 | 28.4205 | 20000526 | 234655.30 | 70133919 | 99753296 | 49980721 | 0.000000 | 254033691 | 38215181 | 0.000000
10-04-2025 0:20:20000 | -2824525 | 28.2452 | 20916692 | 234657.41 | 69718292 | 99726921 | 49978676 | 0.000000 | 256941467 | 38607563 | 0.000000
10-04-2025 0:20:25000 | -2936045 | 29.3605 | 19810563 | 234596.55 | 72454643 | 99773140 | 49955193 | 0.000000 | 259738220 | 39005779 | 0.000000
10-04-2025 0:20:30000 | -3103511 | 31.0351 | 21289150 | 234608.84 | 76592728 | 99765549 | 49926533 | 0.000000 | 262557281 | 39428569 | 0.000000
10-04-2025 0:20:35000 | -3027370 | 30.2737 | 21277896 | 234622.75 | 74722160 | 99753914 | 49931782 | 0.000000 | 265567596 | 39854395 | 0.000000
10-04-2025 0:20:40000 | -2860726 | 28.6073 | 20414232 | 234661.98 | 70601028 | 99746353 | 49964085 | 0.000000 | 268395935 | 40260696 | 0.000000
10-04-2025 0:20:45000 | -2697862 | 26.9786 | 19489139 | 234693.72 | 66578979 | 99740089 | 49999115 | 0.000000 | 271222595 | 40644697 | 0.000000
10-04-2025 0:20:50000 | -2883158 | 28.8316 | 19258353 | 234617.92 | 71140205 | 99777657 | 49958466 | 0.000000 | 273750549 | 41030879 | 0.000000
10-04-2025 0:20:55000 | -3045333 | 30.4533 | 25487791 | 234707.69 | 75207199 | 99651588 | 49933552 | 0.000000 | 276926025 | 41449736 | 0.000000
10-04-2025 0:21:00000 | -2969944 | 29.6994 | 21838457 | 234650.33 | 73306801 | 99730743 | 49959068 | 0.000000 | 280283691 | 41866860 | 0.000000
10-04-2025 0:21:05000 | -2913396 | 29.134 | 22176543 | 234710.64 | 71908951 | 99711548 | 49968052 | 0.000000 | 283312897 | 42273638 | 0.000000
10-04-2025 0:21:10000 | -2927402 | 29.274 | 24091680 | 234768.47 | 72268440 | 99663071 | 49963440 | 0.000000 | 286372345 | 42679976 | 0.000000
10-04-2025 0:21:15000 | -2677440 | 26.7744 | 27050945 | 234895.55 | 66182739 | 99493492 | 50016846 | 0.000000 | 290075775 | 43069653 | 0.000000
10-04-2025 0:21:20000 | -2582853 | 25.8285 | 23084959 | 234777.83 | 63808472 | 99602959 | 50045433 | 0.000000 | 293455292 | 43428984 | 0.000000
10-04-2025 0:21:25000 | -2643816 | 26.4382 | 25931938 | 234838.13 | 65347885 | 99522408 | 50034966 | 0.000000 | 296901886 | 43790928 | 0.000000
10-04-2025 0:21:30000 | -2776928 | 27.7693 | 26951816 | 234825.95 | 68635262 | 99532303 | 50024155 | 0.000000 | 300568359 | 44170186 | 0.000000
10-04-2025 0:21:35000 | -2910380 | 29.1038 | 28077202 | 234807.98 | 71931427 | 99537872 | 50012215 | 0.000000 | 304359436 | 44567314 | 0.000000
10-04-2025 0:21:40000 | -3077910 | 30.7791 | 24721614 | 234652.89 | 76011955 | 99678993 | 49984394 | 0.000000 | 308101196 | 44982397 | 0.000000
10-04-2025 0:21:45000 | -3165769 | 31.6577 | 27482048 | 234730.28 | 78186798 | 99625320 | 49955475 | 0.000000 | 311733337 | 45420747 | 0.000000
10-04-2025 0:21:50000 | -3182161 | 31.8216 | 23726172 | 234644.88 | 78548691 | 99723198 | 49942627 | 0.000000 | 315318176 | 45861958 | 0.000000
10-04-2025 0:21:55000 | -3233250 | 32.3325 | 20643481 | 234555.44 | 79779892 | 99796799 | 49921455 | 0.000000 | 318395203 | 46305923 | 0.000000
10-04-2025 0:22:00000 | -3257639 | 32.5764 | 22730127 | 234632.44 | 80384712 | 99757462 | 49906898 | 0.000000 | 321500031 | 46760137 | 0.000000
10-04-2025 0:22:05000 | -2988864 | 29.8886 | 23925220 | 234811.52 | 73770432 | 99681145 | 49946945 | 0.000000 | 324735291 | 47191235 | 0.000000
10-04-2025 0:22:10000 | -2549876 | 25.4988 | 23591812 | 234905.73 | 62982918 | 99574715 | 50041904 | 0.000000 | 328133667 | 47567544 | 0.000000
10-04-2025 0:22:15000 | -2545376 | 25.4538 | 22339993 | 234763.78 | 62879593 | 99617058 | 50036125 | 0.000000 | 331340637 | 47916904 | 0.000000
10-04-2025 0:22:20000 | -2661633 | 26.6163 | 25954985 | 234846.84 | 65781792 | 99527901 | 50019688 | 0.000000 | 334728851 | 48280439 | 0.000000
10-04-2025 0:22:25000 | -2758258 | 27.5826 | 27564487 | 234818.05 | 68191032 | 99504364 | 50016808 | 0.000000 | 338442017 | 48658218 | 0.000000
10-04-2025 0:22:30000 | -2923134 | 29.2313 | 29342556 | 234825.38 | 72266449 | 99499962 | 49999012 | 0.000000 | 342384277 | 49056362 | 0.000000
10-04-2025 0:22:35000 | -2918640 | 29.1864 | 31680034 | 234917.13 | 72185738 | 99416069 | 50010315 | 0.000000 | 346671204 | 49463271 | 0.000000
10-04-2025 0:22:40000 | -2908829 | 29.0883 | 30400400 | 234878.06 | 71931114 | 99458305 | 50014690 | 0.000000 | 350982697 | 49866772 | 0.000000
10-04-2025 0:22:45000 | -2953273 | 29.5327 | 30710635 | 234889.80 | 73017151 | 99463669 | 50004349 | 0.000000 | 355232758 | 50272529 | 0.000000
10-04-2025 0:22:50000 | -3023648 | 30.2365 | 31839670 | 234883.84 | 74770103 | 99450142 | 49991741 | 0.000000 | 359602844 | 50688291 | 0.000000
10-04-2025 0:22:55000 | -3055703 | 30.557 | 31937244 | 234910.09 | 75542778 | 99458244 | 49988483 | 0.000000 | 363926514 | 51112144 | 0.000000
10-04-2025 0:23:00000 | -3089792 | 30.8979 | 30082905 | 234855.63 | 76350914 | 99529373 | 49977436 | 0.000000 | 368135834 | 51539941 | 0.000000
10-04-2025 0:23:05000 | -3097704 | 30.977 | 29483740 | 234821.69 | 76540390 | 99550102 | 49983212 | 0.000000 | 372397797 | 51968979 | 0.000000
10-04-2025 0:23:10000 | -3065417 | 30.6542 | 31268240 | 234922.00 | 75767548 | 99483795 | 49986401 | 0.000000 | 376549835 | 52396929 | 0.000000
10-04-2025 0:23:15000 | -2998543 | 29.9854 | 28560115 | 234841.19 | 74086151 | 99549469 | 49995789 | 0.000000 | 380786774 | 52817349 | 0.000000
10-04-2025 0:23:20000 | -2960536 | 29.6054 | 28843184 | 234873.09 | 73159393 | 99528763 | 50003326 | 0.000000 | 384814392 | 53231108 | 0.000000
10-04-2025 0:23:25000 | -3070198 | 30.702 | 26867776 | 234734.91 | 75837372 | 99619270 | 49974617 | 0.000000 | 388698242 | 53650093 | 0.000000
10-04-2025 0:23:30000 | -3145488 | 31.4549 | 28751531 | 234782.61 | 77704735 | 99584846 | 49950314 | 0.000000 | 392605011 | 54086128 | 0.000000
10-04-2025 0:23:35000 | -3103022 | 31.0302 | 29625774 | 234837.00 | 76673569 | 99547325 | 49959705 | 0.000000 | 396742218 | 54520288 | 0.000000
10-04-2025 0:23:40000 | -3017479 | 30.1748 | 27286299 | 234809.89 | 74532913 | 99593636 | 49966217 | 0.000000 | 400638641 | 54943545 | 0.000000
10-04-2025 0:23:45000 | -2943738 | 29.4374 | 27140598 | 234838.03 | 72713936 | 99577667 | 49974529 | 0.000000 | 404388550 | 55355552 | 0.000000
10-04-2025 0:23:50000 | -2964806 | 29.6481 | 25446040 | 234756.39 | 73219841 | 99633705 | 49958885 | 0.000000 | 408015778 | 55765596 | 0.000000
10-04-2025 0:23:55000 | -3020503 | 30.205 | 28636174 | 234834.80 | 74627419 | 99553596 | 49947784 | 0.000000 | 411822021 | 56182637 | 0.000000
10-04-2025 0:24:00000 | -3053061 | 30.5306 | 26833481 | 234754.80 | 75410347 | 99615990 | 49947899 | 0.000000 | 415676697 | 56604102 | 0.000000
10-04-2025 0:24:05000 | -3100255 | 31.0025 | 27115337 | 234753.13 | 76572693 | 99619705 | 49935520 | 0.000000 | 419444092 | 57032231 | 0.000000
10-04-2025 0:24:10000 | -2913803 | 29.138 | 26488342 | 234856.95 | 71961113 | 99589348 | 49972942 | 0.000000 | 423126587 | 57448950 | 0.000000
10-04-2025 0:24:15000 | -2749437 | 27.4944 | 27749006 | 234902.75 | 67956459 | 99494553 | 50006084 | 0.000000 | 427006042 | 57835269 | 0.000000
10-04-2025 0:24:20000 | -2782403 | 27.824 | 27117476 | 234839.19 | 68765762 | 99528427 | 49998154 | 0.000000 | 430770630 | 58218638 | 0.000000
10-04-2025 0:24:25000 | -2902712 | 29.0271 | 27756624 | 234801.78 | 71734680 | 99545921 | 49988369 | 0.000000 | 434563080 | 58614194 | 0.000000
10-04-2025 0:24:30000 | -3028901 | 30.289 | 26849231 | 234742.27 | 74824318 | 99609421 | 49957432 | 0.000000 | 438168427 | 59029248 | 0.000000
10-04-2025 0:24:35000 | -3084096 | 30.841 | 26359482 | 234738.42 | 76165810 | 99636742 | 49946259 | 0.000000 | 441832825 | 59458164 | 0.000000
10-04-2025 0:24:40000 | -3013637 | 30.1364 | 25489619 | 234739.44 | 74424225 | 99644211 | 49958183 | 0.000000 | 445448822 | 59881499 | 0.000000
10-04-2025 0:24:45000 | -2978196 | 29.782 | 25685193 | 234780.41 | 73543961 | 99630157 | 49961754 | 0.000000 | 448963318 | 60298389 | 0.000000
10-04-2025 0:24:50000 | -2855339 | 28.5534 | 26393716 | 234826.58 | 70539490 | 99575493 | 49987888 | 0.000000 | 452643860 | 60703442 | 0.000000
10-04-2025 0:24:55000 | -2786019 | 27.8602 | 26585000 | 234826.97 | 68844582 | 99547806 | 49998173 | 0.000000 | 456335236 | 61092949 | 0.000000
10-04-2025 0:25:00000 | -2826838 | 28.2684 | 27254563 | 234822.58 | 69863998 | 99538437 | 49985123 | 0.000000 | 460065948 | 61482261 | 0.000000
10-04-2025 0:25:05000 | -2829936 | 28.2994 | 27554023 | 234830.83 | 69948860 | 99529335 | 49979351 | 0.000000 | 463920471 | 61875801 | 0.000000
10-04-2025 0:25:10000 | -2938086 | 29.3809 | 26475220 | 234763.09 | 72586525 | 99596458 | 49959530 | 0.000000 | 467581482 | 62278354 | 0.000000
10-04-2025 0:25:15000 | -3032945 | 30.3295 | 25521716 | 234700.25 | 74909752 | 99647820 | 49939213 | 0.000000 | 471157867 | 62694702 | 0.000000
10-04-2025 0:25:20000 | -3054160 | 30.5416 | 27353853 | 234777.09 | 75440765 | 99601326 | 49948597 | 0.000000 | 474903687 | 63117695 | 0.000000
10-04-2025 0:25:25000 | -3050325 | 30.5033 | 26484407 | 234761.42 | 75335098 | 99625191 | 49946281 | 0.000000 | 478653107 | 63541992 | 0.000000
10-04-2025 0:25:30000 | -3020565 | 30.2056 | 27812583 | 234808.81 | 74621109 | 99578766 | 49947392 | 0.000000 | 482472412 | 63964053 | 0.000000
10-04-2025 0:25:35000 | -3000268 | 30.0027 | 29466565 | 234855.67 | 74149170 | 99521172 | 49956978 | 0.000000 | 486553864 | 64380757 | 0.000000
10-04-2025 0:25:40000 | -3006761 | 30.0676 | 27607441 | 234815.38 | 74273163 | 99581123 | 49955833 | 0.000000 | 490470856 | 64797344 | 0.000000
10-04-2025 0:25:45000 | -3018921 | 30.1892 | 27099177 | 234787.11 | 74571823 | 99599533 | 49954922 | 0.000000 | 494327515 | 65215903 | 0.000000
10-04-2025 0:25:50000 | -2991020 | 29.9102 | 27610234 | 234795.52 | 73895981 | 99576645 | 49957287 | 0.000000 | 498148315 | 65632280 | 0.000000
10-04-2025 0:25:55000 | -2965670 | 29.6567 | 27767891 | 234824.91 | 73269798 | 99564522 | 49954174 | 0.000000 | 501868195 | 66046851 | 0.000000
10-04-2025 0:26:00000 | -2975380 | 29.7538 | 26719155 | 234778.97 | 73498222 | 99599213 | 49956268 | 0.000000 | 505573730 | 66461045 | 0.000000
10-04-2025 0:26:05000 | -2990224 | 29.9022 | 26174458 | 234763.34 | 73854538 | 99619080 | 49957203 | 0.000000 | 509318726 | 66875654 | 0.000000
10-04-2025 0:26:10000 | -2946503 | 29.465 | 27086772 | 234782.52 | 72800934 | 99580116 | 49968109 | 0.000000 | 513153625 | 67288115 | 0.000000
10-04-2025 0:26:15000 | -2935256 | 29.3526 | 26635537 | 234775.02 | 72516388 | 99590805 | 49969330 | 0.000000 | 516911865 | 67693931 | 0.000000
10-04-2025 0:26:20000 | -3032779 | 30.3278 | 26303325 | 234730.92 | 74911751 | 99625999 | 49937126 | 0.000000 | 520514160 | 68109575 | 0.000000
10-04-2025 0:26:25000 | -3073056 | 30.7306 | 26874009 | 234756.73 | 75900520 | 99619797 | 49932854 | 0.000000 | 524274658 | 68536875 | 0.000000
10-04-2025 0:26:30000 | -2987450 | 29.8745 | 25643674 | 234755.34 | 73778381 | 99633614 | 49944378 | 0.000000 | 527883789 | 68959902 | 0.000000
10-04-2025 0:26:35000 | -2943249 | 29.4325 | 24272808 | 234728.20 | 72679253 | 99661667 | 49946030 | 0.000000 | 531327576 | 69369648 | 0.000000
10-04-2025 0:26:40000 | -2881397 | 28.814 | 25363804 | 234786.66 | 71167587 | 99614807 | 49956837 | 0.000000 | 534764099 | 69772285 | 0.000000
10-04-2025 0:26:45000 | -2772556 | 27.7256 | 27347546 | 234816.86 | 68538574 | 99517059 | 49974991 | 0.000000 | 538414368 | 70163315 | 0.000000
10-04-2025 0:26:50000 | -2824396 | 28.244 | 25293020 | 234719.08 | 69789825 | 99601418 | 49978870 | 0.000000 | 542054016 | 70550356 | 0.000000
10-04-2025 0:26:55000 | -2894422 | 28.9442 | 25550186 | 234720.59 | 71509384 | 99612648 | 49973450 | 0.000000 | 545537720 | 70947158 | 0.000000
10-04-2025 0:27:00000 | -2922925 | 29.2293 | 25440378 | 234712.58 | 72209175 | 99623360 | 49969284 | 0.000000 | 549094788 | 71351333 | 0.000000
10-04-2025 0:27:05000 | -2989171 | 29.8917 | 24539036 | 234666.39 | 73828239 | 99664726 | 49951546 | 0.000000 | 552487915 | 71763296 | 0.000000
10-04-2025 0:27:10000 | -3015707 | 30.1571 | 24035618 | 234655.86 | 74472054 | 99683891 | 49948231 | 0.000000 | 555896667 | 72180293 | 0.000000
10-04-2025 0:27:15000 | -3037156 | 30.3716 | 22569836 | 234584.73 | 74992554 | 99725021 | 49955318 | 0.000000 | 559225525 | 72597393 | 0.000000
10-04-2025 0:27:20000 | -3171254 | 31.7125 | 23194895 | 234575.16 | 78290726 | 99733589 | 49905960 | 0.000000 | 562308289 | 73033701 | 0.000000
10-04-2025 0:27:25000 | -3168884 | 31.6888 | 23608069 | 234626.53 | 78228867 | 99723640 | 49906288 | 0.000000 | 565499634 | 73475229 | 0.000000
10-04-2025 0:27:30000 | -3013832 | 30.1383 | 21685046 | 234599.86 | 74404594 | 99742149 | 49930019 | 0.000000 | 568655762 | 73901206 | 0.000000
10-04-2025 0:27:35000 | -2966512 | 29.6651 | 20824255 | 234593.17 | 73223358 | 99754524 | 49922516 | 0.000000 | 571643311 | 74314624 | 0.000000
10-04-2025 0:27:40000 | -3084837 | 30.8484 | 20757524 | 234552.91 | 76143272 | 99774376 | 49897945 | 0.000000 | 574412659 | 74736694 | 0.000000
10-04-2025 0:27:45000 | -3006046 | 30.0605 | 22877275 | 234623.38 | 74223175 | 99711662 | 49910500 | 0.000000 | 577570251 | 75163809 | 0.000000
10-04-2025 0:27:50000 | -2883679 | 28.8368 | 20167875 | 234583.23 | 71186134 | 99756325 | 49928104 | 0.000000 | 580526306 | 75568735 | 0.000000
10-04-2025 0:27:55000 | -2941812 | 29.4181 | 19124978 | 234557.97 | 72601547 | 99789345 | 49908997 | 0.000000 | 583104370 | 75975952 | 0.000000
10-04-2025 0:28:00000 | -2941258 | 29.4126 | 19751582 | 234587.73 | 72587326 | 99775284 | 49912937 | 0.000000 | 585785156 | 76385654 | 0.000000
10-04-2025 0:28:05000 | -2916468 | 29.1647 | 18460352 | 234556.20 | 71970100 | 99800278 | 49927490 | 0.000000 | 588432129 | 76789302 | 0.000000
10-04-2025 0:28:10000 | -2815809 | 28.1581 | 20866448 | 234723.34 | 69491287 | 99726547 | 49940319 | 0.000000 | 590981201 | 77186284 | 0.000000
10-04-2025 0:28:15000 | -2752796 | 27.528 | 19226294 | 234639.91 | 67939369 | 99756989 | 49954300 | 0.000000 | 593720764 | 77570815 | 0.000000
10-04-2025 0:28:20000 | -2731037 | 27.3104 | 18981844 | 234638.28 | 67409950 | 99759331 | 49972416 | 0.000000 | 596371094 | 77952617 | 0.000000
10-04-2025 0:28:25000 | -2748042 | 27.4804 | 18082042 | 234590.66 | 67820038 | 99784218 | 49977356 | 0.000000 | 598808716 | 78332822 | 0.000000
10-04-2025 0:28:30000 | -2894533 | 28.9453 | 18726804 | 234540.03 | 71441788 | 99791367 | 49970013 | 0.000000 | 601378113 | 78727036 | 0.000000
10-04-2025 0:28:35000 | -2921253 | 29.2125 | 19550537 | 234569.13 | 72105080 | 99776802 | 49969151 | 0.000000 | 604241516 | 79130591 | 0.000000
10-04-2025 0:28:40000 | -2970971 | 29.7097 | 21410784 | 234600.66 | 73341629 | 99741325 | 49956791 | 0.000000 | 607161072 | 79538701 | 0.000000
10-04-2025 0:28:45000 | -3090403 | 30.904 | 20825547 | 234546.88 | 76282486 | 99773712 | 49926441 | 0.000000 | 610057922 | 79963091 | 0.000000
10-04-2025 0:28:50000 | -3059697 | 30.597 | 20840239 | 234550.91 | 75528214 | 99768845 | 49933632 | 0.000000 | 613110046 | 80390625 | 0.000000
10-04-2025 0:28:55000 | -2912718 | 29.1272 | 21029722 | 234598.13 | 71911949 | 99740372 | 49958408 | 0.000000 | 615963379 | 80803955 | 0.000000
10-04-2025 0:29:00000 | -2833033 | 28.3303 | 18761128 | 234524.23 | 69938698 | 99781448 | 49970264 | 0.000000 | 618725525 | 81199297 | 0.000000
10-04-2025 0:29:05000 | -2876935 | 28.7693 | 19574482 | 234499.22 | 71036148 | 99769333 | 49948505 | 0.000000 | 621415710 | 81596284 | 0.000000
10-04-2025 0:29:10000 | -2940052 | 29.4005 | 19796429 | 234532.61 | 72587418 | 99774078 | 49938927 | 0.000000 | 624283203 | 81999902 | 0.000000
10-04-2025 0:29:15000 | -2982780 | 29.8278 | 22509824 | 234609.08 | 73652382 | 99716454 | 49941647 | 0.000000 | 627361023 | 82412617 | 0.000000
10-04-2025 0:29:20000 | -2969689 | 29.6969 | 21700886 | 234590.64 | 73321564 | 99734070 | 49939754 | 0.000000 | 630402832 | 82824307 | 0.000000
10-04-2025 0:29:25000 | -2952796 | 29.528 | 21137803 | 234623.70 | 72879822 | 99744759 | 49937305 | 0.000000 | 633236877 | 83236504 | 0.000000
10-04-2025 0:29:30000 | -2903069 | 29.0307 | 22747729 | 234654.91 | 71680618 | 99694412 | 49959625 | 0.000000 | 636266846 | 83641289 | 0.000000
10-04-2025 0:29:35000 | -2878412 | 28.7841 | 19443425 | 234582.16 | 71046394 | 99772636 | 49958389 | 0.000000 | 639044739 | 84040947 | 0.000000
10-04-2025 0:29:40000 | -2863800 | 28.638 | 21434241 | 234629.72 | 70701294 | 99721077 | 49962200 | 0.000000 | 641928406 | 84436973 | 0.000000
10-04-2025 0:29:45000 | -2847980 | 28.4798 | 21310347 | 234646.80 | 70314026 | 99721222 | 49959351 | 0.000000 | 644850464 | 84832637 | 0.000000
10-04-2025 0:29:50000 | -2841045 | 28.4105 | 20019081 | 234604.39 | 70140228 | 99752663 | 49953545 | 0.000000 | 647744446 | 85226289 | 0.000000
10-04-2025 0:29:55000 | -2928739 | 29.2874 | 23178501 | 234641.05 | 72334007 | 99688293 | 49942013 | 0.000000 | 650703796 | 85627402 | 0.000000
10-04-2025 0:30:00000 | -2990126 | 29.9013 | 23008542 | 234635.95 | 73824280 | 99705254 | 49932835 | 0.000000 | 653820740 | 86040488 | 0.000000
10-04-2025 0:30:05000 | -2886400 | 28.864 | 23388206 | 234657.17 | 71286629 | 99673325 | 49957199 | 0.000000 | 3341681 | 40799557 | 0.000000
10-04-2025 0:30:10000 | -2888734 | 28.8873 | 20817371 | 234570.45 | 71321075 | 99741348 | 49952042 | 0.000000 | 6365078 | 80925240 | 0.000000
10-04-2025 0:30:15000 | -2911671 | 29.1167 | 23936121 | 234687.64 | 71918556 | 99663803 | 49951958 | 0.000000 | 9413388 | 121367699 | 0.000000
10-04-2025 0:30:20000 | -2857663 | 28.5766 | 22817046 | 234650.64 | 70574577 | 99682755 | 49967609 | 0.000000 | 12544895 | 161380081 | 0.000000
10-04-2025 0:30:25000 | -2801201 | 28.012 | 21173845 | 234603.19 | 69171234 | 99715538 | 49972328 | 0.000000 | 15587529 | 200289703 | 0.000000
10-04-2025 0:30:30000 | -2958275 | 29.5828 | 22697512 | 234536.84 | 73075813 | 99706955 | 49943630 | 0.000000 | 18641722 | 240698669 | 0.000000
10-04-2025 0:30:35000 | -3028463 | 30.2846 | 24686658 | 234595.91 | 74821922 | 99669411 | 49937023 | 0.000000 | 22013742 | 282386139 | 0.000000
10-04-2025 0:30:40000 | -2951388 | 29.5139 | 25076101 | 234703.66 | 72898972 | 99640999 | 49965302 | 0.000000 | 25544994 | 323878937 | 0.000000
10-04-2025 0:30:45000 | -2783670 | 27.8367 | 21593867 | 234663.84 | 68746826 | 99700470 | 49995308 | 0.000000 | 28792337 | 363223267 | 0.000000
10-04-2025 0:30:50000 | -2828133 | 28.2813 | 23435759 | 234688.91 | 69850830 | 99658417 | 49994442 | 0.000000 | 31944016 | 402139313 | 0.000000
10-04-2025 0:30:55000 | -3022501 | 30.225 | 21725784 | 234566.61 | 74619919 | 99742661 | 49951668 | 0.000000 | 34975067 | 442991211 | 0.000000
10-04-2025 0:31:00000 | -3111908 | 31.1191 | 22541245 | 234556.28 | 76832489 | 99738686 | 49931950 | 0.000000 | 38112831 | 485586121 | 0.000000
10-04-2025 0:31:05000 | -3162995 | 31.63 | 25571011 | 234684.05 | 78106163 | 99674805 | 49922848 | 0.000000 | 41313488 | 529511292 | 0.000000
10-04-2025 0:31:10000 | -2985794 | 29.8579 | 24381233 | 234604.50 | 73760460 | 99668259 | 49949604 | 0.000000 | 45007607 | 572023438 | 0.000000
10-04-2025 0:31:15000 | -2830450 | 28.3045 | 26684211 | 234755.52 | 69970154 | 99558548 | 49967430 | 0.000000 | 48433041 | 612550842 | 0.000000
10-04-2025 0:31:20000 | -2892710 | 28.9271 | 20934216 | 234517.84 | 71438049 | 99739159 | 49944839 | 0.000000 | 51489532 | 652341736 | 0.000000
10-04-2025 0:31:25000 | -3025756 | 30.2576 | 23830730 | 234543.17 | 74754669 | 99691284 | 49924519 | 0.000000 | 54645561 | 693725647 | 0.000000
10-04-2025 0:31:30000 | -2982383 | 29.8238 | 24739822 | 234595.66 | 73700645 | 99657707 | 49942165 | 0.000000 | 58084957 | 735567322 | 0.000000
10-04-2025 0:31:35000 | -2824821 | 28.2482 | 20704932 | 234530.88 | 69777718 | 99732460 | 49971214 | 0.000000 | 61328190 | 775314758 | 0.000000
10-04-2025 0:31:40000 | -2837293 | 28.3729 | 22168767 | 234572.11 | 70087402 | 99696152 | 49966610 | 0.000000 | 64306229 | 814320984 | 0.000000
10-04-2025 0:31:45000 | -2838213 | 28.3821 | 23058699 | 234590.69 | 70122528 | 99671600 | 49985180 | 0.000000 | 67523621 | 853551208 | 0.000000
10-04-2025 0:31:50000 | -2893668 | 28.9367 | 22611465 | 234532.17 | 71495483 | 99696091 | 49984188 | 0.000000 | 70802460 | 892922546 | 0.000000
10-04-2025 0:31:55000 | -2973542 | 29.7354 | 22759128 | 234548.45 | 73447296 | 99708374 | 49969353 | 0.000000 | 73899117 | 933610229 | 0.000000
10-04-2025 0:32:00000 | -3058052 | 30.5805 | 24343301 | 234551.53 | 75557289 | 99684662 | 49954742 | 0.000000 | 77154472 | 975970032 | 0.000000
10-04-2025 0:32:05000 | -2979929 | 29.7993 | 25785049 | 234628.97 | 73638550 | 99627724 | 49976391 | 0.000000 | 80660324 | 10178077 | 0.000000
10-04-2025 0:32:10000 | -2895880 | 28.9588 | 27180417 | 234712.19 | 71581833 | 99562416 | 49987186 | 0.000000 | 84201385 | 10587271 | 0.000000
10-04-2025 0:32:15000 | -2874342 | 28.7434 | 23988157 | 234597.66 | 71025215 | 99653564 | 49991211 | 0.000000 | 87675240 | 10986244 | 0.000000
10-04-2025 0:32:20000 | -2870577 | 28.7058 | 25231816 | 234629.19 | 70946426 | 99615921 | 49992496 | 0.000000 | 91189911 | 11382803 | 0.000000
10-04-2025 0:32:25000 | -2937322 | 29.3732 | 24600042 | 234589.45 | 72586624 | 99651131 | 49971581 | 0.000000 | 94434593 | 11786215 | 0.000000
10-04-2025 0:32:30000 | -3020126 | 30.2013 | 22620938 | 234528.13 | 74596092 | 99720673 | 49953194 | 0.000000 | 97552185 | 12202133 | 0.000000
10-04-2025 0:32:35000 | -2949739 | 29.4974 | 24272917 | 234584.11 | 72894569 | 99663139 | 49978210 | 0.000000 | 100935234 | 12617861 | 0.000000
10-04-2025 0:32:40000 | -2837909 | 28.3791 | 24998406 | 234617.03 | 70147964 | 99614273 | 50003632 | 0.000000 | 104466255 | 13017915 | 0.000000
10-04-2025 0:32:45000 | -2794035 | 27.9403 | 24620007 | 234600.63 | 69071983 | 99614021 | 50003300 | 0.000000 | 107813820 | 13408434 | 0.000000
10-04-2025 0:32:50000 | -2761918 | 27.6192 | 25085796 | 234618.80 | 68287476 | 99590050 | 50012520 | 0.000000 | 111371391 | 13794042 | 0.000000
10-04-2025 0:32:55000 | -2835768 | 28.3577 | 25858093 | 234618.83 | 70111824 | 99586838 | 50008457 | 0.000000 | 114904686 | 14182413 | 0.000000
10-04-2025 0:33:00000 | -2913586 | 29.1359 | 25088938 | 234553.23 | 72026764 | 99631302 | 50010258 | 0.000000 | 118404091 | 14581855 | 0.000000
10-04-2025 0:33:05000 | -3037711 | 30.3771 | 26307100 | 234558.75 | 75090187 | 99627106 | 49982494 | 0.000000 | 121882561 | 14998818 | 0.000000
10-04-2025 0:33:10000 | -2983659 | 29.8366 | 28873362 | 234715.16 | 73770638 | 99535027 | 50004303 | 0.000000 | 125693398 | 15420601 | 0.000000
10-04-2025 0:33:15000 | -2863477 | 28.6348 | 25594902 | 234619.88 | 70786346 | 99602905 | 50033295 | 0.000000 | 129422333 | 15823534 | 0.000000
10-04-2025 0:33:20000 | -2884300 | 28.843 | 24105647 | 234573.20 | 71280502 | 99652580 | 50015850 | 0.000000 | 132931580 | 16220281 | 0.000000
10-04-2025 0:33:25000 | -2978079 | 29.7808 | 23582720 | 234509.33 | 73595032 | 99687935 | 49996750 | 0.000000 | 136461075 | 16625962 | 0.000000
10-04-2025 0:33:30000 | -2960662 | 29.6066 | 25770718 | 234599.98 | 73174080 | 99623306 | 50007465 | 0.000000 | 139956543 | 17040249 | 0.000000
10-04-2025 0:33:35000 | -2966029 | 29.6603 | 25539458 | 234595.16 | 73306969 | 99631332 | 50007801 | 0.000000 | 143501541 | 17450868 | 0.000000
10-04-2025 0:33:40000 | -2972782 | 29.7278 | 26316199 | 234619.66 | 73474960 | 99610466 | 49995781 | 0.000000 | 147151108 | 17863411 | 0.000000
10-04-2025 0:33:45000 | -2929627 | 29.2963 | 25992900 | 234623.69 | 72411263 | 99608711 | 50014694 | 0.000000 | 150768845 | 18273872 | 0.000000
10-04-2025 0:33:50000 | -2954705 | 29.547 | 25455117 | 234508.14 | 73048874 | 99630951 | 50007927 | 0.000000 | 154301590 | 18682062 | 0.000000
10-04-2025 0:33:55000 | -3050356 | 30.5036 | 25580793 | 234516.72 | 75395485 | 99650208 | 49979160 | 0.000000 | 157810135 | 19101001 | 0.000000
10-04-2025 0:34:00000 | -2970479 | 29.7048 | 28188296 | 234633.61 | 73466240 | 99552765 | 49994488 | 0.000000 | 161535553 | 19524574 | 0.000000
10-04-2025 0:34:05000 | -2821211 | 28.2121 | 26145171 | 234594.78 | 69769226 | 99573326 | 50032555 | 0.000000 | 165145966 | 19925569 | 0.000000
10-04-2025 0:34:10000 | -2747265 | 27.4727 | 26622146 | 234618.89 | 67962082 | 99533760 | 50049034 | 0.000000 | 168780029 | 20309314 | 0.000000
10-04-2025 0:34:15000 | -2797513 | 27.9751 | 26049036 | 234769.61 | 69132446 | 99569283 | 50043335 | 0.000000 | 172558655 | 20693413 | 0.000000
10-04-2025 0:34:20000 | -2909406 | 29.0941 | 27615815 | 234794.48 | 71903770 | 99552536 | 50029934 | 0.000000 | 176303879 | 21094102 | 0.000000
10-04-2025 0:34:25000 | -2903998 | 29.04 | 27119033 | 234786.77 | 71761787 | 99566795 | 50037785 | 0.000000 | 180150696 | 21498071 | 0.000000
10-04-2025 0:34:30000 | -2890703 | 28.907 | 27102444 | 234797.19 | 71431519 | 99563354 | 50041397 | 0.000000 | 183880310 | 21901394 | 0.000000
10-04-2025 0:34:35000 | -2861522 | 28.6152 | 27942517 | 234821.64 | 70733681 | 99526619 | 50046253 | 0.000000 | 187744492 | 22303008 | 0.000000
10-04-2025 0:34:40000 | -2872432 | 28.7243 | 26977854 | 234790.11 | 70984741 | 99561852 | 50045685 | 0.000000 | 191609375 | 22703545 | 0.000000
10-04-2025 0:34:45000 | -2909847 | 29.0985 | 26027488 | 234718.83 | 71904076 | 99602356 | 50033131 | 0.000000 | 195298950 | 23104534 | 0.000000
10-04-2025 0:34:50000 | -2886452 | 28.8645 | 27529854 | 234786.23 | 71345039 | 99548248 | 50049431 | 0.000000 | 199245987 | 23503918 | 0.000000
10-04-2025 0:34:55000 | -2955291 | 29.5529 | 26413657 | 234728.14 | 73016617 | 99602959 | 50028763 | 0.000000 | 202993362 | 23906919 | 0.000000
10-04-2025 0:35:00000 | -2995473 | 29.9547 | 27530203 | 234778.17 | 74009689 | 99580322 | 50023975 | 0.000000 | 206835327 | 24321545 | 0.000000
10-04-2025 0:35:05000 | -2902008 | 29.0201 | 27508469 | 234794.59 | 71717339 | 99553734 | 50048508 | 0.000000 | 210691071 | 24730630 | 0.000000
10-04-2025 0:35:10000 | -2773174 | 27.7317 | 25677192 | 234807.39 | 68524117 | 99574081 | 50064487 | 0.000000 | 214412735 | 25122310 | 0.000000
10-04-2025 0:35:15000 | -2868423 | 28.6842 | 26939773 | 234793.50 | 70881165 | 99561867 | 50059227 | 0.000000 | 218106979 | 25513342 | 0.000000
10-04-2025 0:35:20000 | -2984260 | 29.8426 | 27511135 | 234743.02 | 73746841 | 99577766 | 50039463 | 0.000000 | 221920273 | 25920757 | 0.000000
10-04-2025 0:35:25000 | -3001169 | 30.0117 | 28539570 | 234803.75 | 74166245 | 99550896 | 50038380 | 0.000000 | 225783203 | 26338760 | 0.000000
10-04-2025 0:35:30000 | -2923415 | 29.2341 | 27638958 | 234791.81 | 72241707 | 99556053 | 50055317 | 0.000000 | 229737915 | 26750105 | 0.000000
10-04-2025 0:35:35000 | -2857031 | 28.5703 | 26580452 | 234795.53 | 70595642 | 99570015 | 50071896 | 0.000000 | 233573914 | 27150347 | 0.000000
10-04-2025 0:35:40000 | -2853985 | 28.5399 | 26433018 | 234785.11 | 70519508 | 99573837 | 50066830 | 0.000000 | 237206161 | 27545708 | 0.000000
10-04-2025 0:35:45000 | -2852963 | 28.5296 | 27538528 | 234789.09 | 70517776 | 99537369 | 50061531 | 0.000000 | 240976242 | 27941858 | 0.000000
10-04-2025 0:35:50000 | -2899980 | 28.9998 | 27389675 | 234761.42 | 71674355 | 99556946 | 50054859 | 0.000000 | 244834152 | 28342209 | 0.000000
10-04-2025 0:35:55000 | -2980229 | 29.8023 | 27107546 | 234741.14 | 73639511 | 99588882 | 50043026 | 0.000000 | 248641464 | 28752268 | 0.000000
10-04-2025 0:36:00000 | -2976019 | 29.7602 | 29395603 | 234824.73 | 73558212 | 99515717 | 50045635 | 0.000000 | 252489304 | 29169824 | 0.000000
10-04-2025 0:36:05000 | -2941398 | 29.414 | 26863862 | 234773.73 | 72669106 | 99585533 | 50050434 | 0.000000 | 256308044 | 29580608 | 0.000000
10-04-2025 0:36:10000 | -2950860 | 29.5086 | 26481985 | 234747.20 | 72900978 | 99599724 | 50044243 | 0.000000 | 259954834 | 29990566 | 0.000000
10-04-2025 0:36:15000 | -2984401 | 29.844 | 27784167 | 234774.16 | 73742310 | 99569435 | 50045380 | 0.000000 | 263804749 | 30403953 | 0.000000
10-04-2025 0:36:20000 | -2843930 | 28.4393 | 33222065 | 235007.05 | 70382889 | 99324593 | 50073936 | 0.000000 | 267902679 | 30813955 | 0.000000
10-04-2025 0:36:25000 | -2606337 | 26.0634 | 30937234 | 234989.50 | 64523140 | 99302872 | 50136593 | 0.000000 | 272323578 | 31185767 | 0.000000
10-04-2025 0:36:30000 | -2563035 | 25.6303 | 31376467 | 234936.02 | 63496128 | 99258995 | 50138447 | 0.000000 | 276704102 | 31542498 | 0.000000
10-04-2025 0:36:35000 | -2764818 | 27.6482 | 33260920 | 234926.55 | 68473839 | 99284149 | 50109909 | 0.000000 | 281203217 | 31915217 | 0.000000
10-04-2025 0:36:40000 | -2860432 | 28.6043 | 33919592 | 234930.81 | 70825905 | 99304245 | 50104050 | 0.000000 | 285888855 | 32306355 | 0.000000
10-04-2025 0:36:45000 | -2897288 | 28.9729 | 36677104 | 234992.80 | 71793747 | 99208237 | 50112537 | 0.000000 | 290808167 | 32708591 | 0.000000
10-04-2025 0:36:50000 | -2860325 | 28.6032 | 36994780 | 235030.86 | 70883705 | 99173935 | 50119209 | 0.000000 | 295796417 | 33108447 | 0.000000
10-04-2025 0:36:55000 | -2884179 | 28.8418 | 35304854 | 234943.84 | 71445770 | 99259125 | 50116760 | 0.000000 | 300821289 | 33506140 | 0.000000
10-04-2025 0:37:00000 | -2966591 | 29.6659 | 34601536 | 234927.00 | 73434471 | 99326653 | 50097507 | 0.000000 | 305610931 | 33911533 | 0.000000
10-04-2025 0:37:05000 | -2957825 | 29.5783 | 36631907 | 234975.67 | 73264595 | 99241798 | 50100029 | 0.000000 | 310641449 | 34323623 | 0.000000
10-04-2025 0:37:10000 | -2960143 | 29.6014 | 34330034 | 234936.47 | 73266251 | 99334206 | 50101906 | 0.000000 | 315514618 | 34733828 | 0.000000
10-04-2025 0:37:15000 | -2914394 | 29.1439 | 34636633 | 234949.36 | 72158745 | 99301163 | 50104595 | 0.000000 | 320380585 | 35141509 | 0.000000
10-04-2025 0:37:20000 | -2948185 | 29.4819 | 32501038 | 234845.64 | 72949562 | 99397835 | 50111694 | 0.000000 | 325162537 | 35547161 | 0.000000
10-04-2025 0:37:25000 | -3101050 | 31.0105 | 31566482 | 234813.33 | 76675774 | 99485901 | 50064388 | 0.000000 | 329438202 | 35969019 | 0.000000
10-04-2025 0:37:30000 | -3120590 | 31.2059 | 32436206 | 234828.53 | 77173309 | 99464134 | 50063782 | 0.000000 | 334001404 | 36403472 | 0.000000
10-04-2025 0:37:35000 | -3035227 | 30.3523 | 30308560 | 234806.81 | 75036964 | 99505135 | 50069950 | 0.000000 | 338320160 | 36830911 | 0.000000
10-04-2025 0:37:40000 | -2960750 | 29.6075 | 28904578 | 234807.27 | 73183083 | 99526840 | 50069004 | 0.000000 | 342364655 | 37244539 | 0.000000
10-04-2025 0:37:45000 | -2869055 | 28.6906 | 30191997 | 234902.20 | 70941132 | 99450851 | 50095661 | 0.000000 | 346421631 | 37650261 | 0.000000
10-04-2025 0:37:50000 | -2818905 | 28.1891 | 27738364 | 234796.39 | 69696335 | 99519348 | 50100368 | 0.000000 | 350398163 | 38044846 | 0.000000
10-04-2025 0:37:55000 | -2881006 | 28.8101 | 28668552 | 234810.63 | 71222839 | 99508545 | 50095772 | 0.000000 | 354371918 | 38441108 | 0.000000
10-04-2025 0:38:00000 | -2930253 | 29.3025 | 29733728 | 234801.05 | 72461220 | 99489120 | 50084625 | 0.000000 | 358543671 | 38848259 | 0.000000
10-04-2025 0:38:05000 | -3015177 | 30.1518 | 30669744 | 234805.50 | 74557938 | 99486656 | 50078045 | 0.000000 | 362768585 | 39261157 | 0.000000
10-04-2025 0:38:10000 | -3076213 | 30.7621 | 31832488 | 234849.56 | 76068031 | 99468864 | 50064720 | 0.000000 | 367067017 | 39687302 | 0.000000
10-04-2025 0:38:15000 | -2940537 | 29.4054 | 29604219 | 234834.75 | 72696945 | 99497032 | 50080421 | 0.000000 | 371316193 | 40100798 | 0.000000
10-04-2025 0:38:20000 | -2886358 | 28.8636 | 29534126 | 234853.50 | 71366646 | 99480576 | 50094788 | 0.000000 | 375404694 | 40503533 | 0.000000
10-04-2025 0:38:25000 | -2873088 | 28.7309 | 30492605 | 234866.84 | 71058434 | 99441513 | 50084290 | 0.000000 | 379400757 | 40906089 | 0.000000
10-04-2025 0:38:30000 | -2942880 | 29.4288 | 29475308 | 234797.06 | 72761421 | 99502159 | 50071239 | 0.000000 | 383417999 | 41312070 | 0.000000
10-04-2025 0:38:35000 | -2986147 | 29.8615 | 29285215 | 234768.86 | 73825768 | 99522552 | 50071011 | 0.000000 | 387476440 | 41726338 | 0.000000
10-04-2025 0:38:40000 | -2919107 | 29.1911 | 28712332 | 234792.53 | 72169556 | 99519745 | 50085712 | 0.000000 | 391470642 | 42133438 | 0.000000
10-04-2025 0:38:45000 | -2843569 | 28.4357 | 27693352 | 234821.42 | 70284149 | 99529114 | 50102547 | 0.000000 | 395317108 | 42532231 | 0.000000
10-04-2025 0:38:50000 | -2759955 | 27.5996 | 27161733 | 234805.25 | 68229851 | 99519226 | 50121361 | 0.000000 | 399233795 | 42916919 | 0.000000
10-04-2025 0:38:55000 | -2865620 | 28.6562 | 27435488 | 234762.69 | 70836983 | 99544815 | 50104824 | 0.000000 | 402990997 | 43308408 | 0.000000
10-04-2025 0:39:00000 | -2974763 | 29.7476 | 28184163 | 234758.73 | 73520943 | 99554176 | 50092396 | 0.000000 | 406880981 | 43714785 | 0.000000
10-04-2025 0:39:05000 | -3063752 | 30.6375 | 31192271 | 234838.69 | 75743118 | 99485725 | 50078873 | 0.000000 | 410896423 | 44138755 | 0.000000
10-04-2025 0:39:10000 | -3080946 | 30.8095 | 29405977 | 234750.61 | 76151405 | 99547607 | 50072151 | 0.000000 | 415075256 | 44565811 | 0.000000
10-04-2025 0:39:15000 | -3066666 | 30.6667 | 30325911 | 234813.39 | 75804840 | 99514610 | 50079586 | 0.000000 | 419151642 | 44995000 | 0.000000
10-04-2025 0:39:20000 | -2866703 | 28.667 | 28429875 | 234810.45 | 70872002 | 99511833 | 50111561 | 0.000000 | 423228516 | 45402749 | 0.000000
10-04-2025 0:39:25000 | -2763711 | 27.6371 | 28823350 | 234864.78 | 68344322 | 99460556 | 50128735 | 0.000000 | 427097412 | 45791724 | 0.000000
10-04-2025 0:39:30000 | -2821481 | 28.2148 | 27057395 | 234773.95 | 69745346 | 99543327 | 50115456 | 0.000000 | 430929626 | 46175483 | 0.000000
10-04-2025 0:39:35000 | -3023584 | 30.2358 | 29671172 | 234736.17 | 74768883 | 99521950 | 50082268 | 0.000000 | 434997894 | 46586099 | 0.000000
10-04-2025 0:39:40000 | -3125986 | 31.2599 | 29419983 | 234713.44 | 77272362 | 99560043 | 50061878 | 0.000000 | 439104584 | 47015601 | 0.000000
10-04-2025 0:39:45000 | -3046187 | 30.4619 | 30187395 | 234786.31 | 75305443 | 99512558 | 50076485 | 0.000000 | 443349670 | 47445303 | 0.000000
10-04-2025 0:39:50000 | -2935759 | 29.3576 | 26044626 | 234725.20 | 72527138 | 99608788 | 50085121 | 0.000000 | 447160217 | 47858750 | 0.000000
10-04-2025 0:39:55000 | -2923714 | 29.2371 | 25564270 | 234715.64 | 72227753 | 99619911 | 50089401 | 0.000000 | 450812195 | 48263311 | 0.000000
10-04-2025 0:40:00000 | -2882843 | 28.8284 | 25989272 | 234727.39 | 71232956 | 99596092 | 50088810 | 0.000000 | 454556488 | 48664917 | 0.000000
10-04-2025 0:40:05000 | -2832362 | 28.3236 | 29024106 | 234846.53 | 70030746 | 99479065 | 50103630 | 0.000000 | 458392822 | 49061968 | 0.000000
10-04-2025 0:40:10000 | -2829030 | 28.2903 | 27415303 | 234767.36 | 69935913 | 99533730 | 50098068 | 0.000000 | 462243225 | 49455308 | 0.000000
10-04-2025 0:40:15000 | -2941625 | 29.4163 | 27079856 | 234728.08 | 72698303 | 99578949 | 50076061 | 0.000000 | 466024750 | 49857715 | 0.000000
10-04-2025 0:40:20000 | -3047782 | 30.4778 | 27791152 | 234706.44 | 75315628 | 99586838 | 50062077 | 0.000000 | 469807007 | 50276226 | 0.000000
10-04-2025 0:40:25000 | -2960757 | 29.6076 | 27241484 | 234753.11 | 73160988 | 99579391 | 50078007 | 0.000000 | 473594055 | 50694287 | 0.000000
10-04-2025 0:40:30000 | -2927191 | 29.2719 | 25582668 | 234684.23 | 72326973 | 99620262 | 50091972 | 0.000000 | 477316925 | 51100376 | 0.000000
10-04-2025 0:40:35000 | -2941606 | 29.4161 | 26743084 | 234754.33 | 72686661 | 99589287 | 50076138 | 0.000000 | 480885193 | 51508472 | 0.000000
10-04-2025 0:40:40000 | -2833835 | 28.3383 | 27821396 | 234787.20 | 70061150 | 99521530 | 50108852 | 0.000000 | 484720886 | 51910464 | 0.000000
10-04-2025 0:40:45000 | -2737702 | 27.377 | 25195513 | 234725.91 | 67661804 | 99579178 | 50132557 | 0.000000 | 488335876 | 52293711 | 0.000000
10-04-2025 0:40:50000 | -2937501 | 29.375 | 25782581 | 234682.53 | 72596092 | 99617027 | 50095665 | 0.000000 | 491775543 | 52688311 | 0.000000
10-04-2025 0:40:55000 | -3046968 | 30.4697 | 26513530 | 234662.64 | 75282906 | 99623543 | 50070797 | 0.000000 | 495379364 | 53107471 | 0.000000
10-04-2025 0:41:00000 | -3085633 | 30.8563 | 27234678 | 234700.59 | 76241211 | 99612747 | 50072224 | 0.000000 | 499180176 | 53533115 | 0.000000
10-04-2025 0:41:05000 | -3049542 | 30.4954 | 26881140 | 234719.55 | 75336464 | 99613747 | 50073235 | 0.000000 | 502844604 | 53960664 | 0.000000
10-04-2025 0:41:10000 | -2909937 | 29.0994 | 25799312 | 234729.61 | 71892181 | 99609276 | 50088287 | 0.000000 | 506451233 | 54371670 | 0.000000
10-04-2025 0:41:15000 | -2957049 | 29.5705 | 23704888 | 234648.78 | 73026306 | 99680229 | 50079403 | 0.000000 | 509785950 | 54778960 | 0.000000
10-04-2025 0:41:20000 | -3012739 | 30.1274 | 24906736 | 234665.06 | 74411148 | 99660011 | 50060829 | 0.000000 | 513210938 | 55194878 | 0.000000
10-04-2025 0:41:25000 | -2969338 | 29.6934 | 26790630 | 234749.91 | 73363586 | 99595444 | 50078560 | 0.000000 | 516838806 | 55610278 | 0.000000
10-04-2025 0:41:30000 | -2915691 | 29.1569 | 26126770 | 234706.20 | 72049545 | 99600929 | 50092346 | 0.000000 | 520528259 | 56017173 | 0.000000
10-04-2025 0:41:35000 | -2938525 | 29.3852 | 24537185 | 234654.97 | 72587456 | 99653183 | 50071247 | 0.000000 | 523989624 | 56424561 | 0.000000
10-04-2025 0:41:40000 | -2961583 | 29.6158 | 26110493 | 234692.78 | 73173264 | 99613609 | 50073780 | 0.000000 | 527567871 | 56837085 | 0.000000
10-04-2025 0:41:45000 | -2967137 | 29.6714 | 25983779 | 234690.63 | 73308914 | 99618752 | 50077599 | 0.000000 | 531201172 | 57252720 | 0.000000
10-04-2025 0:41:50000 | -2874312 | 28.7431 | 25764185 | 234716.28 | 71020004 | 99600677 | 50095924 | 0.000000 | 534857849 | 57655073 | 0.000000
10-04-2025 0:41:55000 | -2903528 | 29.0353 | 24382664 | 234646.70 | 71738289 | 99649254 | 50084648 | 0.000000 | 538335022 | 58056025 | 0.000000
10-04-2025 0:42:00000 | -2840027 | 28.4003 | 27259053 | 234744.86 | 70208397 | 99542534 | 50102757 | 0.000000 | 542126770 | 58454551 | 0.000000
10-04-2025 0:42:05000 | -2798431 | 27.9843 | 27477271 | 234766.86 | 69191277 | 99521416 | 50115612 | 0.000000 | 546007751 | 58842554 | 0.000000
10-04-2025 0:42:10000 | -2924182 | 29.2418 | 27208623 | 234747.41 | 72266197 | 99569901 | 50099380 | 0.000000 | 549777100 | 59235483 | 0.000000
10-04-2025 0:42:15000 | -3114653 | 31.1465 | 29418291 | 234739.58 | 76980240 | 99556908 | 50058414 | 0.000000 | 553766174 | 59659146 | 0.000000
10-04-2025 0:42:20000 | -3090017 | 30.9002 | 30446685 | 234796.23 | 76386528 | 99518074 | 50064526 | 0.000000 | 558044739 | 60091934 | 0.000000
10-04-2025 0:42:25000 | -2948574 | 29.4857 | 27436355 | 234782.09 | 72856522 | 99569878 | 50092899 | 0.000000 | 562115601 | 60506831 | 0.000000
10-04-2025 0:42:30000 | -2871299 | 28.713 | 27232498 | 234781.66 | 70963005 | 99553246 | 50102482 | 0.000000 | 566005310 | 60908896 | 0.000000
10-04-2025 0:42:35000 | -2834261 | 28.3426 | 27245151 | 234794.08 | 70051041 | 99541145 | 50102715 | 0.000000 | 569836487 | 61303618 | 0.000000
10-04-2025 0:42:40000 | -2772379 | 27.7238 | 28330552 | 234824.83 | 68561478 | 99481926 | 50118855 | 0.000000 | 573762268 | 61691548 | 0.000000
10-04-2025 0:42:45000 | -2856541 | 28.5654 | 29699355 | 234856.44 | 70636559 | 99463860 | 50111637 | 0.000000 | 577756531 | 62083491 | 0.000000
10-04-2025 0:42:50000 | -2939838 | 29.3984 | 29970127 | 234816.84 | 72689064 | 99484375 | 50098534 | 0.000000 | 581864990 | 62485586 | 0.000000
10-04-2025 0:42:55000 | -3039969 | 30.3997 | 31502310 | 234842.67 | 75170273 | 99467354 | 50082642 | 0.000000 | 586084778 | 62902861 | 0.000000
10-04-2025 0:43:00000 | -3016707 | 30.1671 | 32079136 | 234883.05 | 74602493 | 99439362 | 50080803 | 0.000000 | 590491333 | 63324365 | 0.000000
10-04-2025 0:43:05000 | -3050350 | 30.5035 | 30951897 | 234833.02 | 75413078 | 99489136 | 50084381 | 0.000000 | 594826965 | 63746323 | 0.000000
10-04-2025 0:43:10000 | -3001278 | 30.0128 | 30960483 | 234884.03 | 74197807 | 99472137 | 50083656 | 0.000000 | 599070984 | 64170693 | 0.000000
10-04-2025 0:43:15000 | -2890680 | 28.9068 | 29436931 | 234845.52 | 71475922 | 99485489 | 50105949 | 0.000000 | 603280090 | 64576958 | 0.000000
10-04-2025 0:43:20000 | -2767388 | 27.6739 | 30122542 | 234905.13 | 68451744 | 99412819 | 50125568 | 0.000000 | 607382690 | 64970049 | 0.000000
10-04-2025 0:43:25000 | -2881549 | 28.8155 | 28918911 | 234827.45 | 71243484 | 99500175 | 50110737 | 0.000000 | 611417664 | 65361479 | 0.000000
10-04-2025 0:43:30000 | -2954051 | 29.5405 | 31500444 | 234898.89 | 73057091 | 99436256 | 50090000 | 0.000000 | 615574036 | 65772441 | 0.000000
10-04-2025 0:43:35000 | -2872275 | 28.7228 | 32287715 | 234934.03 | 71071533 | 99374107 | 50119209 | 0.000000 | 620073242 | 66179165 | 0.000000
10-04-2025 0:43:40000 | -2822546 | 28.2255 | 28794282 | 234849.77 | 69785187 | 99483673 | 50129635 | 0.000000 | 624264282 | 66572861 | 0.000000
10-04-2025 0:43:45000 | -2873158 | 28.7316 | 31724846 | 234899.36 | 71083008 | 99395912 | 50128426 | 0.000000 | 628445007 | 66968560 | 0.000000
10-04-2025 0:43:50000 | -2943811 | 29.4381 | 32190244 | 234886.08 | 72831429 | 99407448 | 50126518 | 0.000000 | 632934326 | 67372129 | 0.000000
10-04-2025 0:43:55000 | -3030772 | 30.3077 | 30692087 | 234804.20 | 74939262 | 99491150 | 50098324 | 0.000000 | 637325012 | 67785488 | 0.000000
10-04-2025 0:44:00000 | -3115513 | 31.1551 | 32296479 | 234875.02 | 77025665 | 99466988 | 50088108 | 0.000000 | 641767273 | 68213179 | 0.000000
10-04-2025 0:44:05000 | -3027630 | 30.2763 | 31322407 | 234868.63 | 74855057 | 99469109 | 50092304 | 0.000000 | 646245361 | 68642021 | 0.000000
10-04-2025 0:44:10000 | -2953625 | 29.5362 | 30625835 | 234881.38 | 73029411 | 99466728 | 50108086 | 0.000000 | 650460083 | 69056064 | 0.000000
10-04-2025 0:44:15000 | -2824662 | 28.2466 | 31613506 | 234951.23 | 69882713 | 99379524 | 50129547 | 0.000000 | 654757019 | 69455527 | 0.000000
10-04-2025 0:44:20000 | -2792999 | 27.93 | 31479690 | 234950.00 | 69110077 | 99370819 | 50135986 | 0.000000 | 659072693 | 69845005 | 0.000000
10-04-2025 0:44:25000 | -2953322 | 29.5332 | 31959072 | 234883.97 | 73050102 | 99419579 | 50110367 | 0.000000 | 663456055 | 70246597 | 0.000000
10-04-2025 0:44:30000 | -3078573 | 30.7857 | 32210283 | 234829.67 | 76138031 | 99457108 | 50087238 | 0.000000 | 667970337 | 70667065 | 0.000000
10-04-2025 0:44:35000 | -3146737 | 31.4674 | 33349021 | 234890.31 | 77816887 | 99443100 | 50065887 | 0.000000 | 672538513 | 71103550 | 0.000000
10-04-2025 0:44:40000 | -2965534 | 29.6553 | 31203816 | 234875.89 | 73336678 | 99450974 | 50104408 | 0.000000 | 677153748 | 71526221 | 0.000000
10-04-2025 0:44:45000 | -2767872 | 27.6787 | 32845337 | 235021.00 | 68507881 | 99303261 | 50142048 | 0.000000 | 681498291 | 71922686 | 0.000000
10-04-2025 0:44:50000 | -2630515 | 26.3052 | 32990334 | 235055.14 | 65154778 | 99222725 | 50171162 | 0.000000 | 686106201 | 72292451 | 0.000000
10-04-2025 0:44:55000 | -2617438 | 26.1744 | 33615474 | 234992.97 | 64880455 | 99185364 | 50178875 | 0.000000 | 690882874 | 72653794 | 0.000000
10-04-2025 0:45:00000 | -2870412 | 28.7041 | 34850459 | 234956.14 | 71085930 | 99270996 | 50133560 | 0.000000 | 695626221 | 73037539 | 0.000000
10-04-2025 0:45:05000 | -3094604 | 30.946 | 38262666 | 234983.17 | 76645279 | 99244270 | 50098194 | 0.000000 | 5243644 | 41797119 | 0.000000
10-04-2025 0:45:10000 | -2994282 | 29.9428 | 39821938 | 235116.81 | 74211380 | 99127197 | 50119835 | 0.000000 | 10761290 | 84621277 | 0.000000
10-04-2025 0:45:15000 | -2722271 | 27.2227 | 37518667 | 235150.44 | 67507607 | 99063583 | 50185574 | 0.000000 | 16205133 | 123850891 | 0.000000
10-04-2025 0:45:20000 | -2763714 | 27.6371 | 34899883 | 235032.53 | 68464409 | 99212090 | 50173714 | 0.000000 | 21136980 | 161581604 | 0.000000
10-04-2025 0:45:25000 | -3000177 | 30.0018 | 36081052 | 234983.09 | 74278595 | 99284592 | 50134373 | 0.000000 | 26130936 | 201777481 | 0.000000
10-04-2025 0:45:30000 | -2986014 | 29.8601 | 39920251 | 235110.27 | 74010925 | 99118141 | 50138359 | 0.000000 | 31462681 | 243622589 | 0.000000
10-04-2025 0:45:35000 | -2874968 | 28.7497 | 38314934 | 235079.89 | 71268250 | 99123604 | 50168766 | 0.000000 | 36953693 | 284372406 | 0.000000
10-04-2025 0:45:40000 | -2929188 | 29.2919 | 33704187 | 234886.61 | 72513420 | 99344521 | 50158909 | 0.000000 | 41994804 | 324248383 | 0.000000
10-04-2025 0:45:45000 | -3137534 | 31.3753 | 34728970 | 234892.83 | 77626205 | 99392975 | 50098824 | 0.000000 | 46619453 | 366755219 | 0.000000
10-04-2025 0:45:50000 | -3033819 | 30.3382 | 33977227 | 234931.95 | 75060707 | 99378693 | 50118385 | 0.000000 | 51451668 | 410025177 | 0.000000
10-04-2025 0:45:55000 | -2955786 | 29.5579 | 30951938 | 234890.63 | 73088982 | 99456192 | 50132130 | 0.000000 | 55987907 | 451466156 | 0.000000
10-04-2025 0:46:00000 | -2950343 | 29.5034 | 29925754 | 234873.22 | 72931168 | 99489517 | 50124931 | 0.000000 | 60178497 | 492526550 | 0.000000
10-04-2025 0:46:05000 | -3004379 | 30.0438 | 29816743 | 234831.52 | 74264137 | 99511139 | 50112553 | 0.000000 | 64337624 | 534250244 | 0.000000
10-04-2025 0:46:10000 | -3013098 | 30.131 | 30960737 | 234887.94 | 74485474 | 99476227 | 50122356 | 0.000000 | 68650253 | 576002991 | 0.000000
10-04-2025 0:46:15000 | -2900301 | 29.003 | 29755720 | 234885.70 | 71706573 | 99477829 | 50137177 | 0.000000 | 72939522 | 616885620 | 0.000000
10-04-2025 0:46:20000 | -2839579 | 28.3958 | 30976409 | 234936.03 | 70232506 | 99410248 | 50148014 | 0.000000 | 77179977 | 656951416 | 0.000000
10-04-2025 0:46:25000 | -2772710 | 27.7271 | 32370647 | 234975.28 | 68628242 | 99325394 | 50167339 | 0.000000 | 81553711 | 695846619 | 0.000000
10-04-2025 0:46:30000 | -2845193 | 28.4519 | 30735046 | 234895.03 | 70376892 | 99421593 | 50154739 | 0.000000 | 85914864 | 734544495 | 0.000000
10-04-2025 0:46:35000 | -3006751 | 30.0675 | 31482813 | 234841.75 | 74363724 | 99456291 | 50127468 | 0.000000 | 90363625 | 775266479 | 0.000000
10-04-2025 0:46:40000 | -3159761 | 31.5976 | 34380894 | 234917.30 | 78147980 | 99413239 | 50100460 | 0.000000 | 94973869 | 818533569 | 0.000000
10-04-2025 0:46:45000 | -3123559 | 31.2356 | 32729465 | 234889.30 | 77232826 | 99455513 | 50092266 | 0.000000 | 99511543 | 862232788 | 0.000000
10-04-2025 0:46:50000 | -2958877 | 29.5888 | 32028713 | 234929.67 | 73178734 | 99419235 | 50120396 | 0.000000 | 104017708 | 904572693 | 0.000000
10-04-2025 0:46:55000 | -2931071 | 29.3107 | 30201462 | 234903.88 | 72458565 | 99473335 | 50122997 | 0.000000 | 108341225 | 945361877 | 0.000000
10-04-2025 0:47:00000 | -2884495 | 28.845 | 30012656 | 234900.28 | 71314880 | 99463051 | 50124371 | 0.000000 | 112466888 | 985762329 | 0.000000
10-04-2025 0:47:05000 | -2926851 | 29.2685 | 29553003 | 234889.80 | 72343903 | 99494095 | 50119709 | 0.000000 | 116514519 | 10261194 | 0.000000
10-04-2025 0:47:10000 | -2968910 | 29.6891 | 29614849 | 234828.16 | 73395157 | 99506180 | 50107765 | 0.000000 | 120664772 | 10669294 | 0.000000
10-04-2025 0:47:15000 | -3132440 | 31.3244 | 29830042 | 234793.80 | 77414398 | 99549629 | 50072147 | 0.000000 | 124733406 | 11097422 | 0.000000
10-04-2025 0:47:20000 | -3094693 | 30.9469 | 30478015 | 234854.20 | 76478561 | 99518539 | 50069366 | 0.000000 | 128972885 | 11531388 | 0.000000
10-04-2025 0:47:25000 | -2922199 | 29.222 | 29028113 | 234892.58 | 72218422 | 99510231 | 50102524 | 0.000000 | 133158783 | 11946819 | 0.000000
10-04-2025 0:47:30000 | -2785933 | 27.8593 | 32141445 | 234986.50 | 68946556 | 99341057 | 50123371 | 0.000000 | 137365997 | 12340823 | 0.000000
10-04-2025 0:47:35000 | -3002353 | 30.0235 | 30615769 | 234870.70 | 74223129 | 99484100 | 50080936 | 0.000000 | 141527206 | 12744598 | 0.000000
10-04-2025 0:47:40000 | -3091148 | 30.9115 | 31392356 | 234832.36 | 76426758 | 99488281 | 50066761 | 0.000000 | 145994202 | 13166350 | 0.000000
10-04-2025 0:47:45000 | -3106009 | 31.0601 | 31585806 | 234883.44 | 76779877 | 99486908 | 50055790 | 0.000000 | 150262634 | 13599230 | 0.000000
10-04-2025 0:47:50000 | -2914335 | 29.1434 | 30687092 | 234927.88 | 72058693 | 99450195 | 50096924 | 0.000000 | 154628281 | 14014574 | 0.000000
10-04-2025 0:47:55000 | -2776312 | 27.7631 | 29110039 | 234919.91 | 68645432 | 99454803 | 50123108 | 0.000000 | 158781418 | 14402841 | 0.000000
10-04-2025 0:48:00000 | -2843012 | 28.4301 | 29955354 | 234889.95 | 70308601 | 99449493 | 50109337 | 0.000000 | 162878082 | 14792395 | 0.000000
10-04-2025 0:48:05000 | -2863810 | 28.6381 | 33756560 | 234988.41 | 70884224 | 99312454 | 50120628 | 0.000000 | 167509598 | 15188206 | 0.000000
10-04-2025 0:48:10000 | -2981633 | 29.8163 | 32869021 | 234909.83 | 73766342 | 99397858 | 50095703 | 0.000000 | 172060043 | 15596161 | 0.000000
10-04-2025 0:48:15000 | -3171848 | 31.7185 | 33076313 | 234846.69 | 78441658 | 99460670 | 50054527 | 0.000000 | 176699951 | 16025663 | 0.000000
10-04-2025 0:48:20000 | -3187597 | 31.876 | 34039338 | 234885.73 | 78834679 | 99434662 | 50054649 | 0.000000 | 181415695 | 16469183 | 0.000000
10-04-2025 0:48:25000 | -2933966 | 29.3397 | 32828723 | 234982.70 | 72577560 | 99379829 | 50093475 | 0.000000 | 186086502 | 16891813 | 0.000000
10-04-2025 0:48:30000 | -2760098 | 27.601 | 31563215 | 234972.78 | 68298439 | 99352486 | 50131420 | 0.000000 | 190587601 | 17282500 | 0.000000
10-04-2025 0:48:35000 | -2863536 | 28.6354 | 29986990 | 234883.67 | 70815620 | 99456154 | 50110390 | 0.000000 | 194818604 | 17671311 | 0.000000
10-04-2025 0:48:40000 | -2992223 | 29.9222 | 31921235 | 234856.23 | 74014618 | 99435776 | 50092915 | 0.000000 | 199367569 | 18077788 | 0.000000
10-04-2025 0:48:45000 | -3110424 | 31.1042 | 32025178 | 234846.72 | 76910706 | 99474129 | 50057720 | 0.000000 | 203890396 | 18502205 | 0.000000
10-04-2025 0:48:50000 | -3136077 | 31.3608 | 31761877 | 234849.78 | 77524094 | 99491043 | 50053928 | 0.000000 | 208366638 | 18937444 | 0.000000
10-04-2025 0:48:55000 | -2911178 | 29.1118 | 31730896 | 234946.52 | 72004547 | 99411224 | 50096283 | 0.000000 | 212846252 | 19356290 | 0.000000
10-04-2025 0:49:00000 | -2828612 | 28.2861 | 28992068 | 234908.78 | 69933914 | 99478836 | 50101162 | 0.000000 | 216841187 | 19754268 | 0.000000
10-04-2025 0:49:05000 | -2831437 | 28.3144 | 29353992 | 234870.78 | 70023727 | 99466904 | 50106731 | 0.000000 | 221011139 | 20144700 | 0.000000
10-04-2025 0:49:10000 | -2930792 | 29.3079 | 29178208 | 234834.84 | 72444740 | 99508072 | 50090946 | 0.000000 | 224988159 | 20545552 | 0.000000
10-04-2025 0:49:15000 | -3006398 | 30.064 | 31277139 | 234840.78 | 74348640 | 99463188 | 50085773 | 0.000000 | 229246857 | 20958870 | 0.000000
10-04-2025 0:49:20000 | -3043182 | 30.4318 | 30870144 | 234866.73 | 75235588 | 99489433 | 50070030 | 0.000000 | 233481018 | 21377866 | 0.000000
10-04-2025 0:49:25000 | -3035908 | 30.3591 | 33615024 | 234912.75 | 75114067 | 99392578 | 50083073 | 0.000000 | 238093246 | 21801050 | 0.000000
10-04-2025 0:49:30000 | -3031160 | 30.3116 | 29582207 | 234840.03 | 74911842 | 99527145 | 50074928 | 0.000000 | 242259979 | 22224739 | 0.000000
10-04-2025 0:49:35000 | -2968256 | 29.6826 | 29577332 | 234837.72 | 73380142 | 99507202 | 50093575 | 0.000000 | 246397705 | 22639482 | 0.000000
10-04-2025 0:49:40000 | -3089440 | 30.8944 | 28212351 | 234772.09 | 76329102 | 99585632 | 50062355 | 0.000000 | 250297974 | 23061423 | 0.000000
10-04-2025 0:49:45000 | -3198052 | 31.9805 | 28060244 | 234707.64 | 78998749 | 99617279 | 50026573 | 0.000000 | 254196594 | 23502532 | 0.000000
10-04-2025 0:49:50000 | -3112659 | 31.1266 | 28638931 | 234758.38 | 76921631 | 99579399 | 50043709 | 0.000000 | 258219757 | 23940676 | 0.000000
10-04-2025 0:49:55000 | -2979737 | 29.7974 | 27272939 | 234783.83 | 73618156 | 99583748 | 50063606 | 0.000000 | 262083954 | 24360381 | 0.000000
10-04-2025 0:50:00000 | -2914811 | 29.1481 | 27466003 | 234775.06 | 72035263 | 99558975 | 50070694 | 0.000000 | 265858948 | 24768787 | 0.000000
10-04-2025 0:50:05000 | -2908745 | 29.0875 | 25260251 | 234667.70 | 71875198 | 99625038 | 50065220 | 0.000000 | 269598694 | 25170022 | 0.000000
10-04-2025 0:50:10000 | -2868463 | 28.6846 | 28982046 | 234752.59 | 70946045 | 99493454 | 50074661 | 0.000000 | 273548706 | 25570376 | 0.000000
10-04-2025 0:50:15000 | -2891391 | 28.9139 | 27974771 | 234736.08 | 71487679 | 99535217 | 50064342 | 0.000000 | 277480988 | 25971260 | 0.000000
10-04-2025 0:50:20000 | -3053739 | 30.5374 | 26742732 | 234621.27 | 75470268 | 99618736 | 50029392 | 0.000000 | 281202545 | 26384937 | 0.000000
10-04-2025 0:50:25000 | -3097724 | 30.9772 | 29675791 | 234751.86 | 76567230 | 99544266 | 50028713 | 0.000000 | 285239197 | 26816404 | 0.000000
10-04-2025 0:50:30000 | -2982464 | 29.8246 | 28110308 | 234736.55 | 73719048 | 99558769 | 50043064 | 0.000000 | 289229980 | 27236665 | 0.000000
10-04-2025 0:50:35000 | -2944920 | 29.4492 | 26930471 | 234722.73 | 72778534 | 99584473 | 50052738 | 0.000000 | 293036407 | 27646770 | 0.000000
10-04-2025 0:50:40000 | -2827776 | 28.2778 | 27639365 | 234757.27 | 69914055 | 99525719 | 50069607 | 0.000000 | 296851685 | 28044932 | 0.000000
10-04-2025 0:50:45000 | -2819624 | 28.1962 | 25846365 | 234697.33 | 69695274 | 99582497 | 50066746 | 0.000000 | 300528046 | 28434004 | 0.000000
10-04-2025 0:50:50000 | -2939841 | 29.3984 | 26487559 | 234717.61 | 72649307 | 99596565 | 50037949 | 0.000000 | 304056122 | 28836960 | 0.000000
10-04-2025 0:50:55000 | -2965282 | 29.6528 | 27472434 | 234695.31 | 73303459 | 99573570 | 50044556 | 0.000000 | 307845673 | 29247693 | 0.000000
10-04-2025 0:51:00000 | -2952306 | 29.5231 | 26081785 | 234767.16 | 72923271 | 99612038 | 50041771 | 0.000000 | 311610962 | 29656643 | 0.000000
10-04-2025 0:51:05000 | -2966758 | 29.6676 | 25736047 | 234773.42 | 73269913 | 99625847 | 50037678 | 0.000000 | 315200195 | 30067856 | 0.000000
10-04-2025 0:51:10000 | -2971392 | 29.7139 | 25589050 | 234773.75 | 73377769 | 99631233 | 50044456 | 0.000000 | 318790253 | 30480925 | 0.000000
10-04-2025 0:51:15000 | -2900837 | 29.0084 | 24652278 | 234760.66 | 71639496 | 99640839 | 50060238 | 0.000000 | 322362274 | 30884285 | 0.000000
10-04-2025 0:51:20000 | -2764827 | 27.6483 | 26764766 | 234870.53 | 68321037 | 99534714 | 50073948 | 0.000000 | 326008575 | 31276882 | 0.000000
10-04-2025 0:51:25000 | -2946905 | 29.469 | 25712881 | 234766.97 | 72779900 | 99621498 | 50048302 | 0.000000 | 329476013 | 31674431 | 0.000000
10-04-2025 0:51:30000 | -3121079 | 31.2108 | 28034231 | 234774.88 | 77100082 | 99599022 | 50015636 | 0.000000 | 333247162 | 32098303 | 0.000000
10-04-2025 0:51:35000 | -3073866 | 30.7387 | 28166619 | 234818.20 | 75934647 | 99582802 | 50023636 | 0.000000 | 337243866 | 32529055 | 0.000000
10-04-2025 0:51:40000 | -2954608 | 29.5461 | 27569197 | 234849.72 | 72985039 | 99567490 | 50037716 | 0.000000 | 341063568 | 32945720 | 0.000000
10-04-2025 0:51:45000 | -2852645 | 28.5265 | 26324541 | 234823.63 | 70469559 | 99576912 | 50051842 | 0.000000 | 344855408 | 33345784 | 0.000000
10-04-2025 0:51:50000 | -2879494 | 28.7949 | 25360095 | 234777.80 | 71126831 | 99614410 | 50039455 | 0.000000 | 348409210 | 33742783 | 0.000000
10-04-2025 0:51:55000 | -2882204 | 28.822 | 28737236 | 234905.33 | 71223846 | 99506615 | 50038204 | 0.000000 | 352167023 | 34144819 | 0.000000
10-04-2025 0:52:00000 | -2871019 | 28.7102 | 26724421 | 234789.00 | 70943512 | 99569572 | 50052006 | 0.000000 | 356077393 | 34542747 | 0.000000
10-04-2025 0:52:05000 | -2836642 | 28.3664 | 27713696 | 234842.02 | 70106575 | 99526138 | 50047741 | 0.000000 | 359854462 | 34936670 | 0.000000
10-04-2025 0:52:10000 | -2859573 | 28.5957 | 27243789 | 234821.13 | 70661888 | 99549225 | 50042183 | 0.000000 | 363659698 | 35330981 | 0.000000
10-04-2025 0:52:15000 | -2876207 | 28.7621 | 27172717 | 234817.17 | 71067879 | 99556694 | 50041168 | 0.000000 | 367416443 | 35729766 | 0.000000
10-04-2025 0:52:20000 | -2846761 | 28.4676 | 29911626 | 234866.34 | 70413010 | 99452515 | 50057213 | 0.000000 | 371359436 | 36129275 | 0.000000
10-04-2025 0:52:25000 | -2719680 | 27.1968 | 27819888 | 234860.70 | 67248550 | 99480896 | 50076862 | 0.000000 | 375270874 | 36513411 | 0.000000
10-04-2025 0:52:30000 | -2718869 | 27.1887 | 29566416 | 234893.42 | 67261871 | 99413918 | 50095268 | 0.000000 | 379284668 | 36889314 | 0.000000
10-04-2025 0:52:35000 | -2840417 | 28.4042 | 30771448 | 234855.72 | 70274033 | 99418297 | 50067684 | 0.000000 | 383390717 | 37280381 | 0.000000
10-04-2025 0:52:40000 | -2883590 | 28.8359 | 32592920 | 234921.52 | 71358154 | 99367279 | 50076714 | 0.000000 | 387856567 | 37682090 | 0.000000
10-04-2025 0:52:45000 | -2820625 | 28.2063 | 31779797 | 234922.86 | 69801971 | 99371262 | 50094658 | 0.000000 | 392291077 | 38078503 | 0.000000
10-04-2025 0:52:50000 | -2747130 | 27.4713 | 31773674 | 234923.58 | 68002632 | 99337761 | 50114082 | 0.000000 | 396690552 | 38462163 | 0.000000
10-04-2025 0:52:55000 | -2820452 | 28.2045 | 31975854 | 234911.97 | 69800797 | 99363480 | 50108784 | 0.000000 | 401176208 | 38849255 | 0.000000
10-04-2025 0:53:00000 | -2913861 | 29.1386 | 32302251 | 234906.06 | 72086189 | 99391136 | 50099052 | 0.000000 | 405603119 | 39247261 | 0.000000
10-04-2025 0:53:05000 | -3160427 | 31.6043 | 32727859 | 234817.44 | 78156517 | 99468094 | 50054764 | 0.000000 | 410092712 | 39671670 | 0.000000
10-04-2025 0:53:10000 | -3158335 | 31.5833 | 32909053 | 234829.83 | 78109703 | 99461525 | 50045143 | 0.000000 | 414805847 | 40109707 | 0.000000
10-04-2025 0:53:15000 | -3084506 | 30.8451 | 32871799 | 234912.05 | 76284912 | 99436928 | 50047184 | 0.000000 | 419329346 | 40544146 | 0.000000
10-04-2025 0:53:20000 | -2973330 | 29.7333 | 30331970 | 234868.58 | 73502724 | 99483688 | 50064255 | 0.000000 | 423699310 | 40961357 | 0.000000
10-04-2025 0:53:25000 | -2939725 | 29.3972 | 29569009 | 234838.73 | 72673866 | 99497948 | 50064423 | 0.000000 | 427880035 | 41372573 | 0.000000
10-04-2025 0:53:30000 | -2911119 | 29.1112 | 29548916 | 234843.48 | 71972794 | 99488800 | 50069000 | 0.000000 | 431994354 | 41779805 | 0.000000
10-04-2025 0:53:35000 | -2906931 | 29.0693 | 29451558 | 234873.13 | 71859276 | 99490685 | 50073051 | 0.000000 | 436096619 | 42182910 | 0.000000
10-04-2025 0:53:40000 | -2878202 | 28.782 | 29101094 | 234847.78 | 71156258 | 99492737 | 50075962 | 0.000000 | 440224213 | 42583521 | 0.000000
10-04-2025 0:53:45000 | -2917789 | 29.1779 | 30026606 | 234838.61 | 72149467 | 99474655 | 50062309 | 0.000000 | 444279388 | 42983428 | 0.000000
10-04-2025 0:53:50000 | -3022390 | 30.2239 | 30216294 | 234829.53 | 74717354 | 99503967 | 50046501 | 0.000000 | 448463226 | 43397832 | 0.000000
10-04-2025 0:53:55000 | -2978572 | 29.7857 | 32916348 | 234918.94 | 73691223 | 99394905 | 50062855 | 0.000000 | 452951538 | 43815771 | 0.000000
10-04-2025 0:54:00000 | -2805004 | 28.05 | 30642771 | 234913.38 | 69385086 | 99408585 | 50096138 | 0.000000 | 457334045 | 44213379 | 0.000000
10-04-2025 0:54:05000 | -2825905 | 28.259 | 30047498 | 234866.05 | 69896797 | 99439461 | 50090652 | 0.000000 | 461399902 | 44602544 | 0.000000
10-04-2025 0:54:10000 | -2952229 | 29.5223 | 30275049 | 234838.94 | 73003494 | 99478287 | 50066113 | 0.000000 | 465595337 | 45004561 | 0.000000
10-04-2025 0:54:15000 | -3008690 | 30.0869 | 31705532 | 234861.80 | 74406776 | 99449333 | 50061581 | 0.000000 | 470052002 | 45419922 | 0.000000
10-04-2025 0:54:20000 | -2991495 | 29.915 | 33850222 | 234922.09 | 74044754 | 99365883 | 50074520 | 0.000000 | 474729126 | 45836626 | 0.000000
10-04-2025 0:54:25000 | -2944707 | 29.4471 | 31699956 | 234889.25 | 72835503 | 99425552 | 50078743 | 0.000000 | 479256927 | 46246338 | 0.000000
10-04-2025 0:54:30000 | -2908306 | 29.0831 | 32937139 | 234933.95 | 71965691 | 99364807 | 50083557 | 0.000000 | 483779114 | 46651914 | 0.000000
10-04-2025 0:54:35000 | -2888974 | 28.8897 | 32812903 | 234946.66 | 71488075 | 99361153 | 50088936 | 0.000000 | 488192627 | 47055610 | 0.000000
10-04-2025 0:54:40000 | -2987044 | 29.8704 | 31303105 | 234872.41 | 73867081 | 99455368 | 50067734 | 0.000000 | 492576660 | 47462358 | 0.000000
10-04-2025 0:54:45000 | -3082150 | 30.8215 | 32656531 | 234870.39 | 76227310 | 99443375 | 50047535 | 0.000000 | 497057007 | 47885757 | 0.000000
10-04-2025 0:54:50000 | -3112913 | 31.1291 | 31877563 | 234818.31 | 76974617 | 99479759 | 50031822 | 0.000000 | 501532288 | 48318438 | 0.000000
10-04-2025 0:54:55000 | -3004919 | 30.0492 | 29859749 | 234833.94 | 74279671 | 99509911 | 50044842 | 0.000000 | 505877472 | 48741743 | 0.000000
10-04-2025 0:55:00000 | -2903308 | 29.0331 | 31145701 | 234915.88 | 71800499 | 99429504 | 50063015 | 0.000000 | 510041565 | 49151211 | 0.000000
10-04-2025 0:55:05000 | -2854993 | 28.5499 | 29321172 | 234854.11 | 70591988 | 99476753 | 50071888 | 0.000000 | 514171814 | 49550498 | 0.000000
10-04-2025 0:55:10000 | -2797762 | 27.9776 | 27466169 | 234839.84 | 69153770 | 99521568 | 50079281 | 0.000000 | 518111633 | 49939185 | 0.000000
10-04-2025 0:55:15000 | -2847340 | 28.4734 | 30361619 | 234894.39 | 70417999 | 99436287 | 50086594 | 0.000000 | 522109375 | 50333481 | 0.000000
10-04-2025 0:55:20000 | -2802564 | 28.0256 | 29179397 | 234866.16 | 69300865 | 99462349 | 50112823 | 0.000000 | 526266357 | 50725000 | 0.000000
10-04-2025 0:55:25000 | -2930605 | 29.306 | 29013093 | 234827.97 | 72441643 | 99513519 | 50092960 | 0.000000 | 530225830 | 51123208 | 0.000000
10-04-2025 0:55:30000 | -2991008 | 29.9101 | 29360420 | 234805.03 | 73932251 | 99521660 | 50077332 | 0.000000 | 534311584 | 51537969 | 0.000000
10-04-2025 0:55:35000 | -3069231 | 30.6923 | 30250317 | 234835.31 | 75863670 | 99517807 | 50070976 | 0.000000 | 538499939 | 51962368 | 0.000000
10-04-2025 0:55:40000 | -3071968 | 30.7197 | 31127590 | 234855.08 | 75944420 | 99490555 | 50073013 | 0.000000 | 542710999 | 52389907 | 0.000000
10-04-2025 0:55:45000 | -2953460 | 29.5346 | 30439016 | 234928.55 | 73005180 | 99473106 | 50100788 | 0.000000 | 546924194 | 52807241 | 0.000000
10-04-2025 0:55:50000 | -2939789 | 29.3979 | 28053264 | 234810.78 | 72648079 | 99547775 | 50101818 | 0.000000 | 550999878 | 53212280 | 0.000000
10-04-2025 0:55:55000 | -2957648 | 29.5765 | 28674255 | 234827.77 | 73095146 | 99533325 | 50090454 | 0.000000 | 555005798 | 53619546 | 0.000000
10-04-2025 0:56:00000 | -3066924 | 30.6692 | 30037813 | 234861.17 | 75790413 | 99523796 | 50070297 | 0.000000 | 559107117 | 54040605 | 0.000000
10-04-2025 0:56:05000 | -3083836 | 30.8384 | 30276521 | 234828.48 | 76218979 | 99521507 | 50069427 | 0.000000 | 563449036 | 54468008 | 0.000000
10-04-2025 0:56:10000 | -3158694 | 31.5869 | 29588237 | 234824.44 | 78039131 | 99564140 | 50046467 | 0.000000 | 567445007 | 54903105 | 0.000000
10-04-2025 0:56:15000 | -2998000 | 29.98 | 29267817 | 234886.63 | 74085770 | 99526855 | 50074772 | 0.000000 | 571583374 | 55329204 | 0.000000
10-04-2025 0:56:20000 | -2924024 | 29.2402 | 27005220 | 234837.83 | 72229012 | 99576225 | 50080456 | 0.000000 | 575431458 | 55738970 | 0.000000
10-04-2025 0:56:25000 | -2901892 | 29.0189 | 26952551 | 234797.80 | 71699425 | 99571442 | 50087135 | 0.000000 | 579258606 | 56141406 | 0.000000
10-04-2025 0:56:30000 | -2934279 | 29.3428 | 27658740 | 234811.81 | 72503822 | 99558685 | 50072437 | 0.000000 | 583047607 | 56546958 | 0.000000
10-04-2025 0:56:35000 | -2930700 | 29.307 | 27503628 | 234818.00 | 72410950 | 99562531 | 50073112 | 0.000000 | 587029175 | 56953560 | 0.000000
10-04-2025 0:56:40000 | -3060847 | 30.6085 | 29407678 | 234809.50 | 75643295 | 99541634 | 50052757 | 0.000000 | 591010010 | 57369585 | 0.000000
10-04-2025 0:56:45000 | -3106036 | 31.0604 | 29415059 | 234794.48 | 76751801 | 99554565 | 50044804 | 0.000000 | 595098267 | 57800767 | 0.000000
10-04-2025 0:56:50000 | -3065545 | 30.6554 | 28544836 | 234806.81 | 75742271 | 99569275 | 50042240 | 0.000000 | 599061035 | 58230776 | 0.000000
10-04-2025 0:56:55000 | -2905061 | 29.0506 | 26902974 | 234837.88 | 71766022 | 99573936 | 50069180 | 0.000000 | 602816040 | 58643530 | 0.000000
10-04-2025 0:57:00000 | -2775162 | 27.7516 | 25979827 | 234828.41 | 68570183 | 99564667 | 50099632 | 0.000000 | 606454041 | 59037041 | 0.000000
10-04-2025 0:57:05000 | -2705455 | 27.0545 | 25133757 | 234812.72 | 66850883 | 99571251 | 50114571 | 0.000000 | 609938354 | 59413906 | 0.000000
10-04-2025 0:57:10000 | -2856094 | 28.5609 | 27392683 | 234809.78 | 70584045 | 99543213 | 50089458 | 0.000000 | 613575317 | 59804229 | 0.000000
10-04-2025 0:57:15000 | -2989478 | 29.8948 | 27807498 | 234789.19 | 73869576 | 99570168 | 50062294 | 0.000000 | 617350098 | 60214692 | 0.000000
10-04-2025 0:57:20000 | -2995321 | 29.9532 | 28805278 | 234831.73 | 74019295 | 99540771 | 50073654 | 0.000000 | 621329163 | 60632573 | 0.000000
10-04-2025 0:57:25000 | -2908873 | 29.0887 | 27990361 | 234852.70 | 71876846 | 99540237 | 50094040 | 0.000000 | 625312012 | 61044229 | 0.000000
10-04-2025 0:57:30000 | -2905393 | 29.0539 | 26587471 | 234777.97 | 71784279 | 99583900 | 50089672 | 0.000000 | 629041382 | 61444707 | 0.000000
10-04-2025 0:57:35000 | -2930394 | 29.3039 | 27286389 | 234817.23 | 72394508 | 99569275 | 50079964 | 0.000000 | 632758179 | 61851563 | 0.000000
10-04-2025 0:57:40000 | -2801608 | 28.0161 | 31598416 | 235018.84 | 69298470 | 99369965 | 50112160 | 0.000000 | 636668518 | 62253726 | 0.000000
10-04-2025 0:57:45000 | -2538646 | 25.3865 | 30574648 | 235037.27 | 62849651 | 99282547 | 50181671 | 0.000000 | 641011902 | 62617939 | 0.000000
10-04-2025 0:57:50000 | -2555623 | 25.5562 | 30455173 | 234949.69 | 63284840 | 99297409 | 50172699 | 0.000000 | 645252686 | 62970615 | 0.000000
10-04-2025 0:57:55000 | -2741190 | 27.4119 | 30995608 | 234908.39 | 67843201 | 99366783 | 50149269 | 0.000000 | 649625732 | 63339146 | 0.000000
10-04-2025 0:58:00000 | -2882948 | 28.8295 | 34887327 | 235004.91 | 71380669 | 99275742 | 50135704 | 0.000000 | 654283997 | 63731606 | 0.000000
10-04-2025 0:58:05000 | -2853025 | 28.5302 | 34524136 | 234975.27 | 70646751 | 99275787 | 50146580 | 0.000000 | 659276733 | 64129702 | 0.000000
10-04-2025 0:58:10000 | -2745455 | 27.4546 | 36703955 | 235081.77 | 68078659 | 99118156 | 50173141 | 0.000000 | 664307251 | 64518911 | 0.000000
10-04-2025 0:58:15000 | -2877598 | 28.776 | 34953940 | 235001.72 | 71253685 | 99270325 | 50156578 | 0.000000 | 669143616 | 64909023 | 0.000000
10-04-2025 0:58:20000 | -2944273 | 29.4427 | 36098896 | 235031.84 | 72902199 | 99256744 | 50143486 | 0.000000 | 674068848 | 65314653 | 0.000000
10-04-2025 0:58:25000 | -2970493 | 29.7049 | 37083828 | 235072.95 | 73560997 | 99229729 | 50141113 | 0.000000 | 679096985 | 65728340 | 0.000000
10-04-2025 0:58:30000 | -2974605 | 29.7461 | 35634966 | 235014.63 | 73636070 | 99290062 | 50147892 | 0.000000 | 684137329 | 66141992 | 0.000000
10-04-2025 0:58:35000 | -2951842 | 29.5184 | 36749465 | 235069.98 | 73097496 | 99233925 | 50145428 | 0.000000 | 689139160 | 66553794 | 0.000000
10-04-2025 0:58:40000 | -2999781 | 29.9978 | 36314883 | 235030.41 | 74262352 | 99275200 | 50135338 | 0.000000 | 694187500 | 66967500 | 0.000000
10-04-2025 0:58:45000 | -2953371 | 29.5337 | 37603386 | 235077.92 | 73155609 | 99199158 | 50148041 | 0.000000 | 699321899 | 67383315 | 0.000000
10-04-2025 0:58:50000 | -2894795 | 28.9479 | 37367986 | 235084.86 | 71719452 | 99177101 | 50161411 | 0.000000 | 704491882 | 67790059 | 0.000000
10-04-2025 0:58:55000 | -2895811 | 28.9581 | 36140378 | 235043.28 | 71717522 | 99230202 | 50156410 | 0.000000 | 709513062 | 68191030 | 0.000000
10-04-2025 0:59:00000 | -3029843 | 30.2984 | 33801228 | 234940.00 | 74951302 | 99383453 | 50129436 | 0.000000 | 714354248 | 68601704 | 0.000000
10-04-2025 0:59:05000 | -3166092 | 31.6609 | 34049741 | 234895.73 | 78308731 | 99426674 | 50098980 | 0.000000 | 719150574 | 69033638 | 0.000000
10-04-2025 0:59:10000 | -3224503 | 32.245 | 34386914 | 234921.38 | 79727257 | 99436172 | 50079361 | 0.000000 | 723975586 | 69481138 | 0.000000
10-04-2025 0:59:15000 | -3040083 | 30.4008 | 35108904 | 235027.02 | 75215904 | 99339737 | 50113632 | 0.000000 | 728845215 | 69917837 | 0.000000
10-04-2025 0:59:20000 | -2855310 | 28.5531 | 33187751 | 235024.78 | 70650764 | 99331276 | 50150959 | 0.000000 | 733583130 | 70319790 | 0.000000
10-04-2025 0:59:25000 | -2830898 | 28.309 | 33478208 | 235012.05 | 70066788 | 99307976 | 50145744 | 0.000000 | 738196655 | 70709077 | 0.000000
10-04-2025 0:59:30000 | -3127296 | 31.273 | 33492534 | 234917.30 | 77332405 | 99431396 | 50072403 | 0.000000 | 742491455 | 71132705 | 0.000000
10-04-2025 0:59:35000 | -3070970 | 30.7097 | 38098867 | 235090.83 | 76029869 | 99239212 | 50086582 | 0.000000 | 747634399 | 71562324 | 0.000000
10-04-2025 0:59:40000 | -2953818 | 29.5382 | 36533103 | 235066.48 | 73136192 | 99243813 | 50097698 | 0.000000 | 752804993 | 71980596 | 0.000000
10-04-2025 0:59:45000 | -2934979 | 29.3498 | 37152878 | 235100.25 | 72686172 | 99208298 | 50095573 | 0.000000 | 757930664 | 72388901 | 0.000000
10-04-2025 0:59:50000 | -3019857 | 30.1986 | 37494009 | 235059.59 | 74780968 | 99238037 | 50079472 | 0.000000 | 763040833 | 72804175 | 0.000000
10-04-2025 0:59:55000 | -3026129 | 30.2613 | 37019888 | 235048.23 | 74922859 | 99260010 | 50075241 | 0.000000 | 768184875 | 73224688 | 0.000000
10-04-2025 1:00:00000 | -3123176 | 31.2318 | 35855530 | 234967.39 | 77278183 | 99347435 | 50059448 | 0.000000 | 773244080 | 73651846 | 0.000000
10-04-2025 1:00:05000 | -3082903 | 30.829 | 36581167 | 235012.58 | 76306763 | 99303360 | 50061394 | 0.000000 | 5169286 | 43329529 | 0.000000
10-04-2025 1:00:10000 | -3021903 | 30.219 | 37079756 | 235089.00 | 74807503 | 99255592 | 50057487 | 0.000000 | 10226457 | 85528084 | 0.000000
10-04-2025 1:00:15000 | -2979967 | 29.7997 | 38472258 | 235119.22 | 73819031 | 99176895 | 50059170 | 0.000000 | 15569876 | 127016792 | 0.000000
10-04-2025 1:00:20000 | -2987636 | 29.8764 | 36931589 | 235074.89 | 73969826 | 99244614 | 50060719 | 0.000000 | 20733315 | 168441681 | 0.000000
10-04-2025 1:00:25000 | -2921855 | 29.2186 | 36646006 | 235078.63 | 72360428 | 99222649 | 50068935 | 0.000000 | 25842585 | 209427536 | 0.000000
10-04-2025 1:00:30000 | -2933725 | 29.3373 | 36452192 | 235090.89 | 72639359 | 99236893 | 50066422 | 0.000000 | 30857922 | 249986237 | 0.000000
10-04-2025 1:00:35000 | -2987413 | 29.8741 | 35718137 | 235003.73 | 73951874 | 99292816 | 50055904 | 0.000000 | 35870953 | 291033173 | 0.000000
10-04-2025 1:00:40000 | -3070271 | 30.7027 | 36143315 | 235030.89 | 75975662 | 99314217 | 50035721 | 0.000000 | 40916382 | 333147980 | 0.000000
10-04-2025 1:00:45000 | -3135288 | 31.3529 | 37735171 | 235049.44 | 77604927 | 99283493 | 50020180 | 0.000000 | 46108807 | 376350159 | 0.000000
10-04-2025 1:00:50000 | -3191946 | 31.9195 | 35877175 | 234948.47 | 78965073 | 99374245 | 49994141 | 0.000000 | 51234875 | 420502441 | 0.000000
10-04-2025 1:00:55000 | -3227996 | 32.28 | 37151418 | 235062.70 | 79846977 | 99344208 | 49984997 | 0.000000 | 56262928 | 465172089 | 0.000000
10-04-2025 1:01:00000 | -3072585 | 30.7259 | 39358970 | 235121.56 | 76104263 | 99189514 | 49996342 | 0.000000 | 61613007 | 508681732 | 0.000000
10-04-2025 1:01:05000 | -2944130 | 29.4413 | 35517334 | 235044.23 | 72881950 | 99280174 | 50014660 | 0.000000 | 66701324 | 550153809 | 0.000000
10-04-2025 1:01:10000 | -2879264 | 28.7926 | 37134771 | 235095.16 | 71334061 | 99178528 | 50024086 | 0.000000 | 71751167 | 590496765 | 0.000000
10-04-2025 1:01:15000 | -2852502 | 28.525 | 36326292 | 235084.94 | 70660706 | 99198845 | 50023148 | 0.000000 | 76758682 | 630259338 | 0.000000
10-04-2025 1:01:20000 | -2838499 | 28.385 | 36033398 | 235041.86 | 70322189 | 99203857 | 50024612 | 0.000000 | 81787239 | 669780396 | 0.000000
10-04-2025 1:01:25000 | -2820050 | 28.2005 | 38601296 | 235162.42 | 69921188 | 99076134 | 50037319 | 0.000000 | 86882904 | 709325134 | 0.000000
10-04-2025 1:01:30000 | -2699140 | 26.9914 | 37068477 | 235118.69 | 66949081 | 99070099 | 50058510 | 0.000000 | 92156898 | 747556213 | 0.000000
10-04-2025 1:01:35000 | -2812537 | 28.1254 | 36397629 | 235049.03 | 69704124 | 99172997 | 50045753 | 0.000000 | 97302437 | 785646606 | 0.000000
10-04-2025 1:01:40000 | -2924948 | 29.2495 | 39307517 | 235126.44 | 72505722 | 99109055 | 50032158 | 0.000000 | 102588966 | 825704773 | 0.000000
10-04-2025 1:01:45000 | -2925272 | 29.2527 | 40410315 | 235151.09 | 72544342 | 99059280 | 50042435 | 0.000000 | 108193703 | 866270264 | 0.000000
10-04-2025 1:01:50000 | -2949763 | 29.4976 | 40103018 | 235148.25 | 73129082 | 99088455 | 50034687 | 0.000000 | 113689133 | 907138855 | 0.000000
10-04-2025 1:01:55000 | -2935552 | 29.3555 | 40135762 | 235148.86 | 72784966 | 99078239 | 50038082 | 0.000000 | 119291573 | 947906067 | 0.000000
10-04-2025 1:02:00000 | -3009576 | 30.0958 | 38580662 | 235077.80 | 74556862 | 99188316 | 50014782 | 0.000000 | 124782860 | 988984436 | 0.000000
10-04-2025 1:02:05000 | -3117518 | 31.1752 | 39102874 | 235079.30 | 77202103 | 99222534 | 49993252 | 0.000000 | 130193909 | 10317878 | 0.000000
10-04-2025 1:02:10000 | -3013374 | 30.1337 | 38299160 | 235104.14 | 74635925 | 99201973 | 50010216 | 0.000000 | 135691055 | 10743528 | 0.000000
10-04-2025 1:02:15000 | -2908824 | 29.0882 | 36794568 | 235107.09 | 72039757 | 99209450 | 50027859 | 0.000000 | 140894989 | 11152754 | 0.000000
10-04-2025 1:02:20000 | -2867397 | 28.674 | 35948499 | 235066.92 | 71023834 | 99223267 | 50027283 | 0.000000 | 145984924 | 11552811 | 0.000000
10-04-2025 1:02:25000 | -2880520 | 28.8052 | 36555708 | 235052.39 | 71358765 | 99204330 | 50032970 | 0.000000 | 151148575 | 11951167 | 0.000000
10-04-2025 1:02:30000 | -2917827 | 29.1783 | 35039136 | 235007.83 | 72236504 | 99286667 | 50022007 | 0.000000 | 156161530 | 12351801 | 0.000000
10-04-2025 1:02:35000 | -2900303 | 29.003 | 37248162 | 235091.14 | 71853577 | 99185371 | 50021908 | 0.000000 | 161206146 | 12758981 | 0.000000
10-04-2025 1:02:40000 | -2879872 | 28.7987 | 36496152 | 235067.92 | 71335960 | 99206543 | 50028435 | 0.000000 | 166325378 | 13160159 | 0.000000
10-04-2025 1:02:45000 | -2818729 | 28.1873 | 36626660 | 235107.13 | 69846077 | 99166321 | 50037239 | 0.000000 | 171320358 | 13556041 | 0.000000
10-04-2025 1:02:50000 | -2812214 | 28.1221 | 36478176 | 235096.52 | 69681648 | 99169189 | 50040913 | 0.000000 | 176394791 | 13947517 | 0.000000
10-04-2025 1:02:55000 | -2755012 | 27.5501 | 38103286 | 235145.84 | 68335747 | 99057091 | 50057610 | 0.000000 | 181569122 | 14333254 | 0.000000
10-04-2025 1:03:00000 | -2728578 | 27.2858 | 38484993 | 235124.22 | 67708191 | 99019928 | 50071037 | 0.000000 | 186941574 | 14715280 | 0.000000
10-04-2025 1:03:05000 | -2859096 | 28.591 | 37728738 | 235074.22 | 70869331 | 99140533 | 50053467 | 0.000000 | 192157227 | 15103261 | 0.000000
10-04-2025 1:03:10000 | -2917886 | 29.1789 | 38499924 | 235091.13 | 72318199 | 99140732 | 50046249 | 0.000000 | 197516861 | 15506870 | 0.000000
10-04-2025 1:03:15000 | -2985914 | 29.8591 | 38946660 | 235102.50 | 73985878 | 99160042 | 50041218 | 0.000000 | 202938431 | 15918441 | 0.000000
10-04-2025 1:03:20000 | -2978378 | 29.7838 | 40985669 | 235184.52 | 73840981 | 99066406 | 50039799 | 0.000000 | 208493073 | 16334919 | 0.000000
10-04-2025 1:03:25000 | -2983562 | 29.8356 | 39868433 | 235132.95 | 73950974 | 99118973 | 50035519 | 0.000000 | 214120377 | 16749772 | 0.000000
10-04-2025 1:03:30000 | -3074741 | 30.7474 | 39007173 | 235090.19 | 76154594 | 99204872 | 50018696 | 0.000000 | 219533020 | 17172006 | 0.000000
10-04-2025 1:03:35000 | -3080446 | 30.8045 | 41389199 | 235173.30 | 76340782 | 99109398 | 50025036 | 0.000000 | 225220306 | 17599879 | 0.000000
10-04-2025 1:03:40000 | -2959042 | 29.5904 | 41736348 | 235226.64 | 73386932 | 99019890 | 50052013 | 0.000000 | 230986755 | 18019718 | 0.000000
10-04-2025 1:03:45000 | -2878483 | 28.7848 | 39270479 | 235159.50 | 71364670 | 99082169 | 50062466 | 0.000000 | 236610519 | 18425266 | 0.000000
10-04-2025 1:03:50000 | -2864658 | 28.6466 | 39863425 | 235171.91 | 71047607 | 99045616 | 50059307 | 0.000000 | 242139084 | 18820917 | 0.000000
10-04-2025 1:03:55000 | -2943575 | 29.4357 | 41792666 | 235185.86 | 73027222 | 99007080 | 50043171 | 0.000000 | 247778137 | 19227739 | 0.000000
10-04-2025 1:04:00000 | -2970101 | 29.701 | 42984575 | 235206.33 | 73705948 | 98968910 | 50044201 | 0.000000 | 253650864 | 19639890 | 0.000000
10-04-2025 1:04:05000 | -2970448 | 29.7045 | 41625186 | 235179.97 | 73673149 | 99032394 | 50046509 | 0.000000 | 259486267 | 20052954 | 0.000000
10-04-2025 1:04:10000 | -2908930 | 29.0893 | 41471152 | 235195.41 | 72173111 | 98998993 | 50050518 | 0.000000 | 265282104 | 20460106 | 0.000000
10-04-2025 1:04:15000 | -2909255 | 29.0925 | 41704351 | 235208.23 | 72180328 | 98988098 | 50052868 | 0.000000 | 271096191 | 20864709 | 0.000000
10-04-2025 1:04:20000 | -2953028 | 29.5303 | 42284116 | 235205.95 | 73267776 | 98990341 | 50046154 | 0.000000 | 276944122 | 21273030 | 0.000000
10-04-2025 1:04:25000 | -3145001 | 31.45 | 37931748 | 234984.41 | 77867737 | 99280502 | 50001244 | 0.000000 | 282555481 | 21697876 | 0.000000
10-04-2025 1:04:30000 | -3281441 | 32.8144 | 38649541 | 235009.14 | 81207924 | 99313499 | 49963219 | 0.000000 | 287905396 | 22146577 | 0.000000
10-04-2025 1:04:35000 | -3287185 | 32.8719 | 38246589 | 235033.36 | 81333977 | 99329926 | 49957954 | 0.000000 | 293215790 | 22606301 | 0.000000
10-04-2025 1:04:40000 | -3144861 | 31.4486 | 36283086 | 235049.50 | 77797844 | 99341026 | 49975780 | 0.000000 | 298438965 | 23050859 | 0.000000
10-04-2025 1:04:45000 | -3113120 | 31.1312 | 32957766 | 234935.48 | 76970940 | 99444275 | 49961411 | 0.000000 | 303233948 | 23484355 | 0.000000
10-04-2025 1:04:50000 | -3108930 | 31.0893 | 32649629 | 234949.09 | 76857048 | 99453072 | 49938076 | 0.000000 | 307780151 | 23916348 | 0.000000
10-04-2025 1:04:55000 | -3048753 | 30.4875 | 36020535 | 235036.67 | 75450310 | 99309273 | 49953693 | 0.000000 | 312700592 | 24343853 | 0.000000
10-04-2025 1:05:00000 | -2917331 | 29.1733 | 33519048 | 235002.27 | 72191895 | 99346405 | 49969467 | 0.000000 | 317574707 | 24754692 | 0.000000
10-04-2025 1:05:05000 | -2856327 | 28.5633 | 34172881 | 235041.41 | 70711517 | 99291916 | 49974560 | 0.000000 | 322283905 | 25153550 | 0.000000
10-04-2025 1:05:10000 | -2855342 | 28.5534 | 33093555 | 235011.13 | 70657455 | 99335045 | 49972458 | 0.000000 | 326823975 | 25550364 | 0.000000
10-04-2025 1:05:15000 | -2840357 | 28.4036 | 33098425 | 234981.17 | 70302490 | 99327888 | 49975639 | 0.000000 | 331416718 | 25944959 | 0.000000
10-04-2025 1:05:20000 | -2823454 | 28.2345 | 33346575 | 235003.69 | 69890121 | 99309769 | 49970085 | 0.000000 | 336104523 | 26337705 | 0.000000
10-04-2025 1:05:25000 | -2879638 | 28.7964 | 35135005 | 235038.03 | 71301422 | 99263863 | 49965954 | 0.000000 | 340814667 | 26736223 | 0.000000
10-04-2025 1:05:30000 | -2899968 | 28.9997 | 34880625 | 235014.59 | 71800270 | 99284401 | 49971497 | 0.000000 | 345620575 | 27135698 | 0.000000
10-04-2025 1:05:35000 | -2811976 | 28.1198 | 38917949 | 235165.55 | 69732147 | 99055801 | 49989822 | 0.000000 | 350808258 | 27531621 | 0.000000
10-04-2025 1:05:40000 | -2664655 | 26.6466 | 37017119 | 235119.63 | 66102119 | 99048820 | 50030518 | 0.000000 | 356114777 | 27908103 | 0.000000
10-04-2025 1:05:45000 | -2699352 | 26.9935 | 33487712 | 234987.58 | 66875755 | 99239250 | 50019627 | 0.000000 | 360961273 | 28280166 | 0.000000
10-04-2025 1:05:50000 | -2893701 | 28.937 | 36731497 | 235032.72 | 71702034 | 99203972 | 49987129 | 0.000000 | 365804626 | 28673027 | 0.000000
10-04-2025 1:05:55000 | -3006701 | 30.067 | 35552532 | 234960.28 | 74438416 | 99308159 | 49976559 | 0.000000 | 370910156 | 29083347 | 0.000000
10-04-2025 1:06:00000 | -3082747 | 30.8275 | 36215886 | 234997.95 | 76299332 | 99316994 | 49962425 | 0.000000 | 376003784 | 29508984 | 0.000000
10-04-2025 1:06:05000 | -3143895 | 31.4389 | 34825891 | 234943.25 | 77773468 | 99392052 | 49937752 | 0.000000 | 380963318 | 29942727 | 0.000000
10-04-2025 1:06:10000 | -3137802 | 31.378 | 35649211 | 235019.59 | 77621590 | 99360794 | 49922375 | 0.000000 | 385802460 | 30380979 | 0.000000
10-04-2025 1:06:15000 | -2994327 | 29.9433 | 37486509 | 235114.94 | 74141495 | 99225441 | 49956718 | 0.000000 | 390906677 | 30804058 | 0.000000
10-04-2025 1:06:20000 | -2852225 | 28.5222 | 34496978 | 235018.34 | 70622734 | 99276512 | 49979679 | 0.000000 | 395954285 | 31207258 | 0.000000
10-04-2025 1:06:25000 | -2745467 | 27.4547 | 34297036 | 235050.81 | 68004829 | 99228737 | 49996544 | 0.000000 | 400786133 | 31592712 | 0.000000
10-04-2025 1:06:30000 | -2625631 | 26.2563 | 35208823 | 235094.22 | 65114136 | 99112854 | 50036240 | 0.000000 | 405567383 | 31964441 | 0.000000
10-04-2025 1:06:35000 | -2691408 | 26.9141 | 32014458 | 234958.22 | 66653336 | 99299957 | 50028503 | 0.000000 | 410100128 | 32333582 | 0.000000
10-04-2025 1:06:40000 | -2780133 | 27.8013 | 33608264 | 234966.36 | 68853760 | 99277229 | 50017551 | 0.000000 | 414837982 | 32712354 | 0.000000
10-04-2025 1:06:45000 | -2953904 | 29.539 | 37046082 | 235033.34 | 73169685 | 99222725 | 49989689 | 0.000000 | 419664246 | 33115815 | 0.000000
10-04-2025 1:06:50000 | -2964436 | 29.6444 | 38489077 | 235088.75 | 73459106 | 99167641 | 50002964 | 0.000000 | 424875519 | 33528093 | 0.000000
10-04-2025 1:06:55000 | -2883302 | 28.833 | 37445925 | 235112.30 | 71453308 | 99167191 | 50020382 | 0.000000 | 430076935 | 33932419 | 0.000000
10-04-2025 1:07:00000 | -2865678 | 28.6568 | 33428718 | 234961.92 | 70936371 | 99326485 | 50021076 | 0.000000 | 435120789 | 34326504 | 0.000000
10-04-2025 1:07:05000 | -2906518 | 29.0652 | 36521665 | 235055.44 | 71990364 | 99219780 | 50001667 | 0.000000 | 440094360 | 34726929 | 0.000000
10-04-2025 1:07:10000 | -2968554 | 29.6855 | 35569810 | 234984.72 | 73503494 | 99289772 | 49996628 | 0.000000 | 445125427 | 35136470 | 0.000000
10-04-2025 1:07:15000 | -3076496 | 30.765 | 35489434 | 234979.34 | 76128387 | 99341209 | 49974884 | 0.000000 | 450182770 | 35555994 | 0.000000
10-04-2025 1:07:20000 | -3120322 | 31.2032 | 37820603 | 235050.84 | 77251221 | 99273438 | 49959240 | 0.000000 | 455335693 | 35990161 | 0.000000
10-04-2025 1:07:25000 | -2930947 | 29.3095 | 37619270 | 235133.67 | 72599777 | 99186325 | 49996689 | 0.000000 | 460573029 | 36408574 | 0.000000
10-04-2025 1:07:30000 | -2819449 | 28.1945 | 36529631 | 235109.92 | 69857300 | 99171089 | 50016243 | 0.000000 | 465674835 | 36804783 | 0.000000
10-04-2025 1:07:35000 | -2860626 | 28.6063 | 35946230 | 235068.20 | 70859055 | 99219727 | 49992714 | 0.000000 | 470581573 | 37197883 | 0.000000
10-04-2025 1:07:40000 | -2885916 | 28.8592 | 36193115 | 235057.27 | 71481918 | 99222740 | 49988117 | 0.000000 | 475655762 | 37599521 | 0.000000
10-04-2025 1:07:45000 | -2860863 | 28.6086 | 35301541 | 235049.42 | 70847260 | 99247269 | 49999844 | 0.000000 | 480655853 | 37999038 | 0.000000
10-04-2025 1:07:50000 | -2742046 | 27.4205 | 36521504 | 235144.16 | 67963654 | 99124641 | 50026115 | 0.000000 | 485675385 | 38387041 | 0.000000
10-04-2025 1:07:55000 | -2708676 | 27.0868 | 35227922 | 235077.95 | 67128082 | 99164856 | 50044270 | 0.000000 | 490785248 | 38763337 | 0.000000
10-04-2025 1:08:00000 | -2856919 | 28.5692 | 37414233 | 235104.95 | 70798752 | 99153351 | 50020313 | 0.000000 | 495844421 | 39149539 | 0.000000
10-04-2025 1:08:05000 | -2959858 | 29.5986 | 40324648 | 235116.06 | 73398766 | 99084679 | 50011665 | 0.000000 | 501349762 | 39557195 | 0.000000
10-04-2025 1:08:10000 | -3013018 | 30.1302 | 39976831 | 235120.72 | 74680206 | 99131248 | 50004265 | 0.000000 | 506916504 | 39973247 | 0.000000
10-04-2025 1:08:15000 | -2974565 | 29.7457 | 41352656 | 235228.20 | 73745544 | 99047447 | 50016502 | 0.000000 | 512420593 | 40388955 | 0.000000
10-04-2025 1:08:20000 | -2865557 | 28.6556 | 39357563 | 235136.89 | 71064247 | 99069931 | 50037689 | 0.000000 | 518219421 | 40790034 | 0.000000
10-04-2025 1:08:25000 | -3079883 | 30.7988 | 37643694 | 235007.66 | 76263016 | 99261322 | 49989357 | 0.000000 | 523301514 | 41206406 | 0.000000
10-04-2025 1:08:30000 | -3113829 | 31.1383 | 39078635 | 235093.89 | 77111069 | 99221664 | 49985493 | 0.000000 | 528693420 | 41638599 | 0.000000
10-04-2025 1:08:35000 | -3087430 | 30.8743 | 35656155 | 235005.86 | 76393822 | 99339722 | 49976280 | 0.000000 | 533783691 | 42069673 | 0.000000
10-04-2025 1:08:40000 | -3040366 | 30.4037 | 35309666 | 234999.13 | 75236732 | 99332367 | 49973339 | 0.000000 | 538772827 | 42492427 | 0.000000
10-04-2025 1:08:45000 | -2973782 | 29.7378 | 34946101 | 235059.47 | 73591270 | 99316589 | 49983459 | 0.000000 | 543549438 | 42910566 | 0.000000
10-04-2025 1:08:50000 | -2747111 | 27.4711 | 36263855 | 235177.55 | 68070862 | 99139931 | 50029945 | 0.000000 | 548695618 | 43303750 | 0.000000
10-04-2025 1:08:55000 | -2761269 | 27.6127 | 34952493 | 235084.92 | 68405655 | 99208359 | 50031403 | 0.000000 | 553575500 | 43682866 | 0.000000
10-04-2025 1:09:00000 | -2867663 | 28.6766 | 36070588 | 235051.41 | 71028496 | 99218185 | 50025219 | 0.000000 | 558515137 | 44073613 | 0.000000
10-04-2025 1:09:05000 | -2831785 | 28.3178 | 36029397 | 235038.80 | 70164696 | 99200294 | 50037773 | 0.000000 | 563624573 | 44469863 | 0.000000
10-04-2025 1:09:10000 | -2862676 | 28.6268 | 35094688 | 235028.23 | 70895363 | 99256905 | 50035553 | 0.000000 | 568557678 | 44865952 | 0.000000
10-04-2025 1:09:15000 | -3052952 | 30.5295 | 35690898 | 235021.81 | 75547295 | 99323570 | 49986485 | 0.000000 | 573419922 | 45278774 | 0.000000
10-04-2025 1:09:20000 | -3112347 | 31.1235 | 38658701 | 235068.69 | 77067230 | 99237396 | 49974453 | 0.000000 | 578671692 | 45710527 | 0.000000
10-04-2025 1:09:25000 | -3033610 | 30.3361 | 37210374 | 235094.66 | 75095337 | 99256104 | 49984081 | 0.000000 | 583912415 | 46137534 | 0.000000
10-04-2025 1:09:30000 | -2868712 | 28.6871 | 38127383 | 235178.47 | 71083000 | 99128311 | 50010632 | 0.000000 | 589140930 | 46545273 | 0.000000
10-04-2025 1:09:35000 | -2746607 | 27.4661 | 36217400 | 235131.13 | 68078903 | 99141792 | 50032066 | 0.000000 | 594313477 | 46932554 | 0.000000
10-04-2025 1:09:40000 | -2749670 | 27.4967 | 37908696 | 235166.30 | 68188393 | 99062981 | 50030716 | 0.000000 | 599492554 | 47312153 | 0.000000
10-04-2025 1:09:45000 | -2827058 | 28.2706 | 40129170 | 235160.61 | 70144669 | 99007530 | 50037273 | 0.000000 | 604933472 | 47701035 | 0.000000
10-04-2025 1:09:50000 | -2887746 | 28.8775 | 38791196 | 235104.11 | 71596870 | 99109795 | 50038948 | 0.000000 | 610472534 | 48098340 | 0.000000
10-04-2025 1:09:55000 | -2951206 | 29.5121 | 40374224 | 235150.69 | 73174377 | 99077141 | 50030586 | 0.000000 | 616065002 | 48504473 | 0.000000
10-04-2025 1:10:00000 | -2840035 | 28.4003 | 43082856 | 235298.34 | 70524002 | 98868866 | 50057106 | 0.000000 | 621948059 | 48905332 | 0.000000
10-04-2025 1:10:05000 | -2909200 | 29.092 | 39671228 | 235137.67 | 72132179 | 99083000 | 50044941 | 0.000000 | 627745850 | 49298545 | 0.000000
10-04-2025 1:10:10000 | -3118440 | 31.1844 | 40727495 | 235114.53 | 77275444 | 99157913 | 49999294 | 0.000000 | 633358826 | 49720488 | 0.000000
10-04-2025 1:10:15000 | -3261670 | 32.6167 | 40494014 | 235048.55 | 80769852 | 99238121 | 49963524 | 0.000000 | 639036804 | 50166123 | 0.000000
10-04-2025 1:10:20000 | -3188841 | 31.8884 | 39856809 | 235090.73 | 78959373 | 99227928 | 49966778 | 0.000000 | 644688232 | 50614478 | 0.000000
10-04-2025 1:10:25000 | -2939220 | 29.3922 | 39921660 | 235195.61 | 72853806 | 99090164 | 50014687 | 0.000000 | 650320801 | 51037358 | 0.000000
10-04-2025 1:10:30000 | -2945518 | 29.4552 | 36299656 | 235072.75 | 72933563 | 99249176 | 50001472 | 0.000000 | 655487732 | 51443667 | 0.000000
10-04-2025 1:10:35000 | -2963317 | 29.6332 | 39450142 | 235162.11 | 73432884 | 99125450 | 50001720 | 0.000000 | 660826172 | 51856147 | 0.000000
10-04-2025 1:10:40000 | -2913521 | 29.1352 | 38189419 | 235127.17 | 72198158 | 99151863 | 50009960 | 0.000000 | 666189758 | 52261353 | 0.000000
10-04-2025 1:10:45000 | -2918517 | 29.1852 | 38691526 | 235131.84 | 72330109 | 99132645 | 50002628 | 0.000000 | 671473206 | 52666523 | 0.000000
10-04-2025 1:10:50000 | -2936682 | 29.3668 | 38134512 | 235113.78 | 72762222 | 99167389 | 50000298 | 0.000000 | 676770569 | 53074531 | 0.000000
10-04-2025 1:10:55000 | -2956130 | 29.5613 | 38580793 | 235146.53 | 73234673 | 99159073 | 49996742 | 0.000000 | 682008362 | 53486294 | 0.000000
10-04-2025 1:11:00000 | -2982263 | 29.8226 | 37764402 | 235100.86 | 73860573 | 99207756 | 49995731 | 0.000000 | 687333191 | 53900298 | 0.000000
10-04-2025 1:11:05000 | -2952313 | 29.5231 | 38189568 | 235112.09 | 73149490 | 99173721 | 49997753 | 0.000000 | 692607239 | 54310771 | 0.000000
10-04-2025 1:11:10000 | -3004172 | 30.0417 | 35534326 | 235011.84 | 74363281 | 99307709 | 49987232 | 0.000000 | 697663879 | 54723672 | 0.000000
10-04-2025 1:11:15000 | -3117120 | 31.1712 | 37062798 | 235012.41 | 77168182 | 99300537 | 49961166 | 0.000000 | 702617310 | 55154004 | 0.000000
10-04-2025 1:11:20000 | -2895922 | 28.9592 | 36383450 | 235102.59 | 71717522 | 99219994 | 50007469 | 0.000000 | 707853088 | 55567031 | 0.000000
10-04-2025 1:11:25000 | -2684886 | 26.8489 | 37872742 | 235219.28 | 66598068 | 99019722 | 50046677 | 0.000000 | 713056702 | 55950977 | 0.000000
10-04-2025 1:11:30000 | -2701563 | 27.0156 | 33211331 | 235055.88 | 66897293 | 99252823 | 50049992 | 0.000000 | 717906006 | 56323857 | 0.000000
10-04-2025 1:11:35000 | -2777884 | 27.7788 | 37511655 | 235105.64 | 68881248 | 99100533 | 50051617 | 0.000000 | 722878601 | 56705200 | 0.000000
10-04-2025 1:11:40000 | -2766470 | 27.6647 | 36750879 | 235075.03 | 68588989 | 99129135 | 50064331 | 0.000000 | 728172302 | 57089556 | 0.000000
10-04-2025 1:11:45000 | -2947535 | 29.4753 | 37316873 | 235035.23 | 73022804 | 99208084 | 50035267 | 0.000000 | 733355042 | 57486797 | 0.000000
10-04-2025 1:11:50000 | -3164104 | 31.641 | 40073428 | 235072.63 | 78379288 | 99207504 | 49991402 | 0.000000 | 738752136 | 57915322 | 0.000000
10-04-2025 1:11:55000 | -3197986 | 31.9799 | 40397126 | 235072.63 | 79201103 | 99211578 | 49978718 | 0.000000 | 744289429 | 58360190 | 0.000000
10-04-2025 1:12:00000 | -3083326 | 30.8333 | 38924360 | 235105.58 | 76354019 | 99212555 | 49998936 | 0.000000 | 749769409 | 58795591 | 0.000000
10-04-2025 1:12:05000 | -2896980 | 28.9698 | 38221555 | 235149.19 | 71783386 | 99140846 | 50029423 | 0.000000 | 755063538 | 59205908 | 0.000000
10-04-2025 1:12:10000 | -2798468 | 27.9847 | 37662942 | 235155.94 | 69367470 | 99106476 | 50042084 | 0.000000 | 760219788 | 59599565 | 0.000000
10-04-2025 1:12:15000 | -2864547 | 28.6455 | 38173755 | 235129.33 | 70996902 | 99123703 | 50023876 | 0.000000 | 765383911 | 59992739 | 0.000000
10-04-2025 1:12:20000 | -2915376 | 29.1538 | 37131011 | 235065.88 | 72223373 | 99198669 | 50013443 | 0.000000 | 770652588 | 60396235 | 0.000000
10-04-2025 1:12:25000 | -2978133 | 29.7813 | 37400122 | 235047.84 | 73768181 | 99220657 | 50000584 | 0.000000 | 775903687 | 60806284 | 0.000000
10-04-2025 1:12:30000 | -2971745 | 29.7174 | 37719543 | 235076.73 | 73608231 | 99204079 | 50003262 | 0.000000 | 781187866 | 61219692 | 0.000000
10-04-2025 1:12:35000 | -2838883 | 28.3888 | 39056533 | 235171.81 | 70390388 | 99066856 | 50032116 | 0.000000 | 786511536 | 61623618 | 0.000000
10-04-2025 1:12:40000 | -2646913 | 26.4691 | 41019038 | 235313.70 | 65764282 | 98820427 | 50074871 | 0.000000 | 791952087 | 62003232 | 0.000000
10-04-2025 1:12:45000 | -2514315 | 25.1431 | 43350049 | 235342.58 | 62635818 | 98546028 | 50117695 | 0.000000 | 797907471 | 62357256 | 0.000000
10-04-2025 1:12:50000 | -2521181 | 25.2118 | 42417446 | 235300.11 | 62781086 | 98614044 | 50108574 | 0.000000 | 803827759 | 62706499 | 0.000000
10-04-2025 1:12:55000 | -2737625 | 27.3762 | 45548730 | 235297.70 | 68138313 | 98643967 | 50086506 | 0.000000 | 809939209 | 63074116 | 0.000000
10-04-2025 1:13:00000 | -2847089 | 28.4709 | 47840239 | 235342.89 | 70866692 | 98617470 | 50073269 | 0.000000 | 816485046 | 63462495 | 0.000000
10-04-2025 1:13:05000 | -2868352 | 28.6835 | 49306631 | 235393.73 | 71421700 | 98554497 | 50085205 | 0.000000 | 823260193 | 63863042 | 0.000000
10-04-2025 1:13:10000 | -2831682 | 28.3168 | 47095835 | 235303.84 | 70471779 | 98644974 | 50094208 | 0.000000 | 830014221 | 64259063 | 0.000000
10-04-2025 1:13:15000 | -2876770 | 28.7677 | 47769258 | 235325.58 | 71582626 | 98649216 | 50083675 | 0.000000 | 836550537 | 64653394 | 0.000000
10-04-2025 1:13:20000 | -2936110 | 29.3611 | 48384409 | 235354.63 | 73035599 | 98669243 | 50074314 | 0.000000 | 843221497 | 65058818 | 0.000000
10-04-2025 1:13:25000 | -2923310 | 29.2331 | 48482432 | 235386.84 | 72718666 | 98652466 | 50075142 | 0.000000 | 849922974 | 65464619 | 0.000000
10-04-2025 1:13:30000 | -2881969 | 28.8197 | 48318926 | 235355.63 | 71728806 | 98623466 | 50092834 | 0.000000 | 856673645 | 65866582 | 0.000000
10-04-2025 1:13:35000 | -2866156 | 28.6616 | 47019937 | 235317.47 | 71299629 | 98680908 | 50082321 | 0.000000 | 863268799 | 66263418 | 0.000000
10-04-2025 1:13:40000 | -2989053 | 29.8905 | 45444517 | 235275.16 | 74228226 | 98863899 | 50060257 | 0.000000 | 869692688 | 66671792 | 0.000000
10-04-2025 1:13:45000 | -3138642 | 31.3864 | 44181592 | 235142.95 | 77859032 | 99023720 | 50037235 | 0.000000 | 876056580 | 67097891 | 0.000000
10-04-2025 1:13:50000 | -3210078 | 32.1008 | 43858955 | 235175.45 | 79574516 | 99079491 | 50006573 | 0.000000 | 882057129 | 67540444 | 0.000000
10-04-2025 1:13:55000 | -3128151 | 31.2815 | 41399258 | 235155.89 | 77511749 | 99135590 | 50016819 | 0.000000 | 888114136 | 67978643 | 0.000000
10-04-2025 1:14:00000 | -3029462 | 30.2946 | 40097222 | 235155.33 | 75066971 | 99135414 | 50016800 | 0.000000 | 893753052 | 68405327 | 0.000000
10-04-2025 1:14:05000 | -2975769 | 29.7577 | 38836294 | 235149.67 | 73728523 | 99159103 | 50019951 | 0.000000 | 899205627 | 68821470 | 0.000000
10-04-2025 1:14:10000 | -2919725 | 29.1973 | 38834939 | 235173.13 | 72352547 | 99126999 | 50033993 | 0.000000 | 904564819 | 69230444 | 0.000000
10-04-2025 1:14:15000 | -2878239 | 28.7824 | 39208091 | 235164.52 | 71363976 | 99084885 | 50042118 | 0.000000 | 909940002 | 69634214 | 0.000000
10-04-2025 1:14:20000 | -2914556 | 29.1456 | 38845972 | 235135.73 | 72240158 | 99123451 | 50031731 | 0.000000 | 915332581 | 70036123 | 0.000000
10-04-2025 1:14:25000 | -2954751 | 29.5475 | 39907183 | 235160.91 | 73242889 | 99100220 | 50024906 | 0.000000 | 920779968 | 70445811 | 0.000000
10-04-2025 1:14:30000 | -2928677 | 29.2868 | 38329741 | 235121.58 | 72566582 | 99154404 | 50029617 | 0.000000 | 926167664 | 70855664 | 0.000000
10-04-2025 1:14:35000 | -2847330 | 28.4733 | 38458918 | 235157.13 | 70580879 | 99100098 | 50047726 | 0.000000 | 931473389 | 71255649 | 0.000000
10-04-2025 1:14:40000 | -2804418 | 28.0442 | 38342468 | 235164.59 | 69536316 | 99078262 | 50052700 | 0.000000 | 936848877 | 71644819 | 0.000000
10-04-2025 1:14:45000 | -2861161 | 28.6116 | 37826545 | 235109.89 | 70914719 | 99137360 | 50042759 | 0.000000 | 942139038 | 72037441 | 0.000000
10-04-2025 1:14:50000 | -2854498 | 28.545 | 39021240 | 235155.55 | 70776451 | 99078537 | 50044044 | 0.000000 | 947638489 | 72434297 | 0.000000
10-04-2025 1:14:55000 | -2868844 | 28.6884 | 39333660 | 235147.19 | 71140358 | 99073143 | 50032990 | 0.000000 | 953088440 | 72832227 | 0.000000
10-04-2025 1:15:00000 | -2968100 | 29.681 | 39228245 | 235105.48 | 73566475 | 99137886 | 50023697 | 0.000000 | 958645264 | 73235532 | 0.000000
10-04-2025 1:15:05000 | -3078308 | 30.7831 | 39003213 | 235057.27 | 76259087 | 99206848 | 49994511 | 0.000000 | 5437893 | 42129349 | 0.000000
10-04-2025 1:15:10000 | -3093183 | 30.9318 | 39036892 | 235058.27 | 76616760 | 99213028 | 49985062 | 0.000000 | 10825765 | 85362122 | 0.000000
10-04-2025 1:15:15000 | -2956633 | 29.5663 | 39754583 | 235196.47 | 73274078 | 99108116 | 50012119 | 0.000000 | 16235415 | 127629715 | 0.000000
10-04-2025 1:15:20000 | -2923614 | 29.2361 | 36390630 | 235102.59 | 72386787 | 99234230 | 50012691 | 0.000000 | 21370798 | 168440979 | 0.000000
10-04-2025 1:15:25000 | -2879714 | 28.7971 | 38475388 | 235166.55 | 71368324 | 99119217 | 50020203 | 0.000000 | 26674936 | 208606674 | 0.000000
10-04-2025 1:15:30000 | -2844305 | 28.443 | 38649409 | 235153.36 | 70527672 | 99089378 | 50025528 | 0.000000 | 32029579 | 248264008 | 0.000000
10-04-2025 1:15:35000 | -2782389 | 27.8239 | 38957483 | 235175.53 | 69019203 | 99033981 | 50043999 | 0.000000 | 37449986 | 287176727 | 0.000000
10-04-2025 1:15:40000 | -2808004 | 28.08 | 38384739 | 235151.14 | 69627609 | 99078583 | 50049667 | 0.000000 | 42825062 | 326171906 | 0.000000
10-04-2025 1:15:45000 | -2832437 | 28.3244 | 38962510 | 235133.16 | 70251846 | 99067108 | 50051285 | 0.000000 | 48203049 | 365312836 | 0.000000
10-04-2025 1:15:50000 | -2925001 | 29.25 | 37742825 | 235060.38 | 72474403 | 99177750 | 50044392 | 0.000000 | 53498482 | 405598846 | 0.000000
10-04-2025 1:15:55000 | -2913435 | 29.1344 | 40719121 | 235181.25 | 72268120 | 99037392 | 50053501 | 0.000000 | 59019520 | 446207489 | 0.000000
10-04-2025 1:16:00000 | -2873784 | 28.7378 | 38107869 | 235132.73 | 71222382 | 99132217 | 50053844 | 0.000000 | 64386345 | 486332031 | 0.000000
10-04-2025 1:16:05000 | -2902631 | 29.0263 | 38231653 | 235101.48 | 71943375 | 99143700 | 50044865 | 0.000000 | 69820534 | 526338989 | 0.000000
10-04-2025 1:16:10000 | -2947062 | 29.4706 | 41045698 | 235201.91 | 73083344 | 99043983 | 50037434 | 0.000000 | 75329865 | 567068176 | 0.000000
10-04-2025 1:16:15000 | -2926269 | 29.2627 | 40395840 | 235165.58 | 72567886 | 99060577 | 50056416 | 0.000000 | 80983818 | 607825378 | 0.000000
10-04-2025 1:16:20000 | -2883016 | 28.8302 | 38764041 | 235129.95 | 71478287 | 99108147 | 50054245 | 0.000000 | 86518539 | 648119690 | 0.000000
10-04-2025 1:16:25000 | -2828445 | 28.2844 | 39788928 | 235184.16 | 70162796 | 99024986 | 50058765 | 0.000000 | 92081192 | 687708008 | 0.000000
10-04-2025 1:16:30000 | -2929792 | 29.2979 | 41096167 | 235176.48 | 72677971 | 99030502 | 50040302 | 0.000000 | 97726250 | 727793640 | 0.000000
10-04-2025 1:16:35000 | -2990894 | 29.9089 | 41037778 | 235140.70 | 74168747 | 99071770 | 50031116 | 0.000000 | 103439377 | 769110107 | 0.000000
10-04-2025 1:16:40000 | -3006494 | 30.0649 | 41785640 | 235225.36 | 74540886 | 99047935 | 50024689 | 0.000000 | 109103615 | 811070862 | 0.000000
10-04-2025 1:16:45000 | -3030508 | 30.3051 | 41941816 | 235187.02 | 75139793 | 99055832 | 50023323 | 0.000000 | 114778717 | 853316406 | 0.000000
10-04-2025 1:16:50000 | -3104316 | 31.0432 | 40021006 | 235133.80 | 76896782 | 99179192 | 50007069 | 0.000000 | 120372231 | 896066345 | 0.000000
10-04-2025 1:16:55000 | -3057873 | 30.5787 | 39554736 | 235135.66 | 75746147 | 99173737 | 50007278 | 0.000000 | 125937347 | 938847290 | 0.000000
10-04-2025 1:17:00000 | -2877904 | 28.779 | 39988975 | 235208.41 | 71367218 | 99048378 | 50041794 | 0.000000 | 131461334 | 979917603 | 0.000000
10-04-2025 1:17:05000 | -2801636 | 28.0164 | 36962229 | 235128.06 | 69433380 | 99140907 | 50058208 | 0.000000 | 136815948 | 10188953 | 0.000000
10-04-2025 1:17:10000 | -2873127 | 28.7313 | 39074885 | 235146.80 | 71234406 | 99087814 | 50047592 | 0.000000 | 142123123 | 10586356 | 0.000000
10-04-2025 1:17:15000 | -2792495 | 27.9249 | 40478853 | 235228.52 | 69296120 | 98965660 | 50060711 | 0.000000 | 147548889 | 10981936 | 0.000000
10-04-2025 1:17:20000 | -2786392 | 27.8639 | 40543145 | 235213.33 | 69163071 | 98957947 | 50080040 | 0.000000 | 153112244 | 11368578 | 0.000000
10-04-2025 1:17:25000 | -2952535 | 29.5253 | 39016379 | 235091.13 | 73186935 | 99138153 | 50051643 | 0.000000 | 158499741 | 11768469 | 0.000000
10-04-2025 1:17:30000 | -3003022 | 30.0302 | 39789717 | 235131.98 | 74425117 | 99133591 | 50039982 | 0.000000 | 164069122 | 12181377 | 0.000000
10-04-2025 1:17:35000 | -3085752 | 30.8575 | 40199163 | 235112.83 | 76458344 | 99162094 | 50023968 | 0.000000 | 169637589 | 12604998 | 0.000000
10-04-2025 1:17:40000 | -3053743 | 30.5374 | 40811985 | 235173.42 | 75675163 | 99118729 | 50025414 | 0.000000 | 175193512 | 13032156 | 0.000000
10-04-2025 1:17:45000 | -3022974 | 30.2297 | 38607139 | 235093.47 | 74891960 | 99194321 | 50011543 | 0.000000 | 180642899 | 13451855 | 0.000000
10-04-2025 1:17:50000 | -2947188 | 29.4719 | 40213806 | 235175.73 | 73061989 | 99081894 | 50037613 | 0.000000 | 186252701 | 13866135 | 0.000000
10-04-2025 1:17:55000 | -2969099 | 29.691 | 38023550 | 235107.39 | 73549103 | 99189926 | 50027206 | 0.000000 | 191582123 | 14277437 | 0.000000
10-04-2025 1:18:00000 | -2963669 | 29.6367 | 40512510 | 235172.08 | 73478371 | 99078590 | 50028145 | 0.000000 | 197113663 | 14690326 | 0.000000
10-04-2025 1:18:05000 | -2771399 | 27.714 | 40751440 | 235235.08 | 68800941 | 98936142 | 50068634 | 0.000000 | 202843536 | 15085477 | 0.000000
10-04-2025 1:18:10000 | -2825276 | 28.2528 | 39051599 | 235151.70 | 70066544 | 99058205 | 50060131 | 0.000000 | 208344894 | 15471386 | 0.000000
10-04-2025 1:18:15000 | -2941746 | 29.4175 | 41294614 | 235196.06 | 72954346 | 99029076 | 50041061 | 0.000000 | 213784119 | 15876410 | 0.000000
10-04-2025 1:18:20000 | -2961377 | 29.6138 | 39180684 | 235117.86 | 73393837 | 99136086 | 50045223 | 0.000000 | 219442139 | 16286558 | 0.000000
10-04-2025 1:18:25000 | -3010337 | 30.1034 | 38952361 | 235133.66 | 74566818 | 99173210 | 50026176 | 0.000000 | 224800156 | 16702892 | 0.000000
10-04-2025 1:18:30000 | -2969958 | 29.6996 | 42651143 | 235237.84 | 73672211 | 98984512 | 50048660 | 0.000000 | 230476883 | 17119012 | 0.000000
10-04-2025 1:18:35000 | -2869475 | 28.6947 | 40998184 | 235221.64 | 71184853 | 98994675 | 50062878 | 0.000000 | 236162872 | 17523398 | 0.000000
10-04-2025 1:18:40000 | -2896059 | 28.9606 | 39841062 | 235150.53 | 71818123 | 99066948 | 50053341 | 0.000000 | 241679703 | 17925341 | 0.000000
10-04-2025 1:18:45000 | -2881628 | 28.8163 | 42453848 | 235262.16 | 71533478 | 98932106 | 50054794 | 0.000000 | 247214828 | 18330262 | 0.000000
10-04-2025 1:18:50000 | -2881162 | 28.8116 | 40948806 | 235185.83 | 71480209 | 99005058 | 50054367 | 0.000000 | 252914917 | 18730336 | 0.000000
10-04-2025 1:18:55000 | -2971440 | 29.7144 | 39932236 | 235122.86 | 73660614 | 99109062 | 50040134 | 0.000000 | 258500916 | 19137419 | 0.000000
10-04-2025 1:19:00000 | -3080559 | 30.8056 | 39123423 | 235092.81 | 76301544 | 99203163 | 50012840 | 0.000000 | 263884705 | 19562577 | 0.000000
10-04-2025 1:19:05000 | -3074049 | 30.7405 | 38189973 | 235087.02 | 76114433 | 99237122 | 50009220 | 0.000000 | 269218384 | 19990874 | 0.000000
10-04-2025 1:19:10000 | -2862931 | 28.6293 | 41760205 | 235287.50 | 71026985 | 98952850 | 50030502 | 0.000000 | 274680115 | 20404917 | 0.000000
10-04-2025 1:19:15000 | -2796884 | 27.9688 | 36443247 | 235138.09 | 69294197 | 99161758 | 50050812 | 0.000000 | 279979065 | 20792952 | 0.000000
10-04-2025 1:19:20000 | -2904269 | 29.0427 | 39009939 | 235135.22 | 71990417 | 99109940 | 50039852 | 0.000000 | 285226532 | 21192095 | 0.000000
10-04-2025 1:19:25000 | -2906552 | 29.0655 | 37160762 | 235125.89 | 71987854 | 99192581 | 50047485 | 0.000000 | 290531219 | 21594495 | 0.000000
10-04-2025 1:19:30000 | -2878521 | 28.7852 | 36217058 | 235043.58 | 71306999 | 99217766 | 50045944 | 0.000000 | 295794189 | 21994727 | 0.000000
10-04-2025 1:19:35000 | -2848542 | 28.4854 | 36522263 | 235098.92 | 70557625 | 99188057 | 50044086 | 0.000000 | 300815918 | 22394763 | 0.000000
10-04-2025 1:19:40000 | -2835400 | 28.354 | 34702397 | 235013.53 | 70220078 | 99259346 | 50065510 | 0.000000 | 305885712 | 22784873 | 0.000000
10-04-2025 1:19:45000 | -2991291 | 29.9129 | 36576475 | 235041.95 | 74061867 | 99260704 | 50037842 | 0.000000 | 310725098 | 23192751 | 0.000000
10-04-2025 1:19:50000 | -2977972 | 29.7797 | 36969453 | 235068.97 | 73740547 | 99238220 | 50040737 | 0.000000 | 315780975 | 23608667 | 0.000000
10-04-2025 1:19:55000 | -2956738 | 29.5674 | 35327627 | 235032.84 | 73191177 | 99293755 | 50040215 | 0.000000 | 320739258 | 24023823 | 0.000000
10-04-2025 1:20:00000 | -2941675 | 29.4168 | 34780715 | 235067.05 | 72796211 | 99308273 | 50048676 | 0.000000 | 325548767 | 24433921 | 0.000000
10-04-2025 1:20:05000 | -2857460 | 28.5746 | 37078652 | 235136.58 | 70787155 | 99168587 | 50073215 | 0.000000 | 330542511 | 24837708 | 0.000000
10-04-2025 1:20:10000 | -2740660 | 27.4066 | 34397480 | 235099.23 | 67874550 | 99221573 | 50093945 | 0.000000 | 335524139 | 25224214 | 0.000000
10-04-2025 1:20:15000 | -2797069 | 27.9707 | 34928206 | 235055.03 | 69278976 | 99229324 | 50093819 | 0.000000 | 340395721 | 25606514 | 0.000000
10-04-2025 1:20:20000 | -2937200 | 29.372 | 36657017 | 235037.09 | 72745552 | 99230194 | 50066353 | 0.000000 | 345395630 | 26008530 | 0.000000
10-04-2025 1:20:25000 | -2990806 | 29.9081 | 37276665 | 235060.27 | 74063324 | 99232208 | 50065540 | 0.000000 | 350528656 | 26421707 | 0.000000
10-04-2025 1:20:30000 | -2999921 | 29.9992 | 35900088 | 235003.63 | 74263252 | 99291557 | 50064823 | 0.000000 | 355696686 | 26837935 | 0.000000
10-04-2025 1:20:35000 | -2989034 | 29.8903 | 34316125 | 234980.17 | 73961548 | 99347412 | 50070961 | 0.000000 | 360718689 | 27252856 | 0.000000
10-04-2025 1:20:40000 | -3020633 | 30.2063 | 33658452 | 234987.95 | 74712585 | 99384911 | 50061623 | 0.000000 | 365465302 | 27667744 | 0.000000
10-04-2025 1:20:45000 | -3113916 | 31.1392 | 34241101 | 234956.84 | 77017654 | 99400848 | 50033649 | 0.000000 | 370171326 | 28097598 | 0.000000
10-04-2025 1:20:50000 | -3104952 | 31.0495 | 34806367 | 234999.66 | 76798584 | 99377548 | 50036743 | 0.000000 | 374934387 | 28532271 | 0.000000
10-04-2025 1:20:55000 | -3014192 | 30.1419 | 33204358 | 234985.44 | 74541985 | 99398705 | 50031788 | 0.000000 | 379538483 | 28956267 | 0.000000
10-04-2025 1:21:00000 | -2953071 | 29.5307 | 32218904 | 234969.86 | 73033119 | 99410088 | 50035225 | 0.000000 | 384062073 | 29369526 | 0.000000
10-04-2025 1:21:05000 | -2902231 | 29.0223 | 33429282 | 235017.11 | 71806610 | 99343155 | 50051174 | 0.000000 | 388761902 | 29774558 | 0.000000
10-04-2025 1:21:10000 | -2903275 | 29.0328 | 33446853 | 235003.45 | 71838791 | 99342934 | 50044861 | 0.000000 | 393344574 | 30178145 | 0.000000
10-04-2025 1:21:15000 | -2848340 | 28.4834 | 35775649 | 235094.27 | 70544525 | 99220421 | 50059589 | 0.000000 | 398188141 | 30581028 | 0.000000
10-04-2025 1:21:20000 | -2809996 | 28.1 | 34255713 | 235058.03 | 69567902 | 99265121 | 50055550 | 0.000000 | 402942505 | 30975408 | 0.000000
10-04-2025 1:21:25000 | -2870102 | 28.701 | 33273757 | 235006.41 | 71033157 | 99334686 | 50054401 | 0.000000 | 407608429 | 31371433 | 0.000000
10-04-2025 1:21:30000 | -3002154 | 30.0215 | 32298145 | 234926.72 | 74245323 | 99426270 | 50025501 | 0.000000 | 412156067 | 31780657 | 0.000000
10-04-2025 1:21:35000 | -2957115 | 29.5711 | 33380723 | 234979.81 | 73161919 | 99368896 | 50042736 | 0.000000 | 416806305 | 32195649 | 0.000000
10-04-2025 1:21:40000 | -2804239 | 28.0424 | 33885229 | 235051.53 | 69417633 | 99277832 | 50069679 | 0.000000 | 421470215 | 32594185 | 0.000000
10-04-2025 1:21:45000 | -2783703 | 27.837 | 32302043 | 235012.03 | 68884308 | 99333458 | 50081528 | 0.000000 | 425929657 | 32980632 | 0.000000
10-04-2025 1:21:50000 | -2681131 | 26.8113 | 39402100 | 235270.16 | 66539894 | 98937309 | 50116947 | 0.000000 | 430920898 | 33364688 | 0.000000
10-04-2025 1:21:55000 | -2606284 | 26.0628 | 38000303 | 235178.72 | 64703995 | 98953735 | 50148392 | 0.000000 | 436382019 | 33725190 | 0.000000
10-04-2025 1:22:00000 | -2705687 | 27.0569 | 39828323 | 235206.02 | 67180321 | 98933868 | 50124546 | 0.000000 | 441716309 | 34093303 | 0.000000
10-04-2025 1:22:05000 | -2758821 | 27.5882 | 44036880 | 235288.50 | 68593712 | 98749878 | 50128342 | 0.000000 | 447584961 | 34475859 | 0.000000
10-04-2025 1:22:10000 | -2999080 | 29.9908 | 42289458 | 235146.53 | 74409317 | 99020416 | 50094166 | 0.000000 | 453516479 | 34876938 | 0.000000
10-04-2025 1:22:15000 | -3044248 | 30.4425 | 44861992 | 235244.03 | 75554497 | 98931526 | 50087708 | 0.000000 | 459659515 | 35301084 | 0.000000
10-04-2025 1:22:20000 | -2872562 | 28.7256 | 44927305 | 235326.08 | 71376831 | 98798920 | 50133743 | 0.000000 | 465860443 | 35709697 | 0.000000
10-04-2025 1:22:25000 | -2811214 | 28.1121 | 40793267 | 235194.22 | 69774475 | 98963509 | 50138161 | 0.000000 | 471832306 | 36099590 | 0.000000
10-04-2025 1:22:30000 | -2961826 | 29.6183 | 44076382 | 235240.47 | 73534004 | 98910767 | 50098503 | 0.000000 | 477717682 | 36503445 | 0.000000
10-04-2025 1:22:35000 | -2967585 | 29.6759 | 45120957 | 235265.33 | 73701210 | 98863762 | 50103069 | 0.000000 | 483919342 | 36915229 | 0.000000
10-04-2025 1:22:40000 | -2875235 | 28.7523 | 44067505 | 235282.23 | 71419235 | 98845779 | 50126900 | 0.000000 | 490110077 | 37321719 | 0.000000
10-04-2025 1:22:45000 | -2802041 | 28.0204 | 45354111 | 235337.56 | 69679398 | 98715240 | 50144936 | 0.000000 | 496337799 | 37712869 | 0.000000
10-04-2025 1:22:50000 | -2902411 | 29.0241 | 43956035 | 235227.83 | 72090332 | 98872551 | 50134079 | 0.000000 | 502525574 | 38108364 | 0.000000
10-04-2025 1:22:55000 | -3242784 | 32.4278 | 41355933 | 235057.50 | 80333893 | 99196564 | 50055443 | 0.000000 | 508248779 | 38542502 | 0.000000
10-04-2025 1:23:00000 | -3329877 | 33.2988 | 43352002 | 235143.64 | 82489075 | 99163139 | 50031750 | 0.000000 | 514259888 | 39003330 | 0.000000
10-04-2025 1:23:05000 | -3263310 | 32.6331 | 41208936 | 235119.70 | 80803497 | 99212082 | 50048092 | 0.000000 | 520195984 | 39460669 | 0.000000
10-04-2025 1:23:10000 | -3124977 | 31.2498 | 40539011 | 235173.88 | 77399025 | 99169037 | 50061466 | 0.000000 | 525852966 | 39902805 | 0.000000
10-04-2025 1:23:15000 | -2971267 | 29.7127 | 40287168 | 235197.20 | 73646614 | 99093262 | 50078098 | 0.000000 | 531469055 | 40325486 | 0.000000
10-04-2025 1:23:20000 | -2929529 | 29.2953 | 36901536 | 235098.30 | 72555847 | 99215973 | 50077934 | 0.000000 | 536708435 | 40734236 | 0.000000
10-04-2025 1:23:25000 | -2935183 | 29.3518 | 37439199 | 235121.09 | 72696526 | 99196304 | 50076309 | 0.000000 | 541863037 | 41142412 | 0.000000
10-04-2025 1:23:30000 | -2935537 | 29.3554 | 39357480 | 235164.89 | 72755142 | 99113167 | 50071392 | 0.000000 | 547132568 | 41553296 | 0.000000
10-04-2025 1:23:35000 | -3060846 | 30.6085 | 36784033 | 235033.23 | 75778328 | 99285614 | 50048557 | 0.000000 | 552289551 | 41970508 | 0.000000
10-04-2025 1:23:40000 | -3157330 | 31.5733 | 35759294 | 234987.20 | 78111526 | 99364738 | 50015995 | 0.000000 | 557221558 | 42405513 | 0.000000
10-04-2025 1:23:45000 | -3093473 | 30.9347 | 36926409 | 235066.23 | 76555351 | 99295082 | 50031544 | 0.000000 | 562329529 | 42840522 | 0.000000
10-04-2025 1:23:50000 | -2873713 | 28.7371 | 35138140 | 235084.84 | 71143227 | 99260727 | 50066051 | 0.000000 | 567361023 | 43250669 | 0.000000
10-04-2025 1:23:55000 | -2757553 | 27.5755 | 35388213 | 235111.69 | 68315125 | 99186577 | 50086082 | 0.000000 | 572187500 | 43636187 | 0.000000
10-04-2025 1:24:00000 | -2896598 | 28.966 | 34727209 | 235037.55 | 71706718 | 99288979 | 50066154 | 0.000000 | 576924866 | 44028818 | 0.000000
10-04-2025 1:24:05000 | -2982986 | 29.8299 | 36767671 | 235050.92 | 73863380 | 99248924 | 50045231 | 0.000000 | 581893188 | 44441343 | 0.000000
10-04-2025 1:24:10000 | -2979245 | 29.7924 | 36378081 | 235064.91 | 73755676 | 99262749 | 50055679 | 0.000000 | 587030273 | 44855054 | 0.000000
10-04-2025 1:24:15000 | -3073890 | 30.7389 | 35929385 | 235039.61 | 76061493 | 99323807 | 50034195 | 0.000000 | 591922119 | 45275938 | 0.000000
10-04-2025 1:24:20000 | -3031880 | 30.3188 | 35883279 | 235035.44 | 75040466 | 99306900 | 50031311 | 0.000000 | 596988708 | 45698003 | 0.000000
10-04-2025 1:24:25000 | -2983602 | 29.836 | 34682327 | 235015.36 | 73830009 | 99331146 | 50031567 | 0.000000 | 601800293 | 46118320 | 0.000000
10-04-2025 1:24:30000 | -2868061 | 28.6806 | 33539819 | 235050.34 | 70967056 | 99323158 | 50052086 | 0.000000 | 606469910 | 46524414 | 0.000000
10-04-2025 1:24:35000 | -2735348 | 27.3535 | 32405750 | 235037.77 | 67706604 | 99305542 | 50086700 | 0.000000 | 611007507 | 46907656 | 0.000000
10-04-2025 1:24:40000 | -2823737 | 28.2374 | 31927415 | 234983.98 | 69862251 | 99366844 | 50076141 | 0.000000 | 615467773 | 47291890 | 0.000000
10-04-2025 1:24:45000 | -2921735 | 29.2173 | 32158247 | 234951.05 | 72269394 | 99399727 | 50054306 | 0.000000 | 619959595 | 47693242 | 0.000000
10-04-2025 1:24:50000 | -2975126 | 29.7513 | 32043811 | 234931.11 | 73578789 | 99424973 | 50050743 | 0.000000 | 624600464 | 48102813 | 0.000000
10-04-2025 1:24:55000 | -3043688 | 30.4369 | 32923000 | 234939.42 | 75270538 | 99420067 | 50044617 | 0.000000 | 629224670 | 48521523 | 0.000000
10-04-2025 1:25:00000 | -3068743 | 30.6874 | 32316191 | 234933.38 | 75870361 | 99450089 | 50037960 | 0.000000 | 633775696 | 48946641 | 0.000000
10-04-2025 1:25:05000 | -3042797 | 30.428 | 32649788 | 234975.14 | 75227943 | 99429237 | 50041454 | 0.000000 | 638265930 | 49370542 | 0.000000
10-04-2025 1:25:10000 | -2968985 | 29.6898 | 31716589 | 234958.48 | 73409500 | 99434242 | 50062450 | 0.000000 | 642824524 | 49786748 | 0.000000
10-04-2025 1:25:15000 | -2871589 | 28.7159 | 32836660 | 235019.41 | 71046638 | 99352547 | 50079823 | 0.000000 | 647349060 | 50190488 | 0.000000
10-04-2025 1:25:20000 | -2814245 | 28.1425 | 32255142 | 234999.23 | 69642143 | 99349586 | 50080696 | 0.000000 | 651734863 | 50586289 | 0.000000
10-04-2025 1:25:25000 | -2842723 | 28.4272 | 32129236 | 234987.19 | 70340706 | 99367348 | 50076321 | 0.000000 | 656124573 | 50980781 | 0.000000
10-04-2025 1:25:30000 | -2919250 | 29.1925 | 31213257 | 234911.77 | 72200516 | 99433235 | 50063992 | 0.000000 | 660509949 | 51382339 | 0.000000
10-04-2025 1:25:35000 | -2920144 | 29.2014 | 32669983 | 234987.23 | 72231331 | 99379982 | 50060741 | 0.000000 | 664884216 | 51787798 | 0.000000
10-04-2025 1:25:40000 | -2979388 | 29.7939 | 31903450 | 234938.97 | 73675484 | 99431572 | 50050686 | 0.000000 | 669215881 | 52199678 | 0.000000
10-04-2025 1:25:45000 | -2990635 | 29.9063 | 33950100 | 234995.47 | 73982224 | 99361809 | 50055706 | 0.000000 | 673758728 | 52615210 | 0.000000
10-04-2025 1:25:50000 | -2989576 | 29.8958 | 32641274 | 234970.20 | 73931175 | 99409225 | 50045811 | 0.000000 | 678316040 | 53031514 | 0.000000
10-04-2025 1:25:55000 | -3108411 | 31.0841 | 32157573 | 234909.83 | 76842529 | 99469124 | 50023380 | 0.000000 | 682742004 | 53454878 | 0.000000
10-04-2025 1:26:00000 | -3105070 | 31.0507 | 32376038 | 234942.77 | 76754745 | 99460800 | 50023758 | 0.000000 | 687172424 | 53888779 | 0.000000
10-04-2025 1:26:05000 | -2979435 | 29.7944 | 31058662 | 234940.72 | 73653824 | 99461052 | 50043262 | 0.000000 | 691627686 | 54308169 | 0.000000
10-04-2025 1:26:10000 | -2973832 | 29.7383 | 29768867 | 234913.94 | 73496849 | 99502708 | 50037685 | 0.000000 | 695761230 | 54721777 | 0.000000
10-04-2025 1:26:15000 | -2892909 | 28.9291 | 31102400 | 234992.45 | 71524284 | 99427017 | 50054722 | 0.000000 | 700049255 | 55129980 | 0.000000
10-04-2025 1:26:20000 | -2845025 | 28.4503 | 30587400 | 234945.97 | 70355537 | 99427025 | 50057667 | 0.000000 | 704266968 | 55527319 | 0.000000
10-04-2025 1:26:25000 | -2832384 | 28.3238 | 32371765 | 235020.48 | 70071548 | 99353203 | 50065357 | 0.000000 | 708707947 | 55922095 | 0.000000
10-04-2025 1:26:30000 | -2804246 | 28.0425 | 30906506 | 234920.25 | 69385269 | 99398132 | 50072132 | 0.000000 | 713199646 | 56311499 | 0.000000
10-04-2025 1:26:35000 | -2846127 | 28.4613 | 33762925 | 235048.69 | 70437187 | 99303719 | 50073505 | 0.000000 | 717770752 | 56702456 | 0.000000
10-04-2025 1:26:40000 | -2917308 | 29.1731 | 33628730 | 234976.94 | 72190926 | 99342155 | 50076637 | 0.000000 | 722515564 | 57101675 | 0.000000
10-04-2025 1:26:45000 | -2969203 | 29.692 | 32602122 | 234934.63 | 73445732 | 99402588 | 50062141 | 0.000000 | 727080139 | 57510576 | 0.000000
10-04-2025 1:26:50000 | -3007559 | 30.0756 | 35737297 | 235051.92 | 74431648 | 99301422 | 50057949 | 0.000000 | 731770813 | 57927061 | 0.000000
10-04-2025 1:26:55000 | -2975686 | 29.7569 | 35598579 | 235049.88 | 73648758 | 99292007 | 50071205 | 0.000000 | 736595581 | 58343325 | 0.000000
10-04-2025 1:27:00000 | -2869789 | 28.6979 | 35440105 | 235069.22 | 71060425 | 99246078 | 50088867 | 0.000000 | 741483521 | 58748779 | 0.000000
10-04-2025 1:27:05000 | -2877163 | 28.7716 | 33670391 | 235012.50 | 71202682 | 99322197 | 50084415 | 0.000000 | 746264404 | 59145132 | 0.000000
10-04-2025 1:27:10000 | -2924410 | 29.2441 | 35777676 | 235061.16 | 72404305 | 99259926 | 50073631 | 0.000000 | 751034668 | 59549604 | 0.000000
10-04-2025 1:27:15000 | -2951378 | 29.5138 | 33589385 | 234988.30 | 73021187 | 99358597 | 50069031 | 0.000000 | 755799011 | 59956333 | 0.000000
10-04-2025 1:27:20000 | -3040258 | 30.4026 | 34772942 | 234985.34 | 75220680 | 99352264 | 50046745 | 0.000000 | 760545410 | 60374204 | 0.000000
10-04-2025 1:27:25000 | -3048180 | 30.4818 | 34912898 | 235038.88 | 75403870 | 99350449 | 50055408 | 0.000000 | 765347534 | 60800840 | 0.000000
10-04-2025 1:27:30000 | -3014478 | 30.1448 | 33157200 | 234975.91 | 74555183 | 99400513 | 50058620 | 0.000000 | 770023987 | 61220791 | 0.000000
10-04-2025 1:27:35000 | -3011015 | 30.1102 | 33124084 | 234966.16 | 74467949 | 99400330 | 50065956 | 0.000000 | 774742737 | 61636445 | 0.000000
10-04-2025 1:27:40000 | -3119409 | 31.1941 | 33141882 | 234928.28 | 77128792 | 99440346 | 50036613 | 0.000000 | 779293274 | 62061675 | 0.000000
10-04-2025 1:27:45000 | -3073133 | 30.7313 | 35622739 | 235040.55 | 76034607 | 99334862 | 50040081 | 0.000000 | 784074402 | 62495313 | 0.000000
10-04-2025 1:27:50000 | -3026261 | 30.2626 | 32588469 | 234965.75 | 74827507 | 99425186 | 50032288 | 0.000000 | 788631287 | 62917788 | 0.000000
10-04-2025 1:27:55000 | -3033549 | 30.3355 | 30732434 | 234924.00 | 74976151 | 99490746 | 50011246 | 0.000000 | 793011902 | 63339150 | 0.000000
10-04-2025 1:28:00000 | -3005872 | 30.0587 | 32186216 | 234992.17 | 74314064 | 99431602 | 50026524 | 0.000000 | 797468384 | 63761934 | 0.000000
10-04-2025 1:28:05000 | -2871812 | 28.7181 | 31664993 | 235010.16 | 71021484 | 99397606 | 50052303 | 0.000000 | 801846985 | 64170864 | 0.000000
10-04-2025 1:28:10000 | -2767661 | 27.6766 | 30438723 | 234971.44 | 68456490 | 99400650 | 50079281 | 0.000000 | 806209351 | 64559917 | 0.000000
10-04-2025 1:28:15000 | -2772206 | 27.7221 | 30819600 | 234986.09 | 68580215 | 99387695 | 50075409 | 0.000000 | 810436646 | 64941353 | 0.000000
10-04-2025 1:28:20000 | -2800506 | 28.0051 | 31335442 | 234971.42 | 69279160 | 99379822 | 50090084 | 0.000000 | 814963806 | 65327559 | 0.000000
10-04-2025 1:28:25000 | -2885610 | 28.8561 | 32685913 | 234953.14 | 71403076 | 99364578 | 50074703 | 0.000000 | 819366455 | 65726816 | 0.000000
10-04-2025 1:28:30000 | -3024237 | 30.2424 | 30829185 | 234867.08 | 74768166 | 99484421 | 50052834 | 0.000000 | 823636963 | 66139023 | 0.000000
10-04-2025 1:28:35000 | -3053022 | 30.5302 | 33281064 | 234983.61 | 75501656 | 99411079 | 50059231 | 0.000000 | 828054016 | 66562876 | 0.000000
10-04-2025 1:28:40000 | -2881588 | 28.8159 | 31297527 | 234982.73 | 71261887 | 99415337 | 50091278 | 0.000000 | 832584534 | 66970303 | 0.000000
10-04-2025 1:28:45000 | -2875795 | 28.758 | 30632141 | 234967.73 | 71104202 | 99437485 | 50083355 | 0.000000 | 836747253 | 67369619 | 0.000000
10-04-2025 1:28:50000 | -2886854 | 28.8685 | 31833713 | 234988.28 | 71394333 | 99397499 | 50081123 | 0.000000 | 841001221 | 67771870 | 0.000000
10-04-2025 1:28:55000 | -2861404 | 28.614 | 30619575 | 234938.78 | 70757233 | 99432327 | 50090477 | 0.000000 | 845365173 | 68168398 | 0.000000
10-04-2025 1:29:00000 | -2946291 | 29.4629 | 30606321 | 234905.73 | 72844788 | 99464767 | 50066822 | 0.000000 | 849627380 | 68571787 | 0.000000
10-04-2025 1:29:05000 | -2950108 | 29.5011 | 33886130 | 235025.50 | 72990715 | 99346771 | 50072536 | 0.000000 | 854123230 | 68982046 | 0.000000
10-04-2025 1:29:10000 | -2863622 | 28.6362 | 32391523 | 235002.17 | 70840141 | 99366341 | 50088699 | 0.000000 | 858747314 | 69384604 | 0.000000
10-04-2025 1:29:15000 | -2872679 | 28.7268 | 33591584 | 235005.23 | 71092163 | 99323250 | 50081688 | 0.000000 | 863346252 | 69784893 | 0.000000
10-04-2025 1:29:20000 | -2903151 | 29.0315 | 33198638 | 235006.55 | 71827530 | 99352501 | 50078953 | 0.000000 | 867944092 | 70186577 | 0.000000
10-04-2025 1:29:25000 | -2756288 | 27.5629 | 34987605 | 235090.05 | 68279243 | 99203949 | 50113026 | 0.000000 | 872829224 | 70579385 | 0.000000
10-04-2025 1:29:30000 | -2781256 | 27.8126 | 34854546 | 235078.09 | 68878036 | 99223885 | 50108704 | 0.000000 | 877543884 | 70964575 | 0.000000
10-04-2025 1:29:35000 | -2966345 | 29.6635 | 33180552 | 234930.77 | 73392944 | 99380211 | 50079578 | 0.000000 | 882264832 | 71368130 | 0.000000
10-04-2025 1:29:40000 | -3066099 | 30.661 | 36539822 | 235050.63 | 75884911 | 99297356 | 50067039 | 0.000000 | 887157959 | 71787690 | 0.000000
10-04-2025 1:29:45000 | -3100363 | 31.0036 | 36796748 | 235051.31 | 76725189 | 99303047 | 50070080 | 0.000000 | 892285645 | 72215317 | 0.000000
10-04-2025 1:29:50000 | -3033119 | 30.3312 | 36082043 | 235066.39 | 75058014 | 99299843 | 50063747 | 0.000000 | 897357910 | 72639434 | 0.000000
10-04-2025 1:29:55000 | -3015745 | 30.1575 | 36441653 | 235065.47 | 74646217 | 99277809 | 50058540 | 0.000000 | 902418579 | 73058384 | 0.000000
10-04-2025 1:30:00000 | -2957695 | 29.577 | 38148743 | 235154.83 | 73252380 | 99178429 | 50070522 | 0.000000 | 907582520 | 73472056 | 0.000000
10-04-2025 1:30:05000 | -2871774 | 28.7177 | 37222097 | 235102.41 | 71151680 | 99170456 | 50081703 | 0.000000 | 5333381 | 40156513 | 0.000000
10-04-2025 1:30:10000 | -2891910 | 28.9191 | 38057454 | 235147.22 | 71663956 | 99145164 | 50073818 | 0.000000 | 10543284 | 80099854 | 0.000000
10-04-2025 1:30:15000 | -2943777 | 29.4378 | 39466506 | 235160.86 | 72961060 | 99113228 | 50065475 | 0.000000 | 15937324 | 120790245 | 0.000000
10-04-2025 1:30:20000 | -2935997 | 29.36 | 39128555 | 235133.44 | 72771629 | 99123589 | 50063065 | 0.000000 | 21442059 | 161625305 | 0.000000
10-04-2025 1:30:25000 | -2974958 | 29.7496 | 38266929 | 235101.66 | 73698700 | 99182838 | 50055889 | 0.000000 | 26830582 | 202901489 | 0.000000
10-04-2025 1:30:30000 | -3100993 | 31.0099 | 38449424 | 235069.34 | 76783997 | 99240067 | 50037159 | 0.000000 | 32166161 | 245519394 | 0.000000
10-04-2025 1:30:35000 | -3074210 | 30.7421 | 39042534 | 235103.84 | 76148720 | 99203171 | 50030773 | 0.000000 | 37579071 | 288538849 | 0.000000
10-04-2025 1:30:40000 | -3007816 | 30.0782 | 36539890 | 235085.13 | 74449173 | 99270164 | 50039219 | 0.000000 | 42698292 | 330490234 | 0.000000
10-04-2025 1:30:45000 | -2917088 | 29.1709 | 35808096 | 235088.61 | 72215172 | 99254997 | 50054489 | 0.000000 | 47724892 | 371493469 | 0.000000
10-04-2025 1:30:50000 | -2883861 | 28.8386 | 37053630 | 235114.36 | 71436249 | 99184647 | 50062679 | 0.000000 | 52730171 | 411581451 | 0.000000
10-04-2025 1:30:55000 | -2936576 | 29.3658 | 33973709 | 234997.89 | 72666367 | 99337418 | 50041634 | 0.000000 | 57554279 | 452065735 | 0.000000
10-04-2025 1:31:00000 | -2987306 | 29.8731 | 37680288 | 235098.78 | 73985359 | 99213867 | 50034809 | 0.000000 | 62678070 | 493211243 | 0.000000
10-04-2025 1:31:05000 | -3047581 | 30.4758 | 38289351 | 235074.80 | 75471947 | 99219971 | 50024776 | 0.000000 | 67915092 | 535321106 | 0.000000
10-04-2025 1:31:10000 | -3025336 | 30.2534 | 38132278 | 235110.34 | 74918137 | 99214996 | 50027679 | 0.000000 | 73186279 | 577910522 | 0.000000
10-04-2025 1:31:15000 | -2974819 | 29.7482 | 35557712 | 235048.91 | 73632996 | 99293205 | 50032776 | 0.000000 | 78219849 | 619477661 | 0.000000
10-04-2025 1:31:20000 | -2962290 | 29.6229 | 36234373 | 235067.45 | 73336807 | 99260201 | 50042885 | 0.000000 | 83254662 | 660751953 | 0.000000
10-04-2025 1:31:25000 | -2895886 | 28.9589 | 36473958 | 235095.91 | 71720627 | 99216133 | 50045612 | 0.000000 | 88327820 | 701427917 | 0.000000
10-04-2025 1:31:30000 | -2886276 | 28.8628 | 36226418 | 235058.11 | 71487694 | 99221512 | 50047897 | 0.000000 | 93448761 | 741300964 | 0.000000
10-04-2025 1:31:35000 | -2922754 | 29.2275 | 37447717 | 235084.63 | 72404739 | 99189171 | 50037014 | 0.000000 | 98582596 | 781626404 | 0.000000
10-04-2025 1:31:40000 | -3043701 | 30.437 | 34929036 | 234991.53 | 75314705 | 99347961 | 50017250 | 0.000000 | 103566521 | 823050415 | 0.000000
10-04-2025 1:31:45000 | -3097880 | 30.9788 | 36273569 | 235006.45 | 76676376 | 99321449 | 50010029 | 0.000000 | 108592285 | 865706848 | 0.000000
10-04-2025 1:31:50000 | -3130503 | 31.305 | 36758167 | 235035.33 | 77465240 | 99317680 | 49989243 | 0.000000 | 113726051 | 909120544 | 0.000000
10-04-2025 1:31:55000 | -3038322 | 30.3832 | 34708176 | 234982.22 | 75176758 | 99353836 | 50003273 | 0.000000 | 118798431 | 951870117 | 0.000000
10-04-2025 1:32:00000 | -2937105 | 29.3711 | 34826711 | 235070.28 | 72687149 | 99304329 | 50014786 | 0.000000 | 123671883 | 992936462 | 0.000000
10-04-2025 1:32:05000 | -2849512 | 28.4951 | 34453652 | 235049.91 | 70541077 | 99276947 | 50026230 | 0.000000 | 128539841 | 10328682 | 0.000000
10-04-2025 1:32:10000 | -2792920 | 27.9292 | 35966465 | 235126.88 | 69190636 | 99180992 | 50023952 | 0.000000 | 133433273 | 10719972 | 0.000000
10-04-2025 1:32:15000 | -2859363 | 28.5936 | 34762734 | 235026.67 | 70799202 | 99269066 | 50009041 | 0.000000 | 138355927 | 11112639 | 0.000000
10-04-2025 1:32:20000 | -2829301 | 28.293 | 36274778 | 235113.56 | 70088867 | 99188095 | 50022850 | 0.000000 | 143416779 | 11507776 | 0.000000
10-04-2025 1:32:25000 | -2738785 | 27.3879 | 37885481 | 235129.84 | 67928688 | 99056763 | 50036007 | 0.000000 | 148626892 | 11893105 | 0.000000
10-04-2025 1:32:30000 | -2723523 | 27.2352 | 36936287 | 235109.95 | 67540916 | 99092865 | 50021793 | 0.000000 | 153769699 | 12272493 | 0.000000
10-04-2025 1:32:35000 | -2751984 | 27.5198 | 36920088 | 235100.72 | 68225159 | 99112045 | 50004894 | 0.000000 | 158843353 | 12651616 | 0.000000
10-04-2025 1:32:40000 | -2763809 | 27.6381 | 34963010 | 235022.97 | 68477623 | 99209328 | 49991451 | 0.000000 | 163842957 | 13035082 | 0.000000
10-04-2025 1:32:45000 | -2821731 | 28.2173 | 34111582 | 234984.41 | 69873009 | 99277206 | 49962929 | 0.000000 | 168600220 | 13423524 | 0.000000
10-04-2025 1:32:50000 | -2840024 | 28.4002 | 33878943 | 235013.30 | 70309647 | 99295990 | 49946480 | 0.000000 | 173150055 | 13820338 | 0.000000
10-04-2025 1:32:55000 | -2711794 | 27.1179 | 34825339 | 235114.91 | 67179291 | 99185455 | 49955154 | 0.000000 | 177791809 | 14208352 | 0.000000
10-04-2025 1:33:00000 | -2542865 | 25.4287 | 32990398 | 235066.02 | 63024590 | 99168892 | 49982525 | 0.000000 | 182537277 | 14570219 | 0.000000
10-04-2025 1:33:05000 | -2489566 | 24.8957 | 30948435 | 235014.89 | 61675392 | 99236160 | 49973225 | 0.000000 | 186960434 | 14918621 | 0.000000
10-04-2025 1:33:10000 | -2535853 | 25.3585 | 32357737 | 235028.09 | 62843040 | 99195709 | 49963791 | 0.000000 | 191448853 | 15266870 | 0.000000
10-04-2025 1:33:15000 | -2684656 | 26.8466 | 31418110 | 234924.44 | 66473862 | 99322174 | 49923996 | 0.000000 | 195769714 | 15632039 | 0.000000
10-04-2025 1:33:20000 | -2656309 | 26.5631 | 31294241 | 234962.75 | 65763031 | 99313171 | 49920795 | 0.000000 | 200049774 | 16003240 | 0.000000
10-04-2025 1:33:25000 | -2559759 | 25.5976 | 31304553 | 234978.61 | 63408020 | 99260483 | 49935715 | 0.000000 | 204518341 | 16364501 | 0.000000
10-04-2025 1:33:30000 | -2486622 | 24.8662 | 29620229 | 234979.13 | 61582684 | 99298004 | 49931026 | 0.000000 | 208524994 | 16711993 | 0.000000
10-04-2025 1:33:35000 | -2455161 | 24.5516 | 30525339 | 235010.34 | 60826859 | 99235931 | 49934444 | 0.000000 | 212634567 | 17054899 | 0.000000
10-04-2025 1:33:40000 | -2443440 | 24.4344 | 30599736 | 234981.98 | 60561825 | 99224953 | 49934570 | 0.000000 | 216745667 | 17394496 | 0.000000
10-04-2025 1:33:45000 | -2485662 | 24.8566 | 27846150 | 234886.55 | 61524612 | 99378342 | 49927540 | 0.000000 | 220700699 | 17737823 | 0.000000
10-04-2025 1:33:50000 | -2599539 | 25.9954 | 28246284 | 234876.69 | 64315926 | 99414841 | 49903191 | 0.000000 | 224519043 | 18092087 | 0.000000
10-04-2025 1:33:55000 | -2652286 | 26.5229 | 28852930 | 234880.97 | 65620010 | 99413490 | 49886993 | 0.000000 | 228374634 | 18460667 | 0.000000
10-04-2025 1:34:00000 | -2607656 | 26.0766 | 25668416 | 234839.73 | 64469086 | 99519020 | 49878704 | 0.000000 | 232096359 | 18825161 | 0.000000
10-04-2025 1:34:05000 | -2565241 | 25.6524 | 27915117 | 234921.61 | 63458305 | 99413109 | 49873669 | 0.000000 | 235978043 | 19187603 | 0.000000
10-04-2025 1:34:10000 | -2522906 | 25.2291 | 25975791 | 234875.34 | 62390034 | 99474144 | 49882862 | 0.000000 | 239676453 | 19536464 | 0.000000
10-04-2025 1:34:15000 | -2566812 | 25.6681 | 23133999 | 234741.72 | 63430122 | 99596313 | 49859692 | 0.000000 | 243065033 | 19889084 | 0.000000
10-04-2025 1:34:20000 | -2516014 | 25.1601 | 24319753 | 234828.31 | 62189991 | 99536095 | 49884487 | 0.000000 | 246431793 | 20244010 | 0.000000
10-04-2025 1:34:25000 | -2427265 | 24.2726 | 23729197 | 234830.75 | 60009926 | 99525536 | 49899055 | 0.000000 | 249786896 | 20582102 | 0.000000
10-04-2025 1:34:30000 | -2406292 | 24.0629 | 24085781 | 234844.28 | 59503231 | 99502785 | 49895229 | 0.000000 | 253101028 | 20918479 | 0.000000
10-04-2025 1:34:35000 | -2373142 | 23.7314 | 24813042 | 234851.44 | 58707138 | 99457825 | 49900997 | 0.000000 | 256601685 | 21249814 | 0.000000
10-04-2025 1:34:40000 | -2391090 | 23.9109 | 25971650 | 234852.16 | 59172844 | 99415268 | 49899258 | 0.000000 | 260157623 | 21580525 | 0.000000
10-04-2025 1:34:45000 | -2543827 | 25.4383 | 29889927 | 234966.66 | 62981564 | 99316757 | 49865768 | 0.000000 | 264005981 | 21923152 | 0.000000
10-04-2025 1:34:50000 | -2166011 | 21.6601 | 34713184 | 235198.34 | 53900955 | 98740005 | 49954063 | 0.000000 | 268771576 | 22247539 | 0.000000
10-04-2025 1:34:55000 | -1898816 | 18.9882 | 31245063 | 235126.64 | 47308983 | 98673050 | 50021469 | 0.000000 | 273299011 | 22523186 | 0.000000
10-04-2025 1:35:00000 | -1923183 | 19.2318 | 30043674 | 235056.08 | 47866817 | 98801682 | 50009190 | 0.000000 | 277523529 | 22785852 | 0.000000
10-04-2025 1:35:05000 | -2125113 | 21.2511 | 33105750 | 235083.08 | 52873657 | 98808228 | 49977070 | 0.000000 | 281941193 | 23069673 | 0.000000
10-04-2025 1:35:10000 | -2280274 | 22.8027 | 34957156 | 235085.38 | 56706959 | 98845230 | 49958740 | 0.000000 | 286690125 | 23378191 | 0.000000
10-04-2025 1:35:15000 | -2377560 | 23.7756 | 36060854 | 235117.98 | 59094887 | 98869255 | 49962852 | 0.000000 | 291635864 | 23704109 | 0.000000
10-04-2025 1:35:20000 | -2384904 | 23.849 | 38055730 | 235182.50 | 59332985 | 98750694 | 49972420 | 0.000000 | 296812531 | 24037090 | 0.000000
10-04-2025 1:35:25000 | -2447968 | 24.4797 | 36770906 | 235104.13 | 60833565 | 98890587 | 49962139 | 0.000000 | 301945068 | 24373674 | 0.000000
10-04-2025 1:35:30000 | -2535425 | 25.3543 | 36941282 | 235088.20 | 62972801 | 98955177 | 49941704 | 0.000000 | 307060272 | 24721851 | 0.000000
10-04-2025 1:35:35000 | -2519363 | 25.1936 | 38875891 | 235202.02 | 62617867 | 98830292 | 49948090 | 0.000000 | 312256897 | 25075652 | 0.000000
10-04-2025 1:35:40000 | -2435371 | 24.3537 | 36426357 | 235157.19 | 60501816 | 98899834 | 49964649 | 0.000000 | 317413757 | 25418479 | 0.000000
10-04-2025 1:35:45000 | -2453544 | 24.5354 | 34490793 | 235069.83 | 60899261 | 99026337 | 49960186 | 0.000000 | 322348450 | 25757222 | 0.000000
10-04-2025 1:35:50000 | -2497207 | 24.9721 | 36851211 | 235133.45 | 62025539 | 98928627 | 49950584 | 0.000000 | 327351410 | 26103037 | 0.000000
10-04-2025 1:35:55000 | -2513215 | 25.1321 | 37624351 | 235134.19 | 62441017 | 98897896 | 49950081 | 0.000000 | 332556885 | 26451104 | 0.000000
10-04-2025 1:36:00000 | -2500516 | 25.0052 | 36905107 | 235117.31 | 62113022 | 98928337 | 49950615 | 0.000000 | 337788452 | 26798369 | 0.000000
10-04-2025 1:36:05000 | -2493482 | 24.9348 | 36947109 | 235124.70 | 61940083 | 98919968 | 49953560 | 0.000000 | 342943024 | 27144375 | 0.000000
10-04-2025 1:36:10000 | -2507806 | 25.0781 | 36700840 | 235117.17 | 62284355 | 98946037 | 49954967 | 0.000000 | 348042664 | 27491973 | 0.000000
10-04-2025 1:36:15000 | -2435381 | 24.3538 | 37368040 | 235165.59 | 60535404 | 98843224 | 49966560 | 0.000000 | 353162262 | 27834265 | 0.000000
10-04-2025 1:36:20000 | -2385923 | 23.8592 | 34469185 | 235076.25 | 59252563 | 98972496 | 49974316 | 0.000000 | 358174103 | 28168733 | 0.000000
10-04-2025 1:36:25000 | -2320559 | 23.2056 | 35303081 | 235127.13 | 57682358 | 98862503 | 49981739 | 0.000000 | 363029083 | 28496118 | 0.000000
10-04-2025 1:36:30000 | -2362777 | 23.6278 | 32744792 | 235047.50 | 58639233 | 99053314 | 49971962 | 0.000000 | 367600677 | 28820608 | 0.000000
10-04-2025 1:36:35000 | -2559545 | 25.5954 | 33583586 | 235013.61 | 63462410 | 99150162 | 49933487 | 0.000000 | 372281250 | 29164041 | 0.000000
10-04-2025 1:36:40000 | -2718891 | 27.1889 | 39155283 | 235115.59 | 67505051 | 98978882 | 49896687 | 0.000000 | 377414825 | 29536914 | 0.000000
10-04-2025 1:36:45000 | -2653225 | 26.5323 | 37049827 | 235116.56 | 65824875 | 99039055 | 49902111 | 0.000000 | 382614807 | 29912808 | 0.000000
10-04-2025 1:36:50000 | -2445874 | 24.4587 | 36890791 | 235176.31 | 60771317 | 98881584 | 49940521 | 0.000000 | 387807190 | 30265349 | 0.000000
10-04-2025 1:36:55000 | -2258872 | 22.5887 | 35497400 | 235171.09 | 56185017 | 98787659 | 49970928 | 0.000000 | 392829285 | 30590217 | 0.000000
10-04-2025 1:37:00000 | -2205209 | 22.0521 | 34338604 | 235146.30 | 54847416 | 98809242 | 49981064 | 0.000000 | 397689178 | 30900010 | 0.000000
10-04-2025 1:37:05000 | -2317532 | 23.1753 | 34647825 | 235106.78 | 57601551 | 98900833 | 49969166 | 0.000000 | 402474030 | 31214756 | 0.000000
10-04-2025 1:37:10000 | -2467096 | 24.671 | 37507878 | 235130.64 | 61321106 | 98863960 | 49951080 | 0.000000 | 407517365 | 31550164 | 0.000000
10-04-2025 1:37:15000 | -2548609 | 25.4861 | 37629749 | 235092.91 | 63312099 | 98927505 | 49944450 | 0.000000 | 412755035 | 31899126 | 0.000000
10-04-2025 1:37:20000 | -2534294 | 25.3429 | 35681670 | 235075.66 | 62901894 | 99023331 | 49949799 | 0.000000 | 417739014 | 32251772 | 0.000000
10-04-2025 1:37:25000 | -2465424 | 24.6542 | 35948240 | 235116.23 | 61227215 | 98953636 | 49958908 | 0.000000 | 422628479 | 32598547 | 0.000000
10-04-2025 1:37:30000 | -2471189 | 24.7119 | 33553711 | 235051.19 | 61301121 | 99090752 | 49954937 | 0.000000 | 427450775 | 32941594 | 0.000000
10-04-2025 1:37:35000 | -2537122 | 25.3712 | 35896709 | 235116.75 | 62967525 | 99013870 | 49946484 | 0.000000 | 432237274 | 33289600 | 0.000000
10-04-2025 1:37:40000 | -2480987 | 24.8099 | 36407048 | 235154.67 | 61609512 | 98940392 | 49959229 | 0.000000 | 437204895 | 33640139 | 0.000000
10-04-2025 1:37:45000 | -2409825 | 24.0983 | 35412324 | 235117.52 | 59871483 | 98937462 | 49972866 | 0.000000 | 442163727 | 33977822 | 0.000000
10-04-2025 1:37:50000 | -2378714 | 23.7871 | 36335129 | 235143.39 | 59130318 | 98853378 | 49973225 | 0.000000 | 447141174 | 34311011 | 0.000000
10-04-2025 1:37:55000 | -2296172 | 22.9617 | 36947759 | 235181.38 | 57145699 | 98730003 | 49992268 | 0.000000 | 452239899 | 34633269 | 0.000000
10-04-2025 1:38:00000 | -2398554 | 23.9855 | 36798250 | 235127.20 | 59630768 | 98843513 | 49974064 | 0.000000 | 457254852 | 34958682 | 0.000000
10-04-2025 1:38:05000 | -2593618 | 25.9362 | 36974241 | 235075.70 | 64387825 | 98999084 | 49944626 | 0.000000 | 462368866 | 35308286 | 0.000000
10-04-2025 1:38:10000 | -2701573 | 27.0157 | 35749929 | 235016.89 | 66990471 | 99135773 | 49923180 | 0.000000 | 467253387 | 35679111 | 0.000000
10-04-2025 1:38:15000 | -2649530 | 26.4953 | 33928926 | 235058.25 | 65650291 | 99190025 | 49918720 | 0.000000 | 472062714 | 36050867 | 0.000000
10-04-2025 1:38:20000 | -2608326 | 26.0833 | 35023184 | 235100.05 | 64672714 | 99110527 | 49917179 | 0.000000 | 476926880 | 36415403 | 0.000000
10-04-2025 1:38:25000 | -2448363 | 24.4836 | 35739739 | 235167.95 | 60789799 | 98951309 | 49935066 | 0.000000 | 481883209 | 36766934 | 0.000000
10-04-2025 1:38:30000 | -2364365 | 23.6437 | 34395686 | 235118.66 | 58723289 | 98958351 | 49943691 | 0.000000 | 486751740 | 37099565 | 0.000000
10-04-2025 1:38:35000 | -2367672 | 23.6767 | 35354211 | 235134.16 | 58831589 | 98903473 | 49943367 | 0.000000 | 491597534 | 37427993 | 0.000000
10-04-2025 1:38:40000 | -2334374 | 23.3437 | 34380327 | 235080.91 | 57997555 | 98932785 | 49951202 | 0.000000 | 496439117 | 37753267 | 0.000000
10-04-2025 1:38:45000 | -2363065 | 23.6306 | 36194014 | 235124.83 | 58747906 | 98847260 | 49939846 | 0.000000 | 501381805 | 38078855 | 0.000000
10-04-2025 1:38:50000 | -2471241 | 24.7124 | 33985330 | 235054.08 | 61318081 | 99067574 | 49916477 | 0.000000 | 506074951 | 38416404 | 0.000000
10-04-2025 1:38:55000 | -2525403 | 25.254 | 34945562 | 235056.14 | 62665543 | 99056137 | 49914616 | 0.000000 | 510921997 | 38765054 | 0.000000
10-04-2025 1:39:00000 | -2443501 | 24.435 | 34037163 | 235067.08 | 60639702 | 99043716 | 49931839 | 0.000000 | 515635803 | 39108342 | 0.000000
10-04-2025 1:39:05000 | -2352336 | 23.5234 | 33171221 | 235091.39 | 58388184 | 99020340 | 49947227 | 0.000000 | 520170105 | 39440723 | 0.000000
10-04-2025 1:39:10000 | -2259242 | 22.5924 | 35207219 | 235196.22 | 56177006 | 98807426 | 49965412 | 0.000000 | 524845215 | 39761963 | 0.000000
10-04-2025 1:39:15000 | -2253642 | 22.5364 | 34483384 | 235102.16 | 56036446 | 98849533 | 49980232 | 0.000000 | 529836426 | 40073657 | 0.000000
10-04-2025 1:39:20000 | -2357592 | 23.5759 | 35003989 | 235084.52 | 58580101 | 98915680 | 49966515 | 0.000000 | 534625854 | 40392720 | 0.000000
10-04-2025 1:39:25000 | -2388704 | 23.887 | 36833345 | 235139.69 | 59389450 | 98831940 | 49960732 | 0.000000 | 539569946 | 40724470 | 0.000000
10-04-2025 1:39:30000 | -2370784 | 23.7078 | 37306289 | 235145.50 | 58980541 | 98784447 | 49972572 | 0.000000 | 544650146 | 41056050 | 0.000000
10-04-2025 1:39:35000 | -2364473 | 23.6447 | 36451804 | 235131.69 | 58789608 | 98832436 | 49970398 | 0.000000 | 549813293 | 41384146 | 0.000000
10-04-2025 1:39:40000 | -2464827 | 24.6483 | 35069751 | 235053.31 | 61200264 | 99002922 | 49953434 | 0.000000 | 554865417 | 41719009 | 0.000000
10-04-2025 1:39:45000 | -2530964 | 25.3096 | 36934109 | 235120.06 | 62851467 | 98951942 | 49938782 | 0.000000 | 559869507 | 42067939 | 0.000000
10-04-2025 1:39:50000 | -2421942 | 24.2194 | 37501042 | 235160.70 | 60217487 | 98822380 | 49963997 | 0.000000 | 565089355 | 42412148 | 0.000000
10-04-2025 1:39:55000 | -2283277 | 22.8328 | 35765671 | 235160.00 | 56787277 | 98795288 | 49990246 | 0.000000 | 570223816 | 42736621 | 0.000000
10-04-2025 1:40:00000 | -2359756 | 23.5976 | 35546797 | 235124.11 | 58651062 | 98884369 | 49969009 | 0.000000 | 575143372 | 43059097 | 0.000000
10-04-2025 1:40:05000 | -2422500 | 24.225 | 37770325 | 235161.47 | 60238110 | 98806252 | 49957623 | 0.000000 | 580282654 | 43392202 | 0.000000
10-04-2025 1:40:10000 | -2455894 | 24.5589 | 35919121 | 235092.66 | 60998840 | 98947304 | 49959297 | 0.000000 | 585349792 | 43731255 | 0.000000
10-04-2025 1:40:15000 | -2495911 | 24.9591 | 37450732 | 235129.92 | 62016586 | 98892937 | 49945816 | 0.000000 | 590464233 | 44074155 | 0.000000
10-04-2025 1:40:20000 | -2540321 | 25.4032 | 40168086 | 235202.58 | 63173985 | 98772835 | 49936642 | 0.000000 | 595849976 | 44425908 | 0.000000
10-04-2025 1:40:25000 | -2560529 | 25.6053 | 40148337 | 235222.48 | 63658527 | 98792946 | 49940533 | 0.000000 | 601375977 | 44781343 | 0.000000
10-04-2025 1:40:30000 | -2475208 | 24.7521 | 39822271 | 235192.23 | 61592739 | 98730400 | 49962757 | 0.000000 | 607074585 | 45128145 | 0.000000
10-04-2025 1:40:35000 | -2415409 | 24.1541 | 41033330 | 235271.52 | 60168758 | 98587517 | 49966110 | 0.000000 | 612637329 | 45466494 | 0.000000
10-04-2025 1:40:40000 | -2407017 | 24.0702 | 40187988 | 235231.78 | 59940960 | 98634666 | 49965355 | 0.000000 | 618246399 | 45801147 | 0.000000
10-04-2025 1:40:45000 | -2475267 | 24.7527 | 39231064 | 235187.22 | 61570881 | 98767189 | 49943447 | 0.000000 | 623654175 | 46140029 | 0.000000
10-04-2025 1:40:50000 | -2643260 | 26.4326 | 38561563 | 235102.98 | 65642181 | 98952545 | 49917061 | 0.000000 | 629093750 | 46495952 | 0.000000
10-04-2025 1:40:55000 | -2650399 | 26.504 | 38288818 | 235133.56 | 65812706 | 98972557 | 49909000 | 0.000000 | 634332397 | 46866353 | 0.000000
10-04-2025 1:41:00000 | -2595504 | 25.955 | 35521001 | 235079.09 | 64380409 | 99076477 | 49904709 | 0.000000 | 639406616 | 47226641 | 0.000000
10-04-2025 1:41:05000 | -2506192 | 25.0619 | 37707705 | 235164.13 | 62266640 | 98886978 | 49910717 | 0.000000 | 644610413 | 47581079 | 0.000000
10-04-2025 1:41:10000 | -2452534 | 24.5253 | 37885813 | 235171.58 | 60973068 | 98827797 | 49906647 | 0.000000 | 649727356 | 47922319 | 0.000000
10-04-2025 1:41:15000 | -2502293 | 25.0229 | 37112109 | 235140.19 | 62154957 | 98917992 | 49900398 | 0.000000 | 654931580 | 48269434 | 0.000000
10-04-2025 1:41:20000 | -2530081 | 25.3008 | 35365442 | 235081.02 | 62787060 | 99037163 | 49893833 | 0.000000 | 659922974 | 48618657 | 0.000000
10-04-2025 1:41:25000 | -2562594 | 25.6259 | 35156912 | 235043.70 | 63579517 | 99071991 | 49891582 | 0.000000 | 664841858 | 48974443 | 0.000000
10-04-2025 1:41:30000 | -2494293 | 24.9429 | 34793765 | 235090.42 | 61892017 | 99041054 | 49908276 | 0.000000 | 669740540 | 49323062 | 0.000000
10-04-2025 1:41:35000 | -2462193 | 24.6219 | 34972859 | 235104.55 | 61116993 | 99006248 | 49914261 | 0.000000 | 674658325 | 49665654 | 0.000000
10-04-2025 1:41:40000 | -2398535 | 23.9854 | 37923696 | 235208.56 | 59652157 | 98772987 | 49920006 | 0.000000 | 679666321 | 50002817 | 0.000000
10-04-2025 1:41:45000 | -2284457 | 22.8446 | 37064768 | 235197.89 | 56865234 | 98709213 | 49954880 | 0.000000 | 684971741 | 50324614 | 0.000000
10-04-2025 1:41:50000 | -2274567 | 22.7457 | 35421834 | 235113.67 | 56575348 | 98809029 | 49964741 | 0.000000 | 690082947 | 50638438 | 0.000000
10-04-2025 1:41:55000 | -2422171 | 24.2217 | 36066101 | 235100.05 | 60185238 | 98909538 | 49940975 | 0.000000 | 695077881 | 50963262 | 0.000000
10-04-2025 1:42:00000 | -2494253 | 24.9425 | 38102715 | 235114.39 | 62010075 | 98853218 | 49921711 | 0.000000 | 700301270 | 51305674 | 0.000000
10-04-2025 1:42:05000 | -2570819 | 25.7082 | 38279824 | 235145.22 | 63861603 | 98909523 | 49916653 | 0.000000 | 705582336 | 51660620 | 0.000000
10-04-2025 1:42:10000 | -2573087 | 25.7309 | 37632324 | 235138.13 | 63893745 | 98947350 | 49922455 | 0.000000 | 710861877 | 52019888 | 0.000000
10-04-2025 1:42:15000 | -2535637 | 25.3564 | 37804739 | 235180.42 | 62978310 | 98906746 | 49929073 | 0.000000 | 716019409 | 52374063 | 0.000000
10-04-2025 1:42:20000 | -2434748 | 24.3475 | 39769702 | 235234.88 | 60593082 | 98692078 | 49953880 | 0.000000 | 721406311 | 52719136 | 0.000000
10-04-2025 1:42:25000 | -2383672 | 23.8367 | 36037114 | 235153.64 | 59233509 | 98876404 | 49959576 | 0.000000 | 726601868 | 53049727 | 0.000000
10-04-2025 1:42:30000 | -2379603 | 23.796 | 36542788 | 235126.41 | 59163086 | 98841316 | 49949554 | 0.000000 | 731736084 | 53376465 | 0.000000
10-04-2025 1:42:35000 | -2497246 | 24.9725 | 38444097 | 235142.56 | 62081173 | 98835686 | 49925819 | 0.000000 | 736949890 | 53715967 | 0.000000
10-04-2025 1:42:40000 | -2605213 | 26.0521 | 39060027 | 235148.30 | 64729095 | 98894646 | 49911385 | 0.000000 | 742437317 | 54071797 | 0.000000
10-04-2025 1:42:45000 | -2512329 | 25.1233 | 40104690 | 235202.31 | 62493782 | 98749733 | 49918476 | 0.000000 | 748068359 | 54427593 | 0.000000
10-04-2025 1:42:50000 | -2452041 | 24.5204 | 37593767 | 235181.02 | 60947372 | 98845032 | 49931252 | 0.000000 | 753399109 | 54770342 | 0.000000
10-04-2025 1:42:55000 | -2353867 | 23.5387 | 38016296 | 235199.59 | 58574158 | 98720764 | 49944633 | 0.000000 | 758590942 | 55105244 | 0.000000
10-04-2025 1:43:00000 | -2254571 | 22.5457 | 39157737 | 235249.83 | 56208542 | 98525024 | 49962982 | 0.000000 | 763998535 | 55424277 | 0.000000
10-04-2025 1:43:05000 | -2292746 | 22.9275 | 39168550 | 235234.30 | 57134251 | 98571922 | 49963440 | 0.000000 | 769393555 | 55738716 | 0.000000
10-04-2025 1:43:10000 | -2398708 | 23.9871 | 41035664 | 235250.81 | 59769619 | 98568039 | 49960159 | 0.000000 | 774905518 | 56065415 | 0.000000
10-04-2025 1:43:15000 | -2441101 | 24.411 | 40036848 | 235188.44 | 60771217 | 98681557 | 49952450 | 0.000000 | 780520630 | 56404868 | 0.000000
10-04-2025 1:43:20000 | -2451061 | 24.5106 | 41550244 | 235275.48 | 61049351 | 98593399 | 49959400 | 0.000000 | 786155579 | 56745112 | 0.000000
10-04-2025 1:43:25000 | -2403732 | 24.0373 | 40252441 | 235200.89 | 59874161 | 98626709 | 49964001 | 0.000000 | 791883545 | 57080264 | 0.000000
10-04-2025 1:43:30000 | -2407697 | 24.077 | 39804126 | 235219.14 | 59946819 | 98660851 | 49960506 | 0.000000 | 797413940 | 57413687 | 0.000000
10-04-2025 1:43:35000 | -2338973 | 23.3897 | 42081899 | 235292.73 | 58362602 | 98419769 | 49978168 | 0.000000 | 803008179 | 57742192 | 0.000000
10-04-2025 1:43:40000 | -2314667 | 23.1467 | 41307671 | 235264.91 | 57758335 | 98444649 | 49984695 | 0.000000 | 808679932 | 58064810 | 0.000000
10-04-2025 1:43:45000 | -2315323 | 23.1532 | 39951902 | 235212.05 | 57721172 | 98543694 | 49981926 | 0.000000 | 814349854 | 58385840 | 0.000000
10-04-2025 1:43:50000 | -2477162 | 24.7716 | 37483501 | 235118.50 | 61573540 | 98874458 | 49944138 | 0.000000 | 819602600 | 58718008 | 0.000000
10-04-2025 1:43:55000 | -2666246 | 26.6625 | 38688931 | 235076.44 | 66213943 | 98963547 | 49899261 | 0.000000 | 824927612 | 59079097 | 0.000000
10-04-2025 1:44:00000 | -2727987 | 27.2799 | 41886050 | 235211.77 | 67784523 | 98841682 | 49887646 | 0.000000 | 830558411 | 59454712 | 0.000000
10-04-2025 1:44:05000 | -2611116 | 26.1112 | 39700415 | 235177.34 | 64882019 | 98863792 | 49898090 | 0.000000 | 836172791 | 59826680 | 0.000000
10-04-2025 1:44:10000 | -2538598 | 25.386 | 38084519 | 235174.20 | 63070427 | 98893318 | 49900799 | 0.000000 | 841459656 | 60182998 | 0.000000
10-04-2025 1:44:15000 | -2332406 | 23.3241 | 39191209 | 235264.25 | 58088409 | 98617516 | 49939075 | 0.000000 | 846842896 | 60518789 | 0.000000
10-04-2025 1:44:20000 | -2217420 | 22.1742 | 38477092 | 235263.80 | 55278061 | 98527672 | 49962242 | 0.000000 | 852125183 | 60830986 | 0.000000
10-04-2025 1:44:25000 | -2381047 | 23.8105 | 36475259 | 235118.84 | 59198288 | 98846901 | 49936172 | 0.000000 | 857310425 | 61150674 | 0.000000
10-04-2025 1:44:30000 | -2517617 | 25.1762 | 40255659 | 235194.78 | 62631325 | 98745667 | 49911777 | 0.000000 | 862615784 | 61493198 | 0.000000
10-04-2025 1:44:35000 | -2515697 | 25.157 | 40375808 | 235223.38 | 62578674 | 98736420 | 49915325 | 0.000000 | 868209534 | 61844019 | 0.000000
10-04-2025 1:44:40000 | -2495844 | 24.9584 | 39856008 | 235195.00 | 62093369 | 98748840 | 49928036 | 0.000000 | 873735901 | 62193203 | 0.000000
10-04-2025 1:44:45000 | -2425502 | 24.255 | 38360735 | 235198.14 | 60324276 | 98772316 | 49941628 | 0.000000 | 879117615 | 62532559 | 0.000000
10-04-2025 1:44:50000 | -2467650 | 24.6765 | 38357798 | 235172.14 | 61360123 | 98813339 | 49926323 | 0.000000 | 884398254 | 62870688 | 0.000000
10-04-2025 1:44:55000 | -2559857 | 25.5986 | 42327456 | 235244.98 | 63721355 | 98660362 | 49907890 | 0.000000 | 889971252 | 63221968 | 0.000000
10-04-2025 1:45:00000 | -2557334 | 25.5733 | 41250200 | 235210.02 | 63625324 | 98723938 | 49914223 | 0.000000 | 895790466 | 63576494 | 0.000000
10-04-2025 1:45:05000 | -2528488 | 25.2849 | 40301125 | 235228.36 | 62885792 | 98753471 | 49922375 | 0.000000 | 5587562 | 35235062 | 0.000000
10-04-2025 1:45:10000 | -2505909 | 25.0591 | 38813169 | 235173.11 | 62297424 | 98821663 | 49919731 | 0.000000 | 11065546 | 70236259 | 0.000000
10-04-2025 1:45:15000 | -2574334 | 25.7433 | 38059617 | 235144.69 | 63942848 | 98924721 | 49905975 | 0.000000 | 16403925 | 105399200 | 0.000000
10-04-2025 1:45:20000 | -2635407 | 26.3541 | 39399297 | 235169.38 | 65460358 | 98900879 | 49889664 | 0.000000 | 21837275 | 141731522 | 0.000000
10-04-2025 1:45:25000 | -2555626 | 25.5563 | 39820732 | 235193.52 | 63534157 | 98807739 | 49892254 | 0.000000 | 27324696 | 177645233 | 0.000000
10-04-2025 1:45:30000 | -2434320 | 24.3432 | 38742952 | 235218.11 | 60549473 | 98757080 | 49907120 | 0.000000 | 32679405 | 212277481 | 0.000000
10-04-2025 1:45:35000 | -2391968 | 23.9197 | 36043528 | 235124.94 | 59442383 | 98883667 | 49911644 | 0.000000 | 37880215 | 245621887 | 0.000000
10-04-2025 1:45:40000 | -2368792 | 23.6879 | 37725586 | 235183.20 | 58929859 | 98755424 | 49918705 | 0.000000 | 43063343 | 278630066 | 0.000000
10-04-2025 1:45:45000 | -2335390 | 23.3539 | 41891284 | 235303.77 | 58266647 | 98429024 | 49914173 | 0.000000 | 48746254 | 311305939 | 0.000000
10-04-2025 1:45:50000 | -2333685 | 23.3368 | 39725757 | 235221.19 | 58152130 | 98581871 | 49922760 | 0.000000 | 54439678 | 343894043 | 0.000000
10-04-2025 1:45:55000 | -2287823 | 22.8782 | 38793770 | 235214.98 | 57003994 | 98592644 | 49933487 | 0.000000 | 59930386 | 375729675 | 0.000000
10-04-2025 1:46:00000 | -2433271 | 24.3327 | 36688125 | 235133.89 | 60467556 | 98882339 | 49911419 | 0.000000 | 65129593 | 408801910 | 0.000000
10-04-2025 1:46:05000 | -2434281 | 24.3428 | 40445122 | 235241.22 | 60613487 | 98647675 | 49926449 | 0.000000 | 70611290 | 442932343 | 0.000000
10-04-2025 1:46:10000 | -2284633 | 22.8463 | 39048586 | 235255.83 | 56932030 | 98570587 | 49955006 | 0.000000 | 76046631 | 475577698 | 0.000000
10-04-2025 1:46:15000 | -2295980 | 22.9598 | 39011196 | 235224.70 | 57211403 | 98587036 | 49953472 | 0.000000 | 81407890 | 507087463 | 0.000000
10-04-2025 1:46:20000 | -2435399 | 24.354 | 40126465 | 235202.83 | 60635719 | 98669678 | 49943840 | 0.000000 | 86879524 | 540057434 | 0.000000
10-04-2025 1:46:25000 | -2474464 | 24.7446 | 40976348 | 235219.42 | 61606628 | 98656456 | 49935486 | 0.000000 | 92569321 | 574244629 | 0.000000
10-04-2025 1:46:30000 | -2483814 | 24.8381 | 40235549 | 235200.95 | 61815990 | 98713219 | 49931873 | 0.000000 | 98247719 | 608566162 | 0.000000
10-04-2025 1:46:35000 | -2563842 | 25.6384 | 42400771 | 235239.42 | 63826363 | 98659904 | 49919643 | 0.000000 | 104013428 | 643901123 | 0.000000
10-04-2025 1:46:40000 | -2584750 | 25.8475 | 41659385 | 235233.39 | 64300644 | 98725922 | 49910645 | 0.000000 | 109733719 | 679825439 | 0.000000
10-04-2025 1:46:45000 | -2509107 | 25.0911 | 40260325 | 235208.39 | 62418896 | 98737015 | 49908455 | 0.000000 | 115431526 | 714967773 | 0.000000
10-04-2025 1:46:50000 | -2494787 | 24.9479 | 41468940 | 235277.63 | 62104641 | 98646492 | 49904320 | 0.000000 | 121175117 | 749662964 | 0.000000
10-04-2025 1:46:55000 | -2462306 | 24.6231 | 40928110 | 235259.00 | 61298912 | 98646553 | 49919113 | 0.000000 | 126936462 | 784011902 | 0.000000
10-04-2025 1:47:00000 | -2430118 | 24.3012 | 41174282 | 235257.05 | 60533203 | 98594803 | 49922703 | 0.000000 | 132623917 | 817812073 | 0.000000
10-04-2025 1:47:05000 | -2384510 | 23.8451 | 40053040 | 235213.31 | 59398090 | 98618439 | 49926186 | 0.000000 | 138207413 | 851212646 | 0.000000
10-04-2025 1:47:10000 | -2357610 | 23.5761 | 40518379 | 235251.33 | 58752655 | 98555099 | 49934307 | 0.000000 | 143785019 | 883950500 | 0.000000
10-04-2025 1:47:15000 | -2283535 | 22.8353 | 41092295 | 235306.89 | 56977997 | 98419182 | 49951908 | 0.000000 | 149532028 | 916145874 | 0.000000
10-04-2025 1:47:20000 | -2283383 | 22.8338 | 38954316 | 235198.16 | 56906982 | 98575813 | 49955513 | 0.000000 | 155104492 | 947729065 | 0.000000
10-04-2025 1:47:25000 | -2364114 | 23.6411 | 39520217 | 235197.02 | 58884689 | 98631378 | 49952389 | 0.000000 | 160638367 | 980037292 | 0.000000
10-04-2025 1:47:30000 | -2422301 | 24.223 | 41516519 | 235250.75 | 60358307 | 98562813 | 49946957 | 0.000000 | 166313354 | 10134059 | 0.000000
10-04-2025 1:47:35000 | -2422423 | 24.2242 | 42005625 | 235283.78 | 60372749 | 98529640 | 49956886 | 0.000000 | 172095535 | 10469901 | 0.000000
10-04-2025 1:47:40000 | -2424339 | 24.2434 | 41120132 | 235244.75 | 60394920 | 98591866 | 49946335 | 0.000000 | 177901611 | 10806656 | 0.000000
10-04-2025 1:47:45000 | -2461284 | 24.6128 | 41635464 | 235229.48 | 61317116 | 98599213 | 49941566 | 0.000000 | 183669922 | 11145287 | 0.000000
10-04-2025 1:47:50000 | -2433138 | 24.3314 | 43446943 | 235317.95 | 60686386 | 98442894 | 49947464 | 0.000000 | 189558624 | 11484091 | 0.000000
10-04-2025 1:47:55000 | -2494278 | 24.9428 | 40854658 | 235211.42 | 62085930 | 98684982 | 49938164 | 0.000000 | 195394623 | 11825542 | 0.000000
10-04-2025 1:48:00000 | -2598449 | 25.9845 | 41532881 | 235190.19 | 64641319 | 98746567 | 49908989 | 0.000000 | 201083099 | 12182009 | 0.000000
10-04-2025 1:48:05000 | -2621447 | 26.2145 | 42642666 | 235220.19 | 65230011 | 98702644 | 49900009 | 0.000000 | 206980652 | 12545934 | 0.000000
10-04-2025 1:48:10000 | -2564006 | 25.6401 | 42000396 | 235246.22 | 63805889 | 98684761 | 49901787 | 0.000000 | 212846451 | 12907677 | 0.000000
10-04-2025 1:48:15000 | -2460297 | 24.603 | 40743760 | 235256.08 | 61249695 | 98656326 | 49913120 | 0.000000 | 218580963 | 13253860 | 0.000000
10-04-2025 1:48:20000 | -2371863 | 23.7186 | 40853887 | 235264.64 | 59110176 | 98548813 | 49933407 | 0.000000 | 224163757 | 13589630 | 0.000000
10-04-2025 1:48:25000 | -2300856 | 23.0086 | 39491802 | 235229.66 | 57343506 | 98558762 | 49942112 | 0.000000 | 229744843 | 13913464 | 0.000000
10-04-2025 1:48:30000 | -2316723 | 23.1672 | 40343889 | 235214.20 | 57773609 | 98517365 | 49939693 | 0.000000 | 235346786 | 14232671 | 0.000000
10-04-2025 1:48:35000 | -2442363 | 24.4236 | 41544365 | 235233.23 | 60852692 | 98583969 | 49930195 | 0.000000 | 240979370 | 14566879 | 0.000000
10-04-2025 1:48:40000 | -2403188 | 24.0319 | 40809458 | 235238.97 | 59869019 | 98588615 | 49942654 | 0.000000 | 246786362 | 14902478 | 0.000000
10-04-2025 1:48:45000 | -2338201 | 23.382 | 39966807 | 235245.61 | 58267586 | 98570404 | 49953945 | 0.000000 | 252560394 | 15227178 | 0.000000
10-04-2025 1:48:50000 | -2394305 | 23.943 | 40201951 | 235215.14 | 59639408 | 98619492 | 49936764 | 0.000000 | 258065552 | 15553251 | 0.000000
10-04-2025 1:48:55000 | -2434419 | 24.3442 | 43736094 | 235322.72 | 60727745 | 98424210 | 49935078 | 0.000000 | 263989075 | 15890958 | 0.000000
10-04-2025 1:49:00000 | -2430135 | 24.3013 | 43958340 | 235320.08 | 60635063 | 98403053 | 49931602 | 0.000000 | 270079865 | 16228989 | 0.000000
10-04-2025 1:49:05000 | -2382614 | 23.8261 | 42738105 | 235307.56 | 59436409 | 98429039 | 49946568 | 0.000000 | 276016937 | 16563507 | 0.000000
10-04-2025 1:49:10000 | -2346536 | 23.4654 | 40979092 | 235269.70 | 58502445 | 98509117 | 49954861 | 0.000000 | 281825806 | 16891987 | 0.000000
10-04-2025 1:49:15000 | -2306292 | 23.0629 | 40983921 | 235264.17 | 57529499 | 98457489 | 49957401 | 0.000000 | 287549011 | 17214635 | 0.000000
10-04-2025 1:49:20000 | -2204784 | 22.0478 | 41646587 | 235290.02 | 55107395 | 98262360 | 49976631 | 0.000000 | 293349518 | 17527559 | 0.000000
10-04-2025 1:49:25000 | -2244672 | 22.4467 | 41848140 | 235310.34 | 56071171 | 98306160 | 49981804 | 0.000000 | 299060547 | 17838760 | 0.000000
10-04-2025 1:49:30000 | -2360703 | 23.607 | 45033687 | 235347.64 | 59004353 | 98228661 | 49974770 | 0.000000 | 305131348 | 18159791 | 0.000000
10-04-2025 1:49:35000 | -2509826 | 25.0983 | 44322065 | 235267.94 | 62586258 | 98476273 | 49951183 | 0.000000 | 311411469 | 18500129 | 0.000000
10-04-2025 1:49:40000 | -2672544 | 26.7254 | 43570137 | 235200.41 | 66511856 | 98696999 | 49915573 | 0.000000 | 317557648 | 18865032 | 0.000000
10-04-2025 1:49:45000 | -2688427 | 26.8843 | 43435869 | 235249.86 | 66875580 | 98719826 | 49899223 | 0.000000 | 323500641 | 19241104 | 0.000000
10-04-2025 1:49:50000 | -2597037 | 25.9704 | 44777813 | 235328.95 | 64695915 | 98545929 | 49917702 | 0.000000 | 329579102 | 19608231 | 0.000000
10-04-2025 1:49:55000 | -2482514 | 24.8251 | 44410830 | 235345.81 | 61912773 | 98437248 | 49922241 | 0.000000 | 335899109 | 19958607 | 0.000000
10-04-2025 1:50:00000 | -2464926 | 24.6493 | 42456318 | 235297.55 | 61421055 | 98548851 | 49923588 | 0.000000 | 341915192 | 20301166 | 0.000000
10-04-2025 1:50:05000 | -2462056 | 24.6206 | 42738276 | 235278.25 | 61366802 | 98526581 | 49922474 | 0.000000 | 347900879 | 20642634 | 0.000000
10-04-2025 1:50:10000 | -2437988 | 24.3799 | 43077612 | 235305.88 | 60793232 | 98474602 | 49918793 | 0.000000 | 353867645 | 20983818 | 0.000000
10-04-2025 1:50:15000 | -2433522 | 24.3352 | 42983232 | 235303.30 | 60681816 | 98475670 | 49932915 | 0.000000 | 359743744 | 21323137 | 0.000000
10-04-2025 1:50:20000 | -2322330 | 23.2233 | 42652788 | 235302.39 | 57984882 | 98354889 | 49953922 | 0.000000 | 365745758 | 21649756 | 0.000000
10-04-2025 1:50:25000 | -2279276 | 22.7928 | 44348916 | 235379.91 | 57002377 | 98159149 | 49954918 | 0.000000 | 371860840 | 21968604 | 0.000000
10-04-2025 1:50:30000 | -2301889 | 23.0189 | 41371831 | 235255.14 | 57457767 | 98422966 | 49959053 | 0.000000 | 377824524 | 22286240 | 0.000000
10-04-2025 1:50:35000 | -2362167 | 23.6217 | 42109038 | 235280.48 | 58924999 | 98447983 | 49964272 | 0.000000 | 383618011 | 22609546 | 0.000000
10-04-2025 1:50:40000 | -2397113 | 23.9711 | 42262749 | 235258.11 | 59780235 | 98481117 | 49968132 | 0.000000 | 389490417 | 22941641 | 0.000000
10-04-2025 1:50:45000 | -2380465 | 23.8046 | 43499023 | 235310.14 | 59424553 | 98371109 | 49971016 | 0.000000 | 395416870 | 23274399 | 0.000000
10-04-2025 1:50:50000 | -2362560 | 23.6256 | 43642046 | 235303.03 | 58996544 | 98336319 | 49975945 | 0.000000 | 401561554 | 23601589 | 0.000000
10-04-2025 1:50:55000 | -2457271 | 24.5727 | 41641128 | 235216.81 | 61220314 | 98594353 | 49949402 | 0.000000 | 407492065 | 23934897 | 0.000000
10-04-2025 1:51:00000 | -2508507 | 25.0851 | 44679033 | 235295.53 | 62567211 | 98450607 | 49938534 | 0.000000 | 413496674 | 24281970 | 0.000000
10-04-2025 1:51:05000 | -2534995 | 25.3499 | 44543564 | 235322.67 | 63193962 | 98491074 | 49947758 | 0.000000 | 419597382 | 24633643 | 0.000000
10-04-2025 1:51:10000 | -2590350 | 25.9035 | 42262222 | 235233.06 | 64459961 | 98695061 | 49929630 | 0.000000 | 425557190 | 24988896 | 0.000000
10-04-2025 1:51:15000 | -2671427 | 26.7143 | 42631392 | 235213.34 | 66448509 | 98750481 | 49908531 | 0.000000 | 431435944 | 25355815 | 0.000000
10-04-2025 1:51:20000 | -2670899 | 26.709 | 43461094 | 235237.25 | 66469017 | 98701820 | 49899277 | 0.000000 | 437399933 | 25728560 | 0.000000
10-04-2025 1:51:25000 | -2504182 | 25.0418 | 42783145 | 235331.94 | 62369606 | 98571762 | 49924568 | 0.000000 | 443446564 | 26084998 | 0.000000
10-04-2025 1:51:30000 | -2459419 | 24.5942 | 42668735 | 235308.77 | 61289421 | 98528183 | 49928524 | 0.000000 | 449447449 | 26425234 | 0.000000
10-04-2025 1:51:35000 | -2476290 | 24.7629 | 44088403 | 235320.00 | 61751862 | 98451759 | 49920914 | 0.000000 | 455369171 | 26768638 | 0.000000
10-04-2025 1:51:40000 | -2410537 | 24.1054 | 43656689 | 235318.81 | 60146698 | 98399269 | 49936390 | 0.000000 | 461501678 | 27108643 | 0.000000
10-04-2025 1:51:45000 | -2368730 | 23.6873 | 40723540 | 235244.88 | 59032860 | 98554123 | 49944283 | 0.000000 | 467451935 | 27438140 | 0.000000
10-04-2025 1:51:50000 | -2372853 | 23.7285 | 42474277 | 235297.45 | 59192829 | 98435432 | 49938431 | 0.000000 | 473223206 | 27768372 | 0.000000
10-04-2025 1:51:55000 | -2392559 | 23.9256 | 42011353 | 235291.81 | 59651215 | 98493134 | 49937431 | 0.000000 | 478964905 | 28101760 | 0.000000
10-04-2025 1:52:00000 | -2412712 | 24.1271 | 41269048 | 235239.05 | 60127846 | 98568459 | 49931057 | 0.000000 | 484815460 | 28434036 | 0.000000
10-04-2025 1:52:05000 | -2483230 | 24.8323 | 41786377 | 235209.81 | 61856075 | 98613564 | 49917728 | 0.000000 | 490643768 | 28774185 | 0.000000
10-04-2025 1:52:10000 | -2483357 | 24.8336 | 42486157 | 235248.67 | 61876625 | 98567886 | 49920170 | 0.000000 | 496487061 | 29119304 | 0.000000
10-04-2025 1:52:15000 | -2620971 | 26.2097 | 37036396 | 235034.11 | 65068199 | 99016312 | 49895058 | 0.000000 | 501975067 | 29471504 | 0.000000
10-04-2025 1:52:20000 | -2715001 | 27.15 | 36344937 | 235064.72 | 67318886 | 99115845 | 49855709 | 0.000000 | 506961029 | 29846995 | 0.000000
10-04-2025 1:52:25000 | -2620327 | 26.2033 | 35089663 | 235051.94 | 64991272 | 99115242 | 49875362 | 0.000000 | 511989288 | 30221033 | 0.000000
10-04-2025 1:52:30000 | -2474158 | 24.7416 | 33327781 | 235065.06 | 61366161 | 99104912 | 49903091 | 0.000000 | 516694824 | 30570493 | 0.000000
10-04-2025 1:52:35000 | -2536740 | 25.3674 | 30817109 | 234983.30 | 62829395 | 99270164 | 49879436 | 0.000000 | 521083435 | 30919507 | 0.000000
10-04-2025 1:52:40000 | -2585355 | 25.8535 | 33910374 | 235065.36 | 64087685 | 99150749 | 49875301 | 0.000000 | 525601074 | 31276299 | 0.000000
10-04-2025 1:52:45000 | -2534559 | 25.3456 | 32568855 | 235024.08 | 62823051 | 99184486 | 49879917 | 0.000000 | 530181519 | 31631826 | 0.000000
10-04-2025 1:52:50000 | -2539328 | 25.3933 | 32089907 | 235021.69 | 62922642 | 99210945 | 49869427 | 0.000000 | 534635132 | 31984026 | 0.000000
10-04-2025 1:52:55000 | -2467429 | 24.6743 | 34448899 | 235091.73 | 61235138 | 99039406 | 49888531 | 0.000000 | 539358337 | 32329131 | 0.000000
10-04-2025 1:53:00000 | -2398646 | 23.9865 | 33790264 | 235073.66 | 59537952 | 99022278 | 49901325 | 0.000000 | 544127686 | 32665508 | 0.000000
10-04-2025 1:53:05000 | -2305749 | 23.0575 | 31584790 | 235027.64 | 57218941 | 99074783 | 49915833 | 0.000000 | 548667847 | 32989387 | 0.000000
10-04-2025 1:53:10000 | -2285005 | 22.85 | 33156812 | 235095.33 | 56754536 | 98963547 | 49920383 | 0.000000 | 553046326 | 33308572 | 0.000000
10-04-2025 1:53:15000 | -2388717 | 23.8872 | 33287998 | 235026.09 | 59302654 | 99042923 | 49906384 | 0.000000 | 557586365 | 33633247 | 0.000000
10-04-2025 1:53:20000 | -2386148 | 23.8615 | 34529600 | 235078.86 | 59264427 | 98969131 | 49920357 | 0.000000 | 562434204 | 33964656 | 0.000000
10-04-2025 1:53:25000 | -2258420 | 22.5842 | 35675518 | 235153.33 | 56187748 | 98775200 | 49944984 | 0.000000 | 567437744 | 34283862 | 0.000000
10-04-2025 1:53:30000 | -2368568 | 23.6857 | 35295210 | 235093.75 | 58856308 | 98907883 | 49931744 | 0.000000 | 572349854 | 34605818 | 0.000000
10-04-2025 1:53:35000 | -2439972 | 24.3997 | 37519561 | 235152.73 | 60663700 | 98838295 | 49928097 | 0.000000 | 577490234 | 34941831 | 0.000000
10-04-2025 1:53:40000 | -2407026 | 24.0703 | 37431953 | 235158.98 | 59850266 | 98812309 | 49929550 | 0.000000 | 582640869 | 35279023 | 0.000000
10-04-2025 1:53:45000 | -2426058 | 24.2606 | 37181443 | 235156.08 | 60311245 | 98845879 | 49926003 | 0.000000 | 587720154 | 35617395 | 0.000000
10-04-2025 1:53:50000 | -2422379 | 24.2238 | 37988110 | 235175.17 | 60252083 | 98792572 | 49944302 | 0.000000 | 592860229 | 35957595 | 0.000000
10-04-2025 1:53:55000 | -2349632 | 23.4963 | 36566531 | 235137.27 | 58446152 | 98810577 | 49949226 | 0.000000 | 598003174 | 36285923 | 0.000000
10-04-2025 1:54:00000 | -2537949 | 25.3795 | 36452585 | 235080.44 | 63020454 | 98984207 | 49901611 | 0.000000 | 602927368 | 36625881 | 0.000000
10-04-2025 1:54:05000 | -2616731 | 26.1673 | 39126008 | 235161.91 | 64999840 | 98900551 | 49889324 | 0.000000 | 608258606 | 36985818 | 0.000000
10-04-2025 1:54:10000 | -2564021 | 25.6402 | 38206201 | 235127.00 | 63697277 | 98907967 | 49886646 | 0.000000 | 613797119 | 37344934 | 0.000000
10-04-2025 1:54:15000 | -2509097 | 25.091 | 38376284 | 235160.97 | 62361572 | 98850464 | 49896126 | 0.000000 | 619033569 | 37696287 | 0.000000
10-04-2025 1:54:20000 | -2527503 | 25.275 | 37789956 | 235145.09 | 62796280 | 98900658 | 49885410 | 0.000000 | 624207397 | 38048005 | 0.000000
10-04-2025 1:54:25000 | -2452338 | 24.5234 | 39994221 | 235236.95 | 61031113 | 98696098 | 49906189 | 0.000000 | 629603943 | 38395425 | 0.000000
10-04-2025 1:54:30000 | -2282124 | 22.8212 | 37223474 | 235164.16 | 56825451 | 98695740 | 49953999 | 0.000000 | 635144897 | 38715962 | 0.000000
10-04-2025 1:54:35000 | -2340911 | 23.4091 | 39587021 | 235237.36 | 58329933 | 98600052 | 49935188 | 0.000000 | 640367126 | 39036345 | 0.000000
10-04-2025 1:54:40000 | -2358147 | 23.5815 | 40153757 | 235217.08 | 58781433 | 98581078 | 49931549 | 0.000000 | 645960266 | 39363701 | 0.000000
10-04-2025 1:54:45000 | -2426278 | 24.2628 | 39556709 | 235204.02 | 60396481 | 98696907 | 49915161 | 0.000000 | 651442017 | 39697036 | 0.000000
10-04-2025 1:54:50000 | -2513828 | 25.1383 | 39666746 | 235174.47 | 62525333 | 98777824 | 49898464 | 0.000000 | 657024231 | 40041147 | 0.000000
10-04-2025 1:54:55000 | -2454354 | 24.5435 | 42087881 | 235285.91 | 61167557 | 98561340 | 49913651 | 0.000000 | 662828064 | 40387588 | 0.000000
10-04-2025 1:55:00000 | -2358718 | 23.5872 | 40577769 | 235289.05 | 58785110 | 98552284 | 49950108 | 0.000000 | 668532654 | 40719082 | 0.000000
10-04-2025 1:55:05000 | -2363634 | 23.6363 | 40440088 | 235241.52 | 58896641 | 98567734 | 49953518 | 0.000000 | 674149597 | 41046094 | 0.000000
10-04-2025 1:55:10000 | -2659065 | 26.5907 | 38266841 | 235073.22 | 66023300 | 98980293 | 49885212 | 0.000000 | 679468201 | 41398350 | 0.000000
10-04-2025 1:55:15000 | -2774702 | 27.747 | 43463633 | 235224.03 | 68979576 | 98795280 | 49860897 | 0.000000 | 685229553 | 41780347 | 0.000000
10-04-2025 1:55:20000 | -2577658 | 25.7766 | 42951660 | 235289.41 | 64165779 | 98639969 | 49896992 | 0.000000 | 691264404 | 42151143 | 0.000000
10-04-2025 1:55:25000 | -2504367 | 25.0437 | 39133950 | 235187.08 | 62265881 | 98801010 | 49899982 | 0.000000 | 696804077 | 42502876 | 0.000000
10-04-2025 1:55:30000 | -2452478 | 24.5248 | 38377085 | 235167.61 | 60989433 | 98797691 | 49906902 | 0.000000 | 702291626 | 42843037 | 0.000000
10-04-2025 1:55:35000 | -2478977 | 24.7898 | 39450200 | 235187.83 | 61665882 | 98757294 | 49889801 | 0.000000 | 707623779 | 43186030 | 0.000000
10-04-2025 1:55:40000 | -2538801 | 25.388 | 37857207 | 235120.92 | 63079334 | 98906448 | 49879890 | 0.000000 | 712907227 | 43537061 | 0.000000
10-04-2025 1:55:45000 | -2531628 | 25.3163 | 38026313 | 235162.13 | 62904251 | 98890663 | 49876537 | 0.000000 | 718062317 | 43895645 | 0.000000
10-04-2025 1:55:50000 | -2413021 | 24.1302 | 36454480 | 235179.84 | 59961002 | 98877998 | 49902683 | 0.000000 | 723197021 | 44235557 | 0.000000
10-04-2025 1:55:55000 | -2265049 | 22.6505 | 35029312 | 235135.75 | 56326744 | 98825180 | 49932693 | 0.000000 | 728230835 | 44556890 | 0.000000
10-04-2025 1:56:00000 | -2146900 | 21.469 | 37968352 | 235257.16 | 53567547 | 98471924 | 49958889 | 0.000000 | 733273621 | 44860962 | 0.000000
10-04-2025 1:56:05000 | -2227033 | 22.2703 | 35335396 | 235111.73 | 55426025 | 98764534 | 49951870 | 0.000000 | 738192688 | 45163882 | 0.000000
10-04-2025 1:56:10000 | -2320404 | 23.204 | 37154209 | 235159.91 | 57739010 | 98742218 | 49954025 | 0.000000 | 743242798 | 45482373 | 0.000000
10-04-2025 1:56:15000 | -2395392 | 23.9539 | 36909402 | 235104.56 | 59563690 | 98833618 | 49949848 | 0.000000 | 748496399 | 45809009 | 0.000000
10-04-2025 1:56:20000 | -2417911 | 24.1791 | 39036873 | 235194.20 | 60168770 | 98721649 | 49945713 | 0.000000 | 753804871 | 46144990 | 0.000000
10-04-2025 1:56:25000 | -2485098 | 24.851 | 37554700 | 235113.56 | 61764156 | 98877335 | 49941265 | 0.000000 | 759160461 | 46483252 | 0.000000
10-04-2025 1:56:30000 | -2460974 | 24.6097 | 39794729 | 235228.42 | 61238037 | 98717697 | 49943989 | 0.000000 | 764583557 | 46827529 | 0.000000
10-04-2025 1:56:35000 | -2473891 | 24.7389 | 40253879 | 235232.03 | 61563778 | 98701912 | 49936466 | 0.000000 | 770127502 | 47170869 | 0.000000
10-04-2025 1:56:40000 | -2530180 | 25.3018 | 40664915 | 235257.50 | 62933891 | 98732956 | 49919960 | 0.000000 | 775524597 | 47522354 | 0.000000
10-04-2025 1:56:45000 | -2584908 | 25.8491 | 39928560 | 235175.45 | 64251938 | 98827911 | 49920151 | 0.000000 | 781140930 | 47880659 | 0.000000
10-04-2025 1:56:50000 | -2541948 | 25.4195 | 37778020 | 235126.97 | 63149799 | 98913589 | 49931667 | 0.000000 | 786788940 | 48233179 | 0.000000
10-04-2025 1:56:55000 | -2389648 | 23.8965 | 42471362 | 235348.42 | 59590446 | 98457047 | 49954433 | 0.000000 | 792421387 | 48576255 | 0.000000
10-04-2025 1:57:00000 | -2302718 | 23.0272 | 40441868 | 235276.84 | 57433094 | 98492546 | 49982712 | 0.000000 | 798137207 | 48900928 | 0.000000
10-04-2025 1:57:05000 | -2382554 | 23.8255 | 37948730 | 235133.84 | 59286224 | 98755173 | 49972179 | 0.000000 | 803734131 | 49222212 | 0.000000
10-04-2025 1:57:10000 | -2517323 | 25.1732 | 39530081 | 235173.81 | 62628765 | 98789391 | 49940731 | 0.000000 | 809334167 | 49561885 | 0.000000
10-04-2025 1:57:15000 | -2567204 | 25.672 | 41773496 | 235252.94 | 63870701 | 98701836 | 49923908 | 0.000000 | 815024353 | 49918730 | 0.000000
10-04-2025 1:57:20000 | -2463674 | 24.6367 | 42137881 | 235302.88 | 61373756 | 98568649 | 49949020 | 0.000000 | 820880493 | 50267559 | 0.000000
10-04-2025 1:57:25000 | -2255613 | 22.5561 | 41658589 | 235320.89 | 56333649 | 98336937 | 49991390 | 0.000000 | 826686646 | 50593457 | 0.000000
10-04-2025 1:57:30000 | -2389554 | 23.8955 | 40353186 | 235245.06 | 59526409 | 98603882 | 49962509 | 0.000000 | 832184021 | 50917544 | 0.000000
10-04-2025 1:57:35000 | -2423669 | 24.2367 | 44498257 | 235357.94 | 60491074 | 98356026 | 49953728 | 0.000000 | 838107971 | 51256680 | 0.000000
10-04-2025 1:57:40000 | -2567660 | 25.6766 | 40946646 | 235165.31 | 63875092 | 98752205 | 49931820 | 0.000000 | 843976685 | 51604058 | 0.000000
10-04-2025 1:57:45000 | -2589088 | 25.8909 | 42710835 | 235264.45 | 64450241 | 98666489 | 49927460 | 0.000000 | 849751587 | 51967324 | 0.000000
10-04-2025 1:57:50000 | -2339295 | 23.3929 | 41098091 | 235262.95 | 58332790 | 98491554 | 49977074 | 0.000000 | 855752319 | 52303789 | 0.000000
10-04-2025 1:57:55000 | -2231808 | 22.3181 | 41016440 | 235328.33 | 55734184 | 98352837 | 49990452 | 0.000000 | 861301147 | 52620205 | 0.000000
10-04-2025 1:58:00000 | -2362151 | 23.6215 | 40539932 | 235256.00 | 58860973 | 98559036 | 49976494 | 0.000000 | 866806885 | 52939619 | 0.000000
10-04-2025 1:58:05000 | -2473545 | 24.7355 | 40293933 | 235179.31 | 61582245 | 98699020 | 49955585 | 0.000000 | 872406677 | 53275649 | 0.000000
10-04-2025 1:58:10000 | -2608431 | 26.0843 | 39838486 | 235141.36 | 64831398 | 98853699 | 49929630 | 0.000000 | 877785461 | 53630444 | 0.000000
10-04-2025 1:58:15000 | -2504957 | 25.0496 | 44586079 | 235366.69 | 62454544 | 98452621 | 49954853 | 0.000000 | 883554199 | 53990317 | 0.000000
10-04-2025 1:58:20000 | -2351931 | 23.5193 | 47135039 | 235471.17 | 58862316 | 98050331 | 49986778 | 0.000000 | 889774536 | 54325742 | 0.000000
10-04-2025 1:58:25000 | -2352260 | 23.5226 | 45514561 | 235394.78 | 58806793 | 98179001 | 49974392 | 0.000000 | 896181824 | 54650591 | 0.000000
10-04-2025 1:58:30000 | -2376838 | 23.7684 | 47541201 | 235422.73 | 59494713 | 98057716 | 49965744 | 0.000000 | 902643982 | 54982393 | 0.000000
10-04-2025 1:58:35000 | -2421561 | 24.2156 | 43953633 | 235278.13 | 60443130 | 98392334 | 49956169 | 0.000000 | 908942932 | 55315503 | 0.000000
10-04-2025 1:58:40000 | -2615065 | 26.1506 | 42723569 | 235203.00 | 65083412 | 98691566 | 49925636 | 0.000000 | 914966248 | 55666885 | 0.000000
10-04-2025 1:58:45000 | -2661151 | 26.6115 | 42792847 | 235194.77 | 66206047 | 98731621 | 49902527 | 0.000000 | 921060364 | 56033364 | 0.000000
10-04-2025 1:58:50000 | -2700098 | 27.001 | 41136104 | 235175.09 | 67097160 | 98859291 | 49884861 | 0.000000 | 926811340 | 56406431 | 0.000000
10-04-2025 1:58:55000 | -2672778 | 26.7278 | 38194341 | 235113.11 | 66350159 | 98994339 | 49874203 | 0.000000 | 932311096 | 56779751 | 0.000000
10-04-2025 1:59:00000 | -2557485 | 25.5749 | 39683950 | 235216.11 | 63573082 | 98817459 | 49892174 | 0.000000 | 937794067 | 57141772 | 0.000000
10-04-2025 1:59:05000 | -2366361 | 23.6636 | 39722058 | 235244.47 | 58933300 | 98620216 | 49923027 | 0.000000 | 943317627 | 57479370 | 0.000000
10-04-2025 1:59:10000 | -2371873 | 23.7187 | 39092971 | 235244.17 | 59049114 | 98668793 | 49918423 | 0.000000 | 948653442 | 57806763 | 0.000000
10-04-2025 1:59:15000 | -2429286 | 24.2929 | 39083328 | 235185.08 | 60448509 | 98730408 | 49892811 | 0.000000 | 954100281 | 58142095 | 0.000000
10-04-2025 1:59:20000 | -2430988 | 24.3099 | 39993044 | 235216.80 | 60528000 | 98673630 | 49904625 | 0.000000 | 959656189 | 58480298 | 0.000000
10-04-2025 1:59:25000 | -2472068 | 24.7207 | 38791768 | 235155.97 | 61484444 | 98791084 | 49890511 | 0.000000 | 965032471 | 58821753 | 0.000000
10-04-2025 1:59:30000 | -2530597 | 25.306 | 40928096 | 235246.19 | 62958870 | 98717232 | 49885811 | 0.000000 | 970460876 | 59169072 | 0.000000
10-04-2025 1:59:35000 | -2415006 | 24.1501 | 43960830 | 235329.67 | 60268543 | 98383286 | 49914543 | 0.000000 | 976626221 | 59512617 | 0.000000
10-04-2025 1:59:40000 | -2238776 | 22.3878 | 41556982 | 235313.59 | 55921619 | 98320473 | 49951073 | 0.000000 | 982526794 | 59831680 | 0.000000
10-04-2025 1:59:45000 | -2360841 | 23.6084 | 39371641 | 235195.98 | 58800529 | 98637749 | 49931614 | 0.000000 | 988013000 | 60151826 | 0.000000
10-04-2025 1:59:50000 | -2433744 | 24.3374 | 42163926 | 235266.95 | 60670410 | 98532234 | 49922550 | 0.000000 | 993677795 | 60487900 | 0.000000
10-04-2025 1:59:55000 | -2486233 | 24.8623 | 41665894 | 235254.59 | 61912567 | 98624641 | 49908951 | 0.000000 | 999357056 | 60828882 | 0.000000
10-04-2025 2:00:00000 | -2564409 | 25.6441 | 41025303 | 235196.94 | 63792999 | 98744377 | 49896183 | 0.000000 | 10052219 | 61181733 | 0.000000
10-04-2025 2:00:05000 | -2600692 | 26.0069 | 43922246 | 235276.38 | 64768486 | 98603661 | 49889832 | 0.000000 | 6001646 | 35980721 | 0.000000
10-04-2025 2:00:10000 | -2416453 | 24.1645 | 44751558 | 235339.72 | 60347500 | 98328026 | 49936157 | 0.000000 | 12448669 | 70630676 | 0.000000
10-04-2025 2:00:15000 | -2334647 | 23.3465 | 46599126 | 235471.47 | 58421387 | 98065636 | 49939312 | 0.000000 | 18662985 | 103263168 | 0.000000
10-04-2025 2:00:20000 | -2428141 | 24.2814 | 45630054 | 235344.81 | 60658829 | 98279701 | 49912418 | 0.000000 | 25153849 | 136240112 | 0.000000
10-04-2025 2:00:25000 | -2504786 | 25.0479 | 44059316 | 235282.13 | 62452446 | 98487946 | 49904934 | 0.000000 | 31370792 | 170775543 | 0.000000
10-04-2025 2:00:30000 | -2493564 | 24.9356 | 44504297 | 235308.20 | 62194004 | 98444374 | 49904343 | 0.000000 | 37397633 | 205423798 | 0.000000
10-04-2025 2:00:35000 | -2458095 | 24.581 | 44489375 | 235310.34 | 61340374 | 98401283 | 49922684 | 0.000000 | 43563553 | 239984085 | 0.000000
10-04-2025 2:00:40000 | -2244566 | 22.4457 | 44707363 | 235422.14 | 56168240 | 98073494 | 49958710 | 0.000000 | 49734478 | 272441956 | 0.000000
10-04-2025 2:00:45000 | -2281021 | 22.8102 | 43689854 | 235346.09 | 57019974 | 98214668 | 49955753 | 0.000000 | 55883083 | 303651337 | 0.000000
10-04-2025 2:00:50000 | -2321477 | 23.2148 | 49463398 | 235455.45 | 58275669 | 97804565 | 49973480 | 0.000000 | 62581123 | 335633301 | 0.000000
10-04-2025 2:00:55000 | -2464790 | 24.6479 | 46976211 | 235335.91 | 61605335 | 98231819 | 49933105 | 0.000000 | 69123573 | 368946899 | 0.000000
10-04-2025 2:01:00000 | -2555839 | 25.5584 | 47348882 | 235336.72 | 63816376 | 98326927 | 49911449 | 0.000000 | 75758575 | 404049927 | 0.000000
10-04-2025 2:01:05000 | -2548761 | 25.4876 | 48748398 | 235448.81 | 63678154 | 98219620 | 49932320 | 0.000000 | 82452217 | 439711151 | 0.000000
10-04-2025 2:01:10000 | -2417181 | 24.1718 | 49113213 | 235469.34 | 60522495 | 97997604 | 49957417 | 0.000000 | 89346222 | 473923218 | 0.000000
10-04-2025 2:01:15000 | -2351918 | 23.5192 | 49061050 | 235472.91 | 58955090 | 97892822 | 49965633 | 0.000000 | 96169052 | 506816833 | 0.000000
10-04-2025 2:01:20000 | -2378298 | 23.783 | 50122280 | 235478.97 | 59642708 | 97850594 | 49949242 | 0.000000 | 103050316 | 539631470 | 0.000000
10-04-2025 2:01:25000 | -2476024 | 24.7602 | 49009258 | 235402.22 | 61949860 | 98096825 | 49936600 | 0.000000 | 109941277 | 573177734 | 0.000000
10-04-2025 2:01:30000 | -2526123 | 25.2612 | 50227744 | 235464.30 | 63193481 | 98080009 | 49922352 | 0.000000 | 116791573 | 608289490 | 0.000000
10-04-2025 2:01:35000 | -2558330 | 25.5833 | 49658774 | 235435.64 | 63947338 | 98167755 | 49918571 | 0.000000 | 123777771 | 643696777 | 0.000000
10-04-2025 2:01:40000 | -2552420 | 25.5242 | 50709868 | 235476.53 | 63847317 | 98083008 | 49933922 | 0.000000 | 130771423 | 679223511 | 0.000000
10-04-2025 2:01:45000 | -2487496 | 24.875 | 49989507 | 235443.77 | 62260372 | 98039864 | 49940849 | 0.000000 | 137738663 | 714027710 | 0.000000
10-04-2025 2:01:50000 | -2375411 | 23.7541 | 51333564 | 235534.30 | 59615463 | 97743683 | 49960129 | 0.000000 | 144827621 | 747600708 | 0.000000
10-04-2025 2:01:55000 | -2395766 | 23.9577 | 46910313 | 235383.41 | 59927219 | 98136436 | 49947346 | 0.000000 | 151612961 | 780476257 | 0.000000
10-04-2025 2:02:00000 | -2414029 | 24.1403 | 50208711 | 235489.47 | 60499550 | 97904800 | 49951191 | 0.000000 | 158481155 | 813905640 | 0.000000
10-04-2025 2:02:05000 | -2181494 | 21.8149 | 56050610 | 235740.63 | 55212418 | 96854103 | 50010460 | 0.000000 | 165937241 | 845753662 | 0.000000
10-04-2025 2:02:10000 | -1992964 | 19.9296 | 54244014 | 235679.42 | 50653675 | 96489830 | 50054146 | 0.000000 | 173573730 | 874247620 | 0.000000
10-04-2025 2:02:15000 | -1956974 | 19.5697 | 56899629 | 235728.47 | 49968369 | 96023544 | 50058491 | 0.000000 | 181268326 | 901635254 | 0.000000
10-04-2025 2:02:20000 | -2040172 | 20.4017 | 57783438 | 235694.48 | 51993797 | 96215324 | 50055805 | 0.000000 | 189228455 | 929302673 | 0.000000
10-04-2025 2:02:25000 | -2328291 | 23.2829 | 57117578 | 235576.19 | 58803356 | 97120262 | 50007568 | 0.000000 | 197182495 | 959980164 | 0.000000
10-04-2025 2:02:30000 | -2592403 | 25.924 | 60960049 | 235685.89 | 65279778 | 97344872 | 49962566 | 0.000000 | 205246017 | 994844910 | 0.000000
10-04-2025 2:02:35000 | -2694404 | 26.944 | 61062466 | 235637.56 | 67733902 | 97526878 | 49942188 | 0.000000 | 213842606 | 10319080 | 0.000000
10-04-2025 2:02:40000 | -2549171 | 25.4917 | 60054106 | 235693.47 | 64196205 | 97335449 | 49968723 | 0.000000 | 222300827 | 10684498 | 0.000000
10-04-2025 2:02:45000 | -2362961 | 23.6296 | 57093560 | 235664.30 | 59600887 | 97202911 | 50000496 | 0.000000 | 230404785 | 11021938 | 0.000000
10-04-2025 2:02:50000 | -2239919 | 22.3992 | 55390547 | 235656.78 | 56588974 | 97075874 | 50021671 | 0.000000 | 238244476 | 11337853 | 0.000000
10-04-2025 2:02:55000 | -2220870 | 22.2087 | 54953506 | 235642.64 | 56098728 | 97072411 | 50029682 | 0.000000 | 245767426 | 11645870 | 0.000000
10-04-2025 2:03:00000 | -2468758 | 24.6876 | 54458032 | 235520.16 | 62017971 | 97652367 | 49982697 | 0.000000 | 253273682 | 11974478 | 0.000000
10-04-2025 2:03:05000 | -2785088 | 27.8509 | 51918203 | 235360.95 | 69541367 | 98306488 | 49919418 | 0.000000 | 260680176 | 12342869 | 0.000000
10-04-2025 2:03:10000 | -2924105 | 29.2411 | 54046606 | 235417.80 | 72969124 | 98334427 | 49885796 | 0.000000 | 267960938 | 12744387 | 0.000000
10-04-2025 2:03:15000 | -3004922 | 30.0492 | 51216411 | 235381.88 | 74806282 | 98578384 | 49866852 | 0.000000 | 275214600 | 13159358 | 0.000000
10-04-2025 2:03:20000 | -2854168 | 28.5417 | 50590923 | 235439.41 | 71122520 | 98465149 | 49891026 | 0.000000 | 282284790 | 13569395 | 0.000000
10-04-2025 2:03:25000 | -2618568 | 26.1857 | 47390864 | 235429.98 | 65302933 | 98401474 | 49926392 | 0.000000 | 288992157 | 13945944 | 0.000000
10-04-2025 2:03:30000 | -2414253 | 24.1425 | 46886675 | 235454.77 | 60348423 | 98165886 | 49950546 | 0.000000 | 295552155 | 14292191 | 0.000000
10-04-2025 2:03:35000 | -2491546 | 24.9155 | 44126069 | 235297.50 | 62137871 | 98467674 | 49918167 | 0.000000 | 301841553 | 14632562 | 0.000000
10-04-2025 2:03:40000 | -2579782 | 25.7978 | 46392319 | 235329.83 | 64353340 | 98421242 | 49906872 | 0.000000 | 308312134 | 14985238 | 0.000000
10-04-2025 2:03:45000 | -2544039 | 25.4404 | 47738286 | 235385.45 | 63531017 | 98284592 | 49914707 | 0.000000 | 314949188 | 15342638 | 0.000000
10-04-2025 2:03:50000 | -2511659 | 25.1166 | 45050908 | 235329.27 | 62653770 | 98429176 | 49907982 | 0.000000 | 321360565 | 15689238 | 0.000000
10-04-2025 2:03:55000 | -2564404 | 25.644 | 49382783 | 235455.94 | 64079536 | 98195862 | 49896641 | 0.000000 | 327947754 | 16045082 | 0.000000
10-04-2025 2:04:00000 | -2422654 | 24.2265 | 50274063 | 235518.56 | 60700680 | 97913979 | 49933495 | 0.000000 | 334845734 | 16391484 | 0.000000
10-04-2025 2:04:05000 | -2338843 | 23.3884 | 45566470 | 235383.38 | 58505722 | 98154533 | 49951706 | 0.000000 | 341424286 | 16719574 | 0.000000
10-04-2025 2:04:10000 | -2352069 | 23.5207 | 42671167 | 235268.64 | 58710258 | 98393883 | 49936222 | 0.000000 | 347615570 | 17044194 | 0.000000
10-04-2025 2:04:15000 | -2361454 | 23.6145 | 49124551 | 235484.66 | 59186626 | 97904030 | 49934254 | 0.000000 | 354001831 | 17373945 | 0.000000
10-04-2025 2:04:20000 | -2316306 | 23.1631 | 45767192 | 235375.08 | 57968288 | 98103325 | 49954552 | 0.000000 | 360619537 | 17694844 | 0.000000
10-04-2025 2:04:25000 | -2433941 | 24.3394 | 47359824 | 235371.81 | 60869923 | 98159027 | 49932835 | 0.000000 | 367129150 | 18026793 | 0.000000
10-04-2025 2:04:30000 | -2328763 | 23.2876 | 53090054 | 235583.86 | 58580673 | 97498459 | 49959549 | 0.000000 | 374232941 | 18356942 | 0.000000
10-04-2025 2:04:35000 | -2306769 | 23.0677 | 48444590 | 235423.41 | 57855774 | 97865143 | 49954746 | 0.000000 | 381265533 | 18678804 | 0.000000
10-04-2025 2:04:40000 | -2329140 | 23.2914 | 51084707 | 235521.38 | 58515572 | 97678192 | 49957539 | 0.000000 | 388074127 | 19001801 | 0.000000
10-04-2025 2:04:45000 | -2423117 | 24.2312 | 49112578 | 235435.28 | 60683132 | 98007164 | 49949615 | 0.000000 | 394911713 | 19330397 | 0.000000
10-04-2025 2:04:50000 | -2324958 | 23.2496 | 50721777 | 235492.19 | 58393093 | 97701981 | 49971512 | 0.000000 | 402041687 | 19656549 | 0.000000
10-04-2025 2:04:55000 | -2353238 | 23.5324 | 50317510 | 235475.39 | 59051666 | 97789513 | 49956203 | 0.000000 | 409014099 | 19981559 | 0.000000
10-04-2025 2:05:00000 | -2497804 | 24.978 | 50123877 | 235399.28 | 62528801 | 98045380 | 49924809 | 0.000000 | 416024353 | 20317000 | 0.000000
10-04-2025 2:05:05000 | -2636109 | 26.3611 | 53070693 | 235480.69 | 65975426 | 98033066 | 49909424 | 0.000000 | 423338226 | 20674885 | 0.000000
10-04-2025 2:05:10000 | -2484855 | 24.8485 | 52856362 | 235517.45 | 62325005 | 97811623 | 49924591 | 0.000000 | 430842407 | 21030620 | 0.000000
10-04-2025 2:05:15000 | -2388191 | 23.8819 | 51379385 | 235521.69 | 59937378 | 97763107 | 49944416 | 0.000000 | 438069977 | 21366956 | 0.000000
10-04-2025 2:05:20000 | -2283799 | 22.838 | 52185176 | 235587.45 | 57471882 | 97487328 | 49975483 | 0.000000 | 445266327 | 21688674 | 0.000000
10-04-2025 2:05:25000 | -2223754 | 22.2375 | 52740645 | 235598.30 | 56053089 | 97300880 | 49990147 | 0.000000 | 452525482 | 22001519 | 0.000000
10-04-2025 2:05:30000 | -2339897 | 23.399 | 54035210 | 235591.84 | 58903606 | 97435692 | 49975327 | 0.000000 | 459826019 | 22321709 | 0.000000
10-04-2025 2:05:35000 | -2479152 | 24.7915 | 54427065 | 235548.42 | 62257877 | 97673889 | 49954422 | 0.000000 | 467211029 | 22662036 | 0.000000
10-04-2025 2:05:40000 | -2507330 | 25.0733 | 52140742 | 235494.69 | 62838943 | 97905464 | 49949833 | 0.000000 | 474562592 | 23011509 | 0.000000
10-04-2025 2:05:45000 | -2563085 | 25.6308 | 53174463 | 235535.77 | 64214287 | 97915031 | 49941174 | 0.000000 | 481738129 | 23366843 | 0.000000
10-04-2025 2:05:50000 | -2566737 | 25.6674 | 54562568 | 235550.69 | 64364212 | 97814384 | 49953667 | 0.000000 | 489318695 | 23725188 | 0.000000
10-04-2025 2:05:55000 | -2473052 | 24.7305 | 54175605 | 235591.80 | 62087696 | 97683601 | 49967617 | 0.000000 | 496966492 | 24074199 | 0.000000
10-04-2025 2:06:00000 | -2361746 | 23.6175 | 56334854 | 235697.84 | 59525612 | 97271072 | 49986050 | 0.000000 | 504573212 | 24408127 | 0.000000
10-04-2025 2:06:05000 | -2526393 | 25.2639 | 51610269 | 235440.94 | 63279976 | 97976509 | 49944054 | 0.000000 | 511950500 | 24746428 | 0.000000
10-04-2025 2:06:10000 | -2657457 | 26.5746 | 54978076 | 235544.97 | 66560356 | 97926323 | 49913502 | 0.000000 | 519380005 | 25112100 | 0.000000
10-04-2025 2:06:15000 | -2612350 | 26.1235 | 54609561 | 235529.67 | 65467705 | 97884132 | 49925617 | 0.000000 | 527014832 | 25480305 | 0.000000
10-04-2025 2:06:20000 | -2510549 | 25.1055 | 45903999 | 235300.11 | 62672966 | 98369171 | 49922695 | 0.000000 | 533999695 | 25834260 | 0.000000
10-04-2025 2:06:25000 | -2552960 | 25.5296 | 33749043 | 234967.70 | 63327190 | 99137505 | 49914120 | 0.000000 | 539314758 | 26186709 | 0.000000
10-04-2025 2:06:30000 | -2436653 | 24.3665 | 38111604 | 235168.67 | 60592426 | 98798798 | 49937984 | 0.000000 | 544455017 | 26532937 | 0.000000
10-04-2025 2:06:35000 | -2349971 | 23.4997 | 38136824 | 235204.14 | 58495174 | 98708611 | 49958317 | 0.000000 | 549858093 | 26861665 | 0.000000
10-04-2025 2:06:40000 | -2338625 | 23.3863 | 36961738 | 235157.88 | 58187160 | 98773949 | 49951775 | 0.000000 | 555110779 | 27183235 | 0.000000

## FLUJO
Prueba | Hora | Totalizador flujo diesel (lt) | lt/min
Pmax | 13:00 | 17827780 | 712
Pmax | 14:00 | 17870314 | 708
Pmax | 15:00 | 17913176 | 716
Pmax | 16:00 | 17954980 | 704
Pmax | 17:00 | 17996990 | 691
CEN E1 | 17:30 | 18017986 | 706
CEN E1 | 17:40 | 18025014 | 698
CEN E1 | 17:50 | 18032042 | 704
Pmax/CEN E1 | 18:00 | 18039068 | 708 | 42240
CEN E2 | 18:45 | 18069046 | 651
CEN E2 | 18:55 | 18075644 | 661
CEN E2 | 19:05 | 18082224 | 655 | 39390
CEN E2 | 19:15 | 18088880 | 659
CEN E3 | 20:00 | 18114980 | 578
CEN E3 | 20:10 | 18120606 | 552
CEN E3 | 20:20 | 18126228 | 565 | 34050
CEN E3 | 20:30 | 18131828 | 575
CEN E4 | 21:15 | 18153980 | 478
CEN E4 | 21:25 | 18158736 | 483
CEN E4 | 21:35 | 18163488 | 478
CEN E4 | 21:45 | 18168240 | 484 | 28900
CEN E5 | 22:30 | 18186230 | 385
CEN E5 | 22:40 | 18190106 | 394
CEN E5 | 22:50 | 18193978 | 377 | 23265
CEN E5 | 23:00 | 18197852 | 395
CEN E6 | 23:45 | 18212902 | 305
CEN E6 | 23:55 | 18216038 | 312
CEN E6 | 0:05 | 18219188 | 314 | 18825
CEN E6 | 0:15 | 18222342 | 324
CEN E7 | 1:00 | 18233634 | 249
CEN E7 | 1:10 | 18236080 | 244
CEN E7 | 1:20 | 18238526 | 247 | 14760
CEN E7 | 1:30 | 18240982 | 244
CEN E8 (25 MW) | 1:35 | 18242166 | 205
CEN E8 (25 MW) | 1:45 | 18244424 | 228
CEN E8 (25 MW) | 1:55 | 18246682 | 228
CEN E8 (25 MW) | 2:05 | 18248944 | 225

## Comparation 2025 - 2019
|  | kJ to kCal | 4.184 | kJ/kCal
2019 |  | Consumo Esp. Corregido (kJ/kWh) | Consumo Esp. Corregido (kCal/kWh) | Potencia Bruta Corregida (kW) | Potencia Neta Corregida (kW)
|  | 11964 | 2859.4646 | 129918 | 128697
|  | 12037 | 2876.912 | 115791 | 114795
|  | 12328 | 2946.4627 | 98720 | 97817
|  | 12505 | 2988.7667 | 82566 | 81721
|  | 13566 | 3242.3518 | 64152 | 63363
|  | 15351 | 3668.9771 | 56798 | 46154
|  | 19240 | 4598.4704 | 29864 | 29361
2025 | Escalón | Consumo Esp. Corregido (kJ/kWh) | Consumo Esp. Corregido (kCal/kWh) | Potencia Bruta Corregida (kW) | Potencia Neta Corregida (kW)
| 136 | 12158.704 | 2906 | 129048 | 127837
| 126 | 12104.312 | 2893 | 124288 | 123151
| 107 | 12807.224 | 3061 | 104184 | 103215
| 88 | 12698.44 | 3035 | 86651 | 85789
| 68 | 13288.384 | 3176 | 67737 | 66953
| 49 | 14999.64 | 3585 | 48920 | 48214
| 30 | 19154.352 | 4578 | 29984 | 29455